## Executive Summary
Executive Summary: DISIS-2017-001 Phase One
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on March 31, 2017. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 1.2 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2017-001 Phase 1 includes study requests in the following cluster groups: 01 - Woodward, 02 - Hitchland, 03 - Spearville, 04 - Northwest Kansas, 06 - South Texas Panhandle/New Mexico, 07 - Southwestern Oklahoma, 08 - North Oklahoma/South Central Kansas, 09 - Nebraska, 10 - Southeast Oklahoma/Northeast Texas, 12 - Northwest Arkansas, 13 - Northeast Kansas/Northwest Missouri, 14 - South Central Oklahoma, 15 - Eastern South Dakota, 16 - Western North Dakota, 17 - Western South Dakota, 18 - Eastern North Dakota NOTE: per SPP Tariff Attachment V; section 8.4.2 DISIS Phase One will consist of a power flow analysis and calculation of the short-circuit ratio. The Short Circuit Ratio tab has been added to the workbook and will be added to the DISIS Manual.
DISIS Manual Version 1.2
http://opsportal.spp.org/documents/studies/DISIS_Manual.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
14472
The minimum cost of interconnecting all requests included in this DISIS is estimated at:
8532555217.574
Models Used in Study
2019 ITP Series
Winter: 2019, 2024
Summer: 2020, 2024, 2029
Light: 2024 & Spring: 2020
By: SPP Generator Interconnection Department
Published: October 29, 2020
Phase One Disclaimer: Alternate solutions provided by Transmission Owners will be considered during Phase 2 of the DISIS.

## Revision History
Revision History
Date | Author | Change Description
4413300% | SPP | Phase 1 Posting

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Service | Area | POI | Status
ASGI-2016-001 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 2.5 | 0 | ER | SPS | Wolfforth 115kV | DISIS STAGE
ASGI-2017-007 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 4.2 | 0 | ER/NR | SPS | SPS Erskine 115kV | DISIS STAGE
GEN-2016-005 | 03 - Spearville | 18 | DIS-17-1 | Wind | 150 | 0 | ER/NR | SUNC | Clark-Thistle 345kV | DISIS STAGE
GEN-2016-034 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 90 | 0 | ER | WAPA | Laramie River Station (GEN-2016-023 Tap)-Sidney 345kV | DISIS STAGE
GEN-2016-037 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | AEPW | Chisholm-Gracemont 345kV | DISIS STAGE
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 112 | 0 | ER | SPS | Swisher 115kV | DISIS STAGE
GEN-2016-049 | 03 - Spearville | 18 | DIS-17-1 | Wind | 310.2 | 55.8 | ER | SUNC | Post Rock - Spearville 345kV | DISIS STAGE
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 300 | 0 | ER | OKGE | Renfrow 345kV | DISIS STAGE
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 54 | 0 | ER/NR | SPS | Lakeview-Brownfield 69kV line | DISIS STAGE
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 108 | 0 | ER/NR | SPS | Bailey County 115kV | DISIS STAGE
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 100 | 0 | ER/NR | SPS | Yoakum-Seagraves 115kV circuit | DISIS STAGE
GEN-2016-093 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 70 | 0 | ER | NPPD | Bobcat 115kV | DISIS STAGE
GEN-2016-103 | 15 - Eastern South Dakota | 18 | DIS-17-1 | Wind | 250.7 | 0 | ER/NR | WAPA | Fort Thompson-Leland Olds 345kV | DISIS STAGE
GEN-2016-107 | 01 - Woodward | 18 | DIS-17-1 | Wind | 141.75 | 0 | ER/NR | WFEC | Okeene-Cederdale 138kV Line | DISIS STAGE
GEN-2016-109 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 102 | 0 | ER/NR | NPPD | Fairbury 115kV | DISIS STAGE
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER/NR | AEPW | Shidler 138kV | DISIS STAGE
GEN-2016-159 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 427.8 | 0 | ER/NR | NPPD | Turtle Creek 345kV | DISIS STAGE
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 64 | 0 | ER | SPS | Hobbs-Yoakum 230kV | DISIS STAGE
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 231 | 0 | ER | SPS | Newhart 115kV | DISIS STAGE
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 42 | 0 | ER/NR | WERE | Creswell 69kV Sub | DISIS STAGE
GEN-2017-001 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 250 | 0 | ER/NR | NPPD | Sweetwater 345kV | DISIS STAGE
GEN-2017-004 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 201.6 | 0 | ER/NR | SUNC | Elm Creek - Summit 345kV | DISIS STAGE
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 195 | 0 | ER | WERE | Marmaton - Litchfield 161kV | DISIS STAGE
GEN-2017-006 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 73.6 | 0 | ER | NPPD | Moore (GEN-2015-088 Tap)-Pauline 345kV | DISIS STAGE
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 297.5 | 0 | ER | SPS | Pleasant Hill 230kV sub | DISIS STAGE
GEN-2017-008 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 305 | 23 | ER | NPPD | Moore (GEN-2016-096 Tap)-Pauline 345kV | DISIS STAGE
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 302.5 | 0 | ER | WERE | Neosho - Caney River 345kV | DISIS STAGE
GEN-2017-010 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER | WAPA | Rhame 230kV Sub | DISIS STAGE
GEN-2017-011 | 01 - Woodward | 18 | DIS-17-1 | Solar | 151.8 | 0 | ER/NR | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | DISIS STAGE
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 201.6 | 0 | ER/NR | SPS | Newhart-Potter County 230kV | DISIS STAGE
GEN-2017-013 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SUNC | Mingo 345kV | DISIS STAGE
GEN-2017-014 | 17 - Western South Dakota | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | WAPA | Underwood - Philip Tap 230kV | DISIS STAGE
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 33 | 0 | ER/NR | SPS | Norton 115kV Switching Station | DISIS STAGE
GEN-2017-018 | 03 - Spearville | 18 | DIS-17-1 | Solar | 190 | 21.5 | ER/NR | SUNC | Thistle 345kV sub | DISIS STAGE
GEN-2017-021 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SUNC | Post Rock - Spearville 345kV | DISIS STAGE
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 65 | 0 | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-023 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 85 | 0 | ER/NR | WFEC | Hugo Power Plant 138kV Sub | DISIS STAGE
GEN-2017-024 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 50 | 0 | ER/NR | WFEC | Frogville 138kV sub | DISIS STAGE
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 235 | 8 | ER/NR | SPS | Tolk 230kV | DISIS STAGE
GEN-2017-027 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Wind | 140 | 0 | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | DISIS STAGE
GEN-2017-028 | 01 - Woodward | 18 | DIS-17-1 | Solar | 50 | 0 | ER/NR | OKGE | El Reno SW 138kV switch station | DISIS STAGE
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | DISIS STAGE
GEN-2017-031 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 100 | 0 | ER | NPPD | Wildhorse - Covalt 115kV | DISIS STAGE
GEN-2017-032 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SPS | Finney - Lamar 345kV | DISIS STAGE
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | AEPW | Oklaunion 345kV sub | DISIS STAGE
GEN-2017-036 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 100 | 0 | ER/NR | WFEC | Snyder 138kV | DISIS STAGE
GEN-2017-037 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 20 | 0 | ER | NPPD | Bobcat 115kV | DISIS STAGE
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | DISIS STAGE
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER | SPS | Needmore 230kV sub | DISIS STAGE
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 200.1 | 0 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | DISIS STAGE
GEN-2017-047 | 02 - Hitchland | 18 | DIS-17-1 | Wind | 102 | 0 | ER/NR | SPS | Cole 115kV | DISIS STAGE
GEN-2017-048 | 16 - Western North Dakota | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | WAPA | Neset 230kV | DISIS STAGE
GEN-2017-049 | 03 - Spearville | 18 | DIS-17-1 | Solar | 50 | 0 | ER | MIDW | Tap Pawnee Valley - Hanston 69kV | DISIS STAGE
GEN-2017-050 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Solar | 25 | 0.6 | ER | WERE | Tap Neosho â€“ Crawford 69kV | DISIS STAGE
GEN-2017-051 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 30 | 2.6 | ER | OMPA | Tap Lake Creek SW - Russell SW 69kV | DISIS STAGE
GEN-2017-052 | 03 - Spearville | 18 | DIS-17-1 | Solar | 25 | 0 | ER | SUNC | Tap Bear Creek-Johnson Corner 115kV | DISIS STAGE
GEN-2017-053 | 07 - Southwestern Oklahoma | 18 | DIS-17-1 | Solar | 50 | 8.9 | ER | WFEC | Tap Hollister SW - PSO Walters 69kV | DISIS STAGE
GEN-2017-055 | 09 - Nebraska | 18 | DIS-17-1 | Solar | 228.25 | 0 | ER/NR | LES | Wagener 115kV Sub | DISIS STAGE
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas | 18 | DIS-17-1 | Solar | 72.5 | 0 | ER/NR | AEPW | Hosston 69kV | DISIS STAGE
GEN-2017-058 | 02 - Hitchland | 18 | DIS-17-1 | Solar | 135 | 27 | ER | SPS | Hereford Northeast 115kV | DISIS STAGE
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 90 | 0 | ER/NR | SPS | TUCO 230kV | DISIS STAGE
GEN-2017-060 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 149.4 | 29.9 | ER | EMDE | LaRussell Energy Center 161kV | DISIS STAGE
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 101.5 | 0 | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | DISIS STAGE
GEN-2017-064 | 17 - Western South Dakota | 18 | DIS-17-1 | Solar | 110 | 0 | ER/NR | WAPA | Underwood - Wayside 230kV | DISIS STAGE
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 200.25 | 0 | ER/NR | AEPW | Oklaunion 345kV sub | DISIS STAGE
GEN-2017-066 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 150.75 | 0 | ER/NR | WFEC | Oney 138kV Sub | DISIS STAGE
GEN-2017-067 | 01 - Woodward | 18 | DIS-17-1 | Solar | 200.25 | 0 | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 103.5 | 0 | ER/NR | WERE | Wichita 345kV | DISIS STAGE
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 3.6 | 0 | ER/NR | SPS | Norton 115kV Switching Station | DISIS STAGE
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | 0 | ER/NR | OKGE | Greenwood 138kV sub | DISIS STAGE
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 52.2 | 0 | ER/NR | OKGE | Greenwood 138kV sub | DISIS STAGE
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | 0 | ER/NR | GRDA | Dry Gulch 161kV sub | DISIS STAGE
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 72.5 | 0 | ER/NR | AEPW | Pryor Junction 138kV sub | DISIS STAGE
GEN-2017-075 | 14 - South Central Oklahoma | 18 | DIS-17-1 | Solar | 200 | 0 | ER/NR | OKGE | Hugo-Sunnyside 345kV | DISIS STAGE
GEN-2017-076 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Solar | 52.2 | 0 | ER/NR | AEPW | Chamber Springs 161kV sub | DISIS STAGE
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 124.7 | 0 | ER/NR | AEPW | Explorer Claremore Tap EXCLART4 | DISIS STAGE
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Wind | 300 | 0 | ER/NR | SPS | Eddy County-Tolk (Crossroads) 345kV | DISIS STAGE
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 49.88 | 0 | ER | SPS | Hart Industrial 115kV sub | DISIS STAGE
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 525 | 0 | ER | SPS | Tolk 230kV | DISIS STAGE
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 300 | 0 | ER | SPS | Amarillo South-Swisher 230kV | DISIS STAGE
GEN-2017-082 | 12 - Northwest Arkansas | 18 | DIS-17-1 | Wind | 149.4 | 28.8 | ER | EMDE | Asbury Plant 161kV | DISIS STAGE
GEN-2017-083 | 04 - Northwest Kansas | 18 | DIS-17-1 | Wind | 100 | 0 | ER/NR | SUNC | Mingo 115kV | DISIS STAGE
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 89.25 | 0 | ER | SPS | Newhart-Swisher 230kV | DISIS STAGE
GEN-2017-085 | 09 - Nebraska | 18 | DIS-17-1 | Wind | 0.6 | 0 | ER/NR | NPPD | Friend 115kV | DISIS STAGE
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Wind | 150 | 0 | ER/NR | WERE | Viola 345kV | DISIS STAGE
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 128 | 0 | ER/NR | SPS | Clovis Interchange 115kV | DISIS STAGE
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Solar | 150 | 150 | ER | KCPL | Adrian 161kV sub | DISIS STAGE
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 26.25 | 0 | ER | SPS | Lamton 115kV | DISIS STAGE
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas | 18 | DIS-17-1 | Solar | 200 | 0 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2017-094 | 15 - Eastern South Dakota | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | WAPA | Fort Thompson-Huron 230kV | DISIS STAGE
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri | 18 | DIS-17-1 | Wind | 200 | 122.7 | ER/NR | KCPL | Eastown - Iatan 345kV | DISIS STAGE
GEN-2017-097 | 17 - Western South Dakota | 18 | DIS-17-1 | Solar | 128 | 0 | ER/NR | WAPA | Underwood 115kV Sub | DISIS STAGE
GEN-2017-099 | 03 - Spearville | 18 | DIS-17-1 | Wind | 200 | 0 | ER/NR | SUNC | Post Rock - Spearville 345kV | DISIS STAGE
GEN-2017-100 | 02 - Hitchland | 18 | DIS-17-1 | Solar | 102.6 | 0 | ER/NR | SPS | Texas County 115kV | DISIS STAGE
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 18 | DIS-17-1 | Solar | 240 | 0 | ER/NR | SPS | Hobbs 230kV | DISIS STAGE
ASGI-2018-001GIA-61 | 13 - Northeast Kansas/Northwest Missouri | 17.5 | DIS-17-1-PQ | Wind | 242 |  | ER/NR | AECI | Maryville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
AshburyRetired | 08 - North Oklahoma/South Central Kansas | 17.5 | DIS-17-1-PQ | Retired Coal | 198 |  | ER | EMDE | Asbury Plant 161kV
BEPCAyrshire | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 21 |  | ER | BEPC-SPP | Ayershire 69kV
BEPCGerled | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 |  | ER | BEPC-SPP | Gerled Tap 69kV
BEPCHummel | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 |  | ER | BEPC-SPP | Hummel 69kV
BEPCNDPW0 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 7.5 |  | ER | BEPC-SPP | SW Minot 115kV
BEPCNDPW1 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 5 |  | ER | BEPC-SPP | ND Prairie Wind 115kV
J718 | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Solar | 49.98 |  | ER/NR | XEL
J748 | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 200 |  | ER/NR | MEC
NPPDSpringview | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 3 |  | ER | NPPD
SPSChanning | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Wind | 4.2 |  | ER | SPS
SPSLeaCounty | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Solar | 5.5 |  | ER | SPS
SWPANixaSolar | 12 - Northwest Arkansas | 17.5 | DIS-17-1-PQ | Solar | 7.9 |  | ER | SWPA
WAPAMPSWind | 18 - Eastern North Dakota | 17.5 | DIS-17-1-PQ | Wind | 1.5 |  | ER | WAPA
WAPATitanWind | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 25 |  | ER | WAPA
ASGI-2016-009 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 3 |  | ER | SPS | Wolfforth 12.47kV
ASGI-2016-010 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 90 |  | ER | SPS | Powell Corner 115kV
GEN-2016-036 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 44.6 |  | ER | WAPA | Granite Falls 115kV | FACILITY STUDY STAGE
GEN-2016-074 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 200 |  | ER | NPPD | Sweetwater 345kV | FACILITY STUDY STAGE
GEN-2016-087 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 98.9 |  | ER | WAPA | Bismark-Glenham 230kV line | FACILITY STUDY STAGE
GEN-2016-088 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 151.2 |  | ER/NR | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 303.6 |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-092 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 175 |  | ER | WAPA | Fort Thompson-Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-094 | 17 - Western South Dakota | 17 | DIS-16-2 | Wind | 200 |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | FACILITY STUDY STAGE
GEN-2016-095 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 200 |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | FACILITY STUDY STAGE
GEN-2016-097 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 100 |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | FACILITY STUDY STAGE
GEN-2016-100 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-101 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 195 |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-102 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 150.9 |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-106 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 400 |  | ER | NPPD | Gerald Gentleman Station 345kV | FACILITY STUDY STAGE
GEN-2016-110 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 152 |  | ER | WAPA | Laramie River-Stegall 345kV Line | FACILITY STUDY STAGE
GEN-2016-111 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | FACILITY STUDY STAGE
GEN-2016-112 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 220 |  | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | FACILITY STUDY STAGE
GEN-2016-114 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 310 |  | ER/NR | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | FACILITY STUDY STAGE
GEN-2016-115 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 300 |  | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 01 - Woodward | 17 | DIS-16-2 | Wind | 288 |  | ER | WFEC | Dover Switchyard 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 600 |  | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-121 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Solar | 110 |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-122 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 225 |  | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | FACILITY STUDY STAGE
GEN-2016-123 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 298 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-124 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 150 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-125 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 74 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 172.5 |  | ER/NR | OKGE | Arbuckle 138kV | IA PENDING
GEN-2016-128 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 176 |  | ER | OKGE | Woodring 345kV | FACILITY STUDY STAGE
GEN-2016-130 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 |  | ER | WAPA | Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-131 | 01 - Woodward | 17 | DIS-16-2 | Wind | 2.5 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 6.12 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-134 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-135 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-136 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 75 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-137 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-138 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-139 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-140 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 75 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-141 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-142 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-143 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-144 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-145 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-146 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 |  | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-147 | 09 - Nebraska | 17 | DIS-16-2 | Solar | 40 |  | ER | NPPD | Sidney 115kV Sub | FACILITY STUDY STAGE
GEN-2016-149 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-151 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 |  | ER | BEPC-SPP | Tande 345kV | IA PENDING
GEN-2016-153 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 134 |  | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2016-157 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 |  | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-158 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 |  | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-160 | 04 - Northwest Kansas | 17 | DIS-16-2 | Battery | 20 |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-161 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 3.02 |  | ER | SPS | Martin 115kV | FACILITY STUDY STAGE
GEN-2016-162 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 |  | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-163 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 |  | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-167 | 10 - Southeast Oklahoma/Northeast Texas | 17 | DIS-16-2 | Solar | 73.5 |  | ER/NR | AEPW | Lieberman - North Benton 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Gas Turbine | 17 |  | ER | SPS | XTO-Cornell 115kV station | IA PENDING
ASGI-2016-011 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 7.4 |  | ER | SWPA | Allen 138kV
ASGI-2016-012 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 61.73 |  | ER | SWPA | Tupelo 138kV
ASGI-2016-013 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 4.92 |  | ER | WFEC | Ashland 138kV
ASGI-2017-006GIA-53 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | Dis-16-2-PQ | Wind | 242 |  | ER/NR | AECI | Maryville 161kV
J302 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 101.2 |  | ER/NR | MDU | 230kV Heskett-Wishek
J476 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 246 |  | ER/NR | AMMO | Atchison County to Booneville 345kV Line Tap
J503 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 98.8 |  | ER/NR | MDU | 230kV Heskett-Wishek, 20 miles NW of Wishek
J512 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 250 |  | ER/NR | MP | Nobles - Fenton 115kV line
J541 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 400 |  | ER/NR | AMMO | Zachary-Ottumwa 345kV line
J555 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 140 |  | ER/NR | MEC
J569 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 100 |  | ER/NR | XEL | NSP Rock County
J583 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 200 |  | ER/NR | MEC | Fallow Avenue 345kV . Zip Code 50002
J587 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 200 |  | ER/NR | XEL | J460 on the Brookings-H081 345kV line
J590 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 90 |  | ER/NR | MEC | Obrien - Kossuth 345kV line
J611 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 110 |  | ER/NR | MEC | Clarinda - Merryville 161kV tap
ASGI-2016-002 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Wind | 0.35 |  | ER | SPS | SP-Yuma 115kV
ASGI-2016-003 | 13 - Northeast Kansas/Northwest Missouri | 16 | DIS-16-1 | Diesel | 12 |  | ER | KCPL | Paola 161kV
ASGI-2016-004 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Wind | 10 |  | ER | SPS | Palo Duro 115kV
GEN-2015-036 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 303.6 |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-041 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | CT | 0 |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 200 |  | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-089 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 200 |  | ER | WAPA | Utica 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 01 - Woodward | 16 | DIS-16-1 | Wind | 176 |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 01 - Woodward | 16 | DIS-16-1 | Wind | 248.4 |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | WITHDRAWN
GEN-2016-004 | 16 - Western North Dakota | 16 | DIS-16-1 | Wind | 202 |  | ER/NR | WAPA | Basin Electric 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-007 | 18 - Eastern North Dakota | 16 | DIS-16-1 | Wind | 100.05 |  | ER | WAPA | Valley City 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-009 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Steam Turbine | 29 |  | ER | OKGE | Osage 69kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-013 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-014 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Spearville | 16 | DIS-16-1 | Wind | 78.2 |  | ER | MIDW | North Kinsley 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-017 | 15 - Eastern South Dakota | 16 | DIS-16-1 | Wind | 250.24 |  | ER | WAPA | Fort Thompson-Leland Olds 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 01 - Woodward | 16 | DIS-16-1 | Wind | 150 |  | ER | WFEC | Moreland 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 09 - Nebraska | 16 | DIS-16-1 | WIND | 300 |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 151.8 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA PENDING
GEN-2016-028 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 100 |  | ER | AEPW | Clayton 138kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Solar | 100 |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 1.5 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200 |  | ER/NR | OKGE | Crescent 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 230 |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 - Spearville | 16 | DIS-16-1 | Wind | 299 |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-047 | 01 - Woodward | 16 | DIS-16-1 | CT | 24 |  | ER | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 |  | ER | NPPD | Axtell â€“ Post Rock 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-051 | 07 - Southwestern Oklahoma | 16 | DIS-16-1 | Wind | 9.8 |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250.7 |  | ER | OKGE | Sooner-Woodring 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-063 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 200 |  | ER/NR | OKGE | Hugo-Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 04 - Northwest Kansas | 16 | DIS-16-1 | Wind | 73.6 |  | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250 |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-070 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 5.3 |  | ER | SPS | Martin 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200.1 |  | ER | OKGE | Middleton Tap 138kV | IA PENDING
GEN-2016-073 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | WIND | 220 |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA PENDING
GEN-2016-075 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 50 |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
PQOKGEMustang | 01 - Woodward | 16 | DIS-16-1 | CT | 444.1 |  | ER | OKGE
G359R | 18 - Eastern North Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 |  | ER/NR | MDU | Merricourt
J432 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 98 |  | ER/NR | XEL | Brookings 345kV
J460 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | XEL | on Brookings - H081 345kV line approx. 10 miles west of proposed
J475 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | MEC
J488 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 151.8 |  | ER | OTP | 345kV at new Tap on proposed MVP Big Stone to Ellendale line
J493 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 |  | ER/NR | OTP | Big Stone - Brookings 345kV
J495 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | ALTW | Ledyard-Colby 345kV line
J498 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 |  | ER/NR | MEC | MEC 345kV Grimes-Lehigh line (18 miles south of Leigh )
J499 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 |  | ER/NR | MEC | MEC 345kV Fallow-Grimes line (18 miles east of Fallow )
J500 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 500 |  | ER/NR | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J506 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 |  | ER/NR | MEC | Raun-Lakefield Jct 345kV line tap (T-19N, R-43W)
J510 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Gas | 284.5 |  | ER/NR | OTP | Scandinavia Township 113N, Range 48W
J524 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Solar | 100 |  | ER/NR | MEC | Webster 161kV bus
J526 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 300 |  | ER/NR | OTP | Brooking County to Big Stone South 345kV line
J527 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | MEC | Booneville Cooper 345kV line
J529 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | MEC | Obrien - Kossuth 345kV line
J530 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | MEC | Montezuma - Hills 345kV Line
J534 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 |  | ER/NR | ALTW | Kossuth â€“ Webster 345kV Line
J535 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 210 |  | ER/NR | ALTW | J411 â€“ Lehigh 345kV Line
ASGI-2015-006 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Solar | 9 |  | ER | SWPA | Tupelo 138kV
GEN-2015-034 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-045 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Battery | 20 |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-046 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 300 |  | ER | WAPA | Tande 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 01 - Woodward | 15 | DIS-15-2 | Wind | 200 |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-052 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-055 | 07 - Southwestern Oklahoma | 15 | DIS-15-2 | Solar | 40 |  | ER | WFEC | Erick 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-057 | 01 - Woodward | 15 | DIS-15-2 | Wind | 100 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 4.5 |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 197.8 |  | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 202.4 |  | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 248.4 |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-069 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 |  | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200.1 |  | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 09 - Nebraska | 15 | DIS-15-2 | Wind | 300 |  | ER/NR | NPPD | Moore-Pauline 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 219.99 |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-092 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Wind | 250 |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 01 - Woodward | 15 | DIS-15-2 | Wind | 250 |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-096 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 150 |  | ER | BEPC-SPP | Brady 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  | ER/NR | BEPC-SPP | Edgeley 115kV [Pomona 115kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  | ER/NR | BEPC-SPP | Ft Thompson 69kV [Hyde 69kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | BEPC-SPP | Nelson 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002IS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 53 |  | ER/NR | WAPA | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-006IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 10 |  | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV] | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-013IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-014IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 16 |  | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2008-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 5 |  | ER/NR | WAPA | Nelson 115kV
GEN-2009-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | BEPC-SPP | Groton-Watertown 345kV
GEN-2009-018IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER | BEPC-SPP | Groton 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020AIS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | WAPA | Tripp Junction 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-026IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 110 |  | ER/NR | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2010-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 |  | ER/NR | BEPC-SPP | Bismarck-Glenham 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 34 |  | ER/NR | BEPC-SPP | Wessington Springs 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 19.5 |  | ER | WAPA | Redfield NW 115kV
GEN-2014-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 103.24 |  | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-006IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Gas | 125 |  | ER/NR | BEPC-SPP | Williston 115kV
GEN-2014-010IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | BEPC-SPP | Neset 115kV
GEN-2014-014IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | BEPC-SPP | Belfield-Rhame 230kV
J412 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | MEC | LeHigh - Raun 345kV line
J436 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER | OTP | Big Stone South - Ellendale 345kV line
J437 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 |  | ER | OTP | Big Stone South - Ellendale 345kV line
J442 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | OTP | Big Stone via a radial 230kV line
J455 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 300 |  | ER | ALTW | Kossuth â€“ Obrien 345kV line
MPC00100 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 |  | ER | OTP | Langdon 115kV
MPC00200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 60 |  | ER | OTP | Langdon 115kV
MPC00300 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  | ER | OTP | Langdon 115kV
MPC00500 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 327.8 |  | ER/NR | OTP | Maple River 230kV
MPC01200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 49.6 |  | ER | OTP | Maple River 230kV
MPC01300 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Coal | 493 |  | ER/NR | OTP | Square Butte 230kV
MPC02100 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 |  | ER | OTP | Center - Mandan 230kV
ASGI-2015-001 | 03 - Spearville | 14 | DIS-15-1 | Thermal | 6.13 |  | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-002 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 2 |  | ER | SPS | SP-Yuma 69kV
ASGI-2015-004 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Thermal | 54 |  | ER | GRDA | Coffeyville City 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 13 - Northeast Kansas/Northwest Missouri | 14 | DIS-15-1 | Wind | 200.11 |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-007 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 160 |  | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 07 - Southwestern Oklahoma | 14 | DIS-15-1 | Solar | 120 |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-014 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 150 |  | ER | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 154.58 |  | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 |  | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 - Spearville | 14 | DIS-15-1 | Solar | 20 |  | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 220 |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 219.98 |  | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-029 | 01 - Woodward | 14 | DIS-15-1 | Wind | 161 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/ON SCHEDULE
G736 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | OTP | Big Stone South 230kV
GEN-2007-017IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 166 |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 234 |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
J299 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Combined Cycle | 73 |  | ER | XEL | Wilmarth
J385 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 100 |  | ER/NR | XEL | Chisago 115kV
J400 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 62.5 |  | ER/NR | XEL | Lyon County 115kV
J405 | 16 - Western North Dakota | 13.5 | DIS-15-2-PQ | Gas | 40 |  | ER/NR | MDU | MDUs existing Lewis & Clark Jct
J407 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Glenworth 161kV
J411 | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 300 |  | ER/NR | MEC | LeHigh - Raun 345kV Line
J426 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | XEL | Chanarambie 35.4kV
ASGI-2014-014 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Thermal | 56.4 |  | ER | GRDA | Ferguson 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CT/ST | 260 |  | ER/NR | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 148.35 |  | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 01 - Woodward | 13 | DIS-14-2 | Wind | 100 |  | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 13 - Northeast Kansas/Northwest Missouri | 13 | DIS-14-2 | Wind | 300 |  | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 04 - Northwest Kansas | 13 | DIS-14-2 | Wind | 2.42 |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CC | 50 |  | ER | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 35.8 |  | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 30 |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-039 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 73.4 |  | ER/NR | NPPD | Friend 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 320 |  | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 01 - Woodward | 13 | DIS-14-2 | Wind | 250 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 14 - South Central Oklahoma | 13 | DIS-14-2 | Wind | 249.9 |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Wind | 248.4 |  | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G237 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Gas | 579.04 |  | ER | XEL | Highbridge
J285 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 250 |  | ER/NR | MEC | Proposed O'Brien County 345kV
J316 | 16 - Western North Dakota | 12.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | MDU | MDU 230kV Tatanka-Ellendale line
J320 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Wind | 55 |  | ER | XEL | Xcel's existing High Bridge 115kV
J343 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | MEC | 161kV on Creston-Clarinda line
GEN-2014-001 | 08 - North Oklahoma/South Central Kansas | 12 | DIS-14-1 | Wind | 200.6 |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 01 - Woodward | 12 | DIS-14-1 | Wind | 10.53 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 01 - Woodward | 12 | DIS-14-1 | Wind | 5.67 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 73.5 |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 36.6 |  | ER | SUNC | Garden City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Wind | 1.65 |  | ER | SPS | Clovis Intg. 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 75.6 |  | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-022 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Solar | 25 |  | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Gas | 559.4 |  | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Wind | 299 |  | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-030 | 02 - Hitchland | 11 | DIS-13-2 | Wind | 300 |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-032 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 202.5 |  | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 28.02 |  | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J274 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | MEC | Winterset. - Creston 161kV
J278 | 15 - Eastern South Dakota | 10.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | 161kV bus at the Pleasant Valley Station
J279 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Coal | 30 |  | ER/NR | MEC | Raun 345kV
J289 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 20 |  | ER/NR | MEC | 161kV sybstation on Winterset Junction to Creston 161kV Line
J290 | 16 - Western North Dakota | 10.5 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | XEL | 230kV Rugby to Glenboro
ASGI-2013-001 | 02 - Hitchland | 10 | DIS-13-1 | Wind | 11.5 |  | ER | SPS | PanTex South 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 |  | ER | SPS | FE Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-003 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 |  | ER | SPS | Clovis Intg. 115kV
GEN-2006-010 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 651 |  | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-007 | 14 - South Central Oklahoma | 10 | DIS-13-1 | Wind | 100 |  | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-008 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-011 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 30 |  | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 147 |  | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012PQ | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 1299 |  | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-016 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | CT | 203 |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J262 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | OTP | OTP Jamestown 345/115kV
J263 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | OTP | OTP Jamestown 345/115kV
ASGI-2012-002 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 18.15 |  | ER | SPS | FE-Clovis Interchange 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-020 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 478 |  | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 09 - Nebraska | 9 | DIS-12-2 | Gas | 4.8 |  | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 - Spearville | 9 | DIS-12-2 | Wind | 180 |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 07 - Southwestern Oklahoma | 9 | DIS-12-2 | Wind | 74 |  | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 299 |  | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 98.82 |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-034 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-035 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-036 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-037 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 203 |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | CT | 121.5 |  | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
H081 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 201 |  | ER | XEL | Brookings County - Lyon County 345kV
J171 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Biomass | 7 |  | ER/NR | XEL | Benson 115kV
J183 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Split Rock
J191 | 09 - Nebraska | 8.5 | DIS-15-2-PQ | Wind | 101.2 |  | ER/NR | MEC | Rolling Hills 345kV
J200 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Gas | 99 |  | ER/NR | MDU | RM Heskett Station 115kV & 41.6kV
J249 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Wind | 90 |  | ER/NR | MDU | MDU Tatanka
ASGI-2012-006 | 03 - Spearville | 8 | DIS-12-1 | Steam | 22.5 |  | ER | SUNC | ABBK 2 69kV
ASGI-2012-008 | 13 - Northeast Kansas/Northwest Missouri | 8 | PQ | Gas | 3.55 |  | ER | WERE | Sheffield 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 06 - South Texas Panhandle/New Mexico | 8 | DIS-12-1 | Wind | 61.2 |  | ER | SPS | Tap Grassland Â- Borden County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 14 - South Central Oklahoma | 8 | DIS-12-1 | Wind | 40.8 |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 - Spearville | 8 | DIS-12-1 | Gas | 120 |  | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
G735 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | ALTW | Lime Creek
G826 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Xcel Lakefield Generation SW - Lakefield Junction 345kV
G830 | 16 - Western North Dakota | 7.5 | DIS-15-2-PQ | Wind | 99 |  | ER/NR | GRE | GRE McHenry
G870 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 201 |  | ER/NR | ALTW | Hayward - Winnebago 161kV
H096 | 09 - Nebraska | 7.5 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | ALTW | Grand Junction - Perry 161kV
ASGI-2011-004 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Wind | 19.8 |  | ER | SPS | Pleasant Hill 69kV | Commerical Operation
GEN-2011-037 | 07 - Southwestern Oklahoma | 7 | DIS-11-2 | Wind | 6.6 |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 111 |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-045 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | NG CT | 205 |  | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Diesel CT | 23 |  | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-048 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | CT | 175 |  | ER/NR | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 108 |  | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 01 - Woodward | 7 | DIS-11-2 | Wind | 300 |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 |  | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056A | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 |  | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056APQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 4.5 |  | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056BPQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056PQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 |  | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | 08 - North Oklahoma/South Central Kansas | 7 | DIS-11-2 | Wind | 150 |  | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-002 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 20 |  | ER | SPS | Herring 115kV | Commerical Operation
ASGI-2011-003 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 10 |  | ER | SPS | Hendricks 69kV | Commerical Operation
GEN-2004-008 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 904.5 |  | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 08 - North Oklahoma/South Central Kansas | 6 | DIS-11-1 | Gas | 4.5 |  | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 04 - Northwest Kansas | 6 | DIS-11-1 | Wind | 201 |  | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 - Spearville | 6 | DIS-11-1 | Wind | 600 |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 01 - Woodward | 6 | DIS-11-1 | Wind | 100.8 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-011 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 50 |  | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 198 |  | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 73.6 |  | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 01 - Woodward | 6 | DIS-11-1 | Wind | 175 |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 01 - Woodward | 6 | DIS-11-1 | Wind | 165.6 |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 299 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-025 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 79.96 |  | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-027 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 120 |  | ER/NR | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-020 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 30 |  | ER | SPS | Tap LE-Tatum - LE-Crossroads 69kV | Commerical Operation
ASGI-2010-021 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 15 |  | ER | SPS | Tap LE-Saunders Tap - LE-Anderson 69kV | Commerical Operation
ASGI-2011-001 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 27.3 |  | ER | SPS | Lovington 115kV | Commerical Operation
GEN-2010-001 | 02 - Hitchland | 5 | DIS-10-2 | Wind | 300 |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 4.6 |  | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036PQ | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 1.17 |  | ER | WERE | Westar 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 01 - Woodward | 5 | DIS-10-2 | Wind | 300 |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 09 - Nebraska | 5 | DIS-10-2 | Wind | 200 |  | ER | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 46.5 |  | ER | SPS | Lovington 115kV | Commerical Operation
GEN-2008-022 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Wind | 299.65 |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | 07 - Southwestern Oklahoma | 4 | DIS-10-1 | Wind | 99 |  | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | 01 - Woodward | 4 | DIS-10-1 | Wind | 197.8 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 263.13 |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-098 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 |  | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 09 - Nebraska | 4 | DIS-10-1 | Wind | 89.66 |  | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 198.69 |  | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 48.3 |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 09 - Nebraska | 4 | DIS-10-1 | Wind | 72 |  | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 |  | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 299.2 |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-006 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 205 |  | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 - Spearville | 4 | DIS-10-1 | Wind | 165.6 |  | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 01 - Woodward | 4 | DIS-10-1 | Wind | 29.7 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 358.8 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-037N1 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 75 |  | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044N | 09 - Nebraska | 3 | DIS-09-1 | Wind | 40.5 |  | ER | NPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | 03 - Spearville | 3 | DIS-09-1 | Wind | 131.1 |  | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 07 - Southwestern Oklahoma | 3 | DIS-09-1 | Wind | 150 |  | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 02 - Hitchland | 3 | DIS-09-1 | Wind | 161 |  | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 - Spearville | 3 | DIS-09-1 | Wind | 98.9 |  | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 201 |  | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 04 - Northwest Kansas | 3 | DIS-09-1 | Wind | 200.48 |  | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 - Spearville | 3 | DIS-09-1 | Wind | 200.1 |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 13 - Northeast Kansas/Northwest Missouri | 3 | DIS-09-1 | CT | 687.1 |  | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | 08 - North Oklahoma/South Central Kansas | 3 | DIS-09-1 | Wind | 59.8 |  | ER | OKGE | TAP Deer Creek â€“ Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 01 - Woodward | 2 | ICS1 | Wind | 198.9 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 299.2 |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 01 - Woodward | 2 | ICS1 | Wind | 200 |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 01 - Woodward | 2 | ICS1 | Wind | 299.2 |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | 02 - Hitchland | 2 | ICS1 | Wind | 200 |  | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | 01 - Woodward | 2 | ICS1 | Wind | 151.8 |  | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | 07 - Southwestern Oklahoma | 2 | ICS1 | Gas | 150 |  | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 01 - Woodward | 2 | ICS1 | Wind | 424 |  | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 01 - Woodward | 2 | ICS1 | Wind | 101.2 |  | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 300 |  | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 - Spearville | 2 | ICS1 | Wind | 250 |  | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 150 |  | ER | AECI | Remington 138kV | GIA Executed
ASGI-2016-005NWE205 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | WAPA | Kimball 69kV
Coyote | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 452 |  | ER | OTP | Coyote 345kV
G034 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Biomass | 55 |  | ER/NR | XEL
G132 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 90 |  | ER/NR | MDU | Ellendale Sub 230kV
G255 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | XEL | Yankee
G261 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Combined Cycle | 677.1 |  | ER | XEL
G287 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | XEL | Nobles County
G349 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  | ER | XEL | Brookings County
G362 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | GRE | Pleasant Valley
G370 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 205 |  | ER | XEL | Anson 4
G380 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | OTP | Rugby 115kV
G389 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 200 |  | ER/NR | GRE | Elk River 230kV
G514 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | XEL | Lakefield Station via Trimont G263 Interconnect
G540 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | ALTW | Adams - Lime Creek 161kV
G548 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | ALTW | Barton 161kV
G586 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 30 |  | ER/NR | XEL | Xcel New Yankee Sub 34.5kV
G595 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | ALTW | Lime Creek 161kV
G602 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 32 |  | ER/NR | XEL | Nobles County 115kV
G604 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 44 |  | ER/NR | ALTW | Owatonna - County Line 69kV
G612 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 150 |  | ER | ALTW | ITC Midwest Fernald 115kV
G619 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 50 |  | ER/NR | OTP | GRE Tamarac 41kV
G621 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER/NR | XEL | Golf - Wookstock 34.5kV
G645 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 50 |  | ER/NR | GRE
G685 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | XEL | Lake Lillian - Atwater 69kV
G741 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Waste Heat Recovery | 8 |  | ER/NR | ALTW | Near Alliant 69kV line
G752 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 |  | ER/NR | MDU | Bison - Hettinger 230kV
G788 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 49 |  | ER/NR | GRE | Ladish 115kV
G930 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 60 |  | ER/NR | XEL | Sherco
G930SHERCO | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 2491.5 |  | ER/NR | XEL
G971 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 |  | ER | XEL | 69kV line in SE 1/4 of Sec 17 in Cosmos Twp
GEN-2001-014 | 01 - Woodward | 1 | PQ | Wind | 94.5 |  | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 74.25 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 180 |  | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-036 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 80 |  | ER | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037 | 01 - Woodward | 1 | PQ | Wind | 102 |  | ER | OKGE | FPL Moreland Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039A | 03 - Spearville | 1 | PQ | Wind | 104 |  | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 04 - Northwest Kansas | 1 | PQ | Wind | 100 |  | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 153 |  | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 123 |  | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 02 - Hitchland | 1 | PQ | Wind | 240 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 02 - Hitchland | 1 | PQ | Wind | 79.8 |  | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-022 | 02 - Hitchland | 1 | PQ | Wind | 239.2 |  | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A | 03 - Spearville | 1 | PQ | Wind | 100.5 |  | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 |  | ER | WFEC | Anadarko - Paradise (Blue Canyon) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 04 - Northwest Kansas | 1 | PQ | Wind | 201 |  | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 04 - Northwest Kansas | 1 | PQ | Wind | 249.3 |  | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | 02 - Hitchland | 1 | PQ | Wind | 159.1 |  | ER | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 09 - Nebraska | 1 | PQ | Wind | 75 |  | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 120 |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-014 | 03 - Spearville | 1 | PQ | Wind | 152 |  | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 150 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-020 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 27 |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 20.6 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023N | 09 - Nebraska | 1 | PQ | Coal | 75 |  | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 30.6 |  | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008 | 01 - Woodward | 1 | PQ | Wind | 120 |  | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 - Spearville | 1 | PQ | Wind | 248.4 |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 199.8 |  | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-001IS | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 10 |  | ER/NR | XEL
GEN-2006-002 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100.8 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 150 |  | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 168.12 |  | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 09 - Nebraska | 1 | PQ | Wind | 42 |  | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | 03 - Spearville | 1 | PQ | Wind | 94 |  | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 01 - Woodward | 1 | PQ | Wind | 18.9 |  | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 604 |  | ER | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 132 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N005 | 09 - Nebraska | 1 | PQ | Wind | 80 |  | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 09 - Nebraska | 1 | PQ | Wind | 80 |  | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 02 - Hitchland | 1 | PQ | Wind | 370 |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | 01 - Woodward | 1 | PQ | Wind | 129.6 |  | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 09 - Nebraska | 1 | PQ | Wind | 81 |  | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 09 - Nebraska | 1 | PQ | Wind | 60 |  | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GrayCountyWindMontezuma | 03 - Spearville | 1 | PQ | Wind | 110 |  | ER | SUNC | Gray County Tap 115kV
H092 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 60 |  | ER/NR | MP | MP Boswell
H092BOSWELL | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 585 |  | ER/NR | MP | MP Boswell
J091 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 66 |  | ER/NR | ALTW
J279NEAL | 09 - Nebraska | 1 | DIS-15-2-PQ | Coal | 680 |  | ER/NR | MEC
J416 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | ALTW
LlanoEstacadoWhiteDeer | 02 - Hitchland | 1 | PQ | Wind | 80 |  | ER | SPS | Llano Wind 115kV
MPC00500GRE | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 51 |  | ER/NR | GRE
NPPDBrokenBow | 09 - Nebraska | 1 | PQ | Heat | 7.3 |  | ER | NPPD | Broken Bow 115kV
NPPDBuffaloCountySolar | 09 - Nebraska | 1 | PQ | Solar | 10 |  | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 09 - Nebraska | 1 | PQ | Wind | 20 |  | ER | NPPD | Tekamah & Oakland 115kV
NPPDBurwell | 09 - Nebraska | 1 | PQ | Heat | 3.3 |  | ER | NPPD | Ord 115kV
NPPDColumbusHydro | 09 - Nebraska | 1 | PQ | Hydro | 45 |  | ER | NPPD | Columbus 115kV
NPPDOrd | 09 - Nebraska | 1 | PQ | Heat | 10.8 |  | ER | NPPD | Ord 115kV
NPPDStuart | 09 - Nebraska | 1 | PQ | Heat | 1.8 |  | ER | NPPD | Ainsworth 115kV
R15 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | MEC | Pomeroy 161kV
R22 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 |  | ER/NR | MEC
R23 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 100 |  | ER/NR | MEC | Monona - Carroll 161kV
R26 | 13 - Northeast Kansas/Northwest Missouri | 1 | DIS-15-2-PQ | Wind | 400 |  | ER | MEC | MEC Cooper - Booneville 345kV
R34 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 |  | ER/NR | MEC | Council Bluffs - Madison County 345kV
R35 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 |  | ER/NR | MEC | Pomeroy Wind Farm site
R39 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 499.98 |  | ER/NR | MEC | Raun - Lakefield Junction
R42 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 |  | ER/NR | MEC
R49 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 12 |  | ER/NR | MEC | Pomeroy Generating station
R65 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 92 |  | ER/NR | MEC | R34 Expansion
SPSCarson | 02 - Hitchland | 1 | PQ | Wind | 10 |  | ER | SPS | Martin 115kV | Commerical Operation
SPSDumas19thSt | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | Dumas 19th Street 115kV
SPSEtter | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | Etter 115kV
SPSHopi | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | Hopi 115kV
SPSJal | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | S Jal 115kV
SPSLeaRoad | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | Lea Road 115kV
SPSMonument | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | Monument 115kV
SPSMooreE | 02 - Hitchland | 1 | PQ | Wind | 17.5 |  | ER | SPS | Moore East 115kV
SPSOcotillo | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 |  | ER | SPS | S_Jal 115kV
SPSSherman | 02 - Hitchland | 1 | PQ | Wind | 20 |  | ER | SPS | Sherman 115kV
Sunray | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 34.5 |  | ER | SPS | Valero 115kV
WAPASEAMSFtRandallHydro | 09 - Nebraska | 1 | PQ | Hydro | 351.2 |  | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSFtRandleHydro | 09 - Nebraska | 1 | PQ | Hydro | 351.2 |  | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSGavinsPointHydro | 09 - Nebraska | 1 | PQ | Hydro | 102 |  | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSGavinsPtHydro | 09 - Nebraska | 1 | PQ | Hydro | 102 |  | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSSpiritMoundHeat | 09 - Nebraska | 1 | PQ | Heat | 120 |  | ER | BEPC-SPP | Spirit Mound (WAPA) 115kV
Young1 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Coal | 274 |  | ER | OTP

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name | Detail
09ALL | ERIS | Thermal | KELLY 5 - TECHILL5 161 | 19WP, 20G, 24L, 24WP | Base Case | 112 |  | 132.54 | 0 |  |  | Kelly to Tecumseh Hill 161kV Rebuild | Rebuild the existing Northwest to Matthewson 345kV 11.1 mile line to achieve a minimum light/emergency rating of 1301 MVA
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 337376 TO BUS 508809 CKT 1 |  |  |  | 0 |  |  | Eastowne 161kV Reactive Support | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 337376 TO BUS 508809 CKT 1 |  |  |  | 0 |  |  | Hawthorne to Craig 345kV New Build | Build a new 25 mile 345kV line from Hawthorn to Craig
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 337376 TO BUS 508809 CKT 1 |  |  |  | 0 |  |  | Longwood 345kV Reactive Support | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 337376 TO BUS 508809 CKT 1 |  |  |  | 0 |  |  | Mark Moore 161kV Reactive Support | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 337376 TO BUS 508809 CKT 1 |  |  |  | 0 |  |  | Mark Moore to Elm Creek 345kV New Build | Build a new 102 mile 345kV line from Mark Moore to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 337376 TO BUS 508809 CKT 1 |  |  |  | 0 |  |  | Sibley 161kV Reactive Support | Install a 100 MVAR capacitor bank at Sibley 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 337376 TO BUS 508809 CKT 1 |  |  |  | 0 |  |  | Southwest Shreveport 345kV Reactive Support | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 337376 TO BUS 508809 CKT 1 |  |  |  | 0 |  |  | Valiant to Petersburg 345kV New Build CKT 2 | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 500250 TO BUS 507760 CKT 1 |  |  |  | 0 |  |  | Eastowne 161kV Reactive Support | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 500250 TO BUS 507760 CKT 1 |  |  |  | 0 |  |  | Hawthorne to Craig 345kV New Build | Build a new 25 mile 345kV line from Hawthorn to Craig
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 500250 TO BUS 507760 CKT 1 |  |  |  | 0 |  |  | Longwood 345kV Reactive Support | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 500250 TO BUS 507760 CKT 1 |  |  |  | 0 |  |  | Mark Moore 161kV Reactive Support | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 500250 TO BUS 507760 CKT 1 |  |  |  | 0 |  |  | Mark Moore to Elm Creek 345kV New Build | Build a new 102 mile 345kV line from Mark Moore to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 500250 TO BUS 507760 CKT 1 |  |  |  | 0 |  |  | Sibley 161kV Reactive Support | Install a 100 MVAR capacitor bank at Sibley 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 500250 TO BUS 507760 CKT 1 |  |  |  | 0 |  |  | Southwest Shreveport 345kV Reactive Support | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 500250 TO BUS 507760 CKT 1 |  |  |  | 0 |  |  | Valiant to Petersburg 345kV New Build CKT 2 | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 505480 TO BUS 506932 CKT 1 |  |  |  | 0 |  |  | Eastowne 161kV Reactive Support | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 505480 TO BUS 506932 CKT 1 |  |  |  | 0 |  |  | Hawthorne to Craig 345kV New Build | Build a new 25 mile 345kV line from Hawthorn to Craig
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 505480 TO BUS 506932 CKT 1 |  |  |  | 0 |  |  | Longwood 345kV Reactive Support | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 505480 TO BUS 506932 CKT 1 |  |  |  | 0 |  |  | Mark Moore 161kV Reactive Support | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 505480 TO BUS 506932 CKT 1 |  |  |  | 0 |  |  | Mark Moore to Elm Creek 345kV New Build | Build a new 102 mile 345kV line from Mark Moore to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 505480 TO BUS 506932 CKT 1 |  |  |  | 0 |  |  | Sibley 161kV Reactive Support | Install a 100 MVAR capacitor bank at Sibley 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 505480 TO BUS 506932 CKT 1 |  |  |  | 0 |  |  | Southwest Shreveport 345kV Reactive Support | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 505480 TO BUS 506932 CKT 1 |  |  |  | 0 |  |  | Valiant to Petersburg 345kV New Build CKT 2 | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 510907 TO BUS 510911 CKT 1 |  |  |  | 0 |  |  | Eastowne 161kV Reactive Support | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 510907 TO BUS 510911 CKT 1 |  |  |  | 0 |  |  | Hawthorne to Craig 345kV New Build | Build a new 25 mile 345kV line from Hawthorn to Craig
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 510907 TO BUS 510911 CKT 1 |  |  |  | 0 |  |  | Longwood 345kV Reactive Support | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 510907 TO BUS 510911 CKT 1 |  |  |  | 0 |  |  | Mark Moore 161kV Reactive Support | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 510907 TO BUS 510911 CKT 1 |  |  |  | 0 |  |  | Mark Moore to Elm Creek 345kV New Build | Build a new 102 mile 345kV line from Mark Moore to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 510907 TO BUS 510911 CKT 1 |  |  |  | 0 |  |  | Sibley 161kV Reactive Support | Install a 100 MVAR capacitor bank at Sibley 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 510907 TO BUS 510911 CKT 1 |  |  |  | 0 |  |  | Southwest Shreveport 345kV Reactive Support | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN BRANCH FROM BUS 510907 TO BUS 510911 CKT 1 |  |  |  | 0 |  |  | Valiant to Petersburg 345kV New Build CKT 2 | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN LINE FROM BUS 635017 TO BUS 640139 CKT 1 |  |  |  | 0 |  |  | Eastowne 161kV Reactive Support | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN LINE FROM BUS 635017 TO BUS 640139 CKT 1 |  |  |  | 0 |  |  | Hawthorne to Craig 345kV New Build | Build a new 25 mile 345kV line from Hawthorn to Craig
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN LINE FROM BUS 635017 TO BUS 640139 CKT 1 |  |  |  | 0 |  |  | Mark Moore 161kV Reactive Support | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN LINE FROM BUS 635017 TO BUS 640139 CKT 1 |  |  |  | 0 |  |  | Mark Moore to Elm Creek 345kV New Build | Build a new 102 mile 345kV line from Mark Moore to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN LINE FROM BUS 635017 TO BUS 640139 CKT 1 |  |  |  | 0 |  |  | Sibley 161kV Reactive Support | Install a 100 MVAR capacitor bank at Sibley 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN LINE FROM BUS 635200 TO BUS 645451 CKT 1 |  |  |  | 0 |  |  | Eastowne 161kV Reactive Support | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN LINE FROM BUS 635200 TO BUS 645451 CKT 1 |  |  |  | 0 |  |  | Hawthorne to Craig 345kV New Build | Build a new 25 mile 345kV line from Hawthorn to Craig
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN LINE FROM BUS 635200 TO BUS 645451 CKT 1 |  |  |  | 0 |  |  | Mark Moore 161kV Reactive Support | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN LINE FROM BUS 635200 TO BUS 645451 CKT 1 |  |  |  | 0 |  |  | Mark Moore to Elm Creek 345kV New Build | Build a new 102 mile 345kV line from Mark Moore to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge |  | OPEN LINE FROM BUS 635200 TO BUS 645451 CKT 1 |  |  |  | 0 |  |  | Sibley 161kV Reactive Support | Install a 100 MVAR capacitor bank at Sibley 161kV Substation
00NR | NRIS | Thermal | CIRCLE 3 - CIRC TX-1 115 1 | 19WP20SP24SP, 24WP, 29SP | P11:RENO-G16-111-TAP |  | 308 | 121.91 | 375.4828 |  |  | 2nd Circle 230/115kV New Transformer | Build a new 230/115kV transformer at 2nd Circle
00NR | NRIS | Thermal | CIRCLE 6 - CIRC TX-1 115 1 | 19WP20SP24SP, 24WP, 29SP | P11:RENO-G16-111-TAP |  | 308 | 120.9 | 372.372 |  |  | 2nd Circle 230/115kV New Transformer | Build a new 230/115kV transformer at 2nd Circle
09ALL | ERIS | Thermal | FAIRBRY7 - HEBRN N7115 | 19WP20SP, 24L, 24SP, 24WP, 29SP | P12:115:NPPD:1175B:FAIRBRY7:HARBINE7:BTB |  | 99 | 101.32 | 100.3068 |  |  | Fairbury to Hebron N 115kV Rebuild | Rebuild the existing Fairbury to Hebron 115kV 22 mile line to achieve a minimum emergency rating of 101 MVA
00NR | NRIS | Thermal | GAINES 3 - OXY_WSEM_TP3 115 1 | 24SP, 29SP | P12:115:SPS:T89.1.DC_N.HIGG |  | 119.5 | 124.06 | 148.2517 |  |  | Gaines to Johnson Draw 115kV New Build | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit
00NR | NRIS | Thermal | GAINES 3 - OXY_WSEM_TP3 115 1 | 24SP, 29SP | P12:115:SPS:T89.1.DC_N.HIGG |  | 119.5 | 124.06 | 148.2517 |  |  | Seminole to Cunningham 230kV New Build | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA
06ALL | ERIS | Thermal | LAMTON 3 - HALE_CNTY 3 115 1 | 19WP, 20G, 20SP, 24L, 24SP | P12:115:SPS:V09.1.HALECTR.PLANTX |  | 79.7 | 122.24 | 97.4253 |  |  | Lampton to Hale County 115kV Rebuild | Rebuild the existing Lampton to Hale Coutny 115kV 20.06 mile line to achieve a minimum summer/emergency rating of 98 MVA
00NR | NRIS | Thermal | DENVER_N 3 - HIGGEAST 3 115 1 | 24SP, 29SP | P12:115:SPS:W35.1.GAINES.JNSDRW |  | 119.5 | 142.46 | 170.2397 |  |  | Gaines to Johnson Draw 115kV New Build | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit
00NR | NRIS | Thermal | HIGGEAST 3 - HIGG 3 115 1 | 29SP | P12:115:SPS:W35.1.GAINES.JNSDRW |  | 159.4 | 104.04 | 165.8398 |  |  | Gaines to Johnson Draw 115kV New Build | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit
00NR | NRIS | Thermal | JOHNSON_DRW3 - HIGG 3 115 1 | 24SP, 29SP | P12:115:SPS:W35.1.GAINES.JNSDRW |  | 105.6 | 123.83 | 130.7645 |  |  | Gaines to Johnson Draw 115kV New Build | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit
00NR | NRIS | Thermal | DENVER_N 3 - HIGGEAST 3 115 1 | 24SP, 29SP | P12:115:SPS:W35.1.GAINES.JNSDRW |  | 119.5 | 142.46 | 170.2397 |  |  | Seminole to Cunningham 230kV New Build | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA
00NR | NRIS | Thermal | HIGGEAST 3 - HIGG 3 115 1 | 29SP | P12:115:SPS:W35.1.GAINES.JNSDRW |  | 159.4 | 104.04 | 165.8398 |  |  | Seminole to Cunningham 230kV New Build | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA
00NR | NRIS | Thermal | JOHNSON_DRW3 - HIGG 3 115 1 | 24SP, 29SP | P12:115:SPS:W35.1.GAINES.JNSDRW |  | 105.6 | 123.83 | 130.7645 |  |  | Seminole to Cunningham 230kV New Build | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA
06ALL | ERIS | Thermal | NORTON 3 - PLSNT_HILL 3 115 1 | 20G, 20SP, 24L, 24SP, 29SP | P12:115:SPS:W59.1.LOPEZ.CMPBLL |  | 128.1 | 116.77 | 149.5824 |  |  | Norton to Pleasant Hills 115kV Rebuild | Rebuild the existing Norton to Pleasant Hills 115kV 54.54 mile line to achieve a minimum spring/emergency rating of 150 MVA
00NR | NRIS | Thermal | LOGAN___-BE7 - KW1A 115 1 | 19WP | P12:115:UMZ:# 5503 #: IN . PROPER N-1 (LINE) FOR 603023-652440-1 |  | 203 | 110.74 | 224.8022 |  |  | Logan 230/115kV New Transformer CKT3 | Build a new 230/115kV transformer at Logan as a third circuit
09ALL | ERIS | Thermal | BEATRCE7 - HARBINE7 115 | 19WP20SP, 24L, 24SP, 24WP, 29SP | P12:115:WERE:KNOB-NPPD_115:: |  | 99 | 145.43 | 143.9757 |  |  | Beatrice to Harbine 115kV Rebuild | Rebuild the existing Beatrice to Harbine 115kV 14.08 mile line to achieve a minimum light/emergency rating of 144 MVA.
00NR | NRIS | Thermal | S.W.S.-4 - ANADARK4 138 1 | 20SP24SP, 29SP | P12:138:AEPW:CORNVIL4:S.W.S.-4 |  | 212 | 123.97 | 262.8164 |  |  | Gracemont to Anadark 138kV New Build CKT 2 | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit
00NR | NRIS | Thermal | S.W.S.-4 - NORGE--4 138 1 | 29SP | P12:138:AEPW:CORNVIL4:S.W.S.-4 |  | 136 | 100.65 | 136.884 |  |  | Gracemont to Anadark 138kV New Build CKT 2 | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit
00NR | NRIS | Thermal | 4REMNGTON - SHIDLER4 138 1 | 20SP, 24SP | P12:138:AEPW:MOUNDRD4:SHIDLER4 |  | 174 | 102.18 | 177.7932 |  |  | Shilder to Remington 138kV Rebuild | Rebuild the existing Shidler to Remington 138kV 5.0 mile line to achieve a minimum summer/emergency rating of 178 MVA
00NR | NRIS | Thermal | MUSTANG4 - SW 5TH 4 138 1 | 20SP24SP, 29SP | P12:138:OKGE:BKRBKR130 |  | 287 | 106.91 | 306.8317 |  |  | Mustang to SW 5th St. 138kV Rebuild | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA
01ALL | ERIS | Thermal | EL RENO4 - SCOTTSW4 138 | 20G | P12:138:OKGE:BKRBKR423 |  | 136 | 106.84 | 145.3024 |  |  | El Reno to Scott Switch 138kV Rebuild | Rebuild the existing El Reno to Scott Switch 138kV 6.45 mile line to achieve a minimum spring/emergency rating of 146 MVA
01ALL | ERIS | Thermal | DOVERSW4 - OKEENE 4 138 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:138:OKGE:BKRBKR87 |  | 83 | 137.4 | 114.042 |  |  | Dover Switch to Okeene 138kV Rebuild | Rebuild the existing Dover Switch to Okeene 138kV 27.24 mile line to acieve a minimum winter/normal rating of 121 MVA
00NR | NRIS | Thermal | S BROWN4 - BROWN 4 138 1 | 19WP24WP, | P12:138:OKGE-SWPA-WFEC:BKRBKR250 |  | 143 | 109.98 | 157.2714 |  |  | Brown to South Brown 138kV Rebuild | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA
00NR | NRIS | Thermal | GRACMNT4 - ANADARK4 138 1 | 19WP24SP, 24WP, 29SP | P12:138:OKGE-WFEC:BKRBKR368 |  | 412 | 114.09 | 470.0508 |  |  | Gracemont to Anadark 138kV New Build CKT 2 | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit
07ALL | ERIS | Thermal | ANADARK4 - CHERRYRD 4 138 | 20G, 20SP, 24L, 24SP | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4 | 145 | 169 | 129.84 | 219.4296 |  |  | Anadark to Cherry Road 138kV Rebuild | Rebuild the existing Anadark to Cherry Road 138kV 25.15 mile line to achieve a minimum light/emergency rating of 189 MVA
07ALL | ERIS | Thermal | WALTRS-2 - ESQNDLJ2 69 | 24L | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4 | 58 | 68 | 112.31 | 76.3708 |  |  | Essaquandale Jct. to Walters 69kV Rebuild | Rebuild the existing Essaquandale Jct. to Walters 69kV 1.19 mile line to achieve a minimum light/emergency rating of 66 MVA
07ALL | ERIS | Thermal | GEROJCT2 - ESQNDLJ2 69 | 20G, 24L | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4 | 58 | 68 | 113.73 | 77.3364 |  |  | Geronimo Jct. to Essaquanadable Jct. 69kV Rebuild | Rebuild the existing Geronimo Jct. to Essaquanadale Jct. 69kV 3.83 mile line to achieve a minimum light/emergency rating of 67 MVA
07ALL | ERIS | Thermal | GEROJCT2 - GRANFLD2 69 | 20G, 20SP, 24L, 29SP | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4 | 58 | 68 | 120.62 | 82.0216 |  |  | Geronimo Jct. to Granfield 69kV Rebuild | Rebuild the existing Geronimo Jct. to Granfield 69kV 14.93 mile line to achieve a minimum light/emergency rating of 71 MVA
00NR | NRIS | Thermal | GRDA1 5 - GRDAUTO1 161 1 | 19WP24SP | P12:161:AECI:CHOTEAU-MAID |  | 560 | 113.15 | 633.64 |  |  | Tonnece to Tontitown 345kV New Build | Build a new 18 mile 345kV line from Tonnece to Tontitown
00NR | NRIS | Thermal | GRDA1 7 - GRDAUTO1 161 1 | 19WP24SP | P12:161:AECI:CHOTEAU-MAID |  | 560 | 114.58 | 641.648 |  |  | Tonnece to Tontitown 345kV New Build | Build a new 18 mile 345kV line from Tonnece to Tontitown
00NR | NRIS | Thermal | 5GRANDVIEW% - EUREKA 5 161 1 | 19WP24WP, | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5 |  | 210 | 130.29 | 273.609 |  |  | Eureka to Grandview 161kV Rebuild | Rebuild the existing Eureka to Grandview 161kV 10.56 mile line to achieve a minimum winter/emergency rating of 274 MVA
00NR | NRIS | Thermal | 5GRANDVIEW% - EUREKA 5 161 1 | 19WP24WP, | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5 |  | 210 | 130.29 | 273.609 |  |  | Eureka to Grandview 161kV Rebuild | Rebuild the existing Northwest to Matthewson 345kV 11.1 mile line to achieve a minimum light/emergency rating of 1301 MVA
12ALL | ERIS | Thermal | ASB349 5 - PUR421 5 161 | 19WP24WP, | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417 |  | 223 | 122.39 | 272.9297 |  |  | Asbury Plant to Purcell Switch 161kV Rebuild | Rebuild the existing Asbury Plant to Purcell Switch 161kV 11.94 mile line to achieve a minimum winter/emergency rating of 329 MVA
08ALL | ERIS | Thermal | ASB349 5 - PUR421 5 161 | 19WP20SP24SP, 24WP, 29SP | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417 |  | 223 | 147.48 | 328.8804 |  |  | Asbury Plant to Purcell Switch 161kV Rebuild | Rebuild the existing Asbury Plant to Purcell Switch 161kV 11.94 mile line to achieve a minimum winter/emergency rating of 329 MVA
12ALL | ERIS | Thermal | CARTHAG5 - CAR395 5 161 | 19WP24WP, | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417 |  | 222 | 112.38 | 249.4836 |  |  | Carthage to Car 395 161kV Rebuild | Rebuild the existing Carthage to Car 395 161kV 4.14 mile line to achieve a minimum winter/emergency rating of 305 MVA
08ALL | ERIS | Thermal | CARTHAG5 - CAR395 5 161 | 19WP20SP24SP, 24WP, 29SP | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417 |  | 222 | 137.08 | 304.3176 |  |  | Carthage to Car 395 161kV Rebuild | Rebuild the existing Carthage to Car 395 161kV 4.14 mile line to achieve a minimum winter/emergency rating of 305 MVA
08ALL | ERIS | Thermal | CAR395 5 - PUR421 5 161 | 19WP24WP, | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417 |  | 279 | 113.49 | 316.6371 |  |  | Essaquandale Jct. to Walters 69kV Rebuild | Rebuild the existing Essaquandale Jct. to Walters 69kV 1.19 mile line to achieve a minimum light/emergency rating of 66 MVA
12ALL | ERIS | Thermal | ASB349 5 - CJ 366 5 161 | 19WP24WP, | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA) |  | 223 | 129.21 | 288.1383 |  |  | Asbury Plant to Carl Junction NE 161kV Rebuild | Rebuild the existing Asbury Plant to Carl Junction NE 161kV 12.3 mile line to achieve a minimum winter/emergency rating of 342 MVA
08ALL | ERIS | Thermal | ASB349 5 - CJ 366 5 161 | 19WP20SP24SP, 24WP, 29SP | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA) |  | 223 | 153.21 | 341.6583 |  |  | Asbury Plant to Carl Junction NE 161kV Rebuild | Rebuild the existing Asbury Plant to Carl Junction NE 161kV 12.3 mile line to achieve a minimum winter/emergency rating of 342 MVA
00NR | NRIS | Thermal | CARTHAG5 - ATL109 5 161 1 | 29SP | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA) |  | 222 | 117.62 | 261.1164 |  |  | Carthage to Joplin Atlas Jct. 161kV Rebuild | Rebuild the existing Cartahage to Joplin Atlas Jct. 161kV 8.2 mile line to achieve a minimum summer/emergency rating of 262 MVA
08ALL | ERIS | Thermal | ASB349 5 - LITCH 5 161 | 19WP20SP24SP, 24WP, 29SP | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA) |  | 223 | 153.21 | 341.6583 |  |  | Litchfield to Asbury Plant 161kV Rebuild | Rebuild the existing Litchfield to Asbury Plant 161kV 6.8 mile line to achieve a minimum winter/emergency rating of 329 MVA
12ALL | ERIS | Thermal | ORO110 5 - FIR417 5 161 | 19WP24WP, | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA) |  | 223 | 116.27 | 259.2821 |  |  | Oronogo Jct. to Joplin Fir Road 161kV Rebuild | Rebuild the existing Oronogo Jct. to Fir Road 161kV 2.86 mile line to achieve a minimum winter/emergency rating of 312 MVA
08ALL | ERIS | Thermal | ORO110 5 - FIR417 5 161 | 19WP20SP24SP, 24WP, | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA) |  | 223 | 139.63 | 311.3749 |  |  | Oronogo Jct. to Joplin Fir Road 161kV Rebuild | Rebuild the existing Oronogo Jct. to Fir Road 161kV 2.86 mile line to achieve a minimum winter/emergency rating of 312 MVA
08ALL | ERIS | Thermal | FRANKLIN2 - FRAN TX-1 69 | 20G, 24WP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 111.42 | 122.562 |  |  | Franklin 161/69kV New Transformer CKT 2 | Build a new 161/69kV Transformer at Franklin as a second circuit
08ALL | ERIS | Thermal | FRANKLIN5 161/69XFR | 20G, 24WP | P12:161:WERE:FRAN-LITC_161:: |  | 110 | 113.53 | 124.883 |  |  | Franklin 161/69kV New Transformer CKT 2 | Build a new 161/69kV Transformer at Franklin as a second circuit
00NR | NRIS | Thermal | NEOSHO 5 - RIV4525 161 1 | 24WP, | P12:161:WERE:LITC-EMDE_161:: |  | 335 | 106.75 | 357.6125 |  |  | Neosho to Riverton 161kV Rebuild | Rebuild the existing Neosho to Riverton 161kV 28.4 mile line to achieve a minimum winter/normal rating of 324 MVA
08ALL | ERIS | Thermal | PUR421 5 - LITCH 5 161 | 20G, 24WP | P12:161:WERE:NSES-EMDE_161:: |  | 251 | 110.51 | 277.3801 |  |  | Litchfield to Asbury Plant 161kV Rebuild | Rebuild the existing Litchfield to Asbury Plant 161kV 6.8 mile line to achieve a minimum winter/emergency rating of 329 MVA
08ALL | ERIS | Thermal | LITCH 5 - FRANKLIN5 161 | 20G | P12:161:WERE:NSES-EMDE_161:: |  | 251 | 100.73 | 252.8323 |  |  | Wolf Creek to Blackberry 345kV | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA
08ALL | ERIS | Thermal | LITCH 5 - FRANKLIN5 161 | 20G | P12:161:WERE:NSES-EMDE_161:: |  | 251 | 100.73 | 252.8323 |  |  | Wolf Creek to West Gardner 345kV New Build | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW:SWEETWT6:CHISHOLM6 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW:SWEETWT6:CHISHOLM6 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW:SWEETWT6:CHISHOLM6 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW:SWEETWT6:CHISHOLM6 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW:SWEETWT6:CHISHOLM6 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW:SWEETWT6:CHISHOLM6 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW:SWEETWT6:CHISHOLM6 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW:SWEETWT6:CHISHOLM6 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Thermal | POTTER_CO 6 - WAUK 90343-A 230 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, | P12:230:AEPW:SWEETWT6:CHISHOLM6 |  | 559 | 142.15 | 794.6185 |  |  | Potter County 345/230kV New Transformer CKT 2 | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA
06ALL | ERIS | Thermal | POTTER_CO 7 345/230XFR 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, | P12:230:AEPW:SWEETWT6:CHISHOLM6 |  | 559 | 141.69 | 792.0471 |  |  | Potter County 345/230kV New Transformer CKT 2 | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW:SWEETWT6:CHISHOLM6 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
00NR | NRIS | Thermal | CHADRON7 - WAYSIDE7 115 1 | 20SP, 24SP, 24WP, 29SP | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z |  | 160 | 128.23 | 205.168 |  |  | Shannon 230/115kV New Transformer | Build a new 230/115kV transformer at Shannon
00NR | NRIS | Thermal | WAYSIDE4 - WAYSIDE T1 115 1 | 20SP24SP, 29SP | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z |  | 187 | 114.63 | 214.3581 |  |  | Shannon 230/115kV New Transformer | Build a new 230/115kV transformer at Shannon
00NR | NRIS | Thermal | WAYSIDE7 - WAYSIDE T1 115 1 | 20SP24SP, 29SP | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z |  | 187 | 111.58 | 208.6546 |  |  | Shannon 230/115kV New Transformer | Build a new 230/115kV transformer at Shannon
00NR | NRIS | Thermal | CHADRON7 - WAYSIDE7 115 1 | 20SP, 24SP, 24WP, 29SP | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z |  | 160 | 128.23 | 205.168 |  |  | Wayside to Shannon 230kV New Build | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA
00NR | NRIS | Thermal | WAYSIDE4 - WAYSIDE T1 115 1 | 20SP24SP, 29SP | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z |  | 187 | 114.63 | 214.3581 |  |  | Wayside to Shannon 230kV New Build | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA
00NR | NRIS | Thermal | WAYSIDE7 - WAYSIDE T1 115 1 | 20SP24SP, 29SP | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z |  | 187 | 111.58 | 208.6546 |  |  | Wayside to Shannon 230kV New Build | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA
00NR | NRIS | Thermal | SCOTBLF7 - VICTRYH7 115 1 | 20SP, 24SP, 24WP, 29SP | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX |  | 155 | 126 | 195.3 |  |  | Shannon 230/115kV New Transformer | Build a new 230/115kV transformer at Shannon
00NR | NRIS | Thermal | SCOTBLF7 - VICTRYH7 115 1 | 20SP, 24SP, 24WP, 29SP | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX |  | 155 | 126 | 195.3 |  |  | Victory Hill 230kV Reactive Support | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation
00NR | NRIS | Thermal | SCOTBLF7 - VICTRYH7 115 1 | 20SP, 24SP, 24WP, 29SP | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX |  | 155 | 126 | 195.3 |  |  | Wayside to Shannon 230kV New Build | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA
00NR | NRIS | Thermal | WATERTN4 - APPLEDORN 4 230 1 | 20SP24SP, 29SP | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT |  | 352 | 106.62 | 375.3024 |  |  | Watertown to Appledorn 230kV Rebuild | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA
00NR | NRIS | Thermal | G17-064-TAP - 640404 WAYSIDE4 230 1 | 19WP20SP24SP, 24WP, | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP) |  | 341 | 127.21 | 433.7861 |  |  | G17-064 Tap to Wayside 230kV Rebuild | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA
17ALL | ERIS | Non-Converge | Non-Converge |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP) |  |  |  | 0 |  |  | New Underwood 230kV Reactive Support | Install a new 75 MVAR capacitor bank at New Underwood 230kV Substation
00NR | NRIS | Thermal | NUNDRWD7 - WICKSVL7 115 1 | 19WP20SP24SP, 24WP, | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP) |  | 132 | 112.96 | 149.1072 |  |  | New Underwood to Wicksville 115kV Rebuild | Rebuild the existing New Underwood to Wicksville 115kV 12.42 mile line to achieve a minimum summer/emergency rating of 150 MVA
00NR | NRIS | Thermal | PHILIP 7 - WALL 7 115 1 | 20SP, 24SP | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP) |  | 132 | 103.06 | 136.0392 |  |  | Phillip to Wall 115kV Rebuild | Rebuild the existing Phillip to Wall 115kV 26.95 mile line to achieve a minimum summer/emergency rating of 137 MVA
00NR | NRIS | Thermal | WALL 7 - WICKSVL7 115 1 | 20SP, 24SP | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP) |  | 134 | 108.2 | 144.988 |  |  | Wall to Wicksville 115kV Rebuild | Rebuild the existing Wall to Wicksville 115kV 18.29 mile line to achieve a minimum summer/emergency rating of 145 MVA
00NR | NRIS | Thermal | FTRANDL4 - LAKPLAT-ER4 230 1 | 29SP | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT |  | 320 | 110.01 | 352.032 |  |  | Ft. Randall to Lake Platte 230kV Rebuild | Rebuild the existing Ft. Randall to Lake Platte 230kV 43.34 mile line to achieve a minimum summer/emergency rating of 353 MVA
00NR | NRIS | Thermal | FTTHOMP4 - LAKPLAT-ER4 230 1 | 29SP | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT |  | 352 | 104.42 | 367.5584 |  |  | Ft. Thompson to Lake Platte 230kV Rebuild | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA
00NR | NRIS | Thermal | FTTHOMP4 - FTRANDL4 230 1 | 24SP, 29SP | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT |  | 320 | 114.47 | 366.304 |  |  | Ft. Randall to Lake Platte 230kV Rebuild | Rebuild the existing Ft. Randall to Lake Platte 230kV 43.34 mile line to achieve a minimum summer/emergency rating of 353 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:L.E.S7:TERRYRD7 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:L.E.S7:TERRYRD7 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:L.E.S7:TERRYRD7 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:L.E.S7:TERRYRD7 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:L.E.S7:TERRYRD7 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:L.E.S7:TERRYRD7 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:L.E.S7:TERRYRD7 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:L.E.S7:TERRYRD7 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:L.E.S7:TERRYRD7 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
00NR | NRIS | Thermal | NWTXARK7 - VALIANT7 345 1 | 19WP24WP, | P12:345:AEPW:LYDIA7:VALIANT7 |  | 1416 | 114.74 | 1624.7184 |  |  | Lydia 345kV Reactive Support | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation
00NR | NRIS | Thermal | NWTXARK7 - VALIANT7 345 1 | 19WP24WP, | P12:345:AEPW:LYDIA7:VALIANT7 |  | 1416 | 114.74 | 1624.7184 |  |  | Northwest Texarkana 345kV Reactive Support | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation
00NR | NRIS | Thermal | NWTXARK7 - VALIANT7 345 1 | 19WP24WP, | P12:345:AEPW:LYDIA7:VALIANT7 |  | 1416 | 114.74 | 1624.7184 |  |  | Northwest Texarkana to Wilkes 345kV New Build | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes
00NR | NRIS | Thermal | NWTXARK7 - VALIANT7 345 1 | 19WP24WP, | P12:345:AEPW:LYDIA7:VALIANT7 |  | 1416 | 114.74 | 1624.7184 |  |  | Valiant to Turk 345kV New Build | Build a new 84 mile 345kV line from Valiant to Turk
00NR | NRIS | Thermal | NWTXARK7 - WELSH 7 345 1 | 19WP | P12:345:AEPW:LYDIA7:WELSH7 |  | 1186 | 108.29 | 1284.3194 |  |  | Lydia 345kV Reactive Support | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation
00NR | NRIS | Thermal | NWTXARK7 - WELSH 7 345 1 | 19WP | P12:345:AEPW:LYDIA7:WELSH7 |  | 1186 | 108.29 | 1284.3194 |  |  | Northwest Texarkana 345kV Reactive Support | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
00NR | NRIS | Thermal | 4CLEVLND - CLEVLND 4 138 Z1 | 19WP20SP24SP, 24WP, 29SP | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7 |  | 371 | 121.6 | 451.136 |  |  | Cleveland 138kV Substation Upgrade | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
00NR | NRIS | Thermal | NAPLSTP4 - PAYNESW4 138 1 | 20SP, 29SP | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7 |  | 169 | 109 | 184.21 |  |  | Naples Tap to Payne 138kV Rebuild | Rebuild the existing Naples Tap to Payne 138kV 8.9 mile line to achieve a minimum summer/emergency rating of 185 MVA
00NR | NRIS | Thermal | NAPLSTP4 - CORN TP4 138 1 | 19WP20SP | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7 |  | 187 | 108.12 | 202.1844 |  |  | Neosho to Riverton 161kV Rebuild | Rebuild the existing Neosho to Riverton 161kV 28.4 mile line to achieve a minimum winter/normal rating of 324 MVA
00NR | NRIS | Thermal | PITTSB-7 - SEMINOL7 345 1 | 19WP24WP, | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7 |  | 956 | 124.03 | 1185.7268 |  |  | Pittsburg to Seminole 345kV Rebuild | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
00NR | NRIS | Thermal | ST JOE 3 - NASHUA 7 345 1 | 19WP24WP, 29SP | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR |  | 1195 | 106.45 | 1272.0775 |  |  | Nashua to St. Joe 345kV Rebuild | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA
13ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:GMO-OPPD:S3458-HOLT |  |  |  | 0 |  |  | Cooper to Holt 345kV New Build | Build a new 32 mile 345kV line from Cooper to Holt
00NR | NRIS | Thermal | CBLUFFS3 - S3456 3 345 1 | 19WP24SP, 24WP, 29SP | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1 |  | 956 | 125.74 | 1202.0744 |  |  | Council Bluffs to S3456 345kV Rebuild | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA
00NR | NRIS | Thermal | TEKAMAH5 - S1226 5 161 1 | 19WP24SP, 24WP, | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1 |  | 256 | 167.31 | 428.3136 |  |  | Tekamah to S1226 161kV Rebuild | Rebuild the existing Tekamah to S1226 161kV 20.87 mile line to achieve a minimum winter/emergency rating of 429 MVA
00NR | NRIS | Thermal | SPRNDAL4 - DRPSPRG4 138 1 | 19WP20SP24SP29SP | P12:345:OKGE:BKRBKR21 |  | 153 | 116.03 | 177.5259 |  |  | Dripping Spring to Springdale 138kV Rebuild | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA
00NR | NRIS | Thermal | DRPSPRG4 - STIRLNG4 138 1 | 19WP20SP24SP29SP | P12:345:OKGE:BKRBKR21 |  | 153 | 110.61 | 169.2333 |  |  | Dripping Spring to Stirling 138kV Rebuild | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA
00NR | NRIS | Thermal | RUSSET-4 - STIRLNG4 138 1 | 19WP20SP24SP29SP | P12:345:OKGE:BKRBKR21 |  | 153 | 104.79 | 160.3287 |  |  | Russett to Stirling 138kV Rebuild | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR24 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR24 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR24 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR24 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR24 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR24 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR24 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR24 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR24 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR429 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR429 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR429 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR429 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR429 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR429 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR429 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR429 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR429 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR429 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE:BKRBKR429 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-AEPW:BKRBKR25 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-AEPW:BKRBKR25 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-AEPW:BKRBKR25 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-AEPW:BKRBKR25 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-AEPW:BKRBKR25 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-AEPW:BKRBKR25 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-AEPW:BKRBKR25 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-AEPW:BKRBKR25 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-AEPW:BKRBKR25 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-SPS:BKRBKR430 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-SPS:BKRBKR430 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-SPS:BKRBKR430 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-SPS:BKRBKR430 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-SPS:BKRBKR430 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-SPS:BKRBKR430 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-SPS:BKRBKR430 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-SPS:BKRBKR430 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-SPS:BKRBKR430 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-SPS:BKRBKR430 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:OKGE-SPS:BKRBKR430 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
00NR | NRIS | Thermal | GARRISN7 - PICKCITY-RR7 115 1 | 20SP24SP, 29SP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 |  | 120 | 138.46 | 166.152 |  |  | Garrison to Pick City 115kV Rebuild | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA
00NR | NRIS | Thermal | STANTN.T-BE7 - BEULAH 7 115 1 | 20SP24SP, 29SP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 |  | 132 | 127.13 | 167.8116 |  |  | Stanton to Beulah 115kV Rebuild | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA
00NR | NRIS | Thermal | STANTN.T-BE7 - PICKCITY-RR7 115 1 | 20SP24SP, 29SP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 |  | 120 | 139.43 | 167.316 |  |  | Stanton to Pick City 115kV Rebuild | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA
03ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
03ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Finney 345kV Reactive Support | Install a new 250 MVAR capacitor bank at Finney 345kV Substation
03ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Grapevine 345kV New Substation | Build a new 345kV substation at Grapevine
02ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Grapevine 345kV New Substation | Build a new 345kV substation at Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
02ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
03ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1) |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J14.1.EDDY.XRDS |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J14.1.EDDY.XRDS |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J14.1.EDDY.XRDS |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J14.1.EDDY.XRDS |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J14.1.EDDY.XRDS |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J14.1.EDDY.XRDS |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J14.1.EDDY.XRDS |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J14.1.EDDY.XRDS |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J14.1.EDDY.XRDS |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J15.1.XRDS.TOLK |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J15.1.XRDS.TOLK |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J15.1.XRDS.TOLK |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J15.1.XRDS.TOLK |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J15.1.XRDS.TOLK |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J15.1.XRDS.TOLK |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J15.1.XRDS.TOLK |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J15.1.XRDS.TOLK |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J15.1.XRDS.TOLK |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J15.1.XRDS.TOLK |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SPS:J15.1.XRDS.TOLK |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1) |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1) |  |  |  | 0 |  |  | Finney 345kV Reactive Support | Install a new 250 MVAR capacitor bank at Finney 345kV Substation
03ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1) |  |  |  | 0 |  |  | Grapevine 345kV New Substation | Build a new 345kV substation at Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1) |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
09ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1) |  |  |  | 0 |  |  | Mingo to Post Rock 345kV New Build | Build a new 100 mile 345kV line from Mingo to Post Rock
03ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1) |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
09ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1) |  |  |  | 0 |  |  | Mingo to Post Rock 345kV New Build | Build a new 100 mile 345kV line from Mingo to Post Rock
03ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) |  |  |  | 0 |  |  | Finney 345kV Reactive Support | Install a new 250 MVAR capacitor bank at Finney 345kV Substation
03ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) |  |  |  | 0 |  |  | Grapevine 345kV New Substation | Build a new 345kV substation at Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
03ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1) |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
15ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z |  |  |  | 0 |  |  | Chappelle Creek to Ft. Thompson 345k New Build CKT 2 | Build a new 30 mile 345kV line from Chappelle Creek to Ft. Thompson as a second circuit
09ALL | ERIS | Thermal | B.SPRGS7 - BRULE 7 115 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 109 | 167.21 | 182.2589 |  |  | Keystone to Sidney 345kV New Build CKT 2 | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit
09ALL | ERIS | Thermal | BRULE 7 - OGALALA_-TS7115 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 120 | 150.52 | 180.624 |  |  | Keystone to Sidney 345kV New Build CKT 2 | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit
09ALL | ERIS | Thermal | OGALALA4 - SIDNEY___TS4 230 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 320 | 156.77 | 501.664 |  |  | Keystone to Sidney 345kV New Build CKT 2 | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit
09ALL | ERIS | Thermal | SIDNEY___TS4 - SIDNEY__-MB4 230 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 478 | 116.08 | 554.8624 |  |  | Keystone to Sidney 345kV New Build CKT 2 | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit
09ALL | ERIS | Thermal | SIDNEY__-MB3 - SDQ 2A 230 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 496 | 113.86 | 564.7456 |  |  | Keystone to Sidney 345kV New Build CKT 2 | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit
09ALL | ERIS | Thermal | SIDNEY__-MB4 - SDQ 2A 230 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 496 | 114.14 | 566.1344 |  |  | Keystone to Sidney 345kV New Build CKT 2 | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit
17ALL | ERIS | Thermal | OGALALA4 - SIDNEY___TS4 230 | 19WP, 20G, 20SP, 24WP, 29SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 320 | 129.2 | 413.44 |  |  | Keystone to Sidney 345kV New Build CKT 2 | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit
17ALL | ERIS | Thermal | SIDNEY___TS4 - SIDNEY__-MB4 230 | 20SP | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z |  | 478 | 100.83 | 481.9674 |  |  | Keystone to Sidney 345kV New Build CKT 2 | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit
00NR | NRIS | Thermal | SIDNEY__-MB3 - STEGALL_-MB3 345 1 | 20SP24SP, 29SP | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z |  | 765 | 104.73 | 801.1845 |  |  | Sidney to G16-034 Tap 345kV New Build CKT 2 | Build a new 345kV line from Sidney to G16-034 Tap as a second circuit
16ALL | ERIS | Thermal | NESET___-BE4 - TIOGA4 4 230 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z |  | 506 | 140.58 | 711.3348 |  |  | Neset to Tioga 230kV Rebuild | Rebuild the existing Neset to Tioga 230kV 1 mile line to achieve a minimum summer/emergency rating of 712 MVA
15ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON |  |  |  | 0 |  |  | Chappelle Creek to Ft. Thompson 345k New Build CKT 2 | Build a new 30 mile 345kV line from Chappelle Creek to Ft. Thompson as a second circuit
15ALL | ERIS | Non-Converge | Non-Converge |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON |  |  |  | 0 |  |  | Cooper to Holt 345kV New Build | Build a new 32 mile 345kV line from Cooper to Holt
00NR | NRIS | Thermal | 87TH 7 - CRAIG 7 345 2 | 19WP20SP24SP, 24WP, 29SP | P12:345:WERE:87TH-CRAIG_345:: |  | 1254 | 120.3 | 1508.562 |  |  | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA
00NR | NRIS | Thermal | STRANGR7 - 87TH 7 345 2 | 19WP20SP24SP, 24WP, 29SP | P12:345:WERE:87TH-STRA_345:: |  | 1195 | 118.12 | 1411.534 |  |  | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA
00NR | NRIS | Thermal | CHISHLM4 - MAIZE 4 138 1 | 19WP20SP24SP, 24WP, 29SP | P12:345:WERE:BENT-WICH_345:: |  | 382 | 118.19 | 451.4858 |  |  | Wichita to Benton 345kV New Build CKT 2 | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit
00NR | NRIS | Thermal | EVANS N4 - MAIZE 4 138 1 | 19WP20SP24SP, 24WP, 29SP | P12:345:WERE:BENT-WICH_345:: |  | 382 | 123.14 | 470.3948 |  |  | Wichita to Benton 345kV New Build CKT 2 | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit
00NR | NRIS | Thermal | EVANS N4 - WICH TX-11 138 1 | 20SP24SP, 29SP | P12:345:WERE:BENT-WICH_345:: |  | 430 | 108.79 | 467.797 |  |  | Wichita to Benton 345kV New Build CKT 2 | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit
00NR | NRIS | Thermal | EVANS N4 - WICH TX-12 138 1 | 19WP20SP24SP, 24WP, 29SP | P12:345:WERE:BENT-WICH_345:: |  | 430 | 124.15 | 533.845 |  |  | Wichita to Benton 345kV New Build CKT 2 | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit
00NR | NRIS | Thermal | WICHITA7 - WICH TX-11 138 1 | 20SP24SP, 29SP | P12:345:WERE:BENT-WICH_345:: |  | 430 | 110 | 473 |  |  | Wichita to Benton 345kV New Build CKT 2 | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit
00NR | NRIS | Thermal | WICHITA7 - WICH TX-12 138 1 | 19WP20SP24SP, 24WP, 29SP | P12:345:WERE:BENT-WICH_345:: |  | 430 | 125.99 | 541.757 |  |  | Wichita to Benton 345kV New Build CKT 2 | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit
00NR | NRIS | Thermal | CHISHLM4 - MAIZE 4 138 1 | 19WP20SP24SP, 24WP, 29SP | P12:345:WERE:BENT-WICH_345:: |  | 382 | 118.19 | 451.4858 |  |  | Wichita to Benton 345kV Rebuild | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA
00NR | NRIS | Thermal | EVANS N4 - MAIZE 4 138 1 | 19WP20SP24SP, 24WP, 29SP | P12:345:WERE:BENT-WICH_345:: |  | 382 | 123.14 | 470.3948 |  |  | Wichita to Benton 345kV Rebuild | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA
00NR | NRIS | Thermal | EVANS N4 - WICH TX-11 138 1 | 20SP24SP, 29SP | P12:345:WERE:BENT-WICH_345:: |  | 430 | 108.79 | 467.797 |  |  | Wichita to Benton 345kV Rebuild | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA
00NR | NRIS | Thermal | EVANS N4 - WICH TX-12 138 1 | 19WP20SP24SP, 24WP, 29SP | P12:345:WERE:BENT-WICH_345:: |  | 430 | 124.15 | 533.845 |  |  | Wichita to Benton 345kV Rebuild | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA
00NR | NRIS | Thermal | WICHITA7 - WICH TX-11 138 1 | 20SP24SP, 29SP | P12:345:WERE:BENT-WICH_345:: |  | 430 | 110 | 473 |  |  | Wichita to Benton 345kV Rebuild | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA
00NR | NRIS | Thermal | WICHITA7 - WICH TX-12 138 1 | 19WP20SP24SP, 24WP, 29SP | P12:345:WERE:BENT-WICH_345:: |  | 430 | 125.99 | 541.757 |  |  | Wichita to Benton 345kV Rebuild | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA
00NR | NRIS | Thermal | STRANGR7 - IATAN 7 345 2 | 24SP, 29SP | P12:345:WERE:STRA-IATAN_345_1:: |  | 1195 | 104.55 | 1249.3725 |  |  | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA
00NR | NRIS | Thermal | STRANGR7 - IATAN 7 345 2 | 24SP, 29SP | P12:345:WERE:STRA-IATAN_345_1:: |  | 1195 | 104.55 | 1249.3725 |  |  | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA
00NR | NRIS | Thermal | STRANGR7 - IATAN 7 345 1 | 20SP24SP, 29SP | P12:345:WERE:STRA-IATAN_345_2::FUTURE |  | 1195 | 106.35 | 1270.8825 |  |  | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA
00NR | NRIS | Thermal | STRANGR7 - IATAN 7 345 1 | 20SP24SP, 29SP | P12:345:WERE:STRA-IATAN_345_2::FUTURE |  | 1195 | 106.35 | 1270.8825 |  |  | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA
08ALL | ERIS | Thermal | NEOSHO 7 - G17-009-TAP 345 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:WERE:WAVS-LACY_345:: |  | 956 | 138.63 | 1325.3028 |  |  | Wolf Creek to Blackberry 345kV | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA
08ALL | ERIS | Thermal | NEOSHO 7 - G17-009-TAP 345 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P12:345:WERE:WAVS-LACY_345:: |  | 956 | 138.63 | 1325.3028 |  |  | Wolf Creek to West Gardner 345kV New Build | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA
00NR | NRIS | Thermal | GILLIAM2 - SUPEROR2 69.0 1 | 20SP24SP, 29SP | P12:69:AEPW:HOSSTON2:VIVIAN2:SUPEROR2 \BREAKER TO BREAKER IS HOSSTON - SUPERIOR |  | 39 | 103.42 | 40.3338 |  |  | Gilliam to Superior 69kV Rebuild | Rebuild the existing Gilliam to Superior 69kV 6.0 mile line to achieve a minimum summer/emergency rating of 41 MVA
03ALL | ERIS | Thermal | HANSTN 2 - KINSLY 2 69 | 19WP, 20G, 24WP, | P12:69:MIDW:WALNUT CREEK-NEKOMA | 48 | 48 | 109.29 | 52.4592 |  |  | Hanston to Kinsley 69kV Rebuild | Rebuild the existing Hanston to Kinsley 69kV 18.75 mile line to achieve a minimum winter/emergency rating of 53 MVA
03ALL | ERIS | Thermal | SEWARD 2 - ZOOK 2 69 | 19WP24WP, | P12:69:MIDW:WALNUT CREEK-NEKOMA | 48 | 48 | 106.13 | 50.9424 |  |  | Seward to Zook 69kV Rebuild | Rebuild the existing Seward to Zook 69kV 16.89 mile line to achieve a minimum winter/emergency rating of 51 MVA
00NR | NRIS | Thermal | FTSMITH7 - FTSMITH5 161 5 | 19WP24WP, 29SP | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1 |  | 478 | 111.34 | 532.2052 |  |  | Ft. Smith 345/161kV New Transformer CKT 2 | Build a new 345/161kV transformer at Ft. Smith as a second circuit
00NR | NRIS | Thermal | FTSMTHW5 - FTSMITH5 161 5 | 19WP24WP, 29SP | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1 |  | 478 | 112.68 | 538.6104 |  |  | Ft. Smith 345/161kV New Transformer CKT 2 | Build a new 345/161kV transformer at Ft. Smith as a second circuit
00NR | NRIS | Thermal | ALTOO E2 - NEODJCT2 69.0 1 | 19WP20SP24SP, 24WP, 29SP | P13:069-138:WERE:MONT_TX-1_138-69:: |  | 36 | 114.75 | 41.31 |  |  | Altoona to Neodesha Jct. 69kV Rebuild | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA
00NR | NRIS | Thermal | GR ISLD4 - GRAND.ISD T5 115 2 | 24SP, 29SP | P13:115-230:NPPD:GR ISLD4:T2 |  | 316 | 100.57 | 317.8012 |  |  | Shell Creek to Grand Island 345kV New Build | Build a new 72 mile 345kV line from Shell Creek to Grand Island
00NR | NRIS | Thermal | GR ISLD4 - GRAND.ISD T2 115 1 | 24SP, 29SP | P13:115-230:NPPD:GR ISLD4:T5 |  | 316 | 100.67 | 318.1172 |  |  | Shell Creek to Grand Island 345kV New Build | Build a new 72 mile 345kV line from Shell Creek to Grand Island
00NR | NRIS | Thermal | MARTIN 7 - WANBLEE 7 115 1 | 24SP, 29SP | P13:115-230:NPPD:WAYSIDE4:T1 |  | 120 | 112.16 | 134.592 |  |  | Martin to Wanblee 115kV Rebuild | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA
00NR | NRIS | Thermal | PHILIP 7 - WANBLEE 7 115 1 | 24SP, 24WP, 29SP | P13:115-230:NPPD:WAYSIDE4:T1 |  | 120 | 115.69 | 138.828 |  |  | Phillip to Wanblee 115kV Rebuild | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA
00NR | NRIS | Thermal | HOSKINS4 - HOSKINS T1 115 1 | 19WP20SP24SP, 24WP, 29SP | P13:115-345:NPPD:NUCOR-2 |  | 187 | 128.74 | 240.7438 |  |  | Hoskins 345/230kV New Transformer CKT3 | Build a new 345/230kV transformer at Hoskins as a third circuit
00NR | NRIS | Thermal | HOSKINS7 - HOSKINS T1 115 1 | 19WP20SP24SP, 24WP, 29SP | P13:115-345:NPPD:NUCOR-2 |  | 187 | 125.18 | 234.0866 |  |  | Hoskins 345/230kV New Transformer CKT3 | Build a new 345/230kV transformer at Hoskins as a third circuit
00NR | NRIS | Thermal | CIMARON4 - CIMARON2 138 1 | 24SP, 29SP | P13:138-345:OKGE:BKRBKR_3W020 |  | 478 | 104.17 | 497.9326 |  |  | Cimarron 345/138kV New Transformer CKT3 | Build a new 345/138kV transformer at Cimarron as a third circuit
00NR | NRIS | Thermal | CIMARON4 - CIMARON2 138 1 | 20SP | P13:138-345:OKGE:BKRBKR_3W020 |  | 478 | 105.29 | 503.2862 |  |  | Cimarron 345/138kV New Transformer CKT3 | Build a new 345/138kV transformer at Cimarron as a third circuit
00NR | NRIS | Thermal | CIMARON7 - CIMARON2 138 1 | 20SP24SP, 29SP | P13:138-345:OKGE:BKRBKR_3W020 |  | 478 | 109.48 | 523.3144 |  |  | Cimarron 345/138kV New Transformer CKT3 | Build a new 345/138kV transformer at Cimarron as a third circuit
00NR | NRIS | Thermal | MTVERN 7 - STORLA__-BE7 115 1 | 20SP, 24SP, 24WP, | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F). |  | 92 | 138.85 | 127.742 |  |  | Mt. Vernon to Storla 115kV Rebuild | Rebuild the existing Mt. Vernon to Storla 115kV 15.0 mile line to achieve a minimum summer/emergency rating of 128 MVA
00NR | NRIS | Thermal | UTICAJC7 - NAPA JCT7 115 1 | 29SP | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F). |  | 120 | 112.06 | 134.472 |  |  | Utica Jct. to Napa Jct. 115kV Rebuild | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA
13ALL | ERIS | Non-Converge | Non-Converge |  | P14:345:GMO-OPPD:S3458 REACTOR |  |  |  | 0 |  |  | Cooper to Holt 345kV New Build | Build a new 32 mile 345kV line from Cooper to Holt
15ALL | ERIS | Non-Converge | Non-Converge |  | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT |  |  |  | 0 |  |  | Chappelle Creek to Ft. Thompson 345k New Build CKT 2 | Build a new 30 mile 345kV line from Chappelle Creek to Ft. Thompson as a second circuit
09ALL | ERIS | Thermal | MOORE 3 - MONOLITH 3 345 | 24L24WP, | P22:345:OPPD:S3458-COOPER |  | 956 | 102.69 | 981.7164 |  |  | Moore to Monolith 345kV Rebuild | Rebuild the existing Moore to Monolith 345kV 0.75 mile line to achieve a minimum winter/emergency rating of 982 MVA
00NR | NRIS | Thermal | CARTHAG5 - LAR382 5 161 1 | 24WP, 29SP | P22:345:SPRM-AECI:17 |  | 222 | 108.78 | 241.4916 |  |  | Carthage to LaRussell Energy Center 161kV Rebuild | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA
00NR | NRIS | Thermal | BEAVER 5 - EUREKA 5 161 | 19WP, 24WP | P22:345:SPRM-AECI:17 |  | 317 | 131.27 | 416.1259 |  |  | Beaver to Eureka 161kV Rebuild | Rebuild the existing Eureka to Beaver 161kV 7.22 mile line to achieve a minimum winter/emergency rating of 417 MVA
00NR | NRIS | Thermal | 5OSAGE CRK#! - EUREKA 5 161 1 | 19WP20SP24SP, 24WP, 29SP | P22:345:SPRM-AECI:17 |  | 220 | 150.79 | 331.738 |  |  | Eureka to Osage 161kV Rebuild | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA
00NR | NRIS | Thermal | SPRGFLD5 - LAR382 5 161 1 | 24WP, 29SP | P22:345:SPRM-AECI:17 |  | 167 | 119.8 | 200.066 |  |  | Springfield to LaRussell Energy Center 161kV Rebuild | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA
00NR | NRIS | Thermal | 5OSAGE CRK#! - EUREKA 5 161 1 | 19WP20SP24SP, 24WP, 29SP | P22:345:SPRM-AECI:17 |  | 220 | 150.79 | 331.738 |  |  | Eureka to Osage 161kV Rebuild | Rebuild the existing Northwest to Matthewson 345kV 11.1 mile line to achieve a minimum light/emergency rating of 1301 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P22:345:SPS:EDDY_COUNTY_19L |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P22:345:SPS:EDDY_COUNTY_19L |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P22:345:SPS:EDDY_COUNTY_19L |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P22:345:SPS:EDDY_COUNTY_19L |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P22:345:SPS:EDDY_COUNTY_19L |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P22:345:SPS:EDDY_COUNTY_19L |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P22:345:SPS:EDDY_COUNTY_19L |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P22:345:SPS:EDDY_COUNTY_19L |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P22:345:SPS:EDDY_COUNTY_19L |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
00NR | NRIS | Thermal | IATAN 7 - G17-030-TAP 345 1 | 19WP20SP24SP, 24WP, 29SP | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33 |  | 1136 | 122.91 | 1396.2576 |  |  | G17-030 Tap to Iatan 345kV Rebuild | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA
00NR | NRIS | Thermal | HAWTH 7 - HAWTHORN22 161 22 | 19WP20SP24SP, 24WP, 29SP | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 |  | 605 | 127.82 | 773.311 |  |  | Hawthorne 345/161kV New Transformer CKT3 | Build a new 345/161kV transformer at Hawthorne as a third circuit
00NR | NRIS | Thermal | HAWTHN5 - HAWTHORN22 161 22 | 19WP20SP24SP, 24WP, 29SP | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 |  | 605 | 129.87 | 785.7135 |  |  | Hawthorne 345/161kV New Transformer CKT3 | Build a new 345/161kV transformer at Hawthorne as a third circuit
00NR | NRIS | Thermal | HAWTH 7 - HAWTHORN22 161 22 | 19WP20SP24SP, 24WP, 29SP | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 |  | 605 | 127.82 | 773.311 |  |  | Nashua to Sibley 345kV New Build | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA
00NR | NRIS | Thermal | HAWTHN5 - HAWTHORN22 161 22 | 19WP20SP24SP, 24WP, 29SP | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20 |  | 605 | 129.87 | 785.7135 |  |  | Nashua to Sibley 345kV New Build | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA
00NR | NRIS | Thermal | NASHUA 7 - NASHUA11 161 11 | 19WP24SP, 24WP, 29SP | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20 |  | 715 | 125.51 | 897.3965 |  |  | Nashua to Sibley 345kV New Build | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA
00NR | NRIS | Thermal | NASHUA-5 - NASHUA11 161 11 | 19WP24SP, 24WP, 29SP | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20 |  | 715 | 125.07 | 894.2505 |  |  | Nashua to Sibley 345kV New Build | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA
00NR | NRIS | Thermal | SIBLEY 5 - SIBLEY11 161 11 | 20SP, 24SP | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22 |  | 440 | 110.59 | 486.596 |  |  | Hawthorne 345/161kV New Transformer CKT3 | Build a new 345/161kV transformer at Hawthorne as a third circuit
00NR | NRIS | Thermal | SIBLEY 5 - SIBLEYPL 161 1 | 20SP | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22 |  | 446 | 113.58 | 506.5668 |  |  | Hawthorne 345/161kV New Transformer CKT3 | Build a new 345/161kV transformer at Hawthorne as a third circuit
00NR | NRIS | Thermal | SIBLEY 7 - SIBLEY11 161 11 | 20SP | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22 |  | 440 | 109.54 | 481.976 |  |  | Hawthorne 345/161kV New Transformer CKT3 | Build a new 345/161kV transformer at Hawthorne as a third circuit
00NR | NRIS | Thermal | SIBLEY 5 - SIBLEY11 161 11 | 20SP, 24SP | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22 |  | 440 | 110.59 | 486.596 |  |  | Nashua to Sibley 345kV New Build | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA
00NR | NRIS | Thermal | SIBLEY 5 - SIBLEYPL 161 1 | 20SP | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22 |  | 446 | 113.58 | 506.5668 |  |  | Nashua to Sibley 345kV New Build | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA
00NR | NRIS | Thermal | SIBLEY 7 - SIBLEY11 161 11 | 20SP | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22 |  | 440 | 109.54 | 481.976 |  |  | Nashua to Sibley 345kV New Build | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA
00NR | NRIS | Thermal | HAWTH 7 - HAWTHORN20 161 20 | 19WP20SP24SP, 24WP, 29SP | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 |  | 550 | 132.87 | 730.785 |  |  | Hawthorne 345/161kV New Transformer CKT3 | Build a new 345/161kV transformer at Hawthorne as a third circuit
00NR | NRIS | Thermal | HAWTHN5 - HAWTHORN20 161 20 | 19WP20SP24SP, 24WP, 29SP | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 |  | 550 | 134.09 | 737.495 |  |  | Hawthorne 345/161kV New Transformer CKT3 | Build a new 345/161kV transformer at Hawthorne as a third circuit
00NR | NRIS | Thermal | HAWTH 7 - HAWTHORN20 161 20 | 19WP20SP24SP, 24WP, 29SP | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 |  | 550 | 132.87 | 730.785 |  |  | Nashua to Sibley 345kV New Build | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA
00NR | NRIS | Thermal | HAWTHN5 - HAWTHORN20 161 20 | 19WP20SP24SP, 24WP, 29SP | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22 |  | 550 | 134.09 | 737.495 |  |  | Nashua to Sibley 345kV New Build | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA
00NR | NRIS | Thermal | DIANA 7 - DIANA 3 138 3 | 19WP | P23:345:AEPW:DIANA CB 11900 NBTB |  | 473 | 104.07 | 492.2511 |  |  | Diana 345kV Substation Upgrade | Update breaker configuration at Diana 345kV
00NR | NRIS | Thermal | SILOAM 5 - SILMCTY5 161 1 | 29SP | P23:345:AEPW:FLINT CREEK CB 19140 NBTB |  | 464 | 106.16 | 492.5824 |  |  | Tonnece to Tontitown 345kV New Build | Build a new 18 mile 345kV line from Tonnece to Tontitown
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco
08ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
08ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
08ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
08ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
00NR | NRIS | Thermal | LYDIA 7 - WELSH 7 345 1 | 19WP20SP24SP, 24WP, | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB |  | 1183 | 133.19 | 1575.6377 |  |  | Lydia 345kV Reactive Support | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation
00NR | NRIS | Thermal | LYDIA 7 - WELSH 7 345 1 | 19WP20SP24SP, 24WP, | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB |  | 1183 | 133.19 | 1575.6377 |  |  | Northwest Texarkana 345kV Reactive Support | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation
00NR | NRIS | Thermal | LYDIA 7 - WELSH 7 345 1 | 19WP20SP24SP, 24WP, | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB |  | 1183 | 133.19 | 1575.6377 |  |  | Northwest Texarkana to Wilkes 345kV New Build | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes
00NR | NRIS | Thermal | LYDIA 7 - WELSH 7 345 1 | 19WP20SP24SP, 24WP, | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB |  | 1183 | 133.19 | 1575.6377 |  |  | Valiant to Turk 345kV New Build | Build a new 84 mile 345kV line from Valiant to Turk
00NR | NRIS | Thermal | LYDIA 7 - VALIANT7 345 1 | 19WP20SP24SP, 24WP, 29SP | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB |  | 1324 | 142.9 | 1891.996 |  |  | Lydia 345kV Reactive Support | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation
00NR | NRIS | Thermal | LYDIA 7 - VALIANT7 345 1 | 19WP20SP24SP, 24WP, 29SP | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB |  | 1324 | 142.9 | 1891.996 |  |  | Northwest Texarkana 345kV Reactive Support | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation
00NR | NRIS | Thermal | LYDIA 7 - VALIANT7 345 1 | 19WP20SP24SP, 24WP, 29SP | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB |  | 1324 | 142.9 | 1891.996 |  |  | Northwest Texarkana to Wilkes 345kV New Build | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes
00NR | NRIS | Thermal | LYDIA 7 - VALIANT7 345 1 | 19WP20SP24SP, 24WP, 29SP | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB |  | 1324 | 142.9 | 1891.996 |  |  | Valiant to Lydia 345kV New Build CKT 2 | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit
00NR | NRIS | Thermal | LYDIA 7 - VALIANT7 345 1 | 19WP20SP24SP, 24WP, 29SP | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB |  | 1324 | 142.9 | 1891.996 |  |  | Valiant to Turk 345kV New Build | Build a new 84 mile 345kV line from Valiant to Turk
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
00NR | NRIS | Thermal | PITTSB-7 - VALIANT7 345 2 | 19WP | P23:345:AEPW:PITTSBURG CB 3425A NBTB |  | 1143 | 100.32 | 1146.6576 |  |  | Pittsburg to Valiant 345kV Rebuild | Rebuild the existing Pittsburg to Valiant 345kV 70.2 mile line to achieve a minimum winter/emergency rating of 1147 MVA
00NR | NRIS | Thermal | ARBUCKL4 - MILL4 138 1 | 24WP, | P23:345:AEPW:PITTSBURG CB 3441A NBTB |  | 191 | 110.88 | 211.7808 |  |  | Arbuckle to Millcreek Tap 138kV Rebuild | Rebuild the existing Arbuckle to Mill Creek Tap 138kV 13.16 mile line to achieve a minimum winter/emergency rating of 212 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
08ALL | ERIS | Thermal | DOMES 4 - WESTERNWALL4 138 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:AEPW:TULSA NORTH CB 3413A NBTB |  | 152 | 142.07 | 215.9464 |  |  | Domes to Western Walls 138kV Rebuild | Rebuild the existing Domes to Western Walls 138kV 5.74 mile line to achieve a minimum winter/emergency rating of 236 MVA
08ALL | ERIS | Thermal | WPAWHSK4 - SHIDLER4 138 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:AEPW:TULSA NORTH CB 3413A NBTB |  | 152 | 151.76 | 230.6752 |  |  | West Pawhuska to Shidler 138kV Rebuild | Rebuild the existing West Pawhuska to Shidler 138kV 16.11 mile line to achieve a minimum winter/emergency rating of 246 MVA
08ALL | ERIS | Thermal | WPAWHSK4 - WESTERNWALL4 138 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P23:345:AEPW:TULSA NORTH CB 3413A NBTB |  | 152 | 150.57 | 228.8664 |  |  | West Pawhuska to Western Walls 138kV Rebuild | Rebuild the existing West Pawhuska to Western Walls 138kV 5.98 mile line to achieve a minimum spring/emergency rating of 244 MVA
00NR | NRIS | Thermal | WELSH 7 - WILKES 7 345 1 | 19WP20SP24SP, 24WP, 29SP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 1220 | 118.92 | 1450.824 |  |  | Lydia 345kV Reactive Support | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation
00NR | NRIS | Thermal | WILKES 4 - WILKES 138 1 | 19WP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 597 | 103.78 | 619.5666 |  |  | Lydia 345kV Reactive Support | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation
00NR | NRIS | Thermal | WILKES 7 - WILKES 138 1 | 19WP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 597 | 102.87 | 614.1339 |  |  | Lydia 345kV Reactive Support | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation
00NR | NRIS | Thermal | WELSH 7 - WILKES 7 345 1 | 19WP20SP24SP, 24WP, 29SP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 1220 | 118.92 | 1450.824 |  |  | Northwest Texarkana 345kV Reactive Support | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation
00NR | NRIS | Thermal | WILKES 4 - WILKES 138 1 | 19WP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 597 | 103.78 | 619.5666 |  |  | Northwest Texarkana 345kV Reactive Support | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation
00NR | NRIS | Thermal | WILKES 7 - WILKES 138 1 | 19WP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 597 | 102.87 | 614.1339 |  |  | Northwest Texarkana 345kV Reactive Support | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation
00NR | NRIS | Thermal | WELSH 7 - WILKES 7 345 1 | 19WP20SP24SP, 24WP, 29SP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 1220 | 118.92 | 1450.824 |  |  | Northwest Texarkana to Wilkes 345kV New Build | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes
00NR | NRIS | Thermal | WILKES 4 - WILKES 138 1 | 19WP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 597 | 103.78 | 619.5666 |  |  | Northwest Texarkana to Wilkes 345kV New Build | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes
00NR | NRIS | Thermal | WILKES 7 - WILKES 138 1 | 19WP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 597 | 102.87 | 614.1339 |  |  | Northwest Texarkana to Wilkes 345kV New Build | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes
00NR | NRIS | Thermal | WELSH 7 - WILKES 7 345 1 | 19WP20SP24SP, 24WP, 29SP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 1220 | 118.92 | 1450.824 |  |  | Valiant to Lydia 345kV New Build CKT 2 | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit
00NR | NRIS | Thermal | WILKES 4 - WILKES 138 1 | 19WP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 597 | 103.78 | 619.5666 |  |  | Valiant to Lydia 345kV New Build CKT 2 | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit
00NR | NRIS | Thermal | WILKES 7 - WILKES 138 1 | 19WP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 597 | 102.87 | 614.1339 |  |  | Valiant to Lydia 345kV New Build CKT 2 | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit
00NR | NRIS | Thermal | WELSH 7 - WILKES 7 345 1 | 19WP20SP24SP, 24WP, 29SP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 1220 | 118.92 | 1450.824 |  |  | Valiant to Turk 345kV New Build | Build a new 84 mile 345kV line from Valiant to Turk
00NR | NRIS | Thermal | WILKES 4 - WILKES 138 1 | 19WP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 597 | 103.78 | 619.5666 |  |  | Valiant to Turk 345kV New Build | Build a new 84 mile 345kV line from Valiant to Turk
00NR | NRIS | Thermal | WILKES 7 - WILKES 138 1 | 19WP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 597 | 102.87 | 614.1339 |  |  | Valiant to Turk 345kV New Build | Build a new 84 mile 345kV line from Valiant to Turk
00NR | NRIS | Thermal | LONGWD 7 - WILKES 7 345 1 | 19WP29SP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 776 | 105.47 | 818.4472 |  |  | Wilkes to Diana 345kV New Build | Build a new 12.5 mile 345kV line from Wilkes to Diana
09ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER |  |  |  | 0 |  |  | Cooper 345kV Reactive Support | Install a 200 MVAR capacitor bank at Cooper 345kV Substation
09ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER |  |  |  | 0 |  |  | Cooper to Hoyt 345kV New Build | Build a new 95 mile 345kV line from Cooper to Hoyt
00NR | NRIS | Thermal | KINZE 4 - UNVRSTY4 138 1 | 20SP24SP, 29SP | P23:345:GRDA:CLEVLND CB10180 |  | 222 | 104.18 | 231.2796 |  |  | Kenzie to University 138kV Rebuild | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA
00NR | NRIS | Thermal | MCELROY4 - UNVRSTY4 138 1 | 20SP24SP, 29SP | P23:345:GRDA:CLEVLND CB10180 |  | 222 | 110.6 | 245.532 |  |  | McElroy to University 138kV Rebuild | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA
00NR | NRIS | Thermal | KINZE 4 - UNVRSTY4 138 1 | 20SP24SP, 29SP | P23:345:GRDA:CLEVLND CB10180 |  | 222 | 104.18 | 231.2796 |  |  | Kenzie to University 138kV Rebuild | Rebuild the existing Northwest to Matthewson 345kV 11.1 mile line to achieve a minimum light/emergency rating of 1301 MVA
08ALL | ERIS | Thermal | 7BLACKBERRY - NEOSHO 7 345 | 20G, 24WP | P23:345:GRDA:GRDA CB9080 |  | 870 | 104.35 | 907.845 |  |  | Wolf Creek to Blackberry 345kV | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA
00NR | NRIS | Thermal | NEO SPA5 - TIP292 5 161 1 | 29SP | P23:345:GRDA:GRDA CB9580 |  | 222 | 108.4 | 240.648 |  |  | Neosho South to Tipton Ford 161kV Rebuild | Rebuild the existing Neosho South to Tipton Ford 161kV 10.6 mile line to achieve a minimum summer/emergency rating of 241 MVA
13ALL | ERIS | Thermal | 87TH7 - CRAIG7 345 | 20G | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN |  | 1254 | 112.91 | 1415.8914 |  |  | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA
13ALL | ERIS | Thermal | STRANGR7 - 87TH7 345kV | 19WP, 20G, 20SP, 24WP, 29SP | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN | 1195 | 1195 | 126.88 | 1516.216 |  |  | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA
00NR | NRIS | Thermal | BENTON 7 - WICHITA7 345 1 | 19WP20SP24SP, 24WP, 29SP | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE |  | 956 | 125.82 | 1202.8392 |  |  | Wichita to Benton 345kV New Build CKT 2 | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit
00NR | NRIS | Thermal | BENTON 7 - WICHITA7 345 1 | 19WP20SP24SP, 24WP, 29SP | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE |  | 956 | 125.82 | 1202.8392 |  |  | Wichita to Benton 345kV Rebuild | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA
00NR | NRIS | Thermal | HOSKINS3 - SHELCRK3 345 1 | 24WP, | P23:345:OPPD:S3451-RAUN&T4 |  | 956 | 101.64 | 971.6784 |  |  | Hoskins to Shell Creek 345kV New Build CKT 2 | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit
00NR | NRIS | Thermal | RAUN 5 - TEKAMAH5 161 1 | 19WP | P23:345:OPPD:S3451-RAUN&T4 |  | 217 | 175.78 | 381.4426 |  |  | Raun to Tekamah 161kV Rebuild | Rebuild the existing Raun to Tekamah 37.07 mile line to achieve a minimum winter/emergency rating of 382 MVA
00NR | NRIS | Thermal | SIOUXCY2 - SC2 KU1B 230 1 | 19WP | P23:345:OPPD:S3451-RAUN&T4 |  | 250 | 106.31 | 265.775 |  |  | Sioux City 230kV Substation Upgrade | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA
00NR | NRIS | Thermal | SIOUXCY2 - SIOUXCY4 230 Z | 19WP20SP24SP, 24WP, 29SP | P23:345:OPPD:S3451-RAUN&T4 |  | 341 | 199.77 | 681.2157 |  |  | Sioux City 230kV Substation Upgrade | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA
00NR | NRIS | Thermal | SIOUXCY3 - SC2 KU1B 230 1 | 19WP | P23:345:OPPD:S3451-RAUN&T4 |  | 250 | 106.7 | 266.75 |  |  | Sioux City 230kV Substation Upgrade | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA
13ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:OPPD:S3458-HOLT |  |  |  | 0 |  |  | Cooper to Holt 345kV New Build | Build a new 32 mile 345kV line from Cooper to Holt
02ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Finney 345kV Reactive Support | Install a new 250 MVAR capacitor bank at Finney 345kV Substation
02ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Grapevine 345kV New Substation | Build a new 345kV substation at Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Grapevine 345kV New Substation | Build a new 345kV substation at Grapevine
02ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
09ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Mingo to Post Rock 345kV New Build | Build a new 100 mile 345kV line from Mingo to Post Rock
02ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK188 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Finney 345kV Reactive Support | Install a new 250 MVAR capacitor bank at Finney 345kV Substation
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Grapevine 345kV New Substation | Build a new 345kV substation at Grapevine
02ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Grapevine 345kV New Substation | Build a new 345kV substation at Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
02ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK282 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
09ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:HLC_BRK382 |  |  |  | 0 |  |  | Mingo to Post Rock 345kV New Build | Build a new 100 mile 345kV line from Mingo to Post Rock
09ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK182 |  |  |  | 0 |  |  | Mingo to Post Rock 345kV New Build | Build a new 100 mile 345kV line from Mingo to Post Rock
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK188 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK188 |  |  |  | 0 |  |  | Finney 345kV Reactive Support | Install a new 250 MVAR capacitor bank at Finney 345kV Substation
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK188 |  |  |  | 0 |  |  | Grapevine 345kV New Substation | Build a new 345kV substation at Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK188 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
09ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK188 |  |  |  | 0 |  |  | Mingo to Post Rock 345kV New Build | Build a new 100 mile 345kV line from Mingo to Post Rock
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK188 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK382 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK382 |  |  |  | 0 |  |  | Finney 345kV Reactive Support | Install a new 250 MVAR capacitor bank at Finney 345kV Substation
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK382 |  |  |  | 0 |  |  | Grapevine 345kV New Substation | Build a new 345kV substation at Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK382 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
09ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK382 |  |  |  | 0 |  |  | Mingo to Post Rock 345kV New Build | Build a new 100 mile 345kV line from Mingo to Post Rock
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK382 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
04ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK388 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
04ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK388 |  |  |  | 0 |  |  | Finney 345kV Reactive Support | Install a new 250 MVAR capacitor bank at Finney 345kV Substation
04ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK388 |  |  |  | 0 |  |  | Grapevine 345kV New Substation | Build a new 345kV substation at Grapevine
04ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK388 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
09ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK388 |  |  |  | 0 |  |  | Mingo to Post Rock 345kV New Build | Build a new 100 mile 345kV line from Mingo to Post Rock
04ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:MO_BRK388 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
09ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:SB_BRK482 |  |  |  | 0 |  |  | Mingo to Post Rock 345kV New Build | Build a new 100 mile 345kV line from Mingo to Post Rock
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:SB_BRK488 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:SB_BRK488 |  |  |  | 0 |  |  | Finney 345kV Reactive Support | Install a new 250 MVAR capacitor bank at Finney 345kV Substation
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:SB_BRK488 |  |  |  | 0 |  |  | Grapevine 345kV New Substation | Build a new 345kV substation at Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:SB_BRK488 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
09ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:SB_BRK488 |  |  |  | 0 |  |  | Mingo to Post Rock 345kV New Build | Build a new 100 mile 345kV line from Mingo to Post Rock
03ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:SB_BRK488 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
09ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:SUNC:SB_BRK582 |  |  |  | 0 |  |  | Mingo to Post Rock 345kV New Build | Build a new 100 mile 345kV line from Mingo to Post Rock
00NR | NRIS | Thermal | NELIGH 7 - PETERSBRG.N7 115 1 | 20SP | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT |  | 137 | 111.37 | 152.5769 |  |  | Shell Creek to Grand Island 345kV New Build | Build a new 72 mile 345kV line from Shell Creek to Grand Island
15ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992) |  |  |  | 0 |  |  | Chappelle Creek to Ft. Thompson 345k New Build CKT 2 | Build a new 30 mile 345kV line from Chappelle Creek to Ft. Thompson as a second circuit
15ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992) |  |  |  | 0 |  |  | Cooper to Holt 345kV New Build | Build a new 32 mile 345kV line from Cooper to Holt
15ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996) |  |  |  | 0 |  |  | Chappelle Creek to Ft. Thompson 345k New Build CKT 2 | Build a new 30 mile 345kV line from Chappelle Creek to Ft. Thompson as a second circuit
15ALL | ERIS | Non-Converge | Non-Converge |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996) |  |  |  | 0 |  |  | Cooper to Holt 345kV New Build | Build a new 32 mile 345kV line from Cooper to Holt
00NR | NRIS | Thermal | HAWTH 7 - NASHUA 7 345 1 | 20SP, 24SP, 24WP, 29SP | P23:345:WERE:87TH_345_BKRS:: |  | 1136 | 144.98 | 1646.9728 |  |  | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA
00NR | NRIS | Thermal | SWISVAL7 - W.GRDNR7 345 1 | 20SP | P23:345:WERE:87TH_345_BKRS:: |  | 956 | 107.29 | 1025.6924 |  |  | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA
00NR | NRIS | Thermal | BENTON 4 - BENT TX-2 138 1 | 20SP24SP, 29SP | P23:345:WERE:BENT_345-50:: |  | 440 | 121.78 | 535.832 |  |  | Benton to Rose Hill 345kV New Build CKT 2 | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit
00NR | NRIS | Thermal | BENTON 7 - BENT TX-2 138 1 | 20SP, 24SP, 24WP, 29SP | P23:345:WERE:BENT_345-50:: |  | 440 | 121.54 | 534.776 |  |  | Benton to Rose Hill 345kV New Build CKT 2 | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit
00NR | NRIS | Thermal | BENTON 4 - BENT TX-2 138 1 | 20SP24SP, 29SP | P23:345:WERE:BENT_345-50:: |  | 440 | 121.78 | 535.832 |  |  | Wichita to Benton 345kV New Build CKT 2 | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit
00NR | NRIS | Thermal | BENTON 7 - BENT TX-2 138 1 | 20SP, 24SP, 24WP, 29SP | P23:345:WERE:BENT_345-50:: |  | 440 | 121.54 | 534.776 |  |  | Wichita to Benton 345kV New Build CKT 2 | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit
00NR | NRIS | Thermal | BENTON 4 - BENT TX-2 138 1 | 20SP24SP, 29SP | P23:345:WERE:BENT_345-50:: |  | 440 | 121.78 | 535.832 |  |  | Wichita to Benton 345kV Rebuild | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA
00NR | NRIS | Thermal | BENTON 7 - BENT TX-2 138 1 | 20SP, 24SP, 24WP, 29SP | P23:345:WERE:BENT_345-50:: |  | 440 | 121.54 | 534.776 |  |  | Wichita to Benton 345kV Rebuild | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA
00NR | NRIS | Thermal | KELLY 5 - TECHILL5 161 1 | 19WP | P23:345:WERE:HOYT_345_BKRS:: |  | 123 | 107.04 | 131.6592 |  |  | Kelly to Tecumseh Hill 161kV Rebuild | Rebuild the existing Northwest to Matthewson 345kV 11.1 mile line to achieve a minimum light/emergency rating of 1301 MVA
13ALL | ERIS | Thermal | HAWTH7 - NASHUA7 345 | 20G | P23:345:WERE:STRA_345-100:: |  | 1325 | 100.69 | 1334.1425 |  |  | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA
08ALL | ERIS | Thermal | FARBER 4 - SC10BEL4 138 | 20SP, 24SP | P23:345:WERE:WICH_345-116:: |  | 160 | 106.97 | 171.152 |  |  | Farber to Belle Plaine 138kV Rebuild | Rebuild the existing Farber to Belle Plain 138kV 10.33 mile line to achieve a minimum summer/emergency rating of 172 MVA
08ALL | ERIS | Thermal | VIOLA 4 - VIOLA TX-1 138 | 20SP24SP, 29SP | P23:345:WERE:WICH_345-116:: |  | 440 | 110.99 | 488.356 |  |  | Viola 345/138kV New Transformer CKT 2 | Build a new 345/138kV transformer as a second circuit
08ALL | ERIS | Thermal | VIOLA 345/138XFR | 20SP24SP, 29SP | P23:345:WERE:WICH_345-116:: |  | 440 | 113.48 | 499.312 |  |  | Viola 345/138kV New Transformer CKT 2 | Build a new 345/138kV transformer as a second circuit
00NR | NRIS | Thermal | EVANS N4 - WICH TX-11 138 1 | 20SP24SP, 29SP | P23:345:WERE:WICH_345-80:: |  | 430 | 108.79 | 467.797 |  |  | Wichita to Benton 345kV New Build CKT 2 | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit
00NR | NRIS | Thermal | WICHITA7 - WICH TX-11 138 1 | 20SP24SP, 29SP | P23:345:WERE:WICH_345-80:: |  | 430 | 110 | 473 |  |  | Wichita to Benton 345kV New Build CKT 2 | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit
00NR | NRIS | Thermal | EVANS N4 - WICH TX-11 138 1 | 20SP24SP, 29SP | P23:345:WERE:WICH_345-80:: |  | 430 | 108.79 | 467.797 |  |  | Wichita to Benton 345kV Rebuild | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA
00NR | NRIS | Thermal | WICHITA7 - WICH TX-11 138 1 | 20SP24SP, 29SP | P23:345:WERE:WICH_345-80:: |  | 430 | 110 | 473 |  |  | Wichita to Benton 345kV Rebuild | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA
00NR | NRIS | Thermal | LAWRENC7 - SIOUXFL7 115 1 | 24WP, | P23:345:XEL:396 BKR SPK |  | 262 | 112.3 | 294.226 |  |  | Lawrence to Sioux Falls 115kV Rebuild | Rebuild the existing Lawrence to Sioux Falls 115kV 1.0 mile line to achieve a minimum winter/emergency rating of 295 MVA
00NR | NRIS | Non-Converge | Non-Converge |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT |  |  |  | 0 |  |  | Eastowne 161kV Reactive Support | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT |  |  |  | 0 |  |  | Hawthorne to Craig 345kV New Build | Build a new 25 mile 345kV line from Hawthorn to Craig
00NR | NRIS | Non-Converge | Non-Converge |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT |  |  |  | 0 |  |  | Longwood 345kV Reactive Support | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT |  |  |  | 0 |  |  | Mark Moore 161kV Reactive Support | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT |  |  |  | 0 |  |  | Mark Moore to Elm Creek 345kV New Build | Build a new 102 mile 345kV line from Mark Moore to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT |  |  |  | 0 |  |  | Sibley 161kV Reactive Support | Install a 100 MVAR capacitor bank at Sibley 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT |  |  |  | 0 |  |  | Southwest Shreveport 345kV Reactive Support | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT |  |  |  | 0 |  |  | Valiant to Petersburg 345kV New Build CKT 2 | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco
08ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
08ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
08ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
08ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT |  |  |  | 0 |  |  | Eastowne 161kV Reactive Support | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT |  |  |  | 0 |  |  | Hawthorne to Craig 345kV New Build | Build a new 25 mile 345kV line from Hawthorn to Craig
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT |  |  |  | 0 |  |  | Longwood 345kV Reactive Support | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT |  |  |  | 0 |  |  | Mark Moore 161kV Reactive Support | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT |  |  |  | 0 |  |  | Mark Moore to Elm Creek 345kV New Build | Build a new 102 mile 345kV line from Mark Moore to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT |  |  |  | 0 |  |  | Sibley 161kV Reactive Support | Install a 100 MVAR capacitor bank at Sibley 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT |  |  |  | 0 |  |  | Southwest Shreveport 345kV Reactive Support | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT |  |  |  | 0 |  |  | Valiant to Petersburg 345kV New Build CKT 2 | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 1N20 NBTB+FAULT |  |  |  | 0 |  |  | Eastowne 161kV Reactive Support | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 1N20 NBTB+FAULT |  |  |  | 0 |  |  | Hawthorne to Craig 345kV New Build | Build a new 25 mile 345kV line from Hawthorn to Craig
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 1N20 NBTB+FAULT |  |  |  | 0 |  |  | Longwood 345kV Reactive Support | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 1N20 NBTB+FAULT |  |  |  | 0 |  |  | Mark Moore 161kV Reactive Support | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 1N20 NBTB+FAULT |  |  |  | 0 |  |  | Mark Moore to Elm Creek 345kV New Build | Build a new 102 mile 345kV line from Mark Moore to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 1N20 NBTB+FAULT |  |  |  | 0 |  |  | Sibley 161kV Reactive Support | Install a 100 MVAR capacitor bank at Sibley 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 1N20 NBTB+FAULT |  |  |  | 0 |  |  | Southwest Shreveport 345kV Reactive Support | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:LONGWOOD CB 1N20 NBTB+FAULT |  |  |  | 0 |  |  | Valiant to Petersburg 345kV New Build CKT 2 | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT |  |  |  | 0 |  |  | Eastowne 161kV Reactive Support | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT |  |  |  | 0 |  |  | Hawthorne to Craig 345kV New Build | Build a new 25 mile 345kV line from Hawthorn to Craig
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT |  |  |  | 0 |  |  | Longwood 345kV Reactive Support | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT |  |  |  | 0 |  |  | Mark Moore 161kV Reactive Support | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT |  |  |  | 0 |  |  | Mark Moore to Elm Creek 345kV New Build | Build a new 102 mile 345kV line from Mark Moore to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT |  |  |  | 0 |  |  | Sibley 161kV Reactive Support | Install a 100 MVAR capacitor bank at Sibley 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT |  |  |  | 0 |  |  | Southwest Shreveport 345kV Reactive Support | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT |  |  |  | 0 |  |  | Valiant to Petersburg 345kV New Build CKT 2 | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT |  |  |  | 0 |  |  | Eastowne 161kV Reactive Support | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT |  |  |  | 0 |  |  | Hawthorne to Craig 345kV New Build | Build a new 25 mile 345kV line from Hawthorn to Craig
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT |  |  |  | 0 |  |  | Longwood 345kV Reactive Support | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT |  |  |  | 0 |  |  | Mark Moore 161kV Reactive Support | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT |  |  |  | 0 |  |  | Mark Moore to Elm Creek 345kV New Build | Build a new 102 mile 345kV line from Mark Moore to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT |  |  |  | 0 |  |  | Sibley 161kV Reactive Support | Install a 100 MVAR capacitor bank at Sibley 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT |  |  |  | 0 |  |  | Southwest Shreveport 345kV Reactive Support | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT |  |  |  | 0 |  |  | Valiant to Petersburg 345kV New Build CKT 2 | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
08ALL | ERIS | Thermal | DOMES 4 - ELIZACK4 138 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT |  | 152 | 138.21 | 210.0792 |  |  | Domes to Elizack 138kV Rebuild | Rebuild the existing Domes to Elizack 138kV 13.59 mile line to achieve a minimum winter/emergency rating of 231 MVA
00NR | NRIS | Thermal | COLMB.E7 - COL.EAST T3 115 1 | 19WP20SP24SP, 24WP, 29SP | P42:345:NPPD:BKR-CE-3306 |  | 187 | 118.8 | 222.156 |  |  | Shell Creek to Grand Island 345kV New Build | Build a new 72 mile 345kV line from Shell Creek to Grand Island
00NR | NRIS | Thermal | E.COL. 4 - COL.EAST T3 115 1 | 19WP20SP24SP, 24WP, 29SP | P42:345:NPPD:BKR-CE-3306 |  | 187 | 122.1 | 228.327 |  |  | Shell Creek to Grand Island 345kV New Build | Build a new 72 mile 345kV line from Shell Creek to Grand Island
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:NPPD:BKR-CPR-3304 |  |  |  | 0 |  |  | Eastowne 161kV Reactive Support | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:NPPD:BKR-CPR-3304 |  |  |  | 0 |  |  | Hawthorne to Craig 345kV New Build | Build a new 25 mile 345kV line from Hawthorn to Craig
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:NPPD:BKR-CPR-3304 |  |  |  | 0 |  |  | Mark Moore 161kV Reactive Support | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:NPPD:BKR-CPR-3304 |  |  |  | 0 |  |  | Mark Moore to Elm Creek 345kV New Build | Build a new 102 mile 345kV line from Mark Moore to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge |  | P42:345:NPPD:BKR-CPR-3304 |  |  |  | 0 |  |  | Sibley 161kV Reactive Support | Install a 100 MVAR capacitor bank at Sibley 161kV Substation
00NR | NRIS | Thermal | COLMBUS4 - MEADOWGROVE4 230 1 | 19WP | P42:345:NPPD:BKR-HOS-3308 |  | 387 | 102.91 | 398.2617 |  |  | Hoskins to Shell Creek 345kV New Build CKT 2 | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit
00NR | NRIS | Thermal | MADISON7 - NORFOLK7 115 1 | 19WP20SP24SP, 24WP, 29SP | P42:345:NPPD:BKR-HOS-3308 |  | 120 | 136.52 | 163.824 |  |  | Madison to Norfolk 115kV Rebuild | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA
00NR | NRIS | Thermal | RAUN 3 - S3451 3 345 1 | 19WP20SP24SP, 24WP, 29SP | P42:345:NPPD:BKR-HOS-3308 |  | 956 | 160.63 | 1535.6228 |  |  | Raun to S3451 345kV Rebuild | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA
00NR | NRIS | Thermal | COLMBUS4 - MEADOWGROVE4 230 1 | 19WP | P42:345:NPPD:BKR-HOS-3308 |  | 387 | 102.91 | 398.2617 |  |  | Shell Creek to Grand Island 345kV New Build | Build a new 72 mile 345kV line from Shell Creek to Grand Island
00NR | NRIS | Thermal | COLMBUS7 - CRESTON7 115 1 | 20SP, 24SP, 24WP, | P42:345:NPPD:BKR-HOS-3308 |  | 120 | 111.08 | 133.296 |  |  | Shell Creek to Grand Island 345kV New Build | Build a new 72 mile 345kV line from Shell Creek to Grand Island
00NR | NRIS | Thermal | CRESTON7 - MADISON7 115 1 | 19WP20SP24SP, 24WP, 29SP | P42:345:NPPD:BKR-HOS-3308 |  | 120 | 127.3 | 152.76 |  |  | Shell Creek to Grand Island 345kV New Build | Build a new 72 mile 345kV line from Shell Creek to Grand Island
00NR | NRIS | Thermal | MADISON7 - NORFOLK7 115 1 | 19WP20SP24SP, 24WP, 29SP | P42:345:NPPD:BKR-HOS-3308 |  | 120 | 136.52 | 163.824 |  |  | Shell Creek to Grand Island 345kV New Build | Build a new 72 mile 345kV line from Shell Creek to Grand Island
09ALL | ERIS | Thermal | HOSKINS3 - HOSKINS T2 230 | 19WP20SP24SP, 24WP, 29SP | P42:345:NPPD:BKR-HOS-3312 |  | 336 | 116.06 | 389.9616 |  |  | Hoskins 345/230kV Transformer Replacement | Replace the existing Hoskins 345/230kV transformer to achieve a minimum rating of 400 MVA
09ALL | ERIS | Thermal | HOSKINS4 - HOSKINS T2 230 | 19WP20SP24SP, 24WP, 29SP | P42:345:NPPD:BKR-HOS-3312 |  | 336 | 114.08 | 383.3088 |  |  | Hoskins 345/230kV Transformer Replacement | Replace the existing Hoskins 345/230kV transformer to achieve a minimum rating of 400 MVA
00NR | NRIS | Thermal | ALBION 7 - PETRSBG7 115 1 | 19WP24SP, 24WP, | P42:345:NPPD:BKR-HOS-3322 |  | 137 | 110.19 | 150.9603 |  |  | Albion to Petersburg 115kV Rebuild | Rebuild the existing Albion to Petersburg 115kV 12.13 mile line to achieve a minimum winter/emergency rating of 151 MVA
00NR | NRIS | Thermal | HOSKINS3 - HOSKN T4 115 1 | 19WP20SP24SP, 24WP, 29SP | P42:345:NPPD:BKR-HOS-3322 |  | 336 | 128.89 | 433.0704 |  |  | Hoskins 345/230kV New Transformer CKT3 | Build a new 345/230kV transformer at Hoskins as a third circuit
00NR | NRIS | Thermal | HOSKINS7 - HOSKN T4 115 1 | 19WP20SP24SP, 24WP, 29SP | P42:345:NPPD:BKR-HOS-3322 |  | 336 | 125.23 | 420.7728 |  |  | Hoskins 345/230kV New Transformer CKT3 | Build a new 345/230kV transformer at Hoskins as a third circuit
00NR | NRIS | Thermal | PETRSBG7 - PETERSBRG.N7 115 Z1 | 19WP24SP, 24WP, 29SP | P42:345:NPPD:BKR-HOS-3322 |  | 137 | 111.69 | 153.0153 |  |  | Shell Creek to Grand Island 345kV New Build | Build a new 72 mile 345kV line from Shell Creek to Grand Island
09ALL | ERIS | Thermal | GENTLMN4 - OGALALA4 230 | 19WP20SP24WP, | P42:345:NPPD:BKR-KEY-3310 |  | 320 | 127.34 | 407.488 |  |  | Keystone to Sidney 345kV New Build CKT 2 | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit
17ALL | ERIS | Thermal | G17-014-TAP - PHILIP_T-BE4 230 | 20G | P42:345:NPPD:BKR-KEY-3310 |  | 342 | 111.83 | 382.4586 |  |  | Keystone to Sidney 345kV New Build CKT 2 | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit
17ALL | ERIS | Thermal | GENTLMN4 - OGALALA4 230 | 20G | P42:345:NPPD:BKR-KEY-3310 |  | 320 | 112.2 | 359.04 |  |  | Keystone to Sidney 345kV New Build CKT 2 | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit
09ALL | ERIS | Thermal | FAIRBRY7 - HARBINE7115 | 19WP, 20G, 24L, 24WP, | P42:345:NPPD:BKR-MOR-3306 |  | 99 | 134.93 | 133.5807 |  |  | Harbine to Fairbury 115kV Rebuild | Rebuild the existing Harbine to Fairbury 115kV 9 mile line to achieve a minimum spring/emergency rating of 134 MVA
03ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:NPPD:BKR-RW-3302 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:NPPD:BKR-RW-3302 |  |  |  | 0 |  |  | Finney 345kV Reactive Support | Install a new 250 MVAR capacitor bank at Finney 345kV Substation
03ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:NPPD:BKR-RW-3302 |  |  |  | 0 |  |  | Grapevine 345kV New Substation | Build a new 345kV substation at Grapevine
03ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:NPPD:BKR-RW-3302 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
03ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:NPPD:BKR-RW-3302 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
02ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BAER7314 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BAER7314 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BAER7314 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BAER7314 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BAER7314 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BAER7314 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BAER7314 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BAER7314 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BAER7314 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BAER7314 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
02ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BAER7314 |  |  |  | 0 |  |  | Grapevine 345kV New Substation | Build a new 345kV substation at Grapevine
02ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BAER7314 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BAER7314 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
02ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BAER7314 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BAER7314 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7304 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7304 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7304 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7304 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7304 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7304 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7304 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7304 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7304 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7304 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7304 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7383 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7383 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7383 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7383 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7383 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7383 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7383 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7383 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7383 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7383 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7383 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7384 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7384 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7384 |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7384 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7384 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7384 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7384 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7384 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7384 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7384 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_BOER7384 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
00NR | NRIS | Thermal | CIMARON4 - CIMARON1 138 1 | 19WP20SP24SP29SP | P42:345:OKGE:SB_CION7382 |  | 478 | 126.7 | 605.626 |  |  | Cimarron 345/138kV New Transformer CKT3 | Build a new 345/138kV transformer at Cimarron as a third circuit
00NR | NRIS | Thermal | CIMARON7 - CIMARON1 138 1 | 19WP20SP24SP29SP | P42:345:OKGE:SB_CION7382 |  | 478 | 132.12 | 631.5336 |  |  | Cimarron 345/138kV New Transformer CKT3 | Build a new 345/138kV transformer at Cimarron as a third circuit
01ALL | ERIS | Thermal | NORTWST7 - MATHWSN7 345 1 | 21G, 24L | P42:345:OKGE:SB_CION7383 |  | 1195 | 107.99 | 1290.4805 |  |  | Northwest to Matthewson 138kV Rebuild | Substation and terminal equipment upgrades requred at Northwest 345kV substation to achieve a minimum light/emergency rating of 1301 MVA
02NR, 07NR | NRIS | Thermal | NORTWST7 - MATHWSN7 345 1 | 24L | P42:345:OKGE:SB_CION7383 |  | 1195 | 107.79 | 1288.0905 |  |  | Northwest to Matthewson 138kV Rebuild | Substation and terminal equipment upgrades requred at Northwest 345kV substation to achieve a minimum light/emergency rating of 1301 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_CION7384 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_CION7384 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_CION7384 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_CION7384 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_CION7384 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_CION7384 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_CION7384 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
00NR | NRIS | Thermal | GRACMNT4 - ANADARK4 138 1 | 19WP24SP, 24WP, 29SP | P42:345:OKGE:SB_CION7384 |  | 412 | 114.09 | 470.0508 |  |  | Gracemont to Anadark 138kV New Build CKT 2 | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit
07ALL | ERIS | Thermal | GRACMNT4 - ANADARK4 138 1 | 24SP | P42:345:OKGE:SB_CION7384 | 200 | 234 | 116.89 | 273.5226 |  |  | Gracemont to Anadark 138kV Rebuild | Rebuild the existing Gracemont to Anadark 138kV 5.09 mile line to achieve a minimum winter/emergency rating of 451 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_CION7384 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_CION7384 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
14ALL | ERIS | Thermal | CARTER 4 - CHIKSAW4 138 | 19WP, 20G, 20SP, 24SP, 24WP, 29SP | P42:345:OKGE:SB_JOCO7303 |  | 191 | 113.37 | 216.5367 |  |  | Carter to Chicksaw 138kV Rebuild | Rebuild the existing Carter to Chicksaw 138kV 2.73 mile line to achieve a minimum summer/emergency rating of 217 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7301 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7301 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7301 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7301 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7301 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7301 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7301 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7301 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7301 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7312 |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7312 |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7312 |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7312 |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7312 |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7312 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7312 |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7312 |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:OKGE:SB_MICO7312 |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
08ALL | ERIS | Thermal | KILDARE4 - WHEAGLE4 138 1 | 20G, 24L | P42:345:OKGE:SB_WONG7383 |  | 222 | 134 | 297.48 |  |  | Kildare to White Eagle 138kV Rebuild | Rebuild the existing Kildare to While Eagle 138 kV 11.22 mile line to achieve a minimm light/emergency rating of 298 MVA
06ALL | ERIS | Thermal | TUCO_INT 6 - SIEM 8743066 230 2 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, | P42:345:SPS:CROSSROADS_6R30_19L |  | 643 | 153.36 | 986.1048 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Thermal | TUCO_INT 7 345/230XFR 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | P42:345:SPS:CROSSROADS_6R30_19L |  | 643 | 181.66 | 1168.0738 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Thermal | TUCO_INT 7 345/230XFR 2 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, | P42:345:SPS:CROSSROADS_6R30_19L |  | 643 | 157.95 | 1015.6185 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Thermal | TOLK 6 - TUCO_INT 6 230 1 | 19WP20SP, 24L, 24SP | P42:345:SPS:CROSSROADS_6R30_19L |  | 478 | 116.04 | 554.6712 |  |  | Tolk to Tuco 230kV Rebuild | Rebuild the existing Tolk to Tuco 230kV 54.58 mile line to achieve a minimum light/emergency rating of 555 MVA
06ALL | ERIS | Thermal | TUCO_INT 7 - CRAWFISH_DR 345 2 | 20G, 20SP, 24L, 24SP, 24WP, | P42:345:SPS:CROSSROADS_6R30_19L |  | 997.3 | 139.51 | 1391.3332 |  |  | Tuco to Crawfish Draw 345kV Rebuild | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA
09ALL | ERIS | Non-Converge | Non-Converge |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796) |  |  |  | 0 |  |  | Stegall 345kV Reactive Support | Install a new 150 MVAR capacitor bank at Stegall 345kV Substation
09ALL | ERIS | Thermal | G16-110-TAP - STEGALL_-MB3 345 | 19WP20SP24SP, 24WP, 29SP | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796) |  | 765 | 104.89 | 802.4085 |  |  | Stegall to GEN-2016-034 Tap New Build | Build a new 345kV 26 mile line from Stegall to GEN-2016-034 Tap
00NR | NRIS | Thermal | FTSMITH7 - FTSMITH5 161 5 | 19WP24WP, 29SP | P42:500:OKGE:SB_FTTH8581 |  | 478 | 111.34 | 532.2052 |  |  | Ft. Smith 345/161kV New Transformer CKT 2 | Build a new 345/161kV transformer at Ft. Smith as a second circuit
00NR | NRIS | Thermal | FTSMTHW5 - FTSMITH5 161 5 | 19WP24WP, 29SP | P42:500:OKGE:SB_FTTH8581 |  | 478 | 112.68 | 538.6104 |  |  | Ft. Smith 345/161kV New Transformer CKT 2 | Build a new 345/161kV transformer at Ft. Smith as a second circuit
00NR | NRIS | Thermal | HAWTH 7 - HAWTHORN22 161 22 | 19WP20SP24SP, 24WP, 29SP | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH |  | 605 | 127.82 | 773.311 |  |  | Hawthorne 345/161kV New Transformer CKT3 | Build a new 345/161kV transformer at Hawthorne as a third circuit
00NR | NRIS | Thermal | HAWTHN5 - HAWTHORN22 161 22 | 19WP20SP24SP, 24WP, 29SP | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH |  | 605 | 129.87 | 785.7135 |  |  | Hawthorne 345/161kV New Transformer CKT3 | Build a new 345/161kV transformer at Hawthorne as a third circuit
00NR | NRIS | Thermal | HAWTH 7 - HAWTHORN22 161 22 | 19WP20SP24SP, 24WP, 29SP | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH |  | 605 | 127.82 | 773.311 |  |  | Nashua to Sibley 345kV New Build | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA
00NR | NRIS | Thermal | HAWTHN5 - HAWTHORN22 161 22 | 19WP20SP24SP, 24WP, 29SP | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH |  | 605 | 129.87 | 785.7135 |  |  | Nashua to Sibley 345kV New Build | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:SPS:TUCO:NR20_19L |  |  |  | 0 |  |  | Beaver County to Grapevine New Build | Build a new 90 mile 345kV line from Beaver County to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:SPS:TUCO:NR20_19L |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:SPS:TUCO:NR20_19L |  |  |  | 0 |  |  | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:SPS:TUCO:NR20_19L |  |  |  | 0 |  |  | Crawfish Draw 765/345kV New Transformer | Build a new 345/765kV transformer at Crawfish Draw
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:SPS:TUCO:NR20_19L |  |  |  | 0 |  |  | Crawfish Draw to Crossroads 765kV New Build | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:SPS:TUCO:NR20_19L |  |  |  | 0 |  |  | Crawfish Draw to Grapevine 345kV New Build | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:SPS:TUCO:NR20_19L |  |  |  | 0 |  |  | Crawfish Draw to Lawton Eastside 345kV New Build | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:SPS:TUCO:NR20_19L |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:SPS:TUCO:NR20_19L |  |  |  | 0 |  |  | Crawfish Draw to Seminole 765kV New Build CKT 2 | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:SPS:TUCO:NR20_19L |  |  |  | 0 |  |  | Grapevine to Chisholm 345kV New Build | Build a new 75 mile 345kV line from Grapevine to Chisholm
06ALL | ERIS | Non-Converge | Non-Converge |  | P43:345:SPS:TUCO:NR20_19L |  |  |  | 0 |  |  | Potter County to Grapevine 345kV New Build | Build a new 65 mile 345kV line from Potter County to Grapevine
00NR | NRIS | Non-Converge | Non-Converge |  | P43:345-500:OKGE:SB_FTTH7306 |  |  |  | 0 |  |  | Eastowne 161kV Reactive Support | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P43:345-500:OKGE:SB_FTTH7306 |  |  |  | 0 |  |  | Hawthorne to Craig 345kV New Build | Build a new 25 mile 345kV line from Hawthorn to Craig
00NR | NRIS | Non-Converge | Non-Converge |  | P43:345-500:OKGE:SB_FTTH7306 |  |  |  | 0 |  |  | Longwood 345kV Reactive Support | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P43:345-500:OKGE:SB_FTTH7306 |  |  |  | 0 |  |  | Mark Moore 161kV Reactive Support | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P43:345-500:OKGE:SB_FTTH7306 |  |  |  | 0 |  |  | Mark Moore to Elm Creek 345kV New Build | Build a new 102 mile 345kV line from Mark Moore to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge |  | P43:345-500:OKGE:SB_FTTH7306 |  |  |  | 0 |  |  | Sibley 161kV Reactive Support | Install a 100 MVAR capacitor bank at Sibley 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P43:345-500:OKGE:SB_FTTH7306 |  |  |  | 0 |  |  | Southwest Shreveport 345kV Reactive Support | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | P43:345-500:OKGE:SB_FTTH7306 |  |  |  | 0 |  |  | Valiant to Petersburg 345kV New Build CKT 2 | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit
13ALL | ERIS | Non-Converge | Non-Converge |  | P44:345:OPPD:S3458-HOL&R1 |  |  |  | 0 |  |  | Cooper to Holt 345kV New Build | Build a new 32 mile 345kV line from Cooper to Holt
03ALL | ERIS | Thermal | FINNEY 7 - G17-032-TAP 345 | 29SP | System Intact |  | 380 | 110.88 | 421.344 |  |  | Finney to G17-032-Tap 345kV Rebuild | Rebuild the existing Finney to G17-032-Tap 345kV 75.75 mile line to achieve a minimum summer/emergency rating of 444 MVA
06ALL | ERIS | Thermal | HALE_CNTY 3 - TUCO_INT 3 115 1 | 19WP, 20G, 20SP, 24L | System Intact | 79.7 |  | 133.32 | 0 |  |  | Hale County to Tuco 115kV Rebuild | Rebuild the existing Hale County to Tuco 115kV 20.73 mile line to achieve a minimum spring/normal rating of 107 MVA
07ALL | ERIS | Thermal | NAPLSTP4 - CORN TP4 138 1 | 20SP | System Intact | 145 | 169 | 100.59 | 169.9971 |  |  | Naples Tap to Cornville Tap 138kV Rebuild | Rebuild the existing Naples Tap to Cornville Tap 138kV 11 mile line to achieve a minimum winter/emergency rating of 203 MVA
01ALL | ERIS | Thermal | OKEENE 4 - G16-107-TAP 138 | 20SP24SP, 29SP | System Intact | 160 |  | 105.91 | 0 |  |  | Okeene to G16-107-Tap 138kV Rebuild | Rebuild the existing Okeene to G16-107-Tap 138kV 16.975 mile line to achieve a minimum summer/normal rating of 170 MVA
03ALL | ERIS | Thermal | SMOKYHL6 - SUMMIT 6 230 | 20G, 24L | System Intact | 319 | 350 | 115.01 | 402.535 |  |  | Smoky Hill to Summit 230kV Rebuild | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA
06ALL | ERIS | Thermal | TOLK 6 - ABBXNL844501 230 1 | 24L, 24SP | System Intact | 478 |  | 120.26 | 0 |  |  | Tolk 345/230kV Transformer CKT 2 | Install a new 345/230kV transformer at Tolk substation
06ALL | ERIS | Thermal | TOLK 7 345/230XFR 1 | 24L, 24SP | System Intact | 478 |  | 119.34 | 0 |  |  | Tolk 345/230kV Transformer CKT 2 | Install a new 345/230kV transformer at Tolk substation
09ALL | ERIS | Thermal | BAILEYV3 - SENECA 3 115 | 24L | System Intact | 86 |  | 108.27 | 0 |  |  | Seneca to Bailyville to Smittyville to Marshall County 115kV CKT 1 Rebuild | Rebuild the existing Baileyville to Seneca 161kV 6.03 mile line to achieve a minimum light/normal rating of 94 MVA.
09ALL | ERIS | Thermal | BAILEYV3 - SMITTYV3 115 | 24L | System Intact | 86 |  | 109.09 | 0 |  |  | Seneca to Bailyville to Smittyville to Marshall County 115kV CKT 1 Rebuild | Rebuild the existing Baileyville to Smittyville 161kV 7.99 mile line to achieve a minimum light/normal rating of 94 MVA.
08ALL | ERIS | Thermal | BV-COM-4 - MOUNDRD4 138 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | 106 |  | 142.2 | 0 |  |  | Batesville Comanche to Mound Road 138kV Rebuild | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA
16ALL | ERIS | Thermal | BROADLND-BE3 - BD KU2A 345/230 | 20SP, 24SP, 29SP | System Intact | 400 |  | 117.45 | 0 |  |  | Broadland 345/230kV Transformer Replacement | Replace the existing Broadland 345/230kV transformer to achieve a minimum rating of 450 MVA
09ALL | ERIS | Thermal | STRANGR7 - 87TH 7 345 | 20G | System Intact | 1195 |  | 106.93 | 0 |  |  | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA
08ALL | ERIS | Thermal | NEOSHO 5 - RIV4525 161 1 | 19WP, 20G, 20SP, 24L, 24SP, 24WP, 29SP | System Intact | 205 |  | 157.88 | 0 |  |  | Neosho to Riverton 161kV Rebuild | Rebuild the existing Neosho to Riverton 161kV 28.4 mile line to achieve a minimum winter/normal rating of 324 MVA
15ALL | ERIS | Thermal | HOLT.CO3 - GRPRAR1-LNX3 345 | 20G, 24L | System Intact | 720 |  | 120.64 |  |  |  | Model Correction | Rating correction
09ALL | ERIS | Thermal | SMOKYHL6 - SUMMIT 6 230 | 20G, 24L | System Intact | 319 |  | 121.33 | 0 |  |  | Smoky Hill to Summit 230kV Rebuild | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA
09ALL | ERIS | Thermal | S HAYS6 - GRTBEND6 230 | 20G | System Intact | 297 |  | 112.93 | 0 |  |  | South Hays to Great Bend 230kV Rebuild | Rebuild the existing South Hays to Great Bend 230kV 39.2 mile line to achieve a minimum spring/normal rating of 336 MVA
08ALL | ERIS | Thermal | TOLK 345/230XFR 1 | 24L | System Intact | 478 |  | 110.74 | 0 |  |  | Tolk 345/230kV Transformer CKT 2 | Install a new 345/230kV transformer at Tolk substation
08ALL | ERIS | Thermal | TOLK 6 - ABBXNL844501 230 | 24L | System Intact | 478 |  | 110.9 | 0 |  |  | Tolk 345/230kV Transformer CKT 2 | Install a new 345/230kV transformer at Tolk substation
08ALL | ERIS | Thermal | WAVERLY7 - LACYGNE7 345 | 19WP, 20G, 24L, 24WP, | System Intact | 1141 |  | 112.67 | 0 |  |  | Wolf Creek to Blackberry 345kV | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA
08ALL | ERIS | Thermal | WAVERLY7 - LACYGNE7 345 | 19WP, 20G, 24L, 24WP, | System Intact | 1141 |  | 112.67 | 0 |  |  | Wolf Creek to West Gardner 345kV New Build | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA
00NR | NRIS | Non-Converge | Non-Converge |  | TRIP LINE FROM BUS 640226 TO BUS 640342 CKT 1 TRIP LINE FROM BUS 640226 TO BUS 640520 CKT 1 |  |  |  | 0 |  |  | Eastowne 161kV Reactive Support | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | TRIP LINE FROM BUS 640226 TO BUS 640342 CKT 1 TRIP LINE FROM BUS 640226 TO BUS 640520 CKT 1 |  |  |  | 0 |  |  | Hawthorne to Craig 345kV New Build | Build a new 25 mile 345kV line from Hawthorn to Craig
00NR | NRIS | Non-Converge | Non-Converge |  | TRIP LINE FROM BUS 640226 TO BUS 640342 CKT 1 TRIP LINE FROM BUS 640226 TO BUS 640520 CKT 1 |  |  |  | 0 |  |  | Mark Moore 161kV Reactive Support | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | TRIP LINE FROM BUS 640226 TO BUS 640342 CKT 1 TRIP LINE FROM BUS 640226 TO BUS 640520 CKT 1 |  |  |  | 0 |  |  | Mark Moore to Elm Creek 345kV New Build | Build a new 102 mile 345kV line from Mark Moore to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge |  | TRIP LINE FROM BUS 640226 TO BUS 640342 CKT 1 TRIP LINE FROM BUS 640226 TO BUS 640520 CKT 1 |  |  |  | 0 |  |  | Sibley 161kV Reactive Support | Install a 100 MVAR capacitor bank at Sibley 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | TRIP LINE FROM BUS 652573 TO BUS 659206 CKT 1 TRIP LINE FROM BUS 659135 TO BUS 659167 TO BUS 659206 CKT 1 |  |  |  | 0 |  |  | Eastowne 161kV Reactive Support | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | TRIP LINE FROM BUS 652573 TO BUS 659206 CKT 1 TRIP LINE FROM BUS 659135 TO BUS 659167 TO BUS 659206 CKT 1 |  |  |  | 0 |  |  | Hawthorne to Craig 345kV New Build | Build a new 25 mile 345kV line from Hawthorn to Craig
00NR | NRIS | Non-Converge | Non-Converge |  | TRIP LINE FROM BUS 652573 TO BUS 659206 CKT 1 TRIP LINE FROM BUS 659135 TO BUS 659167 TO BUS 659206 CKT 1 |  |  |  | 0 |  |  | Mark Moore 161kV Reactive Support | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation
00NR | NRIS | Non-Converge | Non-Converge |  | TRIP LINE FROM BUS 652573 TO BUS 659206 CKT 1 TRIP LINE FROM BUS 659135 TO BUS 659167 TO BUS 659206 CKT 1 |  |  |  | 0 |  |  | Mark Moore to Elm Creek 345kV New Build | Build a new 102 mile 345kV line from Mark Moore to Elm Creek
00NR | NRIS | Non-Converge | Non-Converge |  | TRIP LINE FROM BUS 652573 TO BUS 659206 CKT 1 TRIP LINE FROM BUS 659135 TO BUS 659167 TO BUS 659206 CKT 1 |  |  |  | 0 |  |  | Sibley 161kV Reactive Support | Install a 100 MVAR capacitor bank at Sibley 161kV Substation

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost
GEN-2016-107 | 01 - Woodward |  | NRIS | 2nd Circle 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at 2nd Circle | 1075800 | 3.26% | 33000000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | 2nd Circle 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at 2nd Circle | 1805100 | 5.47% | 33000000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | 2nd Circle 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at 2nd Circle | 4669500 | 14.15% | 33000000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | 2nd Circle 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at 2nd Circle | 617100 | 1.87% | 33000000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | 2nd Circle 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at 2nd Circle | 366300 | 1.11% | 33000000
GEN-2017-032 | 03 - Spearville |  | NRIS | 2nd Circle 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at 2nd Circle | 6487800 | 19.66% | 33000000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | 2nd Circle 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at 2nd Circle | 732600 | 2.22% | 33000000
GEN-2017-055 | 09 - Nebraska |  | NRIS | 2nd Circle 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at 2nd Circle | 2376000 | 7.2% | 33000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | 2nd Circle 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at 2nd Circle | 2201100 | 6.67% | 33000000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | 2nd Circle 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at 2nd Circle | 1178100 | 3.57% | 33000000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | 2nd Circle 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at 2nd Circle | 3250500 | 9.85% | 33000000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | 2nd Circle 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at 2nd Circle | 742500 | 2.25% | 33000000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | 2nd Circle 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at 2nd Circle | 1498200 | 4.54% | 33000000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | 2nd Circle 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at 2nd Circle | 3811500 | 11.55% | 33000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | 2nd Circle 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at 2nd Circle | 2187900 | 6.63% | 33000000
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 133069 | ERIS | Adrian 161 kV Substation GEN-2017-090 Interconnection (Non-Shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-090 (150 MW/Solar), into the Point of Interconnection (POI) at Adrian 161 kV Substation. | 9955939 | 100% | 9955939
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri | 133068 | ERIS | Adrian 161 kV Substation GEN-2017-090 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-090 (150 MW/Solar), into the Point of Interconnection (POI) at Adrian 161 kV Substation. | 824356 | 100% | 824356
GEN-2016-005 | 03 - Spearville |  | NRIS | Albion to Petersburg 115kV Rebuild | Current Study | Rebuild the existing Albion to Petersburg 115kV 12.13 mile line to achieve a minimum winter/emergency rating of 151 MVA | 159200 | 3.98% | 4000000
GEN-2016-159 | 09 - Nebraska |  | NRIS | Albion to Petersburg 115kV Rebuild | Current Study | Rebuild the existing Albion to Petersburg 115kV 12.13 mile line to achieve a minimum winter/emergency rating of 151 MVA | 1846800 | 46.17% | 4000000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Albion to Petersburg 115kV Rebuild | Current Study | Rebuild the existing Albion to Petersburg 115kV 12.13 mile line to achieve a minimum winter/emergency rating of 151 MVA | 766400 | 19.16% | 4000000
GEN-2017-018 | 03 - Spearville |  | NRIS | Albion to Petersburg 115kV Rebuild | Current Study | Rebuild the existing Albion to Petersburg 115kV 12.13 mile line to achieve a minimum winter/emergency rating of 151 MVA | 146800 | 3.67% | 4000000
GEN-2017-032 | 03 - Spearville |  | NRIS | Albion to Petersburg 115kV Rebuild | Current Study | Rebuild the existing Albion to Petersburg 115kV 12.13 mile line to achieve a minimum winter/emergency rating of 151 MVA | 309600 | 7.74% | 4000000
GEN-2017-047 | 02 - Hitchland |  | NRIS | Albion to Petersburg 115kV Rebuild | Current Study | Rebuild the existing Albion to Petersburg 115kV 12.13 mile line to achieve a minimum winter/emergency rating of 151 MVA | 82400 | 2.06% | 4000000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Albion to Petersburg 115kV Rebuild | Current Study | Rebuild the existing Albion to Petersburg 115kV 12.13 mile line to achieve a minimum winter/emergency rating of 151 MVA | 183200 | 4.58% | 4000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Albion to Petersburg 115kV Rebuild | Current Study | Rebuild the existing Albion to Petersburg 115kV 12.13 mile line to achieve a minimum winter/emergency rating of 151 MVA | 108000 | 2.7% | 4000000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Albion to Petersburg 115kV Rebuild | Current Study | Rebuild the existing Albion to Petersburg 115kV 12.13 mile line to achieve a minimum winter/emergency rating of 151 MVA | 16000 | 0.4% | 4000000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Albion to Petersburg 115kV Rebuild | Current Study | Rebuild the existing Albion to Petersburg 115kV 12.13 mile line to achieve a minimum winter/emergency rating of 151 MVA | 52400 | 1.31% | 4000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Albion to Petersburg 115kV Rebuild | Current Study | Rebuild the existing Albion to Petersburg 115kV 12.13 mile line to achieve a minimum winter/emergency rating of 151 MVA | 246000 | 6.15% | 4000000
GEN-2017-100 | 02 - Hitchland |  | NRIS | Albion to Petersburg 115kV Rebuild | Current Study | Rebuild the existing Albion to Petersburg 115kV 12.13 mile line to achieve a minimum winter/emergency rating of 151 MVA | 83200 | 2.08% | 4000000
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 132965 | ERIS | Altoona - Parson 138 kV GEN-2017-022 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-022 (65 MW/Solar), into the Point of Interconnection (POI) at Altoona - Parson 138 kV. | 4790295 | 100% | 4790295
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas | 132964 | ERIS | Altoona - Parson 138 kV GEN-2017-022 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-022 (65 MW/Solar), into the Point of Interconnection (POI) at Altoona - Parson 138 kV. | 696118 | 100% | 696118
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 2110 | 2.11% | 100000
GEN-2016-107 | 01 - Woodward |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 560 | 0.56% | 100000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 15430 | 15.43% | 100000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 3730 | 3.73% | 100000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 3350 | 3.35% | 100000
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 52970 | 52.97% | 100000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 950 | 0.95% | 100000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 560 | 0.56% | 100000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 1130 | 1.13% | 100000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 770 | 0.77% | 100000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 2620 | 2.62% | 100000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 1260 | 1.26% | 100000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 1130 | 1.13% | 100000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 1240 | 1.24% | 100000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 1650 | 1.65% | 100000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 2050 | 2.05% | 100000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 2160 | 2.16% | 100000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 900 | 0.9% | 100000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 3980 | 3.98% | 100000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | Current Study | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | 1450 | 1.45% | 100000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico | 133055 | ERIS | Amarillo South - Swisher 230 kV GEN-2017-081 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-081 (300 MW/Solar), into the Point of Interconnection (POI) at Amarillo South - Swisher 230 kV. | 7473582 | 100% | 7473582
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico | 133054 | ERIS | Amarillo South - Swisher 230 kV GEN-2017-081 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-081 (300 MW/Solar), into the Point of Interconnection (POI) at Amarillo South - Swisher 230 kV. | 956616 | 100% | 956616
GEN-2017-036 | 07 - Southwestern Oklahoma |  | ERIS | Anadark to Cherry Road 138kV Rebuild | Current Study | Rebuild the existing Anadark to Cherry Road 138kV 25.15 mile line to achieve a minimum light/emergency rating of 189 MVA | 15092327.9242 | 62.24% | 24248598.85
GEN-2017-053 | 07 - Southwestern Oklahoma |  | ERIS | Anadark to Cherry Road 138kV Rebuild | Current Study | Rebuild the existing Anadark to Cherry Road 138kV 25.15 mile line to achieve a minimum light/emergency rating of 189 MVA | 9156270.9258 | 37.76% | 24248598.85
GEN-2016-107 | 01 - Woodward |  | NRIS | Arbuckle to Millcreek Tap 138kV Rebuild | Current Study | Rebuild the existing Arbuckle to Mill Creek Tap 138kV 13.16 mile line to achieve a minimum winter/emergency rating of 212 MVA | 114003.03 | 1.39% | 8200000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Arbuckle to Millcreek Tap 138kV Rebuild | Current Study | Rebuild the existing Arbuckle to Mill Creek Tap 138kV 13.16 mile line to achieve a minimum winter/emergency rating of 212 MVA | 124721.26 | 1.521% | 8200000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Arbuckle to Millcreek Tap 138kV Rebuild | Current Study | Rebuild the existing Arbuckle to Mill Creek Tap 138kV 13.16 mile line to achieve a minimum winter/emergency rating of 212 MVA | 628378.8 | 7.663% | 8200000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Arbuckle to Millcreek Tap 138kV Rebuild | Current Study | Rebuild the existing Arbuckle to Mill Creek Tap 138kV 13.16 mile line to achieve a minimum winter/emergency rating of 212 MVA | 571010.73 | 6.964% | 8200000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Arbuckle to Millcreek Tap 138kV Rebuild | Current Study | Rebuild the existing Arbuckle to Mill Creek Tap 138kV 13.16 mile line to achieve a minimum winter/emergency rating of 212 MVA | 203184.65 | 2.478% | 8200000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Arbuckle to Millcreek Tap 138kV Rebuild | Current Study | Rebuild the existing Arbuckle to Mill Creek Tap 138kV 13.16 mile line to achieve a minimum winter/emergency rating of 212 MVA | 129891.47 | 1.584% | 8200000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Arbuckle to Millcreek Tap 138kV Rebuild | Current Study | Rebuild the existing Arbuckle to Mill Creek Tap 138kV 13.16 mile line to achieve a minimum winter/emergency rating of 212 MVA | 6407.52 | 0.07814% | 8200000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Arbuckle to Millcreek Tap 138kV Rebuild | Current Study | Rebuild the existing Arbuckle to Mill Creek Tap 138kV 13.16 mile line to achieve a minimum winter/emergency rating of 212 MVA | 5891382.68 | 71.85% | 8200000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Arbuckle to Millcreek Tap 138kV Rebuild | Current Study | Rebuild the existing Arbuckle to Mill Creek Tap 138kV 13.16 mile line to achieve a minimum winter/emergency rating of 212 MVA | 273092.9 | 3.33% | 8200000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Arbuckle to Millcreek Tap 138kV Rebuild | Current Study | Rebuild the existing Arbuckle to Mill Creek Tap 138kV 13.16 mile line to achieve a minimum winter/emergency rating of 212 MVA | 257926.96 | 3.145% | 8200000
GEN-2017-082 | 12 - Northwest Arkansas | 133057 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (Non-Shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-082 (149.4 MW/Solar), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | 3400000 | 100% | 3400000
GEN-2017-082 | 12 - Northwest Arkansas | 143123 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (Non-Shared NU) (WERE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2017-082 (149.4 MW/Wind), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | 6649 | 100% | 6649
GEN-2017-082 | 12 - Northwest Arkansas | 133056 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-082 (149.4 MW/Solar), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | 800000 | 100% | 800000
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Asbury Plant to Carl Junction NE 161kV Rebuild | Current Study | Rebuild the existing Asbury Plant to Carl Junction NE 161kV 12.3 mile line to achieve a minimum winter/emergency rating of 342 MVA | 7905954.8 | 40.61% | 19468000
GEN-2017-082 | 12 - Northwest Arkansas |  | ERIS | Asbury Plant to Carl Junction NE 161kV Rebuild | Current Study | Rebuild the existing Asbury Plant to Carl Junction NE 161kV 12.3 mile line to achieve a minimum winter/emergency rating of 342 MVA | 11562045.2 | 59.39% | 19468000
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Asbury Plant to Purcell Switch 161kV Rebuild | Current Study | Rebuild the existing Asbury Plant to Purcell Switch 161kV 11.94 mile line to achieve a minimum winter/emergency rating of 329 MVA | 8607695.6 | 40.61% | 21196000
GEN-2017-082 | 12 - Northwest Arkansas |  | ERIS | Asbury Plant to Purcell Switch 161kV Rebuild | Current Study | Rebuild the existing Asbury Plant to Purcell Switch 161kV 11.94 mile line to achieve a minimum winter/emergency rating of 329 MVA | 12588304.4 | 59.39% | 21196000
GEN-2017-011 | 01 - Woodward | 132951 | ERIS | Badger - Woodward 345 kV GEN-2017-011 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-011 (151.8 MW/Solar), into the Point of Interconnection (POI) at Badger - Woodward 345 kV. | 15000 | 100% | 15000
GEN-2017-011 | 01 - Woodward | 132950 | ERIS | Badger - Woodward 345 kV GEN-2017-011 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-011 (151.8 MW/Solar), into the Point of Interconnection (POI) at Badger - Woodward 345 kV. | 689661 | 100% | 689661
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico | 132913 | ERIS | Bailey County 115 kV Substation GEN-2016-078 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-078 (108 MW/Solar), into the Point of Interconnection (POI) at Bailey County 115 kV Substation. | 1719092 | 100% | 1719092
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico | 132912 | ERIS | Bailey County 115 kV Substation GEN-2016-078 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-078 (108 MW/Solar), into the Point of Interconnection (POI) at Bailey County 115 kV Substation. | 575012 | 100% | 575012
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 171977.9844 | 2.92% | 5889657
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 83633.1294 | 1.42% | 5889657
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 166088.3274 | 2.82% | 5889657
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 155486.9448 | 2.64% | 5889657
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 59485.5357 | 1.01% | 5889657
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 99535.2033 | 1.69% | 5889657
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 359269.077 | 6.1% | 5889657
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 467049.8001 | 7.93% | 5889657
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 310384.9239 | 5.27% | 5889657
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 51828.9816 | 0.88% | 5889657
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 362802.8712 | 6.16% | 5889657
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 334532.5176 | 5.68% | 5889657
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 308618.0268 | 5.24% | 5889657
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 140173.8366 | 2.38% | 5889657
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 335121.4833 | 5.69% | 5889657
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 5300.6913 | 0.09% | 5889657
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 465871.8687 | 7.91% | 5889657
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 76565.541 | 1.3% | 5889657
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 720894.0168 | 12.24% | 5889657
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 457037.3832 | 7.76% | 5889657
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 136640.0424 | 2.32% | 5889657
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 200837.3037 | 3.41% | 5889657
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 41227.599 | 0.7% | 5889657
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | Current Study | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | 379293.9108 | 6.44% | 5889657
GEN-2017-052 | 03 - Spearville | 133007 | ERIS | Bear Creek - Johnson Corner 115 kV GEN-2017-052 Interconnection (Non-Shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-052 (25 MW/Solar), into the Point of Interconnection (POI) at Bear Creek - Johnson Corner 115 kV. | 3372070 | 100% | 3372070
GEN-2017-052 | 03 - Spearville | 133006 | ERIS | Bear Creek - Johnson Corner 115 kV GEN-2017-052 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-052 (25 MW/Solar), into the Point of Interconnection (POI) at Bear Creek - Johnson Corner 115 kV. | 1662749 | 100% | 1662749
GEN-2016-109 | 09 - Nebraska |  | ERIS | Beatrice to Harbine 115kV Rebuild | Current Study | Rebuild the existing Beatrice to Harbine 115kV 14.08 mile line to achieve a minimum light/emergency rating of 144 MVA. | 5520000 | 100% | 5520000
GEN-2016-005 | 03 - Spearville |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 4207266.4828 | 0.025468 | 165200000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 3410306.5864 | 0.020644 | 165200000
GEN-2016-049 | 03 - Spearville |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 7532150.7853 | 0.045594 | 165200000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 1589930.0402 | 0.0096243 | 165200000
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 3224925.0671 | 0.019521 | 165200000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 2935169.277 | 0.017767 | 165200000
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 1870460.1902 | 0.011322 | 165200000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 7079971.2384 | 0.042857 | 165200000
GEN-2017-004 | 04 - Northwest Kansas |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 2619284.4639 | 0.015855 | 165200000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 8781443.4215 | 0.053156 | 165200000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 6471580.1034 | 0.039174 | 165200000
GEN-2017-013 | 04 - Northwest Kansas |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 4979784.7425 | 0.030144 | 165200000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 976716.8732 | 0.0059123 | 165200000
GEN-2017-018 | 03 - Spearville |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 3905404.1963 | 0.02364 | 165200000
GEN-2017-021 | 03 - Spearville |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 5434778.8585 | 0.032898 | 165200000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 6920483.225 | 0.041892 | 165200000
GEN-2017-032 | 03 - Spearville |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 6002949.8936 | 0.036337 | 165200000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 4666547.6009 | 0.028248 | 165200000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 5888142.7527 | 0.035643 | 165200000
GEN-2017-047 | 02 - Hitchland |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 1908848.8887 | 0.011555 | 165200000
GEN-2017-049 | 03 - Spearville |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 1074323.3956 | 0.0065032 | 165200000
GEN-2017-052 | 03 - Spearville |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 765373.2561 | 0.004633 | 165200000
GEN-2017-058 | 02 - Hitchland |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 6485809.5233 | 0.03926 | 165200000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 2663773.2931 | 0.016125 | 165200000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 4673547.4161 | 0.02829 | 165200000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 106550.9361 | 0.00064498 | 165200000
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 8315074.4643 | 0.050333 | 165200000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 1521217.9226 | 0.0092083 | 165200000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 15460654.0201 | 0.093587 | 165200000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 9242782.294 | 0.055949 | 165200000
GEN-2017-083 | 04 - Northwest Kansas |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 2477317.1595 | 0.014996 | 165200000
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 2741569.8512 | 0.016595 | 165200000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 3787014.2718 | 0.022924 | 165200000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 794499.1616 | 0.0048093 | 165200000
GEN-2017-099 | 03 - Spearville |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 5434778.8585 | 0.032898 | 165200000
GEN-2017-100 | 02 - Hitchland |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 2257293.214 | 0.013664 | 165200000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Clark County 345kV New Line | Current Study | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | 6992276.2744 | 0.042326 | 165200000
GEN-2016-005 | 03 - Spearville |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 3048485.46 | 2.547% | 119700000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 2471027.23 | 2.064% | 119700000
GEN-2016-049 | 03 - Spearville |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 5457617.73 | 4.559% | 119700000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 1152025.58 | 0.9624% | 119700000
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 2336704.18 | 1.952% | 119700000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 2126754.01 | 1.777% | 119700000
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 1355291.07 | 1.132% | 119700000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 5129979.16 | 4.286% | 119700000
GEN-2017-004 | 04 - Northwest Kansas |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 1897871.37 | 1.586% | 119700000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 6362825.53 | 5.316% | 119700000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 4689153.38 | 3.917% | 119700000
GEN-2017-013 | 04 - Northwest Kansas |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 3608233.86 | 3.014% | 119700000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 707705.87 | 0.5912% | 119700000
GEN-2017-018 | 03 - Spearville |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 2829763.21 | 2.364% | 119700000
GEN-2017-021 | 03 - Spearville |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 3937911.8 | 3.29% | 119700000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 5014417.93 | 4.189% | 119700000
GEN-2017-032 | 03 - Spearville |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 4349595.05 | 3.634% | 119700000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 3381269.66 | 2.825% | 119700000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 4266408.52 | 3.564% | 119700000
GEN-2017-047 | 02 - Hitchland |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 1383106.61 | 1.155% | 119700000
GEN-2017-049 | 03 - Spearville |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 778429.24 | 0.6503% | 119700000
GEN-2017-052 | 03 - Spearville |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 554571.3 | 0.4633% | 119700000
GEN-2017-058 | 02 - Hitchland |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 4699463.68 | 3.926% | 119700000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 1930106.92 | 1.612% | 119700000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 3386341.56 | 2.829% | 119700000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 77204.28 | 0.0645% | 119700000
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 6024905.65 | 5.033% | 119700000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 1102238.41 | 0.9208% | 119700000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 11202423.04 | 9.359% | 119700000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 6697100.73 | 5.595% | 119700000
GEN-2017-083 | 04 - Northwest Kansas |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 1795005.23 | 1.5% | 119700000
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 1986476.46 | 1.66% | 119700000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 2743980.68 | 2.292% | 119700000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 575675.24 | 0.4809% | 119700000
GEN-2017-099 | 03 - Spearville |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 3937911.8 | 3.29% | 119700000
GEN-2017-100 | 02 - Hitchland |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 1635581.1 | 1.366% | 119700000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Beaver County to Grapevine New Build | Current Study | Build a new 90 mile 345kV line from Beaver County to Grapevine | 5066437.47 | 4.233% | 119700000
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Beaver to Eureka 161kV Rebuild | Current Study | Rebuild the existing Beaver to Eureka 161kV 7.22 mile line to achieve a minimum winter/emergency rating of 417 MVA | 1978845.1919 | 24.74% | 8000000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Beaver to Eureka 161kV Rebuild | Current Study | Rebuild the existing Beaver to Eureka 161kV 7.22 mile line to achieve a minimum winter/emergency rating of 417 MVA | 1496018.918 | 18.7% | 8000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Beaver to Eureka 161kV Rebuild | Current Study | Rebuild the existing Beaver to Eureka 161kV 7.22 mile line to achieve a minimum winter/emergency rating of 417 MVA | 1750896.231 | 21.89% | 8000000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Beaver to Eureka 161kV Rebuild | Current Study | Rebuild the existing Beaver to Eureka 161kV 7.22 mile line to achieve a minimum winter/emergency rating of 417 MVA | 2774239.6591 | 34.68% | 8000000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 607500 | 1.35% | 45000000
GEN-2016-107 | 01 - Woodward |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 859500 | 1.91% | 45000000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 3973500 | 8.83% | 45000000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 9535500 | 21.19% | 45000000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 3978000 | 8.84% | 45000000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 796500 | 1.77% | 45000000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 468000 | 1.04% | 45000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 130500 | 0.29% | 45000000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 288000 | 0.64% | 45000000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 2889000 | 6.42% | 45000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 1800000 | 4% | 45000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 130500 | 0.29% | 45000000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 607500 | 1.35% | 45000000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 8941500 | 19.87% | 45000000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 1471500 | 3.27% | 45000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 1462500 | 3.25% | 45000000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 1674000 | 3.72% | 45000000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 1035000 | 2.3% | 45000000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 2524500 | 5.61% | 45000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | Current Study | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | 1827000 | 4.06% | 45000000
GEN-2016-093 | 09 - Nebraska | 132917 | ERIS | Bobcat 115 kV Substation GEN-2016-093 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-093 (70 MW/Solar), into the Point of Interconnection (POI) at Stegall 115 kV Substation. | 525000 | 100% | 525000
GEN-2016-093 | 09 - Nebraska | 132916 | ERIS | Bobcat 115 kV Substation GEN-2016-093 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-093 (70 MW/Solar), into the Point of Interconnection (POI) at Stegall 115 kV Substation. | 525000 | 100% | 525000
GEN-2017-037 | 09 - Nebraska | 132987 | ERIS | Bobcat 115 kV Substation GEN-2017-037 Interconnection (NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-037 (20 MW/Solar), into the Point of Interconnection (POI) at Stegall 115 kV Substation. | 525000 | 100% | 525000
GEN-2017-037 | 09 - Nebraska | 132986 | ERIS | Bobcat 115 kV Substation GEN-2017-037 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-037 (20 MW/Solar), into the Point of Interconnection (POI) at Stegall 115 kV Substation. | 525000 | 100% | 525000
GEN-2017-048 | 16 - Western North Dakota |  | ERIS | Broadland 345/230kV Transformer Replacement | Current Study | Replace the existing Broadland 345/230kV transformer to achieve a minimum rating of 450 MVA | 3976249.0804 | 66.27% | 6000000
GEN-2017-010 | 16 - Western North Dakota |  | ERIS | Broadland 345/230kV Transformer Replacement | Current Study | Replace the existing Broadland 345/230kV transformer to achieve a minimum rating of 450 MVA | 2023750.9196 | 33.73% | 6000000
GEN-2016-005 | 03 - Spearville |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 6520.5 | 1.89% | 345000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 63600.7845 | 18.44% | 345000
GEN-2016-107 | 01 - Woodward |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 10779.2835 | 3.124% | 345000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 2239.6537 | 0.6492% | 345000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 5925.5475 | 1.718% | 345000
GEN-2017-018 | 03 - Spearville |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 7818.4187 | 2.266% | 345000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 73832.2425 | 21.4% | 345000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 42003.75 | 12.17% | 345000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 31602.69 | 9.16% | 345000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 4283.5846 | 1.242% | 345000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 1448.4537 | 0.4198% | 345000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 42068.5238 | 12.19% | 345000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 42841.8123 | 12.42% | 345000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 1670.6625 | 0.4843% | 345000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 1551.35 | 0.4497% | 345000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 1993.3514 | 0.5778% | 345000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 2586.12 | 0.7496% | 345000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Brown to South Brown 138kV Rebuild | Current Study | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | 2233.2712 | 0.6473% | 345000
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas | 132993 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-040 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-040 (200.1 MW/Wind), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole 345 kV. | 5741321 | 100% | 5741321
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas | 132992 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-040 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-040 (200.1 MW/Wind), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole 345 kV. | 599979 | 100% | 599979
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas | 133073 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-092 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-092 (200 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole | 5741321 | 100% | 5741321
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas | 133072 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-092 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-092 (200 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole | 599979 | 100% | 599979
GEN-2017-027 | 14 - South Central Oklahoma |  | ERIS | Carter to Chicksaw 138kV Rebuild | Current Study | Rebuild the existing Carter to Chicksaw 138kV 2.73 mile line to achieve a minimum summer/emergency rating of 217 MVA | 1285000 | 100% | 1285000
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Carthage to Car 395 161kV Rebuild | Current Study | Rebuild the existing Carthage to Car 395 161kV 4.14 mile line to achieve a minimum winter/emergency rating of 305 MVA | 3126970 | 40.61% | 7700000
GEN-2017-082 | 12 - Northwest Arkansas |  | ERIS | Carthage to Car 395 161kV Rebuild | Current Study | Rebuild the existing Carthage to Car 395 161kV 4.14 mile line to achieve a minimum winter/emergency rating of 305 MVA | 4573030 | 59.39% | 7700000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Carthage to Joplin Atlas Jct. 161kV Rebuild | Current Study | Rebuild the existing Cartahage to Joplin Atlas Jct. 161kV 8.2 mile line to achieve a minimum summer/emergency rating of 262 MVA | 2098445 | 14.15% | 14830000
GEN-2016-107 | 01 - Woodward |  | NRIS | Carthage to Joplin Atlas Jct. 161kV Rebuild | Current Study | Rebuild the existing Cartahage to Joplin Atlas Jct. 161kV 8.2 mile line to achieve a minimum summer/emergency rating of 262 MVA | 1226441 | 8.27% | 14830000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Carthage to Joplin Atlas Jct. 161kV Rebuild | Current Study | Rebuild the existing Cartahage to Joplin Atlas Jct. 161kV 8.2 mile line to achieve a minimum summer/emergency rating of 262 MVA | 3135062 | 21.14% | 14830000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Carthage to Joplin Atlas Jct. 161kV Rebuild | Current Study | Rebuild the existing Cartahage to Joplin Atlas Jct. 161kV 8.2 mile line to achieve a minimum summer/emergency rating of 262 MVA | 142368 | 0.96% | 14830000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Carthage to Joplin Atlas Jct. 161kV Rebuild | Current Study | Rebuild the existing Cartahage to Joplin Atlas Jct. 161kV 8.2 mile line to achieve a minimum summer/emergency rating of 262 MVA | 97878 | 0.66% | 14830000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Carthage to Joplin Atlas Jct. 161kV Rebuild | Current Study | Rebuild the existing Cartahage to Joplin Atlas Jct. 161kV 8.2 mile line to achieve a minimum summer/emergency rating of 262 MVA | 1284278 | 8.66% | 14830000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Carthage to Joplin Atlas Jct. 161kV Rebuild | Current Study | Rebuild the existing Cartahage to Joplin Atlas Jct. 161kV 8.2 mile line to achieve a minimum summer/emergency rating of 262 MVA | 673282 | 4.54% | 14830000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Carthage to Joplin Atlas Jct. 161kV Rebuild | Current Study | Rebuild the existing Cartahage to Joplin Atlas Jct. 161kV 8.2 mile line to achieve a minimum summer/emergency rating of 262 MVA | 1285761 | 8.67% | 14830000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Carthage to Joplin Atlas Jct. 161kV Rebuild | Current Study | Rebuild the existing Cartahage to Joplin Atlas Jct. 161kV 8.2 mile line to achieve a minimum summer/emergency rating of 262 MVA | 1067760 | 7.2% | 14830000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Carthage to Joplin Atlas Jct. 161kV Rebuild | Current Study | Rebuild the existing Cartahage to Joplin Atlas Jct. 161kV 8.2 mile line to achieve a minimum summer/emergency rating of 262 MVA | 1309489 | 8.83% | 14830000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Carthage to Joplin Atlas Jct. 161kV Rebuild | Current Study | Rebuild the existing Cartahage to Joplin Atlas Jct. 161kV 8.2 mile line to achieve a minimum summer/emergency rating of 262 MVA | 252110 | 1.7% | 14830000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Carthage to Joplin Atlas Jct. 161kV Rebuild | Current Study | Rebuild the existing Cartahage to Joplin Atlas Jct. 161kV 8.2 mile line to achieve a minimum summer/emergency rating of 262 MVA | 2257126 | 15.22% | 14830000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 1142812.05 | 9.37% | 12196500
GEN-2016-107 | 01 - Woodward |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 647634.15 | 5.31% | 12196500
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 1566030.6 | 12.84% | 12196500
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 668368.2 | 5.48% | 12196500
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 337843.05 | 2.77% | 12196500
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 136600.8 | 1.12% | 12196500
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 85375.5 | 0.7% | 12196500
GEN-2017-032 | 03 - Spearville |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 604946.4 | 4.96% | 12196500
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 681784.35 | 5.59% | 12196500
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 369553.95 | 3.03% | 12196500
GEN-2017-055 | 09 - Nebraska |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 150016.95 | 1.23% | 12196500
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 63421.8 | 0.52% | 12196500
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 683004 | 5.6% | 12196500
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 579333.75 | 4.75% | 12196500
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 937910.85 | 7.69% | 12196500
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 1056216.9 | 8.66% | 12196500
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 462247.35 | 3.79% | 12196500
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 245149.65 | 2.01% | 12196500
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 1656284.7 | 13.58% | 12196500
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | 121965 | 1% | 12196500
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Carthage to Purcell Switch 161kV Rebuild | Current Study | Rebuild the existing Carthage to Purcell Switch 161kV 7.89 mile line to achieve a minimum winter/emergency rating of 317 MVA | 10856000 | 100% | 10856000
GEN-2017-076 | 12 - Northwest Arkansas | 133045 | ERIS | Chamber Springs 161 kV Substation GEN-2017-076 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-076 (52.2 MW/Solar), into the Point of Interconnection (POI) at Chamber Springs 161 kV Substation. | 1406646 | 100% | 1406646
GEN-2017-076 | 12 - Northwest Arkansas | 133044 | ERIS | Chamber Springs 161 kV Substation GEN-2017-076 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-076 (52.2 MW/Solar), into the Point of Interconnection (POI) at Chamber Springs 161 kV Substation. | 1193983 | 100% | 1193983
GEN-2016-103 | 15 - Eastern South Dakota |  | ERIS | Chappelle Creek to Ft. Thompson 345k New Build CKT 2 | Current Study | Build a new 30 mile 345kV line from Chappelle Creek to Ft. Thompson as a second circuit | 45283831.3362 | 68.72% | 65900000
GEN-2017-010 | 16 - Western North Dakota |  | ERIS | Chappelle Creek to Ft. Thompson 345k New Build CKT 2 | Current Study | Build a new 30 mile 345kV line from Chappelle Creek to Ft. Thompson as a second circuit | 5915530.9223 | 8.977% | 65900000
GEN-2017-048 | 16 - Western North Dakota |  | ERIS | Chappelle Creek to Ft. Thompson 345k New Build CKT 2 | Current Study | Build a new 30 mile 345kV line from Chappelle Creek to Ft. Thompson as a second circuit | 12724800.3274 | 19.31% | 65900000
GEN-2017-094 | 15 - Eastern South Dakota |  | ERIS | Chappelle Creek to Ft. Thompson 345k New Build CKT 2 | Current Study | Build a new 30 mile 345kV line from Chappelle Creek to Ft. Thompson as a second circuit | 1975837.414 | 2.998% | 65900000
GEN-2016-037 | 07 - Southwestern Oklahoma | 132903 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | 20639740 | 100% | 20639740
GEN-2016-037 | 07 - Southwestern Oklahoma | 143127 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | 15000 | 100% | 15000
GEN-2016-037 | 07 - Southwestern Oklahoma | 132902 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | 1146800 | 100% | 1146800
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Cimarron 345/138kV New Transformer CKT3 | Current Study | Build a new 345/138kV transformer at Cimarron as a third circuit | 3663400 | 14.09% | 26000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Cimarron 345/138kV New Transformer CKT3 | Current Study | Build a new 345/138kV transformer at Cimarron as a third circuit | 226200 | 0.87% | 26000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Cimarron 345/138kV New Transformer CKT3 | Current Study | Build a new 345/138kV transformer at Cimarron as a third circuit | 413400 | 1.59% | 26000000
GEN-2016-107 | 01 - Woodward |  | NRIS | Cimarron 345/138kV New Transformer CKT3 | Current Study | Build a new 345/138kV transformer at Cimarron as a third circuit | 6539000 | 25.15% | 26000000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Cimarron 345/138kV New Transformer CKT3 | Current Study | Build a new 345/138kV transformer at Cimarron as a third circuit | 101400 | 0.39% | 26000000
GEN-2017-011 | 01 - Woodward |  | NRIS | Cimarron 345/138kV New Transformer CKT3 | Current Study | Build a new 345/138kV transformer at Cimarron as a third circuit | 2901600 | 11.16% | 26000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Cimarron 345/138kV New Transformer CKT3 | Current Study | Build a new 345/138kV transformer at Cimarron as a third circuit | 912600 | 3.51% | 26000000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Cimarron 345/138kV New Transformer CKT3 | Current Study | Build a new 345/138kV transformer at Cimarron as a third circuit | 1492400 | 5.74% | 26000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Cimarron 345/138kV New Transformer CKT3 | Current Study | Build a new 345/138kV transformer at Cimarron as a third circuit | 915200 | 3.52% | 26000000
GEN-2017-067 | 01 - Woodward |  | NRIS | Cimarron 345/138kV New Transformer CKT3 | Current Study | Build a new 345/138kV transformer at Cimarron as a third circuit | 7761000 | 29.85% | 26000000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Cimarron 345/138kV New Transformer CKT3 | Current Study | Build a new 345/138kV transformer at Cimarron as a third circuit | 954200 | 3.67% | 26000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Cimarron 345/138kV New Transformer CKT3 | Current Study | Build a new 345/138kV transformer at Cimarron as a third circuit | 7800 | 0.03% | 26000000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Cimarron 345/138kV New Transformer CKT3 | Current Study | Build a new 345/138kV transformer at Cimarron as a third circuit | 109200 | 0.42% | 26000000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Cimarron 345/138kV New Transformer CKT3 | Current Study | Build a new 345/138kV transformer at Cimarron as a third circuit | 2600 | 0.01% | 26000000
GEN-2016-005 | 03 - Spearville | 132899 | ERIS | Clark - Thistle 345 kV GEN-2016-005 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-005 (150 MW/Wind), into the Point of Interconnection (POI) at Clark - Thristle 345 kV. | 15081109 | 100% | 15081109
GEN-2016-005 | 03 - Spearville | 132898 | ERIS | Clark - Thistle 345 kV GEN-2016-005 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-005 (150 MW/Wind), into the Point of Interconnection (POI) at Clark - Thirstle 234 kV. | 1054767 | 100% | 1054767
GEN-2016-005 | 03 - Spearville |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 1920.6153 | 1.308% | 146888
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 44655.1744 | 30.4% | 146888
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 705.3258 | 0.4802% | 146888
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 1287.4328 | 0.8765% | 146888
GEN-2016-107 | 01 - Woodward |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 537.526 | 0.3659% | 146888
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 384.0807 | 0.2615% | 146888
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 778.6391 | 0.5301% | 146888
GEN-2017-011 | 01 - Woodward |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 1723.3569 | 1.173% | 146888
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 646.057 | 0.4398% | 146888
GEN-2017-018 | 03 - Spearville |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 1974.6873 | 1.344% | 146888
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 1177.8837 | 0.8019% | 146888
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 830.9788 | 0.5657% | 146888
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 1979.3685 | 1.348% | 146888
GEN-2017-032 | 03 - Spearville |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 3071.111 | 2.091% | 146888
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 7794.8173 | 5.307% | 146888
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 22572.1988 | 15.37% | 146888
GEN-2017-055 | 09 - Nebraska |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 566.466 | 0.3856% | 146888
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 327.0081 | 0.2226% | 146888
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 7806.5096 | 5.315% | 146888
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 24861.1231 | 16.93% | 146888
GEN-2017-067 | 01 - Woodward |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 18613.7607 | 12.67% | 146888
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 334.3343 | 0.2276% | 146888
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 300.3809 | 0.2045% | 146888
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 300.3809 | 0.2045% | 146888
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 98.3126 | 0.06693% | 146888
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 195.5029 | 0.1331% | 146888
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 525.4133 | 0.3577% | 146888
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 610.9447 | 0.4159% | 146888
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Cleveland 138kV Substation Upgrade | Current Study | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | 308.6097 | 0.2101% | 146888
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 133067 | ERIS | Clovis Interchange 115 kV Substation GEN-2017-087 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-087 (128 MW/Solar), into the Point of Interconnection (POI) at Clovis Interchange 115 kV Substation. | 3610830 | 100% | 3610830
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 133066 | ERIS | Clovis Interchange 115 kV Substation GEN-2017-087 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-087 (128 MW/Solar), into the Point of Interconnection (POI) at Clovis Interchange 115 kV Substation. | 634734 | 100% | 634734
GEN-2017-047 | 02 - Hitchland | 132997 | ERIS | Cole 115 kV Substation GEN-2017-047 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-047 (102 MW/Wind), into the Point of Interconnection (POI) at Cole 115 kV Substation. | 13148764 | 100% | 13148764
GEN-2017-047 | 02 - Hitchland | 132996 | ERIS | Cole 115 kV Substation GEN-2017-047 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-047 (102 MW/Wind), into the Point of Interconnection (POI) at Cole 115 kV Substation. | 759404 | 100% | 759404
GEN-2016-034 | 09 - Nebraska |  | ERIS | Cooper 345kV New Substation | Current Study | Build a new 345kV substation at Cooper | 772618.7104 | 1.515% | 51000000
GEN-2016-093 | 09 - Nebraska |  | ERIS | Cooper 345kV New Substation | Current Study | Build a new 345kV substation at Cooper | 635847.3803 | 1.247% | 51000000
GEN-2016-103 | 15 - Eastern South Dakota |  | ERIS | Cooper 345kV New Substation | Current Study | Build a new 345kV substation at Cooper | 8818756.6486 | 17.29% | 51000000
GEN-2016-109 | 09 - Nebraska |  | ERIS | Cooper 345kV New Substation | Current Study | Build a new 345kV substation at Cooper | 1411588.9707 | 2.768% | 51000000
GEN-2016-159 | 09 - Nebraska |  | ERIS | Cooper 345kV New Substation | Current Study | Build a new 345kV substation at Cooper | 7562145.7737 | 14.83% | 51000000
GEN-2017-001 | 09 - Nebraska |  | ERIS | Cooper 345kV New Substation | Current Study | Build a new 345kV substation at Cooper | 2898804.9414 | 5.684% | 51000000
GEN-2017-006 | 09 - Nebraska |  | ERIS | Cooper 345kV New Substation | Current Study | Build a new 345kV substation at Cooper | 1435804.8107 | 2.815% | 51000000
GEN-2017-008 | 09 - Nebraska |  | ERIS | Cooper 345kV New Substation | Current Study | Build a new 345kV substation at Cooper | 4900702.6824 | 9.609% | 51000000
GEN-2017-031 | 09 - Nebraska |  | ERIS | Cooper 345kV New Substation | Current Study | Build a new 345kV substation at Cooper | 900362.6604 | 1.765% | 51000000
GEN-2017-037 | 09 - Nebraska |  | ERIS | Cooper 345kV New Substation | Current Study | Build a new 345kV substation at Cooper | 181670.6801 | 0.3562% | 51000000
GEN-2017-055 | 09 - Nebraska |  | ERIS | Cooper 345kV New Substation | Current Study | Build a new 345kV substation at Cooper | 4789493.5324 | 9.391% | 51000000
GEN-2017-085 | 09 - Nebraska |  | ERIS | Cooper 345kV New Substation | Current Study | Build a new 345kV substation at Cooper | 10959.85 | 0.02149% | 51000000
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri |  | ERIS | Cooper 345kV New Substation | Current Study | Build a new 345kV substation at Cooper | 9960889.5699 | 19.53% | 51000000
GEN-2017-094 | 15 - Eastern South Dakota |  | ERIS | Cooper 345kV New Substation | Current Study | Build a new 345kV substation at Cooper | 6720353.789 | 13.18% | 51000000
GEN-2016-034 | 09 - Nebraska |  | ERIS | Cooper 345kV Reactive Support | Current Study | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | 75746.9324 | 1.515% | 5000000
GEN-2016-093 | 09 - Nebraska |  | ERIS | Cooper 345kV Reactive Support | Current Study | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | 62337.9785 | 1.247% | 5000000
GEN-2016-103 | 15 - Eastern South Dakota |  | ERIS | Cooper 345kV Reactive Support | Current Study | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | 864583.9852 | 17.29% | 5000000
GEN-2016-109 | 09 - Nebraska |  | ERIS | Cooper 345kV Reactive Support | Current Study | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | 138391.0756 | 2.768% | 5000000
GEN-2016-159 | 09 - Nebraska |  | ERIS | Cooper 345kV Reactive Support | Current Study | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | 741386.8406 | 14.83% | 5000000
GEN-2017-001 | 09 - Nebraska |  | ERIS | Cooper 345kV Reactive Support | Current Study | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | 284196.5629 | 5.684% | 5000000
GEN-2017-006 | 09 - Nebraska |  | ERIS | Cooper 345kV Reactive Support | Current Study | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | 140765.1775 | 2.815% | 5000000
GEN-2017-008 | 09 - Nebraska |  | ERIS | Cooper 345kV Reactive Support | Current Study | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | 480461.0473 | 9.609% | 5000000
GEN-2017-031 | 09 - Nebraska |  | ERIS | Cooper 345kV Reactive Support | Current Study | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | 88270.8491 | 1.765% | 5000000
GEN-2017-037 | 09 - Nebraska |  | ERIS | Cooper 345kV Reactive Support | Current Study | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | 17810.851 | 0.3562% | 5000000
GEN-2017-055 | 09 - Nebraska |  | ERIS | Cooper 345kV Reactive Support | Current Study | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | 469558.1894 | 9.391% | 5000000
GEN-2017-085 | 09 - Nebraska |  | ERIS | Cooper 345kV Reactive Support | Current Study | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | 1074.4951 | 0.02149% | 5000000
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri |  | ERIS | Cooper 345kV Reactive Support | Current Study | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | 976557.801 | 19.53% | 5000000
GEN-2017-094 | 15 - Eastern South Dakota |  | ERIS | Cooper 345kV Reactive Support | Current Study | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | 658858.2146 | 13.18% | 5000000
GEN-2016-103 | 15 - Eastern South Dakota |  | ERIS | Cooper to Holt 345kV New Build | Current Study | Build a new 32 mile 345kV line from Cooper to Holt | 21701058.021 | 34.58% | 62750000
GEN-2017-090 | 13 - Northeast Kansas/Northwest Missouri |  | ERIS | Cooper to Holt 345kV New Build | Current Study | Build a new 32 mile 345kV line from Cooper to Holt | 24511600.7972 | 39.06% | 62750000
GEN-2017-094 | 15 - Eastern South Dakota |  | ERIS | Cooper to Holt 345kV New Build | Current Study | Build a new 32 mile 345kV line from Cooper to Holt | 16537341.1818 | 26.35% | 62750000
GEN-2016-034 | 09 - Nebraska |  | ERIS | Cooper to Hoyt 345kV New Build | Current Study | Build a new 95 mile 345kV line from Cooper to Hoyt | 4491793.11 | 3.03% | 148250000
GEN-2016-093 | 09 - Nebraska |  | ERIS | Cooper to Hoyt 345kV New Build | Current Study | Build a new 95 mile 345kV line from Cooper to Hoyt | 3696642.15 | 2.494% | 148250000
GEN-2016-109 | 09 - Nebraska |  | ERIS | Cooper to Hoyt 345kV New Build | Current Study | Build a new 95 mile 345kV line from Cooper to Hoyt | 8206590.76 | 5.536% | 148250000
GEN-2016-159 | 09 - Nebraska |  | ERIS | Cooper to Hoyt 345kV New Build | Current Study | Build a new 95 mile 345kV line from Cooper to Hoyt | 43964239.62 | 29.66% | 148250000
GEN-2017-001 | 09 - Nebraska |  | ERIS | Cooper to Hoyt 345kV New Build | Current Study | Build a new 95 mile 345kV line from Cooper to Hoyt | 16852856.19 | 11.37% | 148250000
GEN-2017-006 | 09 - Nebraska |  | ERIS | Cooper to Hoyt 345kV New Build | Current Study | Build a new 95 mile 345kV line from Cooper to Hoyt | 8347375.05 | 5.631% | 148250000
GEN-2017-008 | 09 - Nebraska |  | ERIS | Cooper to Hoyt 345kV New Build | Current Study | Build a new 95 mile 345kV line from Cooper to Hoyt | 28491340.12 | 19.22% | 148250000
GEN-2017-031 | 09 - Nebraska |  | ERIS | Cooper to Hoyt 345kV New Build | Current Study | Build a new 95 mile 345kV line from Cooper to Hoyt | 5234461.35 | 3.531% | 148250000
GEN-2017-037 | 09 - Nebraska |  | ERIS | Cooper to Hoyt 345kV New Build | Current Study | Build a new 95 mile 345kV line from Cooper to Hoyt | 1056183.47 | 0.7124% | 148250000
GEN-2017-055 | 09 - Nebraska |  | ERIS | Cooper to Hoyt 345kV New Build | Current Study | Build a new 95 mile 345kV line from Cooper to Hoyt | 27844800.64 | 18.78% | 148250000
GEN-2017-085 | 09 - Nebraska |  | ERIS | Cooper to Hoyt 345kV New Build | Current Study | Build a new 95 mile 345kV line from Cooper to Hoyt | 63717.54 | 0.04298% | 148250000
GEN-2016-005 | 03 - Spearville |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 33647.2928 | 1.34% | 2510992
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 85624.8272 | 3.41% | 2510992
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 7281.8768 | 0.29% | 2510992
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 13308.2576 | 0.53% | 2510992
GEN-2016-107 | 01 - Woodward |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 23352.2256 | 0.93% | 2510992
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 41431.368 | 1.65% | 2510992
GEN-2016-159 | 09 - Nebraska |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 537854.4864 | 21.42% | 2510992
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 34400.5904 | 1.37% | 2510992
GEN-2017-011 | 01 - Woodward |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 251.0992 | 0.01% | 2510992
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 61519.304 | 2.45% | 2510992
GEN-2017-018 | 03 - Spearville |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 9290.6704 | 0.37% | 2510992
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 11048.3648 | 0.44% | 2510992
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 53484.1296 | 2.13% | 2510992
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 30885.2016 | 1.23% | 2510992
GEN-2017-028 | 01 - Woodward |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 12806.0592 | 0.51% | 2510992
GEN-2017-032 | 03 - Spearville |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 89893.5136 | 3.58% | 2510992
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 36158.2848 | 1.44% | 2510992
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 31136.3008 | 1.24% | 2510992
GEN-2017-047 | 02 - Hitchland |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 3264.2896 | 0.13% | 2510992
GEN-2017-048 | 16 - Western North Dakota |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 168236.464 | 6.7% | 2510992
GEN-2017-055 | 09 - Nebraska |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 768363.552 | 30.6% | 2510992
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 52228.6336 | 2.08% | 2510992
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 36158.2848 | 1.44% | 2510992
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 48211.0464 | 1.92% | 2510992
GEN-2017-067 | 01 - Woodward |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 55492.9232 | 2.21% | 2510992
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 25109.92 | 1% | 2510992
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 24858.8208 | 0.99% | 2510992
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 108223.7552 | 4.31% | 2510992
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 28374.2096 | 1.13% | 2510992
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 41933.5664 | 1.67% | 2510992
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 33647.2928 | 1.34% | 2510992
GEN-2017-100 | 02 - Hitchland |  | NRIS | Council Bluffs to S3456 345kV Rebuild | Current Study | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 3515.3888 | 0.14% | 2510992
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 366659.7147 | 4.184% | 8764205
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 219514.8915 | 2.505% | 8764205
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 293028.537 | 3.343% | 8764205
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 388810.2845 | 4.436% | 8764205
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 234144.7145 | 2.672% | 8764205
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 664063.3389 | 7.577% | 8764205
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 733281.25 | 8.367% | 8764205
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 422210.3992 | 4.817% | 8764205
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 81367.7932 | 0.9284% | 8764205
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 585349.5023 | 6.679% | 8764205
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 541121.3663 | 6.174% | 8764205
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 500620.5206 | 5.712% | 8764205
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 8876.4765 | 0.1013% | 8764205
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 148852.6823 | 1.698% | 8764205
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 1307695.6672 | 14.92% | 8764205
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 767574.8432 | 8.758% | 8764205
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 263689.2409 | 3.009% | 8764205
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 315540.8344 | 3.6% | 8764205
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 83957.2397 | 0.958% | 8764205
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer | Current Study | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | 837845.703 | 9.56% | 8764205
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 336134.4538 | 4.202% | 8000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 201680.6723 | 2.521% | 8000000
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 268907.563 | 3.361% | 8000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 355342.1369 | 4.442% | 8000000
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 216086.4346 | 2.701% | 8000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 605042.0168 | 7.563% | 8000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 667466.9868 | 8.343% | 8000000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 384153.6615 | 4.802% | 8000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 72028.8115 | 0.9004% | 8000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 533013.2053 | 6.663% | 8000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 494597.8391 | 6.182% | 8000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 456182.473 | 5.702% | 8000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 9603.8415 | 0.12% | 8000000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 134453.7815 | 1.681% | 8000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 1195678.2713 | 14.95% | 8000000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 701080.4322 | 8.764% | 8000000
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 240096.0384 | 3.001% | 8000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 288115.2461 | 3.601% | 8000000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 76830.7323 | 0.9604% | 8000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | Current Study | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 763505.4022 | 9.544% | 8000000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 336134.4538 | 4.202% | 8000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 201680.6723 | 2.521% | 8000000
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 268907.563 | 3.361% | 8000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 355342.1369 | 4.442% | 8000000
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 216086.4346 | 2.701% | 8000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 605042.0168 | 7.563% | 8000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 667466.9868 | 8.343% | 8000000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 384153.6615 | 4.802% | 8000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 72028.8115 | 0.9004% | 8000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 533013.2053 | 6.663% | 8000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 494597.8391 | 6.182% | 8000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 456182.473 | 5.702% | 8000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 9603.8415 | 0.12% | 8000000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 134453.7815 | 1.681% | 8000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 1195678.2713 | 14.95% | 8000000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 701080.4322 | 8.764% | 8000000
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 240096.0384 | 3.001% | 8000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 288115.2461 | 3.601% | 8000000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 76830.7323 | 0.9604% | 8000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | Current Study | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | 763505.4022 | 9.544% | 8000000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 348139.2557 | 1.741% | 20000000
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 168067.2269 | 0.8403% | 20000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 264105.6423 | 1.321% | 20000000
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 768307.3229 | 3.842% | 20000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 564225.6903 | 2.821% | 20000000
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 420168.0672 | 2.101% | 20000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 972388.9556 | 4.862% | 20000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 2629051.6206 | 13.15% | 20000000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 660264.1056 | 3.301% | 20000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 288115.2461 | 1.441% | 20000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 2112845.1381 | 10.56% | 20000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 1692677.0708 | 8.463% | 20000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 48019.2077 | 0.2401% | 20000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 36014.4058 | 0.1801% | 20000000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 216086.4346 | 1.08% | 20000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 4717887.1549 | 23.59% | 20000000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 780312.1248 | 3.902% | 20000000
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 336134.4538 | 1.681% | 20000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 1104441.7767 | 5.522% | 20000000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 120048.0192 | 0.6002% | 20000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Substation | Current Study | Build a new 345/765kV substation at Crawfish Draw | 1752701.0804 | 8.764% | 20000000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 348139.2557 | 1.741% | 20000000
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 168067.2269 | 0.8403% | 20000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 264105.6423 | 1.321% | 20000000
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 768307.3229 | 3.842% | 20000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 564225.6903 | 2.821% | 20000000
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 420168.0672 | 2.101% | 20000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 972388.9556 | 4.862% | 20000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 2629051.6206 | 13.15% | 20000000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 660264.1056 | 3.301% | 20000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 288115.2461 | 1.441% | 20000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 2112845.1381 | 10.56% | 20000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 1692677.0708 | 8.463% | 20000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 48019.2077 | 0.2401% | 20000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 36014.4058 | 0.1801% | 20000000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 216086.4346 | 1.08% | 20000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 4717887.1549 | 23.59% | 20000000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 780312.1248 | 3.902% | 20000000
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 336134.4538 | 1.681% | 20000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 1104441.7767 | 5.522% | 20000000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 120048.0192 | 0.6002% | 20000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw 765/345kV New Transformer | Current Study | Build a new 345/765kV transformer at Crawfish Draw | 1752701.0804 | 8.764% | 20000000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 6614645.8583 | 1.741% | 380000000
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 3193277.3109 | 0.8403% | 380000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 5018007.2029 | 1.321% | 380000000
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 14597839.1357 | 3.842% | 380000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 10720288.1152 | 2.821% | 380000000
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 7983193.2773 | 2.101% | 380000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 18475390.1561 | 4.862% | 380000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 49951980.7923 | 13.15% | 380000000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 12545018.0072 | 3.301% | 380000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 5474189.6759 | 1.441% | 380000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 40144057.623 | 10.56% | 380000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 32160864.3457 | 8.463% | 380000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 912364.946 | 0.2401% | 380000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 684273.7095 | 0.1801% | 380000000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 4105642.2569 | 1.08% | 380000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 89639855.9424 | 23.59% | 380000000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 14825930.3721 | 3.902% | 380000000
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 6386554.6218 | 1.681% | 380000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 20984393.7575 | 5.522% | 380000000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 2280912.3649 | 0.6002% | 380000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Crossroads 765kV New Build | Current Study | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | 33301320.5282 | 8.764% | 380000000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 10274933.7008 | 4.184% | 245600000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 6151483.1405 | 2.505% | 245600000
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 8211561.7207 | 3.343% | 245600000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 10895661.0009 | 4.436% | 245600000
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 6561455.7605 | 2.672% | 245600000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 18609098.7615 | 7.577% | 245600000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 20548797.5417 | 8.367% | 245600000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 11831634.781 | 4.817% | 245600000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 2280175.9202 | 0.9284% | 245600000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 16403294.3413 | 6.679% | 245600000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 15163886.2812 | 6.174% | 245600000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 14028927.7211 | 5.712% | 245600000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 248746.44 | 0.1013% | 245600000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 4171310.1603 | 1.698% | 245600000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 36645657.603 | 14.92% | 245600000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 21509809.6218 | 8.758% | 245600000
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 7389384.0606 | 3.009% | 245600000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 8842425.4207 | 3.6% | 245600000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 2352740.5202 | 0.958% | 245600000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Grapevine 345kV New Build | Current Study | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | 23479015.5019 | 9.56% | 245600000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 23468194.6019 | 4.184% | 560956277
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 14050134.1889 | 2.505% | 560956277
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 18755403.0475 | 3.343% | 560956277
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 24885950.2578 | 4.436% | 560956277
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 14986521.5787 | 2.672% | 560956277
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 42503626.7726 | 7.577% | 560956277
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 46933945.5168 | 8.367% | 560956277
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 27023737.3105 | 4.817% | 560956277
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 5207976.5731 | 0.9284% | 560956277
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 37465517.6994 | 6.679% | 560956277
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 34634679.0213 | 6.174% | 560956277
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 32042406.9767 | 5.712% | 560956277
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 568142.2564 | 0.1013% | 560956277
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 9527372.5901 | 1.698% | 560956277
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 83699558.9382 | 14.92% | 560956277
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 49128920.0079 | 8.758% | 560956277
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 16877530.2313 | 3.009% | 560956277
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 20196311.2099 | 3.6% | 560956277
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 5373715.0848 | 0.958% | 560956277
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | Current Study | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | 53626633.1363 | 9.56% | 560956277
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 11523409.3637 | 1.741% | 662000000
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 5563025.2101 | 0.8403% | 662000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 8741896.7587 | 1.321% | 662000000
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 25430972.389 | 3.842% | 662000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 18675870.3481 | 2.821% | 662000000
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 13907563.0252 | 2.101% | 662000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 32186074.4298 | 4.862% | 662000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 87021608.6435 | 13.15% | 662000000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 21854741.8968 | 3.301% | 662000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 9536614.6459 | 1.441% | 662000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 69935174.0696 | 10.56% | 662000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 56027611.0444 | 8.463% | 662000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 1589435.7743 | 0.2401% | 662000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 1192076.8307 | 0.1801% | 662000000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 7152460.9844 | 1.08% | 662000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 156162064.8259 | 23.59% | 662000000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 25828331.3325 | 3.902% | 662000000
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 11126050.4202 | 1.681% | 662000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 36557022.8091 | 5.522% | 662000000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 3973589.4358 | 0.6002% | 662000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | 58014405.7623 | 8.764% | 662000000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 11523409.3637 | 1.741% | 662000000
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 5563025.2101 | 0.8403% | 662000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 8741896.7587 | 1.321% | 662000000
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 25430972.389 | 3.842% | 662000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 18675870.3481 | 2.821% | 662000000
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 13907563.0252 | 2.101% | 662000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 32186074.4298 | 4.862% | 662000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 87021608.6435 | 13.15% | 662000000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 21854741.8968 | 3.301% | 662000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 9536614.6459 | 1.441% | 662000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 69935174.0696 | 10.56% | 662000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 56027611.0444 | 8.463% | 662000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 1589435.7743 | 0.2401% | 662000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 1192076.8307 | 0.1801% | 662000000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 7152460.9844 | 1.08% | 662000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 156162064.8259 | 23.59% | 662000000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 25828331.3325 | 3.902% | 662000000
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 11126050.4202 | 1.681% | 662000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 36557022.8091 | 5.522% | 662000000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 3973589.4358 | 0.6002% | 662000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | Current Study | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | 58014405.7623 | 8.764% | 662000000
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas | 132933 | ERIS | Creswell 69 kV Substation GEN-2016-173 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-173 (42 MW/Solar), into the Point of Interconnection (POI) at Creswell 69 kV Substation. | 16242935.8 | 100% | 16242935.8
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas | 132932 | ERIS | Creswell 69 kV Substation GEN-2016-173 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-173 (42 MW/Solar), into the Point of Interconnection (POI) at Creswell 69 kV Substation. | 605450.91 | 100% | 605450.91
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 348139.2557 | 1.741% | 20000000
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 168067.2269 | 0.8403% | 20000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 264105.6423 | 1.321% | 20000000
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 768307.3229 | 3.842% | 20000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 564225.6903 | 2.821% | 20000000
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 420168.0672 | 2.101% | 20000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 972388.9556 | 4.862% | 20000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 2629051.6206 | 13.15% | 20000000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 660264.1056 | 3.301% | 20000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 288115.2461 | 1.441% | 20000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 2112845.1381 | 10.56% | 20000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 1692677.0708 | 8.463% | 20000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 48019.2077 | 0.2401% | 20000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 36014.4058 | 0.1801% | 20000000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 216086.4346 | 1.08% | 20000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 4717887.1549 | 23.59% | 20000000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 780312.1248 | 3.902% | 20000000
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 336134.4538 | 1.681% | 20000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 1104441.7767 | 5.522% | 20000000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 120048.0192 | 0.6002% | 20000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer | Current Study | Build a new 765/345kV Transformer at Crossroads | 1752701.0804 | 8.764% | 20000000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 348139.2557 | 1.741% | 20000000
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 168067.2269 | 0.8403% | 20000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 264105.6423 | 1.321% | 20000000
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 768307.3229 | 3.842% | 20000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 564225.6903 | 2.821% | 20000000
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 420168.0672 | 2.101% | 20000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 972388.9556 | 4.862% | 20000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 2629051.6206 | 13.15% | 20000000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 660264.1056 | 3.301% | 20000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 288115.2461 | 1.441% | 20000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 2112845.1381 | 10.56% | 20000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 1692677.0708 | 8.463% | 20000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 48019.2077 | 0.2401% | 20000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 36014.4058 | 0.1801% | 20000000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 216086.4346 | 1.08% | 20000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 4717887.1549 | 23.59% | 20000000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 780312.1248 | 3.902% | 20000000
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 336134.4538 | 1.681% | 20000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 1104441.7767 | 5.522% | 20000000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 120048.0192 | 0.6002% | 20000000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Crossroads 765/345kV New Transformer CKT 2 | Current Study | Build a new 765/345kV Transformer at Crossroads as a second circuit | 1752701.0804 | 8.764% | 20000000
GEN-2016-005 | 03 - Spearville |  | NRIS | Diana 345kV Substation Upgrade | Current Study | Update breaker configuration at Diana 345kV | 374083.3656 | 2.03% | 18427752
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Diana 345kV Substation Upgrade | Current Study | Update breaker configuration at Diana 345kV | 1599528.8736 | 8.68% | 18427752
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Diana 345kV Substation Upgrade | Current Study | Update breaker configuration at Diana 345kV | 2961339.7464 | 16.07% | 18427752
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Diana 345kV Substation Upgrade | Current Study | Update breaker configuration at Diana 345kV | 409096.0944 | 2.22% | 18427752
GEN-2017-018 | 03 - Spearville |  | NRIS | Diana 345kV Substation Upgrade | Current Study | Update breaker configuration at Diana 345kV | 545461.4592 | 2.96% | 18427752
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Diana 345kV Substation Upgrade | Current Study | Update breaker configuration at Diana 345kV | 2207644.6896 | 11.98% | 18427752
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Diana 345kV Substation Upgrade | Current Study | Update breaker configuration at Diana 345kV | 1254929.9112 | 6.81% | 18427752
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Diana 345kV Substation Upgrade | Current Study | Update breaker configuration at Diana 345kV | 2027052.72 | 11% | 18427752
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Diana 345kV Substation Upgrade | Current Study | Update breaker configuration at Diana 345kV | 64497.132 | 0.35% | 18427752
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Diana 345kV Substation Upgrade | Current Study | Update breaker configuration at Diana 345kV | 3095862.336 | 16.8% | 18427752
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Diana 345kV Substation Upgrade | Current Study | Update breaker configuration at Diana 345kV | 3742676.4312 | 20.31% | 18427752
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Diana 345kV Substation Upgrade | Current Study | Update breaker configuration at Diana 345kV | 145579.2408 | 0.79% | 18427752
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Domes to Elizack 138kV Rebuild | Current Study | Rebuild the existing Domes to Elizack 138kV 13.59 mile line to achieve a minimum winter/emergency rating of 231 MVA | 21063272 | 100% | 21063272
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Domes to Western Walls 138kV Rebuild | Current Study | Rebuild the existing Domes to Western Walls 138kV 5.74 mile line to achieve a minimum winter/emergency rating of 236 MVA | 8271597 | 100% | 8271597
GEN-2016-109 | 09 - Nebraska |  | ERIS | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Current Study | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA | 1992600 | 2.46% | 81000000
GEN-2016-159 | 09 - Nebraska |  | ERIS | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Current Study | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA | 7541100 | 9.31% | 81000000
GEN-2017-001 | 09 - Nebraska |  | ERIS | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Current Study | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA | 3045600 | 3.76% | 81000000
GEN-2017-006 | 09 - Nebraska |  | ERIS | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Current Study | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA | 1490400 | 1.84% | 81000000
GEN-2017-008 | 09 - Nebraska |  | ERIS | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Current Study | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA | 5143500 | 6.35% | 81000000
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri |  | ERIS | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Current Study | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA | 14183100 | 17.51% | 81000000
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri |  | ERIS | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Current Study | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA | 14183100 | 17.51% | 81000000
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri |  | ERIS | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Current Study | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA | 14183100 | 17.51% | 81000000
GEN-2017-055 | 09 - Nebraska |  | ERIS | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Current Study | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA | 5046300 | 6.23% | 81000000
GEN-2017-085 | 09 - Nebraska |  | ERIS | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Current Study | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA | 8100 | 0.01% | 81000000
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri |  | ERIS | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | Current Study | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA | 14183100 | 17.51% | 81000000
GEN-2016-107 | 01 - Woodward |  | ERIS | Dover Switch to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover Switch to Okeene 138kV 27.24 mile line to acieve a minimum winter/normal rating of 121 MVA | 26263691.16 | 100% | 26263691.16
GEN-2016-005 | 03 - Spearville |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 343407.5405 | 1.308% | 26263691.16
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 7984380.6802 | 30.4% | 26263691.16
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 126112.8102 | 0.4802% | 26263691.16
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 230194.0063 | 0.8765% | 26263691.16
GEN-2016-107 | 01 - Woodward |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 96110.0753 | 0.3659% | 26263691.16
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 68673.9369 | 0.2615% | 26263691.16
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 139221.2901 | 0.5301% | 26263691.16
GEN-2017-011 | 01 - Woodward |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 308137.5771 | 1.173% | 26263691.16
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 115515.5015 | 0.4398% | 26263691.16
GEN-2017-018 | 03 - Spearville |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 353075.658 | 1.344% | 26263691.16
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 210606.5455 | 0.8019% | 26263691.16
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 148579.6771 | 0.5657% | 26263691.16
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 353912.6546 | 1.348% | 26263691.16
GEN-2017-032 | 03 - Spearville |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 549117.085 | 2.091% | 26263691.16
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 1393719.531 | 5.307% | 26263691.16
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 4035927.0835 | 15.37% | 26263691.16
GEN-2017-055 | 09 - Nebraska |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 101284.5658 | 0.3856% | 26263691.16
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 58469.3156 | 0.2226% | 26263691.16
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 1395810.1208 | 5.315% | 26263691.16
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 4445188.5651 | 16.93% | 26263691.16
GEN-2017-067 | 01 - Woodward |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 3328155.2073 | 12.67% | 26263691.16
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 59779.2399 | 0.2276% | 26263691.16
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 53708.3424 | 0.2045% | 26263691.16
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 53708.3424 | 0.2045% | 26263691.16
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 17578.3789 | 0.06693% | 26263691.16
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 34956.067 | 0.1331% | 26263691.16
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 93944.317 | 0.3577% | 26263691.16
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 109237.3926 | 0.4159% | 26263691.16
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Dover to Okeene 138kV Rebuild | Current Study | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | 55179.6525 | 0.2101% | 26263691.16
GEN-2016-005 | 03 - Spearville |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 1563.92 | 0.3475% | 450000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 16656.71 | 3.701% | 450000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 1994.28 | 0.4432% | 450000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 3693.12 | 0.8207% | 450000
GEN-2016-107 | 01 - Woodward |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 2314.7895 | 0.5144% | 450000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 150.8355 | 0.03352% | 450000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 2562.75 | 0.5695% | 450000
GEN-2017-018 | 03 - Spearville |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 1885.86 | 0.4191% | 450000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 15642.135 | 3.476% | 450000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 17912.87 | 3.981% | 450000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 296627.56 | 65.92% | 450000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 18214.35 | 4.048% | 450000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 4006.8 | 0.8904% | 450000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 704.71 | 0.1566% | 450000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 18241.67 | 4.054% | 450000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 2614.12 | 0.5809% | 450000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 663.07 | 0.1473% | 450000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 801.43 | 0.1781% | 450000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 40523.78 | 9.005% | 450000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 865.55 | 0.1923% | 450000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 1362.8 | 0.3028% | 450000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Dripping Spring to Springdale 138kV Rebuild | Current Study | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | 996.89 | 0.2215% | 450000
GEN-2016-005 | 03 - Spearville |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 4865.53 | 0.3475% | 1400000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 51820.87 | 3.701% | 1400000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 6204.43 | 0.4432% | 1400000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 11489.69 | 0.8207% | 1400000
GEN-2016-107 | 01 - Woodward |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 7201.58 | 0.5144% | 1400000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 469.2 | 0.03351% | 1400000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 7972.44 | 0.5695% | 1400000
GEN-2017-018 | 03 - Spearville |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 5866 | 0.419% | 1400000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 48665.11 | 3.476% | 1400000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 55728.92 | 3.981% | 1400000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 922841.29 | 65.92% | 1400000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 56666.86 | 4.048% | 1400000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 12466.71 | 0.8905% | 1400000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 2192.42 | 0.1566% | 1400000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 56751.86 | 4.054% | 1400000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 8132.83 | 0.5809% | 1400000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 2062.87 | 0.1473% | 1400000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 2493.34 | 0.1781% | 1400000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 126073.99 | 9.005% | 1400000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 2692.81 | 0.1923% | 1400000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 4239.81 | 0.3028% | 1400000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Dripping Spring to Stirling 138kV Rebuild | Current Study | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | 3101.44 | 0.2215% | 1400000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 133039 | ERIS | Dry Gulch 161 kV Substation GEN-2017-073 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-073 (72.5 MW/Solar), into the Point of Interconnection (POI) at Dry Gulch 161 kV Substation. | 42000 | 100% | 42000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas | 133038 | ERIS | Dry Gulch 161 kV Substation GEN-2017-073 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-073 (72.5 MW/Solar), into the Point of Interconnection (POI) at Dry Gulch 161 kV Substation. | 1100000 | 100% | 1100000
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri | 132977 | ERIS | Eastown - Iatan 345 kV GEN-2017-030 Interconnection (Non-Shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-030 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | 3081098 | 100% | 3081098
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri | 132976 | ERIS | Eastown - Iatan 345 kV GEN-2017-030 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-030 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | 11083 | 100% | 11083
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri | 132989 | ERIS | Eastown - Iatan 345 kV GEN-2017-038 Interconnection (Non-Shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-038 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | 3081098 | 100% | 3081098
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri | 132988 | ERIS | Eastown - Iatan 345 kV GEN-2017-038 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-038 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | 11083 | 100% | 11083
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri | 132995 | ERIS | Eastown - Iatan 345 kV GEN-2017-041 Interconnection (Non-Shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-041 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | 3081098 | 100% | 3081098
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri | 132994 | ERIS | Eastown - Iatan 345 kV GEN-2017-041 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-041 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | 11083 | 100% | 11083
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri | 133075 | ERIS | Eastown - Iatan 345 kV GEN-2017-095 Interconnection (Non-Shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-095 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | 3081098 | 100% | 3081098
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri | 133074 | ERIS | Eastown - Iatan 345 kV GEN-2017-095 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-095 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | 11083 | 100% | 11083
GEN-2016-005 | 03 - Spearville |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 495000 | 0.99% | 50000000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 1365000 | 2.73% | 50000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 200000 | 0.4% | 50000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 365000 | 0.73% | 50000000
GEN-2016-093 | 09 - Nebraska |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 580000 | 1.16% | 50000000
GEN-2016-103 | 15 - Eastern South Dakota |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 5415000 | 10.83% | 50000000
GEN-2016-107 | 01 - Woodward |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 700000 | 1.4% | 50000000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 1535000 | 3.07% | 50000000
GEN-2016-159 | 09 - Nebraska |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 6595000 | 13.19% | 50000000
GEN-2017-001 | 09 - Nebraska |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 2460000 | 4.92% | 50000000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 2755000 | 5.51% | 50000000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 6180000 | 12.36% | 50000000
GEN-2017-018 | 03 - Spearville |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 1095000 | 2.19% | 50000000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 180000 | 0.36% | 50000000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 110000 | 0.22% | 50000000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 475000 | 0.95% | 50000000
GEN-2017-028 | 01 - Woodward |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 235000 | 0.47% | 50000000
GEN-2017-031 | 09 - Nebraska |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 830000 | 1.66% | 50000000
GEN-2017-032 | 03 - Spearville |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 50000 | 0.1% | 50000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 730000 | 1.46% | 50000000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 440000 | 0.88% | 50000000
GEN-2017-037 | 09 - Nebraska |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 165000 | 0.33% | 50000000
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 1130000 | 2.26% | 50000000
GEN-2017-047 | 02 - Hitchland |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 355000 | 0.71% | 50000000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 3465000 | 6.93% | 50000000
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 25000 | 0.05% | 50000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 2005000 | 4.01% | 50000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 735000 | 1.47% | 50000000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 650000 | 1.3% | 50000000
GEN-2017-067 | 01 - Woodward |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 875000 | 1.75% | 50000000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 1145000 | 2.29% | 50000000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 500000 | 1% | 50000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 500000 | 1% | 50000000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 560000 | 1.12% | 50000000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 235000 | 0.47% | 50000000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 860000 | 1.72% | 50000000
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 1130000 | 2.26% | 50000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 2520000 | 5.04% | 50000000
GEN-2017-100 | 02 - Hitchland |  | NRIS | Eastowne 161kV Reactive Support | Current Study | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | 355000 | 0.71% | 50000000
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 133049 | ERIS | Eddy County - Tolk 345 kV GEN-2017-078 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-078 (300 MW/Wind), into the Point of Interconnection (POI) at Eddy County - Tolk 345 kV. | 1098575 | 100% | 1098575
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico | 133048 | ERIS | Eddy County - Tolk 345 kV GEN-2017-078 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-078 (300 MW/Wind), into the Point of Interconnection (POI) at Eddy County - Tolk 345 kV. | 1644416 | 100% | 1644416
GEN-2017-028 | 01 - Woodward | 143119 | ERIS | El Reno 138 kV Switching Station GEN-2017-028 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2017-028 (50 MW/Solar), into the Point of Interconnection (POI) at El Reno 138 kV Substation. | 15000 | 100% | 15000
GEN-2017-028 | 01 - Woodward | 132974 | ERIS | El Reno 138 kV Switching Station GEN-2017-028 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-028 (50 MW/Solar), into the Point of Interconnection (POI) at El Reno 138 kV Switching Station. | 400000 | 100% | 400000
GEN-2016-107 | 01 - Woodward |  | ERIS | El Reno to Scott Switch 138kV Rebuild | Current Study | Rebuild the existing El Reno to Scott Switch 138kV 6.45 mile line to achieve a minimum spring/emergency rating of 146 MVA | 6218825.55 | 100% | 6218825.55
GEN-2017-004 | 04 - Northwest Kansas | 132937 | ERIS | Elm Creek - Summit 345 kV GEN-2017-004 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-004 (201.6 MW/Wind), into the Point of Interconnection (POI) at Elm Creek - Summit 345 kV. | 15081109 | 100% | 15081109
GEN-2017-004 | 04 - Northwest Kansas | 132936 | ERIS | Elm Creek - Summit 345 kV GEN-2017-004 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-004 (201.6 MW/Wind), into the Point of Interconnection (POI) at Elm Creek - Summit 345 kV. | 1054767 | 100% | 1054767
ASGI-2017-007 | 06 - South Texas Panhandle/New Mexico | 132897 | ERIS | Erskine 69 kV Substation ASGI-2017-007 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, ASGI-2017-007 (4.2 MW/Wind), into the Point of Interconnection (POI) at Erskine 69 kV Substation. | 4382573.1852 | 100% | 4382573.1852
ASGI-2017-007 | 06 - South Texas Panhandle/New Mexico | 132896 | ERIS | Erskine 69 kV Substation ASGI-2017-007 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, ASGI-2017-007 (4.2 MW/Wind), into the Point of Interconnection (POI) at Erskine 69 kV Substation. | 883481 | 100% | 883481
GEN-2017-053 | 07 - Southwestern Oklahoma |  | ERIS | Essaquandale Jct. to Walters 69kV Rebuild | Current Study | Rebuild the existing Essaquandale Jct. to Walters 69kV 1.19 mile line to achieve a minimum light/emergency rating of 66 MVA | 2350861 | 100% | 2350861
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Eureka to Grandview 161kV Rebuild | Current Study | Rebuild the existing Eureka to Grandview 161kV 10.56 mile line to achieve a minimum winter/emergency rating of 274 MVA | 141250 | 1.13% | 12500000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Eureka to Grandview 161kV Rebuild | Current Study | Rebuild the existing Eureka to Grandview 161kV 10.56 mile line to achieve a minimum winter/emergency rating of 274 MVA | 2418750 | 19.35% | 12500000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Eureka to Grandview 161kV Rebuild | Current Study | Rebuild the existing Eureka to Grandview 161kV 10.56 mile line to achieve a minimum winter/emergency rating of 274 MVA | 281250 | 2.25% | 12500000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Eureka to Grandview 161kV Rebuild | Current Study | Rebuild the existing Eureka to Grandview 161kV 10.56 mile line to achieve a minimum winter/emergency rating of 274 MVA | 180000 | 1.44% | 12500000
GEN-2017-032 | 03 - Spearville |  | NRIS | Eureka to Grandview 161kV Rebuild | Current Study | Rebuild the existing Eureka to Grandview 161kV 10.56 mile line to achieve a minimum winter/emergency rating of 274 MVA | 228750 | 1.83% | 12500000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Eureka to Grandview 161kV Rebuild | Current Study | Rebuild the existing Eureka to Grandview 161kV 10.56 mile line to achieve a minimum winter/emergency rating of 274 MVA | 1462500 | 11.7% | 12500000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Eureka to Grandview 161kV Rebuild | Current Study | Rebuild the existing Eureka to Grandview 161kV 10.56 mile line to achieve a minimum winter/emergency rating of 274 MVA | 765000 | 6.12% | 12500000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Eureka to Grandview 161kV Rebuild | Current Study | Rebuild the existing Eureka to Grandview 161kV 10.56 mile line to achieve a minimum winter/emergency rating of 274 MVA | 167500 | 1.34% | 12500000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Eureka to Grandview 161kV Rebuild | Current Study | Rebuild the existing Eureka to Grandview 161kV 10.56 mile line to achieve a minimum winter/emergency rating of 274 MVA | 1767500 | 14.14% | 12500000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Eureka to Grandview 161kV Rebuild | Current Study | Rebuild the existing Eureka to Grandview 161kV 10.56 mile line to achieve a minimum winter/emergency rating of 274 MVA | 950000 | 7.6% | 12500000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Eureka to Grandview 161kV Rebuild | Current Study | Rebuild the existing Eureka to Grandview 161kV 10.56 mile line to achieve a minimum winter/emergency rating of 274 MVA | 2677500 | 21.42% | 12500000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Eureka to Grandview 161kV Rebuild | Current Study | Rebuild the existing Eureka to Grandview 161kV 10.56 mile line to achieve a minimum winter/emergency rating of 274 MVA | 475000 | 3.8% | 12500000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Eureka to Grandview 161kV Rebuild | Current Study | Rebuild the existing Eureka to Grandview 161kV 10.56 mile line to achieve a minimum winter/emergency rating of 274 MVA | 985000 | 7.88% | 12500000
GEN-2016-107 | 01 - Woodward |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 719900 | 6.26% | 11500000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 235750 | 2.05% | 11500000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 1957300 | 17.02% | 11500000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 132250 | 1.15% | 11500000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 62100 | 0.54% | 11500000
GEN-2017-032 | 03 - Spearville |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 289800 | 2.52% | 11500000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 412850 | 3.59% | 11500000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 977500 | 8.5% | 11500000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 603750 | 5.25% | 11500000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 670450 | 5.83% | 11500000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 307050 | 2.67% | 11500000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 1535250 | 13.35% | 11500000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 88550 | 0.77% | 11500000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 2149350 | 18.69% | 11500000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 565800 | 4.92% | 11500000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Eureka to Osage 161kV Rebuild | Current Study | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | 792350 | 6.89% | 11500000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 133047 | ERIS | Explorer - Claremore 69 kV GEN-2017-077 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-077 (124.7 MW/Solar), into the Point of Interconnection (POI) at Explorer - Claremore 69 kV. | 10334726 | 100% | 10334726
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas | 133046 | ERIS | Explorer - Claremore 69 kV GEN-2017-077 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-077 (124.7 MW/Solar), into the Point of Interconnection (POI) at Explorer - Claremore 69 kV. | 1146800 | 100% | 1146800
GEN-2016-109 | 09 - Nebraska | 132923 | ERIS | Fairbury 115 kV Substation GEN-2016-109 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-109 (102 MW/Wind), into the Point of Interconnection (POI) at Fairbury 115 kV Substation. | 3650000 | 100% | 3650000
GEN-2016-109 | 09 - Nebraska | 132922 | ERIS | Fairbury 115 kV Substation GEN-2016-109 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-109 (102 MW/Wind), into the Point of Interconnection (POI) at Fairbury 115 kV Substation. | 3650000 | 100% | 3650000
GEN-2016-109 | 09 - Nebraska |  | ERIS | Fairbury to Hebron N 115kV Rebuild | Current Study | Rebuild the existing Fairbury to Hebron 115kV 22 mile line to achieve a minimum emergency rating of 101 MVA | 5500000 | 100% | 5500000
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Farber to Belle Plaine 138kV Rebuild | Current Study | Rebuild the existing Farber to Belle Plain 138kV 10.33 mile line to achieve a minimum summer/emergency rating of 172 MVA | 14679632.18 | 100% | 14679632.18
GEN-2017-032 | 03 - Spearville | 132981 | ERIS | Finney - Lamar 345 kV GEN-2017-032 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-032 (200 MW/Wind), into the Point of Interconnection (POI) at Finney - Lamar 345 kV. | 12750261 | 100% | 12750261
GEN-2017-032 | 03 - Spearville | 132980 | ERIS | Finney - Lamar 345 kV GEN-2017-032 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-032 (200 MW/Wind), into the Point of Interconnection (POI) at Finney - Lamar 345 kV. | 1708037 | 100% | 1708037
GEN-2017-032 | 03 - Spearville |  | ERIS | Finney 345kV Reactive Support | Current Study | Install a new 250 MVAR capacitor bank at Finney 345kV Substation | 8500000 | 100% | 8500000
GEN-2017-032 | 03 - Spearville |  | ERIS | Finney to G17-032-Tap 345kV Rebuild | Current Study | Rebuild the existing Finney to G17-032-Tap 345kV 75.75 mile line to achieve a minimum summer/emergency rating of 444 MVA | 150000 | 100% | 150000
GEN-2017-094 | 15 - Eastern South Dakota | 122574 | ERIS | Fort Thompson - Huron 230 kV GEN-2017-094 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-094 (200 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Huron 230 kV. | 4500000 | 100% | 4500000
GEN-2017-094 | 15 - Eastern South Dakota | 122573 | ERIS | Fort Thompson - Huron 230 kV GEN-2017-094 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-094 (200 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Huron 230 kV. | 4500000 | 100% | 4500000
GEN-2016-103 | 15 - Eastern South Dakota | 132919 | ERIS | Fort Thompson - Leland Olds 345 kV GEN-2016-103 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-103 (250.7 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Leland Olds 345 kV. | 1552831 | 100% | 1552831
GEN-2016-103 | 15 - Eastern South Dakota | 132918 | ERIS | Fort Thompson - Leland Olds 345 kV GEN-2016-103 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-103 (250.7 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Leland Olds 345 kV. | 1145002 | 100% | 1145002
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Franklin 161/69kV New Transformer CKT 2 | Current Study | Build a new 161/69kV Transformer at Franklin as a second circuit | 3200000 | 100% | 3200000
GEN-2017-085 | 09 - Nebraska | 133063 | ERIS | Friend 115 kV Substation GEN-2017-085 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-085 (.6 MW/Wind), into the Point of Interconnection (POI) at Friend 115 kV Substation. | 0 | 100% | 0
GEN-2017-085 | 09 - Nebraska | 133062 | ERIS | Friend 115 kV Substation GEN-2017-085 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-085 (.6 MW/Wind), into the Point of Interconnection (POI) at Friend 115 kV Substation. | 0 | 100% | 0
GEN-2017-024 | 14 - South Central Oklahoma | 132969 | ERIS | Frogville 138 kV Substation GEN-2017-024 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-024 (50 MW/Solar), into the Point of Interconnection (POI) at Frogville 138 kV Substation. | 4750000 | 100% | 4750000
GEN-2017-024 | 14 - South Central Oklahoma | 132968 | ERIS | Frogville 138 kV Substation GEN-2017-024 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-024 (50 MW/Solar), into the Point of Interconnection (POI) at Frogville 138 kV Substation. | 400000 | 100% | 400000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Ft. Randall to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Randall to Lake Platte 230kV 43.34 mile line to achieve a minimum summer/emergency rating of 353 MVA | 691221.8292 | 34.56% | 2000000
GEN-2016-103 | 15 - Eastern South Dakota |  | NRIS | Ft. Randall to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Randall to Lake Platte 230kV 43.34 mile line to achieve a minimum summer/emergency rating of 353 MVA | 784290.2559 | 39.21% | 2000000
GEN-2017-094 | 15 - Eastern South Dakota |  | NRIS | Ft. Randall to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Randall to Lake Platte 230kV 43.34 mile line to achieve a minimum summer/emergency rating of 353 MVA | 524487.915 | 26.22% | 2000000
GEN-2016-005 | 03 - Spearville |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 90992.5302 | 1.23% | 7400000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 713426.1019 | 9.641% | 7400000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 131029.2404 | 1.771% | 7400000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 243267.0107 | 3.287% | 7400000
GEN-2016-107 | 01 - Woodward |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 273262.2907 | 3.693% | 7400000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 491245.4113 | 6.638% | 7400000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 757340.702 | 10.23% | 7400000
GEN-2017-018 | 03 - Spearville |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 156976.0704 | 2.121% | 7400000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 99961.5303 | 1.351% | 7400000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 65065.5502 | 0.8793% | 7400000
GEN-2017-028 | 01 - Woodward |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 118718.2703 | 1.604% | 7400000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 471399.6113 | 6.37% | 7400000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 243887.2707 | 3.296% | 7400000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 419436.8611 | 5.668% | 7400000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 238528.2006 | 3.223% | 7400000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 472106.7113 | 6.38% | 7400000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 372458.791 | 5.033% | 7400000
GEN-2017-067 | 01 - Woodward |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 480434.9813 | 6.492% | 7400000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 102587.1003 | 1.386% | 7400000
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 402821.8911 | 5.444% | 7400000
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 168623.1205 | 2.279% | 7400000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 111163.4703 | 1.502% | 7400000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 136256.2004 | 1.841% | 7400000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 70130.1202 | 0.9477% | 7400000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 260039.7807 | 3.514% | 7400000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | Current Study | Build a new 345/161kV transformer at Ft. Smith as a second circuit | 308841.1808 | 4.174% | 7400000
GEN-2017-094 | 15 - Eastern South Dakota |  | NRIS | Ft. Thompson to Ft. Randall 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Ft. Randall 230kV 87.32 mile line to achieve a minimum summer/emergency rating of 367 MVA | 518473.0495 | 18.52% | 2800000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Ft. Thompson to Ft. Randall 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Ft. Randall 230kV 87.32 mile line to achieve a minimum summer/emergency rating of 367 MVA | 148331.4625 | 5.298% | 2800000
GEN-2017-048 | 16 - Western North Dakota |  | NRIS | Ft. Thompson to Ft. Randall 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Ft. Randall 230kV 87.32 mile line to achieve a minimum summer/emergency rating of 367 MVA | 442593.4201 | 15.81% | 2800000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Ft. Thompson to Ft. Randall 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Ft. Randall 230kV 87.32 mile line to achieve a minimum summer/emergency rating of 367 MVA | 683256.4236 | 24.4% | 2800000
GEN-2016-103 | 15 - Eastern South Dakota |  | NRIS | Ft. Thompson to Ft. Randall 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Ft. Randall 230kV 87.32 mile line to achieve a minimum summer/emergency rating of 367 MVA | 775306.4928 | 27.69% | 2800000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Ft. Thompson to Ft. Randall 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Ft. Randall 230kV 87.32 mile line to achieve a minimum summer/emergency rating of 367 MVA | 232039.1515 | 8.287% | 2800000
GEN-2016-005 | 03 - Spearville |  | NRIS | Ft. Thompson to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | 314739.4791 | 0.81% | 38856725.82
GEN-2016-159 | 09 - Nebraska |  | NRIS | Ft. Thompson to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | 3260079.2963 | 8.39% | 38856725.82
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Ft. Thompson to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | 7771.3452 | 0.02% | 38856725.82
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Ft. Thompson to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | 1293928.9698 | 3.33% | 38856725.82
GEN-2017-018 | 03 - Spearville |  | NRIS | Ft. Thompson to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | 170969.5936 | 0.44% | 38856725.82
GEN-2017-032 | 03 - Spearville |  | NRIS | Ft. Thompson to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | 936447.0923 | 2.41% | 38856725.82
GEN-2017-047 | 02 - Hitchland |  | NRIS | Ft. Thompson to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | 194283.6291 | 0.5% | 38856725.82
GEN-2017-055 | 09 - Nebraska |  | NRIS | Ft. Thompson to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | 909247.3842 | 2.34% | 38856725.82
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Ft. Thompson to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | 22039534.8851 | 56.72% | 38856725.82
GEN-2017-067 | 01 - Woodward |  | NRIS | Ft. Thompson to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | 81599.1242 | 0.21% | 38856725.82
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Ft. Thompson to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | 182626.6114 | 0.47% | 38856725.82
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Ft. Thompson to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | 81599.1242 | 0.21% | 38856725.82
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Ft. Thompson to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | 9189615.6564 | 23.65% | 38856725.82
GEN-2017-100 | 02 - Hitchland |  | NRIS | Ft. Thompson to Lake Platte 230kV Rebuild | Current Study | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | 194283.6291 | 0.5% | 38856725.82
GEN-2016-005 | 03 - Spearville |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 86590.3639 | 0.3299% | 26250000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 265018.9924 | 1.01% | 26250000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 34111.3555 | 0.1299% | 26250000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 65598.7605 | 0.2499% | 26250000
GEN-2016-107 | 01 - Woodward |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 128573.5706 | 0.4898% | 26250000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 304378.2487 | 1.16% | 26250000
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 78718.5126 | 0.2999% | 26250000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 551029.5882 | 2.099% | 26250000
GEN-2017-011 | 01 - Woodward |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 115453.8185 | 0.4398% | 26250000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 1149290.2839 | 4.378% | 26250000
GEN-2017-018 | 03 - Spearville |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 202044.1823 | 0.7697% | 26250000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 36735.3059 | 0.1399% | 26250000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 23615.5538 | 0.08996% | 26250000
GEN-2017-028 | 01 - Woodward |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 41983.2067 | 0.1599% | 26250000
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 4872675.9296 | 18.56% | 26250000
GEN-2017-032 | 03 - Spearville |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 28863.4546 | 0.11% | 26250000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 131197.521 | 0.4998% | 26250000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 86590.3639 | 0.3299% | 26250000
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 4872675.9296 | 18.56% | 26250000
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 4872675.9296 | 18.56% | 26250000
GEN-2017-047 | 02 - Hitchland |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 65598.7605 | 0.2499% | 26250000
GEN-2017-055 | 09 - Nebraska |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 986605.3579 | 3.758% | 26250000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 380472.8109 | 1.449% | 26250000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 131197.521 | 0.4998% | 26250000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 123325.6697 | 0.4698% | 26250000
GEN-2017-067 | 01 - Woodward |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 162684.926 | 0.6198% | 26250000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 225659.7361 | 0.8597% | 26250000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 99710.116 | 0.3798% | 26250000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 99710.116 | 0.3798% | 26250000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 110205.9176 | 0.4198% | 26250000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 44607.1571 | 0.1699% | 26250000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 170556.7773 | 0.6497% | 26250000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 293882.447 | 1.12% | 26250000
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 4872675.9296 | 18.56% | 26250000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 469687.1251 | 1.789% | 26250000
GEN-2017-100 | 02 - Hitchland |  | NRIS | G17-030 Tap to Iatan 345kV Rebuild | Current Study | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | 65598.7605 | 0.2499% | 26250000
GEN-2016-005 | 03 - Spearville |  | NRIS | G17-064 Tap to Wayside 230kV Rebuild | Current Study | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | 319950 | 0.81% | 39500000
GEN-2016-159 | 09 - Nebraska |  | NRIS | G17-064 Tap to Wayside 230kV Rebuild | Current Study | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | 3314050 | 8.39% | 39500000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | G17-064 Tap to Wayside 230kV Rebuild | Current Study | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | 7900 | 0.02% | 39500000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | G17-064 Tap to Wayside 230kV Rebuild | Current Study | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | 1315350 | 3.33% | 39500000
GEN-2017-018 | 03 - Spearville |  | NRIS | G17-064 Tap to Wayside 230kV Rebuild | Current Study | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | 173800 | 0.44% | 39500000
GEN-2017-032 | 03 - Spearville |  | NRIS | G17-064 Tap to Wayside 230kV Rebuild | Current Study | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | 951950 | 2.41% | 39500000
GEN-2017-047 | 02 - Hitchland |  | NRIS | G17-064 Tap to Wayside 230kV Rebuild | Current Study | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | 197500 | 0.5% | 39500000
GEN-2017-055 | 09 - Nebraska |  | NRIS | G17-064 Tap to Wayside 230kV Rebuild | Current Study | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | 924300 | 2.34% | 39500000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | G17-064 Tap to Wayside 230kV Rebuild | Current Study | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | 22404400 | 56.72% | 39500000
GEN-2017-067 | 01 - Woodward |  | NRIS | G17-064 Tap to Wayside 230kV Rebuild | Current Study | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | 82950 | 0.21% | 39500000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | G17-064 Tap to Wayside 230kV Rebuild | Current Study | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | 185650 | 0.47% | 39500000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | G17-064 Tap to Wayside 230kV Rebuild | Current Study | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | 82950 | 0.21% | 39500000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | G17-064 Tap to Wayside 230kV Rebuild | Current Study | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | 9341750 | 23.65% | 39500000
GEN-2017-100 | 02 - Hitchland |  | NRIS | G17-064 Tap to Wayside 230kV Rebuild | Current Study | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | 197500 | 0.5% | 39500000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 51103.2 | 0.24% | 21293000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 76654.8 | 0.36% | 21293000
GEN-2017-018 | 03 - Spearville |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 48973.9 | 0.23% | 21293000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 3394104.2 | 15.94% | 21293000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 2280480.3 | 10.71% | 21293000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 44715.3 | 0.21% | 21293000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 3992437.5 | 18.75% | 21293000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 31939.5 | 0.15% | 21293000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 51103.2 | 0.24% | 21293000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 11180954.3 | 52.51% | 21293000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 25551.6 | 0.12% | 21293000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 19163.7 | 0.09% | 21293000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 19163.7 | 0.09% | 21293000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 12775.8 | 0.06% | 21293000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 31939.5 | 0.15% | 21293000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Gaines to Johnson Draw 115kV New Build | Current Study | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | 31939.5 | 0.15% | 21293000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 125507.4493 | 5.229% | 2400000
GEN-2016-103 | 15 - Eastern South Dakota |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 60473.9526 | 2.52% | 2400000
GEN-2016-107 | 01 - Woodward |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 50634.9365 | 2.11% | 2400000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 91430.8569 | 3.81% | 2400000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 239976.0024 | 9.999% | 2400000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 35276.4724 | 1.47% | 2400000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 20637.9362 | 0.8599% | 2400000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 64073.5926 | 2.67% | 2400000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 41995.8004 | 1.75% | 2400000
GEN-2017-048 | 16 - Western North Dakota |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 974782.5217 | 40.62% | 2400000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 126467.3533 | 5.269% | 2400000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 64313.5686 | 2.68% | 2400000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 61193.8806 | 2.55% | 2400000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 46555.3445 | 1.94% | 2400000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 33356.6643 | 1.39% | 2400000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 26397.3603 | 1.1% | 2400000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 57594.2406 | 2.4% | 2400000
GEN-2017-094 | 15 - Eastern South Dakota |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 107749.2251 | 4.49% | 2400000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Garrison to Pick City 115kV Rebuild | Current Study | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | 171582.8417 | 7.149% | 2400000
GEN-2017-053 | 07 - Southwestern Oklahoma |  | ERIS | Geronimo Jct. to Essaquanadable Jct. 69kV Rebuild | Current Study | Rebuild the existing Geronimo Jct. to Essaquanadale Jct. 69kV 3.83 mile line to achieve a minimum light/emergency rating of 67 MVA | 3481274.67 | 100% | 3481274.67
GEN-2017-053 | 07 - Southwestern Oklahoma |  | ERIS | Geronimo Jct. to Granfield 69kV Rebuild | Current Study | Rebuild the existing Geronimo Jct. to Granfield 69kV 14.93 mile line to achieve a minimum light/emergency rating of 71 MVA | 13570608.57 | 100% | 13570608.57
GEN-2016-107 | 01 - Woodward |  | NRIS | Gilliam to Superior 69kV Rebuild | Current Study | Rebuild the existing Gilliam to Superior 69kV 6.0 mile line to achieve a minimum summer/emergency rating of 41 MVA | 23997.6002 | 0.15% | 16000000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Gilliam to Superior 69kV Rebuild | Current Study | Rebuild the existing Gilliam to Superior 69kV 6.0 mile line to achieve a minimum summer/emergency rating of 41 MVA | 84791.5208 | 0.5299% | 16000000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Gilliam to Superior 69kV Rebuild | Current Study | Rebuild the existing Gilliam to Superior 69kV 6.0 mile line to achieve a minimum summer/emergency rating of 41 MVA | 47995.2005 | 0.3% | 16000000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Gilliam to Superior 69kV Rebuild | Current Study | Rebuild the existing Gilliam to Superior 69kV 6.0 mile line to achieve a minimum summer/emergency rating of 41 MVA | 33596.6403 | 0.21% | 16000000
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas |  | NRIS | Gilliam to Superior 69kV Rebuild | Current Study | Rebuild the existing Gilliam to Superior 69kV 6.0 mile line to achieve a minimum summer/emergency rating of 41 MVA | 15761623.8376 | 98.51% | 16000000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Gilliam to Superior 69kV Rebuild | Current Study | Rebuild the existing Gilliam to Superior 69kV 6.0 mile line to achieve a minimum summer/emergency rating of 41 MVA | 47995.2005 | 0.3% | 16000000
GEN-2016-005 | 03 - Spearville |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 77798.4653 | 1.308% | 5950000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 1808849.5161 | 30.4% | 5950000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 28570.6688 | 0.4802% | 5950000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 52150.1083 | 0.8765% | 5950000
GEN-2016-107 | 01 - Woodward |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 21773.594 | 0.3659% | 5950000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 15557.9778 | 0.2615% | 5950000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 31540.3753 | 0.5301% | 5950000
GEN-2017-011 | 01 - Woodward |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 69808.1078 | 1.173% | 5950000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 26169.8643 | 0.4398% | 5950000
GEN-2017-018 | 03 - Spearville |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 79988.7629 | 1.344% | 5950000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 47712.5983 | 0.8019% | 5950000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 33660.5039 | 0.5657% | 5950000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 80178.3832 | 1.348% | 5950000
GEN-2017-032 | 03 - Spearville |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 124401.6553 | 2.091% | 5950000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 315745.0778 | 5.307% | 5950000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 914333.252 | 15.37% | 5950000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 22945.8671 | 0.3856% | 5950000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 13246.1361 | 0.2226% | 5950000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 316218.6978 | 5.315% | 5950000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 1007050.8293 | 16.93% | 5950000
GEN-2017-067 | 01 - Woodward |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 753988.5907 | 12.67% | 5950000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 13542.8975 | 0.2276% | 5950000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 12167.5447 | 0.2045% | 5950000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 12167.5447 | 0.2045% | 5950000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 3982.3555 | 0.06693% | 5950000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 7919.2448 | 0.1331% | 5950000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 21282.9447 | 0.3577% | 5950000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 24747.5681 | 0.4159% | 5950000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | Current Study | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | 12500.8678 | 0.2101% | 5950000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | ERIS | Gracemont to Anadark 138kV Rebuild | Current Study | Rebuild the existing Gracemont to Anadark 138kV 5.09 mile line to achieve a minimum winter/emergency rating of 451 MVA | 3054471.1385 | 62.24% | 4907569.31
GEN-2017-053 | 07 - Southwestern Oklahoma |  | ERIS | Gracemont to Anadark 138kV Rebuild | Current Study | Rebuild the existing Gracemont to Anadark 138kV 5.09 mile line to achieve a minimum winter/emergency rating of 451 MVA | 1853098.1715 | 37.76% | 4907569.31
GEN-2016-005 | 03 - Spearville |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 469312.7321 | 2.547% | 18427752
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 380413.3415 | 2.064% | 18427752
GEN-2016-049 | 03 - Spearville |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 840197.3771 | 4.559% | 18427752
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 177353.7317 | 0.9624% | 18427752
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 359734.3787 | 1.952% | 18427752
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 327412.6605 | 1.777% | 18427752
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 208646.3469 | 1.132% | 18427752
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 789757.5917 | 4.286% | 18427752
GEN-2017-004 | 04 - Northwest Kansas |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 292176.2985 | 1.586% | 18427752
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 979553.6415 | 5.316% | 18427752
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 721892.6949 | 3.917% | 18427752
GEN-2017-013 | 04 - Northwest Kansas |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 555485.7037 | 3.014% | 18427752
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 108950.9462 | 0.5912% | 18427752
GEN-2017-018 | 03 - Spearville |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 435640.5568 | 2.364% | 18427752
GEN-2017-021 | 03 - Spearville |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 606239.449 | 3.29% | 18427752
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 771967.0012 | 4.189% | 18427752
GEN-2017-032 | 03 - Spearville |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 669617.8687 | 3.634% | 18427752
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 520544.6845 | 2.825% | 18427752
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 656811.3462 | 3.564% | 18427752
GEN-2017-047 | 02 - Hitchland |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 212928.5347 | 1.155% | 18427752
GEN-2017-049 | 03 - Spearville |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 119838.7718 | 0.6503% | 18427752
GEN-2017-052 | 03 - Spearville |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 85375.9598 | 0.4633% | 18427752
GEN-2017-058 | 02 - Hitchland |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 723479.9601 | 3.926% | 18427752
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 297138.9445 | 1.612% | 18427752
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 521325.5009 | 2.829% | 18427752
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 11885.5583 | 0.0645% | 18427752
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 927531.0538 | 5.033% | 18427752
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 169689.0231 | 0.9208% | 18427752
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 1724607.131 | 9.359% | 18427752
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 1031015.1326 | 5.595% | 18427752
GEN-2017-083 | 04 - Northwest Kansas |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 276340.1104 | 1.5% | 18427752
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 305817.0055 | 1.66% | 18427752
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 422434.3815 | 2.292% | 18427752
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 88624.9002 | 0.4809% | 18427752
GEN-2017-099 | 03 - Spearville |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 606239.449 | 3.29% | 18427752
GEN-2017-100 | 02 - Hitchland |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 251796.8495 | 1.366% | 18427752
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine 345kV New Substation | Current Study | Build a new 345kV substation at Grapevine | 779975.382 | 4.233% | 18427752
GEN-2016-005 | 03 - Spearville |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 3900278.3432 | 2.547% | 153145988
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 3161469.5615 | 2.064% | 153145988
GEN-2016-049 | 03 - Spearville |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 6982558.558 | 4.559% | 153145988
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 1473918.9277 | 0.9624% | 153145988
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 2989614.6225 | 1.952% | 153145988
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 2721001.2038 | 1.777% | 153145988
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 1733979.8659 | 1.132% | 153145988
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 6563372.8227 | 4.286% | 153145988
GEN-2017-004 | 04 - Northwest Kansas |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 2428165.297 | 1.586% | 153145988
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 8140695.0899 | 5.316% | 153145988
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 5999373.6614 | 3.917% | 153145988
GEN-2017-013 | 04 - Northwest Kansas |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 4616428.9008 | 3.014% | 153145988
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 905449.5796 | 0.5912% | 153145988
GEN-2017-018 | 03 - Spearville |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 3620441.7928 | 2.364% | 153145988
GEN-2017-021 | 03 - Spearville |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 5038223.8368 | 3.29% | 153145988
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 6415522.0396 | 4.189% | 153145988
GEN-2017-032 | 03 - Spearville |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 5564937.6051 | 3.634% | 153145988
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 4326047.4751 | 2.825% | 153145988
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 5458507.5021 | 3.564% | 153145988
GEN-2017-047 | 02 - Hitchland |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 1769567.4879 | 1.155% | 153145988
GEN-2017-049 | 03 - Spearville |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 995934.1274 | 0.6503% | 153145988
GEN-2017-052 | 03 - Spearville |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 709526.8977 | 0.4633% | 153145988
GEN-2017-058 | 02 - Hitchland |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 6012564.8149 | 3.926% | 153145988
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 2469407.9466 | 1.612% | 153145988
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 4332536.5406 | 2.829% | 153145988
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 98776.322 | 0.0645% | 153145988
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 7708355.2914 | 5.033% | 153145988
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 1410220.4704 | 0.9208% | 153145988
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 14332549.2436 | 9.359% | 153145988
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 8568371.8298 | 5.595% | 153145988
GEN-2017-083 | 04 - Northwest Kansas |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 2296556.8038 | 1.5% | 153145988
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 2541527.9875 | 1.66% | 153145988
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 3510690.3282 | 2.292% | 153145988
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 736527.5973 | 0.4809% | 153145988
GEN-2017-099 | 03 - Spearville |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 5038223.8368 | 3.29% | 153145988
GEN-2017-100 | 02 - Hitchland |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 2092587.1639 | 1.366% | 153145988
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Grapevine to Chisholm 345kV New Build | Current Study | Build a new 75 mile 345kV line from Grapevine to Chisholm | 6482076.6248 | 4.233% | 153145988
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 133021 | ERIS | GRDA1 - CLARMR5 161 kV GEN-2017-061 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-061 (101.5 MW/Solar), into the Point of Interconnection (POI) at GRDA1 - CLARMR5 161 kV. | 2135000 | 100% | 2135000
GEN-2017-061 | 08 - North Oklahoma/South Central Kansas | 133020 | ERIS | GRDA1 - CLARMR5 161 kV GEN-2017-061 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-061 (101.5 MW/Solar), into the Point of Interconnection (POI) at GRDA1 - CLARMR5 161 kV. | 2135000 | 100% | 2135000
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas | 133035 | ERIS | Greenwood 138 kV Substation GEN-2017-071 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-071 (124.7 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | 1721000 | 100% | 1721000
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas | 133034 | ERIS | Greenwood 138 kV Substation GEN-2017-071 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-071 (124.7 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | 515000 | 100% | 515000
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas | 133037 | ERIS | Greenwood 138 kV Substation GEN-2017-072 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-072 (52.2 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | 1721000 | 100% | 1721000
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas | 133036 | ERIS | Greenwood 138 kV Substation GEN-2017-072 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-072 (52.2 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | 515000 | 100% | 515000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Hale County to Tuco 115kV Rebuild | Current Study | Rebuild the existing Hale County to Tuco 115kV 20.73 mile line to achieve a minimum spring/normal rating of 107 MVA | 2423728.82 | 16.72% | 14500000
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Hale County to Tuco 115kV Rebuild | Current Study | Rebuild the existing Hale County to Tuco 115kV 20.73 mile line to achieve a minimum spring/normal rating of 107 MVA | 1442250.23 | 9.947% | 14500000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Hale County to Tuco 115kV Rebuild | Current Study | Rebuild the existing Hale County to Tuco 115kV 20.73 mile line to achieve a minimum spring/normal rating of 107 MVA | 3601687.22 | 24.84% | 14500000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Hale County to Tuco 115kV Rebuild | Current Study | Rebuild the existing Hale County to Tuco 115kV 20.73 mile line to achieve a minimum spring/normal rating of 107 MVA | 1677899.25 | 11.57% | 14500000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Hale County to Tuco 115kV Rebuild | Current Study | Rebuild the existing Hale County to Tuco 115kV 20.73 mile line to achieve a minimum spring/normal rating of 107 MVA | 1107807.52 | 7.64% | 14500000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Hale County to Tuco 115kV Rebuild | Current Study | Rebuild the existing Hale County to Tuco 115kV 20.73 mile line to achieve a minimum spring/normal rating of 107 MVA | 2413450.74 | 16.64% | 14500000
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Hale County to Tuco 115kV Rebuild | Current Study | Rebuild the existing Hale County to Tuco 115kV 20.73 mile line to achieve a minimum spring/normal rating of 107 MVA | 919564.61 | 6.342% | 14500000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Hale County to Tuco 115kV Rebuild | Current Study | Rebuild the existing Hale County to Tuco 115kV 20.73 mile line to achieve a minimum spring/normal rating of 107 MVA | 913611.61 | 6.301% | 14500000
GEN-2017-049 | 03 - Spearville |  | ERIS | Hanston to Kinsley 69kV Rebuild | Current Study | Rebuild the existing Hanston to Kinsley 69kV 18.75 mile line to achieve a minimum winter/emergency rating of 53 MVA | 17042793.75 | 100% | 17042793.75
GEN-2016-109 | 09 - Nebraska |  | ERIS | Harbine to Fairbury 115kV Rebuild | Current Study | Rebuild the existing Harbine to Fairbury 115kV 9 mile line to achieve a minimum spring/emergency rating of 134 MVA | 2248888.19 | 99.95% | 2250000
GEN-2017-085 | 09 - Nebraska |  | ERIS | Harbine to Fairbury 115kV Rebuild | Current Study | Rebuild the existing Harbine to Fairbury 115kV 9 mile line to achieve a minimum spring/emergency rating of 134 MVA | 1111.81 | 0.04941% | 2250000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico | 133051 | ERIS | Hart Industrial 115 kV Substation GEN-2017-079 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-079 (49.875 MW/Solar), into the Point of Interconnection (POI) at Hart Industrial 115 kV Substation. | 7124292 | 100% | 7124292
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico | 133050 | ERIS | Hart Industrial 115 kV Substation GEN-2017-079 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-079 (49.875 MW/Solar), into the Point of Interconnection (POI) at Hart Industrial 115 kV Substation. | 583974 | 100% | 583974
GEN-2016-005 | 03 - Spearville |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 52784.1648 | 0.2399% | 22000000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 1488953.314 | 6.768% | 22000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 94571.6285 | 0.4299% | 22000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 173747.8756 | 0.7898% | 22000000
GEN-2016-107 | 01 - Woodward |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 285914.2257 | 1.3% | 22000000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 736778.9663 | 3.349% | 22000000
GEN-2017-011 | 01 - Woodward |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 204538.6384 | 0.9297% | 22000000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 1150254.9235 | 5.228% | 22000000
GEN-2017-018 | 03 - Spearville |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 189143.257 | 0.8597% | 22000000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 215535.3394 | 0.9797% | 22000000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 125362.3913 | 0.5698% | 22000000
GEN-2017-028 | 01 - Woodward |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 116565.0305 | 0.5298% | 22000000
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 2505048.4855 | 11.39% | 22000000
GEN-2017-032 | 03 - Spearville |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 90172.9481 | 0.4099% | 22000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 371688.4935 | 1.689% | 22000000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 490452.8641 | 2.229% | 22000000
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 2505048.4855 | 11.39% | 22000000
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 2505048.4855 | 11.39% | 22000000
GEN-2017-047 | 02 - Hitchland |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 393681.8954 | 1.789% | 22000000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 1187643.7069 | 5.398% | 22000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 404678.5964 | 1.839% | 22000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 371688.4935 | 1.689% | 22000000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 336499.0503 | 1.53% | 22000000
GEN-2017-067 | 01 - Woodward |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 464060.7818 | 2.109% | 22000000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 191342.5972 | 0.8697% | 22000000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 343097.0709 | 1.56% | 22000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 340897.7307 | 1.55% | 22000000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 497050.8847 | 2.259% | 22000000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 215535.3394 | 0.9797% | 22000000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 574027.7917 | 2.609% | 22000000
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 2505048.4855 | 11.39% | 22000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 479456.1632 | 2.179% | 22000000
GEN-2017-100 | 02 - Hitchland |  | NRIS | Hawthorne 345/161kV New Transformer CKT3 | Current Study | Build a new 345/161kV transformer at Hawthorne as a third circuit | 393681.8954 | 1.789% | 22000000
GEN-2016-093 | 09 - Nebraska |  | NRIS | Hawthorne to Craig 345kV New Build | Current Study | Build a new 25 mile 345kV line from Hawthorn to Craig | 614711.0078 | 1.64% | 37489875
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Hawthorne to Craig 345kV New Build | Current Study | Build a new 25 mile 345kV line from Hawthorn to Craig | 5195057.6635 | 13.86% | 37489875
GEN-2016-159 | 09 - Nebraska |  | NRIS | Hawthorne to Craig 345kV New Build | Current Study | Build a new 25 mile 345kV line from Hawthorn to Craig | 10150228.1044 | 27.07% | 37489875
GEN-2017-001 | 09 - Nebraska |  | NRIS | Hawthorne to Craig 345kV New Build | Current Study | Build a new 25 mile 345kV line from Hawthorn to Craig | 3006086.7576 | 8.018% | 37489875
GEN-2017-031 | 09 - Nebraska |  | NRIS | Hawthorne to Craig 345kV New Build | Current Study | Build a new 25 mile 345kV line from Hawthorn to Craig | 877087.6575 | 2.34% | 37489875
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Hawthorne to Craig 345kV New Build | Current Study | Build a new 25 mile 345kV line from Hawthorn to Craig | 2762451.2972 | 7.369% | 37489875
GEN-2017-037 | 09 - Nebraska |  | NRIS | Hawthorne to Craig 345kV New Build | Current Study | Build a new 25 mile 345kV line from Hawthorn to Craig | 176167.1791 | 0.4699% | 37489875
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Hawthorne to Craig 345kV New Build | Current Study | Build a new 25 mile 345kV line from Hawthorn to Craig | 3560825.9598 | 9.498% | 37489875
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas |  | NRIS | Hawthorne to Craig 345kV New Build | Current Study | Build a new 25 mile 345kV line from Hawthorn to Craig | 127440.087 | 0.3399% | 37489875
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Hawthorne to Craig 345kV New Build | Current Study | Build a new 25 mile 345kV line from Hawthorn to Craig | 2766199.5351 | 7.379% | 37489875
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Hawthorne to Craig 345kV New Build | Current Study | Build a new 25 mile 345kV line from Hawthorn to Craig | 1499295.141 | 3.999% | 37489875
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Hawthorne to Craig 345kV New Build | Current Study | Build a new 25 mile 345kV line from Hawthorn to Craig | 577228.6293 | 1.54% | 37489875
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Hawthorne to Craig 345kV New Build | Current Study | Build a new 25 mile 345kV line from Hawthorn to Craig | 2616270.021 | 6.979% | 37489875
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Hawthorne to Craig 345kV New Build | Current Study | Build a new 25 mile 345kV line from Hawthorn to Craig | 3560825.9598 | 9.498% | 37489875
GEN-2017-058 | 02 - Hitchland | 133015 | ERIS | Hereford Northeast 115 kV Substation GEN-2017-058 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-058 (135 MW/Solar), into the Point of Interconnection (POI) at Hereford Northeast 115 kV Substation. | 1419861 | 100% | 1419861
GEN-2017-058 | 02 - Hitchland | 133014 | ERIS | Hereford Northeast 115 kV Substation GEN-2017-058 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-058 (135 MW/Solar), into the Point of Interconnection (POI) at Hereford Northeast 115 kV Substation. | 701784 | 100% | 701784
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico | 132929 | ERIS | Hobbs - Yoakum 230 kV GEN-2016-171 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-171 (64 MW/Solar), into the Point of Interconnection (POI) at Hobbs - Yoakum 230 kV. | 7126227 | 100% | 7126227
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico | 132928 | ERIS | Hobbs - Yoakum 230 kV GEN-2016-171 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-171 (64 MW/Solar), into the Point of Interconnection (POI) at Hobbs - Yoakum 230 kV. | 927894 | 100% | 927894
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 133083 | ERIS | Hobbs 230 kV Substation GEN-2017-104 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-104 (240 MW/Solar), into the Point of Interconnection (POI) at Hobbs 230 kV Substation. | 2530072 | 100% | 2530072
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 133082 | ERIS | Hobbs 230 kV Substation GEN-2017-104 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-104 (240 MW/Solar), into the Point of Interconnection (POI) at Hobbs 230 kV Substation. | 1324666 | 100% | 1324666
GEN-2017-053 | 07 - Southwestern Oklahoma | 133009 | ERIS | Holister SW - PSO Walters 69 kV GEN-2017-053 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-053 (50 MW/Solar), into the Point of Interconnection (POI) at Holister SW - PSO Walters 69 kV. | 4750000 | 100% | 4750000
GEN-2017-053 | 07 - Southwestern Oklahoma | 133008 | ERIS | Holister SW - PSO Walters 69 kV GEN-2017-053 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-053 (50 MW/Solar), into the Point of Interconnection (POI) at Holister SW - PSO Walters 69 kV. | 400000 | 100% | 400000
GEN-2016-159 | 09 - Nebraska |  | NRIS | Hoskins 345/230kV New Transformer CKT3 | Current Study | Build a new 345/230kV transformer at Hoskins as a third circuit | 10000000 | 100% | 10000000
GEN-2016-159 | 09 - Nebraska |  | ERIS | Hoskins 345/230kV Transformer Replacement | Current Study | Replace the existing Hoskins 345/230kV transformer to achieve a minimum rating of 400 MVA | 8302968 | 100% | 8302968
GEN-2016-005 | 03 - Spearville |  | NRIS | Hoskins to Shell Creek 345kV New Build CKT 2 | Current Study | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit | 1402200 | 1.71% | 82000000
GEN-2016-159 | 09 - Nebraska |  | NRIS | Hoskins to Shell Creek 345kV New Build CKT 2 | Current Study | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit | 60647200 | 73.96% | 82000000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Hoskins to Shell Creek 345kV New Build CKT 2 | Current Study | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit | 6068000 | 7.4% | 82000000
GEN-2017-018 | 03 - Spearville |  | NRIS | Hoskins to Shell Creek 345kV New Build CKT 2 | Current Study | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit | 1418600 | 1.73% | 82000000
GEN-2017-032 | 03 - Spearville |  | NRIS | Hoskins to Shell Creek 345kV New Build CKT 2 | Current Study | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit | 2369800 | 2.89% | 82000000
GEN-2017-047 | 02 - Hitchland |  | NRIS | Hoskins to Shell Creek 345kV New Build CKT 2 | Current Study | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit | 754400 | 0.92% | 82000000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Hoskins to Shell Creek 345kV New Build CKT 2 | Current Study | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit | 4887200 | 5.96% | 82000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Hoskins to Shell Creek 345kV New Build CKT 2 | Current Study | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit | 992200 | 1.21% | 82000000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Hoskins to Shell Creek 345kV New Build CKT 2 | Current Study | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit | 237800 | 0.29% | 82000000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Hoskins to Shell Creek 345kV New Build CKT 2 | Current Study | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit | 401800 | 0.49% | 82000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Hoskins to Shell Creek 345kV New Build CKT 2 | Current Study | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit | 2058200 | 2.51% | 82000000
GEN-2017-100 | 02 - Hitchland |  | NRIS | Hoskins to Shell Creek 345kV New Build CKT 2 | Current Study | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit | 762600 | 0.93% | 82000000
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas | 133013 | ERIS | Hosston 69 kV Substation GEN-2017-057 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-057 (72.5 MW/Solar), into the Point of Interconnection (POI) at Houston 69 kV Substation. | 17032809 | 100% | 17032809
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas | 133012 | ERIS | Hosston 69 kV Substation GEN-2017-057 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-057 (72.5 MW/Solar), into the Point of Interconnection (POI) at Houston 69 kV Substation. | 1120262 | 100% | 1120262
GEN-2017-075 | 14 - South Central Oklahoma | 133043 | ERIS | Hugo - Sunnyside 345 kV GEN-2017-075 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-075 (200 MW/Solar), into the Point of Interconnection (POI) at Hugo - Sunnyside 345 kV. | 1430000 | 100% | 1430000
GEN-2017-075 | 14 - South Central Oklahoma | 133042 | ERIS | Hugo - Sunnyside 345 kV GEN-2017-075 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-075 (200 MW/Solar), into the Point of Interconnection (POI) at Hugo - Sunnyside 345 kV. | 915000 | 100% | 915000
GEN-2017-023 | 14 - South Central Oklahoma | 132967 | ERIS | Hugo 138 kV Substation GEN-2017-023 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-023 (85 MW/Solar), into the Point of Interconnection (POI) at Hugo 138 kV Substaion. | 0 | 100% | 0
GEN-2017-023 | 14 - South Central Oklahoma | 132966 | ERIS | Hugo 138 kV Substation GEN-2017-023 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-023 (85 MW/Solar), into the Point of Interconnection (POI) at Hugo 138 kV Substaion. | 750000 | 100% | 750000
GEN-2016-109 | 09 - Nebraska |  | ERIS | Kelly to Goff 115kV Rebuild | Current Study | Rebuild the existing Kelly to Goff 115kV 9.6 mile line to achieve a minimum spring/emergency rating of 90 MVA | 150000 | 100% | 150000
GEN-2016-109 | 09 - Nebraska |  | ERIS | Kelly to Tecumseh Hill 161kV Rebuild | Current Study | Rebuild the existing Kelly to Tecumseh Hill 161kV 52.64 mile line to achieve a minimum spring/emergency rating of 152 MVA | 87500000 | 100% | 87500000
GEN-2016-005 | 03 - Spearville |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 1248.37 | 1.086% | 115000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 5802.92 | 5.046% | 115000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 555.88 | 0.4834% | 115000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 1027.34 | 0.8933% | 115000
GEN-2016-107 | 01 - Woodward |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 6866.46 | 5.971% | 115000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 29257.5 | 25.44% | 115000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 1786.95 | 1.554% | 115000
GEN-2017-018 | 03 - Spearville |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 1794.21 | 1.56% | 115000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 284.02 | 0.247% | 115000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 144.24 | 0.1254% | 115000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 2212.41 | 1.924% | 115000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 1797.33 | 1.563% | 115000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 1933.19 | 1.681% | 115000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 490.84 | 0.4268% | 115000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 2215.73 | 1.927% | 115000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 2854.34 | 2.482% | 115000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 573.54 | 0.4987% | 115000
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 28109 | 24.44% | 115000
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 11766.56 | 10.23% | 115000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 2974.77 | 2.587% | 115000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 3155.34 | 2.744% | 115000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 1766.99 | 1.537% | 115000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 5683.4 | 4.942% | 115000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Kenzie to Kenzie GR 138kV Rebuild | Current Study | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | 698.67 | 0.6075% | 115000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 24289.49 | 2.208% | 1100000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 3813.17 | 0.3467% | 1100000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 7084.44 | 0.644% | 1100000
GEN-2016-107 | 01 - Woodward |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 36191 | 3.29% | 1100000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 146270.09 | 13.3% | 1100000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 11040.68 | 1.004% | 1100000
GEN-2017-018 | 03 - Spearville |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 2840.67 | 0.2582% | 1100000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 9110.86 | 0.8283% | 1100000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 5347.83 | 0.4862% | 1100000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 15456.95 | 1.405% | 1100000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 8142.5 | 0.7402% | 1100000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 3466.31 | 0.3151% | 1100000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 15480.14 | 1.407% | 1100000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 14013.2 | 1.274% | 1100000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 11308.07 | 1.028% | 1100000
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 519645.63 | 47.24% | 1100000
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 217526.08 | 19.78% | 1100000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 12640.43 | 1.149% | 1100000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 8680.87 | 0.7892% | 1100000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 23146.99 | 2.104% | 1100000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Kenzie to University 138kV Rebuild | Current Study | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | 4504.6 | 0.4095% | 1100000
GEN-2016-034 | 09 - Nebraska |  | ERIS | Keystone to Sidney 345kV New Build CKT 2 | Current Study | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit | 48358939.56 | 40.31% | 119967600
GEN-2016-093 | 09 - Nebraska |  | ERIS | Keystone to Sidney 345kV New Build CKT 2 | Current Study | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit | 35834322.12 | 29.87% | 119967600
GEN-2017-031 | 09 - Nebraska |  | ERIS | Keystone to Sidney 345kV New Build CKT 2 | Current Study | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit | 25541102.04 | 21.29% | 119967600
GEN-2017-037 | 09 - Nebraska |  | ERIS | Keystone to Sidney 345kV New Build CKT 2 | Current Study | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit | 10233236.28 | 8.53% | 119967600
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Kildare to White Eagle 138kV Rebuild | Current Study | Rebuild the existing Kildare to While Eagle 138 kV 11.22 mile line to achieve a minimm light/emergency rating of 298 MVA | 2076981.88 | 40.54% | 5123000
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Kildare to White Eagle 138kV Rebuild | Current Study | Rebuild the existing Kildare to While Eagle 138 kV 11.22 mile line to achieve a minimm light/emergency rating of 298 MVA | 2134711.61 | 41.67% | 5123000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Kildare to White Eagle 138kV Rebuild | Current Study | Rebuild the existing Kildare to While Eagle 138 kV 11.22 mile line to achieve a minimm light/emergency rating of 298 MVA | 911306.51 | 17.79% | 5123000
GEN-2017-051 | 07 - Southwestern Oklahoma | 133005 | ERIS | Lake Creek SW - Russell SW 69 kV GEN-2017-051 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-051 (30 MW/Solar), into the Point of Interconnection (POI) at Lake Creek SW - Russell SW 69 kV. | 4750000 | 100% | 4750000
GEN-2017-051 | 07 - Southwestern Oklahoma | 133004 | ERIS | Lake Creek SW - Russell SW 69 kV GEN-2017-051 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-051 (30 MW/Solar), into the Point of Interconnection (POI) at Lake Creek SW - Russell SW 69 kV. | 400000 | 100% | 400000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico | 132911 | ERIS | Lakeview - Brownfield 69 kV GEN-2016-077 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-077 (54 MW/Solar), into the Point of Interconnection (POI) at Lakefield - Brownfield 69 kV. | 5040642 | 100% | 5040642
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico | 132910 | ERIS | Lakeview - Brownfield 69 kV GEN-2016-077 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-077 (54 MW/Solar), into the Point of Interconnection (POI) at Lakefield - Brownfield 69 kV. | 868751 | 100% | 868751
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Lampton to Hale County 115kV Rebuild | Current Study | Rebuild the existing Lampton to Hale Coutny 115kV 20.06 mile line to achieve a minimum summer/emergency rating of 98 MVA | 30000 | 100% | 30000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico | 133071 | ERIS | Lamton 115 kV Substation GEN-2017-091 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-091 (26.3 MW/Solar), into the Point of Interconnection (POI) at Lamton 115 kV Substation. | 1544043 | 100% | 1544043
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico | 133070 | ERIS | Lamton 115 kV Substation GEN-2017-091 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-091 (26.3 MW/Solar), into the Point of Interconnection (POI) at Lamton 115 kV Substation. | 667159 | 100% | 667159
GEN-2016-034 | 09 - Nebraska | 132901 | ERIS | Laramie River - Sidney 345 kV GEN-2016-034 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-034 (90 MW/Wind), into the Point of Interconnection (POI) at Laramie River - Sidney 345 kV. | 19121943 | 100% | 19121943
GEN-2016-034 | 09 - Nebraska | 132900 | ERIS | Laramie River - Sidney 345 kV GEN-2016-034 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-034 (90 MW/Wind), into the Point of Interconnection (POI) at Laramie River - Sidney 345 kV. | 1365130 | 100% | 1365130
GEN-2017-060 | 12 - Northwest Arkansas | 133019 | ERIS | LaRussell Energy Center 161 kV Substation GEN-2017-060 Interconnection (Non-Shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-060 (149.4 MW/Wind), into the Point of Interconnection (POI) at LaRussell Energy Center 161 kV Substation. | 2400000 | 100% | 2400000
GEN-2017-060 | 12 - Northwest Arkansas | 133018 | ERIS | LaRussell Energy Center 161 kV Substation GEN-2017-060 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-060 (149.4 MW/Wind), into the Point of Interconnection (POI) at LaRussell Energy Center 161 kV Substation. | 800000 | 100% | 800000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Lawrence to Sioux Falls 115kV Rebuild | Current Study | Rebuild the existing Lawrence to Sioux Falls 115kV 1.0 mile line to achieve a minimum winter/emergency rating of 295 MVA | 11848.4152 | 12.88% | 92000
GEN-2017-048 | 16 - Western North Dakota |  | NRIS | Lawrence to Sioux Falls 115kV Rebuild | Current Study | Rebuild the existing Lawrence to Sioux Falls 115kV 1.0 mile line to achieve a minimum winter/emergency rating of 295 MVA | 29575.0425 | 32.15% | 92000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Lawrence to Sioux Falls 115kV Rebuild | Current Study | Rebuild the existing Lawrence to Sioux Falls 115kV 1.0 mile line to achieve a minimum winter/emergency rating of 295 MVA | 19897.6102 | 21.63% | 92000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Lawrence to Sioux Falls 115kV Rebuild | Current Study | Rebuild the existing Lawrence to Sioux Falls 115kV 1.0 mile line to achieve a minimum winter/emergency rating of 295 MVA | 5225.0775 | 5.679% | 92000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Lawrence to Sioux Falls 115kV Rebuild | Current Study | Rebuild the existing Lawrence to Sioux Falls 115kV 1.0 mile line to achieve a minimum winter/emergency rating of 295 MVA | 25453.8546 | 27.67% | 92000
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Litchfield to Asbury Plant 161kV Rebuild | Current Study | Rebuild the existing Litchfield to Asbury Plant 161kV 6.8 mile line to achieve a minimum winter/emergency rating of 329 MVA | 16610000 | 100% | 16610000
GEN-2017-048 | 16 - Western North Dakota |  | NRIS | Logan 230/115kV New Transformer CKT3 | Current Study | Build a new 230/115kV transformer at Logan as a third circuit | 6621188 | 100% | 6621188
GEN-2016-005 | 03 - Spearville |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 153765.3765 | 1.23% | 12500000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 1266376.6377 | 10.13% | 12500000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 252525.2525 | 2.02% | 12500000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 470047.0047 | 3.76% | 12500000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 722572.2572 | 5.781% | 12500000
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 140014.0014 | 1.12% | 12500000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 32503.2503 | 0.26% | 12500000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 477547.7548 | 3.82% | 12500000
GEN-2017-018 | 03 - Spearville |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 225022.5023 | 1.8% | 12500000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 911341.1341 | 7.291% | 12500000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 518801.8802 | 4.15% | 12500000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 921342.1342 | 7.371% | 12500000
GEN-2017-032 | 03 - Spearville |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 161266.1266 | 1.29% | 12500000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 1063856.3856 | 8.511% | 12500000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 376287.6288 | 3.01% | 12500000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 138763.8764 | 1.11% | 12500000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 1066356.6357 | 8.531% | 12500000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 293779.3779 | 2.35% | 12500000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 190019.0019 | 1.52% | 12500000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 197519.752 | 1.58% | 12500000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 1847684.7685 | 14.78% | 12500000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 42504.2504 | 0.34% | 12500000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 352535.2535 | 2.82% | 12500000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 487548.7549 | 3.9% | 12500000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Longwood 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | 190019.0019 | 1.52% | 12500000
GEN-2016-005 | 03 - Spearville |  | NRIS | Lydia 345kV Reactive Support | Current Study | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation | 265500 | 1.77% | 15000000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Lydia 345kV Reactive Support | Current Study | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation | 2179500 | 14.53% | 15000000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Lydia 345kV Reactive Support | Current Study | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation | 1357500 | 9.05% | 15000000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Lydia 345kV Reactive Support | Current Study | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation | 741000 | 4.94% | 15000000
GEN-2017-018 | 03 - Spearville |  | NRIS | Lydia 345kV Reactive Support | Current Study | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation | 385500 | 2.57% | 15000000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Lydia 345kV Reactive Support | Current Study | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation | 1552500 | 10.35% | 15000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Lydia 345kV Reactive Support | Current Study | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation | 1885500 | 12.57% | 15000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Lydia 345kV Reactive Support | Current Study | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation | 210000 | 1.4% | 15000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Lydia 345kV Reactive Support | Current Study | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation | 1888500 | 12.59% | 15000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Lydia 345kV Reactive Support | Current Study | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation | 385500 | 2.57% | 15000000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Lydia 345kV Reactive Support | Current Study | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation | 3082500 | 20.55% | 15000000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Lydia 345kV Reactive Support | Current Study | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation | 87000 | 0.58% | 15000000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Lydia 345kV Reactive Support | Current Study | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation | 685500 | 4.57% | 15000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Lydia 345kV Reactive Support | Current Study | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation | 294000 | 1.96% | 15000000
GEN-2016-005 | 03 - Spearville |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 8300 | 1.66% | 500000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 4800 | 0.96% | 500000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 950 | 0.19% | 500000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 1750 | 0.35% | 500000
GEN-2016-107 | 01 - Woodward |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 3450 | 0.69% | 500000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 4900 | 0.98% | 500000
GEN-2016-159 | 09 - Nebraska |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 306900 | 61.38% | 500000
GEN-2017-011 | 01 - Woodward |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 5700 | 1.14% | 500000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 42350 | 8.47% | 500000
GEN-2017-018 | 03 - Spearville |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 7350 | 1.47% | 500000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 200 | 0.04% | 500000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 100 | 0.02% | 500000
GEN-2017-028 | 01 - Woodward |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 900 | 0.18% | 500000
GEN-2017-032 | 03 - Spearville |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 15450 | 3.09% | 500000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 2950 | 0.59% | 500000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 1450 | 0.29% | 500000
GEN-2017-047 | 02 - Hitchland |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 3750 | 0.75% | 500000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 46300 | 9.26% | 500000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 6500 | 1.3% | 500000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 2950 | 0.59% | 500000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 2350 | 0.47% | 500000
GEN-2017-067 | 01 - Woodward |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 3450 | 0.69% | 500000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 4300 | 0.86% | 500000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 1150 | 0.23% | 500000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 1150 | 0.23% | 500000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 500 | 0.1% | 500000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 50 | 0.01% | 500000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 2050 | 0.41% | 500000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 14250 | 2.85% | 500000
GEN-2017-100 | 02 - Hitchland |  | NRIS | Madison to Norfolk 115kV Rebuild | Current Study | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | 3750 | 0.75% | 500000
GEN-2016-005 | 03 - Spearville |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 328397.4197 | 4.54% | 7232700
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 173602.1602 | 2.4% | 7232700
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 26040.324 | 0.36% | 7232700
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 47740.5941 | 0.6601% | 7232700
GEN-2016-093 | 09 - Nebraska |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 332014.1314 | 4.59% | 7232700
GEN-2016-103 | 15 - Eastern South Dakota |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 81737.6838 | 1.13% | 7232700
GEN-2016-107 | 01 - Woodward |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 103437.9538 | 1.43% | 7232700
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 57867.3867 | 0.8001% | 7232700
GEN-2016-159 | 09 - Nebraska |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 305250.465 | 4.22% | 7232700
GEN-2017-001 | 09 - Nebraska |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 1719384.7285 | 23.77% | 7232700
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 112118.0618 | 1.55% | 7232700
GEN-2017-011 | 01 - Woodward |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 194579.0879 | 2.69% | 7232700
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 151901.8902 | 2.1% | 7232700
GEN-2017-018 | 03 - Spearville |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 245936.3936 | 3.4% | 7232700
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 6510.081 | 0.09001% | 7232700
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 4340.054 | 0.06001% | 7232700
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 39060.486 | 0.5401% | 7232700
GEN-2017-028 | 01 - Woodward |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 26040.324 | 0.36% | 7232700
GEN-2017-031 | 09 - Nebraska |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 480299.3099 | 6.641% | 7232700
GEN-2017-032 | 03 - Spearville |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 620627.7228 | 8.581% | 7232700
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 71610.8911 | 0.9901% | 7232700
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 52803.9904 | 0.7301% | 7232700
GEN-2017-037 | 09 - Nebraska |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 94757.8458 | 1.31% | 7232700
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 33273.7474 | 0.46% | 7232700
GEN-2017-047 | 02 - Hitchland |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 153348.5749 | 2.12% | 7232700
GEN-2017-055 | 09 - Nebraska |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 853543.9544 | 11.8% | 7232700
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 10850.135 | 0.15% | 7232700
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 211939.3039 | 2.93% | 7232700
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 72334.2334 | 1% | 7232700
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 79567.6568 | 1.1% | 7232700
GEN-2017-067 | 01 - Woodward |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 103437.9538 | 1.43% | 7232700
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 68717.5218 | 0.9501% | 7232700
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 0 | 0% | 7232700
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 1446.6847 | 0.02% | 7232700
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 39783.8284 | 0.5501% | 7232700
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 5786.7387 | 0.08001% | 7232700
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 4340.054 | 0.06001% | 7232700
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 33273.7474 | 0.46% | 7232700
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 129478.2778 | 1.79% | 7232700
GEN-2017-100 | 02 - Hitchland |  | NRIS | Mark Moore 161kV Reactive Support | Current Study | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | 155518.6019 | 2.15% | 7232700
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Mark Moore to Elm Creek 345kV New Build | Current Study | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | 10557440 | 5.12% | 206200000
GEN-2016-093 | 09 - Nebraska |  | NRIS | Mark Moore to Elm Creek 345kV New Build | Current Study | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | 20145740 | 9.77% | 206200000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mark Moore to Elm Creek 345kV New Build | Current Study | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | 3505400 | 1.7% | 206200000
GEN-2016-159 | 09 - Nebraska |  | NRIS | Mark Moore to Elm Creek 345kV New Build | Current Study | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | 18516760 | 8.98% | 206200000
GEN-2017-001 | 09 - Nebraska |  | NRIS | Mark Moore to Elm Creek 345kV New Build | Current Study | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | 104399060 | 50.63% | 206200000
GEN-2017-031 | 09 - Nebraska |  | NRIS | Mark Moore to Elm Creek 345kV New Build | Current Study | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | 29156680 | 14.14% | 206200000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Mark Moore to Elm Creek 345kV New Build | Current Study | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | 4371440 | 2.12% | 206200000
GEN-2017-037 | 09 - Nebraska |  | NRIS | Mark Moore to Elm Creek 345kV New Build | Current Study | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | 5773600 | 2.8% | 206200000
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mark Moore to Elm Creek 345kV New Build | Current Study | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | 2020760 | 0.98% | 206200000
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas |  | NRIS | Mark Moore to Elm Creek 345kV New Build | Current Study | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | 680460 | 0.33% | 206200000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Mark Moore to Elm Creek 345kV New Build | Current Study | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | 4371440 | 2.12% | 206200000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mark Moore to Elm Creek 345kV New Build | Current Study | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | 61860 | 0.03% | 206200000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Mark Moore to Elm Creek 345kV New Build | Current Study | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | 350540 | 0.17% | 206200000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mark Moore to Elm Creek 345kV New Build | Current Study | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | 268060 | 0.13% | 206200000
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mark Moore to Elm Creek 345kV New Build | Current Study | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | 2020760 | 0.98% | 206200000
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas | 132939 | ERIS | Marmaton - Litchfield 161 kV GEN-2017-005 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-005 (195 MW/Wind), into the Point of Interconnection (POI) at Marmaton - Litchfield 161 kV. | 11434128 | 100% | 11434128
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas | 132938 | ERIS | Marmaton - Litchfield 161 kV GEN-2017-005 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-005 (195 MW/Wind), into the Point of Interconnection (POI) at Marmaton - Litchfield 161 kV. | 1216477 | 100% | 1216477
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Martin to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | 132013.2013 | 1.5% | 8800000
GEN-2016-107 | 01 - Woodward |  | NRIS | Martin to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | 56325.6326 | 0.6401% | 8800000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Martin to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | 68646.8647 | 0.7801% | 8800000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Martin to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | 6502970.297 | 73.9% | 8800000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Martin to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | 20242.0242 | 0.23% | 8800000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Martin to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | 12321.2321 | 0.14% | 8800000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Martin to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | 66006.6007 | 0.7501% | 8800000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Martin to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | 42244.2244 | 0.48% | 8800000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Martin to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | 66006.6007 | 0.7501% | 8800000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Martin to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | 61606.1606 | 0.7001% | 8800000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Martin to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | 49284.9285 | 0.5601% | 8800000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Martin to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | 18481.8482 | 0.21% | 8800000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Martin to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | 14961.4961 | 0.17% | 8800000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Martin to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | 33443.3443 | 0.38% | 8800000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Martin to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | 1655445.5446 | 18.81% | 8800000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 28138.1302 | 2.164% | 1300000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 4417.37 | 0.3398% | 1300000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 8206.9601 | 0.6313% | 1300000
GEN-2016-107 | 01 - Woodward |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 41925.4203 | 3.225% | 1300000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 169446.3913 | 13.03% | 1300000
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 25706.4202 | 1.977% | 1300000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 12790.0601 | 0.9839% | 1300000
GEN-2017-018 | 03 - Spearville |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 3290.78 | 0.2531% | 1300000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 10554.4601 | 0.8119% | 1300000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 6195.19 | 0.4766% | 1300000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 17906.0801 | 1.377% | 1300000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 9432.6701 | 0.7256% | 1300000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 4015.55 | 0.3089% | 1300000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 17932.9401 | 1.379% | 1300000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 16233.5701 | 1.249% | 1300000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 13099.8201 | 1.008% | 1300000
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 601982.8146 | 46.31% | 1300000
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 251992.8019 | 19.38% | 1300000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 14643.2901 | 1.126% | 1300000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 10056.3401 | 0.7736% | 1300000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 26814.6002 | 2.063% | 1300000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | McElroy to University 138kV Rebuild | Current Study | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | 5218.34 | 0.4014% | 1300000
GEN-2017-067 | 01 - Woodward | 133029 | ERIS | Minco 345 kV Substation GEN-2017-067 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-067 (200.25 MW/Solar), into the Point of Interconnection (POI) at Minco 345 kV Substation. | 1082665 | 100% | 1082665
GEN-2017-067 | 01 - Woodward | 133028 | ERIS | Minco 345 kV Substation GEN-2017-067 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-067 (200.25 MW/Solar), into the Point of Interconnection (POI) at Minco 345 kV Substation. | 942335 | 100% | 942335
GEN-2016-037 | 07 - Southwestern Oklahoma |  | ERIS | Minco to Cimarron 345kV Rebuild | Current Study | Rebuild the existing Minco to Cimarron 345kV 20.90 mile line to achieve a minimum winter/emergency rating of 1240 MVA | 1201279.77 | 71.4% | 1682485
GEN-2017-036 | 07 - Southwestern Oklahoma |  | ERIS | Minco to Cimarron 345kV Rebuild | Current Study | Rebuild the existing Minco to Cimarron 345kV 20.90 mile line to achieve a minimum winter/emergency rating of 1240 MVA | 273739.5 | 16.27% | 1682485
GEN-2017-051 | 07 - Southwestern Oklahoma |  | ERIS | Minco to Cimarron 345kV Rebuild | Current Study | Rebuild the existing Minco to Cimarron 345kV 20.90 mile line to achieve a minimum winter/emergency rating of 1240 MVA | 73410.95 | 4.363% | 1682485
GEN-2017-053 | 07 - Southwestern Oklahoma |  | ERIS | Minco to Cimarron 345kV Rebuild | Current Study | Rebuild the existing Minco to Cimarron 345kV 20.90 mile line to achieve a minimum winter/emergency rating of 1240 MVA | 134054.78 | 7.968% | 1682485
GEN-2017-083 | 04 - Northwest Kansas | 133059 | ERIS | Mingo 115 kV Substation GEN-2017-083 Interconnection (Non-Shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-083 (100 MW/Wind), into the Point of Interconnection (POI) at Mingo 115 kV Substation. | 6236939.02 | 100% | 6236939.02
GEN-2017-083 | 04 - Northwest Kansas | 133058 | ERIS | Mingo 115 kV Substation GEN-2017-083 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-083 (100 MW/Wind), into the Point of Interconnection (POI) at Mingo 115 kV Substation. | 2136559.42 | 100% | 2136559.42
GEN-2017-013 | 04 - Northwest Kansas | 132955 | ERIS | Mingo 345 kV Substation GEN-2017-013 Interconnection (Non-Shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-013 (200 MW/Wind), into the Point of Interconnection (POI) at Mingo 345 kV Substation. | 3204601.9 | 100% | 3204601.9
GEN-2017-013 | 04 - Northwest Kansas | 132954 | ERIS | Mingo 345 kV Substation GEN-2017-013 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-013 (200 MW/Wind), into the Point of Interconnection (POI) at Mingo 345 kV Substation. | 2312184.97 | 100% | 2312184.97
GEN-2016-034 | 09 - Nebraska |  | ERIS | Mingo to Post Rock 345kV New Build | Current Study | Build a new 100 mile 345kV line from Mingo to Post Rock | 32803517.625 | 18.48% | 177500000
GEN-2016-093 | 09 - Nebraska |  | ERIS | Mingo to Post Rock 345kV New Build | Current Study | Build a new 100 mile 345kV line from Mingo to Post Rock | 23507079.375 | 13.24% | 177500000
GEN-2016-109 | 09 - Nebraska |  | ERIS | Mingo to Post Rock 345kV New Build | Current Study | Build a new 100 mile 345kV line from Mingo to Post Rock | 6501984.75 | 3.663% | 177500000
GEN-2016-159 | 09 - Nebraska |  | ERIS | Mingo to Post Rock 345kV New Build | Current Study | Build a new 100 mile 345kV line from Mingo to Post Rock | 13030692.125 | 7.341% | 177500000
GEN-2017-001 | 09 - Nebraska |  | ERIS | Mingo to Post Rock 345kV New Build | Current Study | Build a new 100 mile 345kV line from Mingo to Post Rock | 9630661.875 | 5.426% | 177500000
GEN-2017-006 | 09 - Nebraska |  | ERIS | Mingo to Post Rock 345kV New Build | Current Study | Build a new 100 mile 345kV line from Mingo to Post Rock | 5645174.5 | 3.18% | 177500000
GEN-2017-008 | 09 - Nebraska |  | ERIS | Mingo to Post Rock 345kV New Build | Current Study | Build a new 100 mile 345kV line from Mingo to Post Rock | 33419602.375 | 18.83% | 177500000
GEN-2017-031 | 09 - Nebraska |  | ERIS | Mingo to Post Rock 345kV New Build | Current Study | Build a new 100 mile 345kV line from Mingo to Post Rock | 33912333.5 | 19.11% | 177500000
GEN-2017-037 | 09 - Nebraska |  | ERIS | Mingo to Post Rock 345kV New Build | Current Study | Build a new 100 mile 345kV line from Mingo to Post Rock | 6716307.125 | 3.784% | 177500000
GEN-2017-055 | 09 - Nebraska |  | ERIS | Mingo to Post Rock 345kV New Build | Current Study | Build a new 100 mile 345kV line from Mingo to Post Rock | 12303164 | 6.931% | 177500000
GEN-2017-085 | 09 - Nebraska |  | ERIS | Mingo to Post Rock 345kV New Build | Current Study | Build a new 100 mile 345kV line from Mingo to Post Rock | 29482.75 | 0.01661% | 177500000
GEN-2017-006 | 09 - Nebraska | 132941 | ERIS | Moore - Pauline 345 kV GEN-2017-006 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-006 (73.6 MW/Wind), into the Point of Interconnection (POI) at Moore - Pauline 345 kV. | 3150000 | 100% | 3150000
GEN-2017-006 | 09 - Nebraska | 132940 | ERIS | Moore - Pauline 345 kV GEN-2017-006 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-006 (73.6 MW/Wind), into the Point of Interconnection (POI) at Moore - Pauline 345 kV. | 3150000 | 100% | 3150000
GEN-2017-008 | 09 - Nebraska | 132945 | ERIS | Moore - Pauline 345 kV GEN-2017-008 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-008 (305 MW/Solar), into the Point of Interconnection (POI) at Moore - Pauline 345 kV Substation. | 1200000 | 100% | 1200000
GEN-2017-008 | 09 - Nebraska | 132944 | ERIS | Moore - Pauline 345 kV GEN-2017-008 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-008 (305 MW/Solar), into the Point of Interconnection (POI) at Moore - Pauline 345 kV Substation. | 1200000 | 100% | 1200000
GEN-2017-001 | 09 - Nebraska |  | ERIS | Moore to Monolith 345kV Rebuild | Current Study | Rebuild the existing Moore to Monolith 345kV 0.75 mile line to achieve a minimum winter/emergency rating of 982 MVA | 638399.3468 | 31.92% | 2000000
GEN-2017-006 | 09 - Nebraska |  | ERIS | Moore to Monolith 345kV Rebuild | Current Study | Rebuild the existing Moore to Monolith 345kV 0.75 mile line to achieve a minimum winter/emergency rating of 982 MVA | 304027.4885 | 15.2% | 2000000
GEN-2017-008 | 09 - Nebraska |  | ERIS | Moore to Monolith 345kV Rebuild | Current Study | Rebuild the existing Moore to Monolith 345kV 0.75 mile line to achieve a minimum winter/emergency rating of 982 MVA | 1057573.1647 | 52.88% | 2000000
GEN-2016-103 | 15 - Eastern South Dakota |  | NRIS | Mt. Vernon to Storla 115kV Rebuild | Current Study | Rebuild the existing Mt. Vernon to Storla 115kV 15.0 mile line to achieve a minimum summer/emergency rating of 128 MVA | 1982178.2178 | 25.74% | 7700000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Mt. Vernon to Storla 115kV Rebuild | Current Study | Rebuild the existing Mt. Vernon to Storla 115kV 15.0 mile line to achieve a minimum summer/emergency rating of 128 MVA | 103960.396 | 1.35% | 7700000
GEN-2017-048 | 16 - Western North Dakota |  | NRIS | Mt. Vernon to Storla 115kV Rebuild | Current Study | Rebuild the existing Mt. Vernon to Storla 115kV 15.0 mile line to achieve a minimum summer/emergency rating of 128 MVA | 2401870.187 | 31.19% | 7700000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Mt. Vernon to Storla 115kV Rebuild | Current Study | Rebuild the existing Mt. Vernon to Storla 115kV 15.0 mile line to achieve a minimum summer/emergency rating of 128 MVA | 359625.9626 | 4.67% | 7700000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mt. Vernon to Storla 115kV Rebuild | Current Study | Rebuild the existing Mt. Vernon to Storla 115kV 15.0 mile line to achieve a minimum summer/emergency rating of 128 MVA | 86248.6249 | 1.12% | 7700000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Mt. Vernon to Storla 115kV Rebuild | Current Study | Rebuild the existing Mt. Vernon to Storla 115kV 15.0 mile line to achieve a minimum summer/emergency rating of 128 MVA | 16941.6942 | 0.22% | 7700000
GEN-2017-094 | 15 - Eastern South Dakota |  | NRIS | Mt. Vernon to Storla 115kV Rebuild | Current Study | Rebuild the existing Mt. Vernon to Storla 115kV 15.0 mile line to achieve a minimum summer/emergency rating of 128 MVA | 2749174.9175 | 35.7% | 7700000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 95878.57 | 22.83% | 420000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 547.56 | 0.1304% | 420000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 826.22 | 0.1967% | 420000
GEN-2016-107 | 01 - Woodward |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 56056.01 | 13.35% | 420000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 1352.67 | 0.3221% | 420000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 19378.51 | 4.614% | 420000
GEN-2017-018 | 03 - Spearville |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 38103.56 | 9.072% | 420000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 12194.19 | 2.903% | 420000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 7323.28 | 1.744% | 420000
GEN-2017-028 | 01 - Woodward |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 42343.55 | 10.08% | 420000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 21256.28 | 5.061% | 420000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 21406.5 | 5.097% | 420000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 8551.33 | 2.036% | 420000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 21288.16 | 5.069% | 420000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 39416.8 | 9.385% | 420000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 13837.61 | 3.295% | 420000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 3076.71 | 0.7326% | 420000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 2744.54 | 0.6535% | 420000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 5572.94 | 1.327% | 420000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Mustang to SW 5th St. 138kV Rebuild | Current Study | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | 8845.01 | 2.106% | 420000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | ERIS | Naples Tap to Cornville Tap 138kV Rebuild | Current Study | Rebuild the existing Naples Tap to Cornville Tap 138kV 11 mile line to achieve a minimum winter/emergency rating of 203 MVA | 6186333.3917 | 58.33% | 10605749
GEN-2017-051 | 07 - Southwestern Oklahoma |  | ERIS | Naples Tap to Cornville Tap 138kV Rebuild | Current Study | Rebuild the existing Naples Tap to Cornville Tap 138kV 11 mile line to achieve a minimum winter/emergency rating of 203 MVA | 1625861.3217 | 15.33% | 10605749
GEN-2017-053 | 07 - Southwestern Oklahoma |  | ERIS | Naples Tap to Cornville Tap 138kV Rebuild | Current Study | Rebuild the existing Naples Tap to Cornville Tap 138kV 11 mile line to achieve a minimum winter/emergency rating of 203 MVA | 2793554.2866 | 26.34% | 10605749
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Naples Tap to Payne 138kV Rebuild | Current Study | Rebuild the existing Naples Tap to Payne 138kV 8.9 mile line to achieve a minimum summer/emergency rating of 185 MVA | 2390290.7635 | 27.86% | 8581015.1
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Naples Tap to Payne 138kV Rebuild | Current Study | Rebuild the existing Naples Tap to Payne 138kV 8.9 mile line to achieve a minimum summer/emergency rating of 185 MVA | 28323.0144 | 0.3301% | 8581015.1
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Naples Tap to Payne 138kV Rebuild | Current Study | Rebuild the existing Naples Tap to Payne 138kV 8.9 mile line to achieve a minimum summer/emergency rating of 185 MVA | 1013620.6074 | 11.81% | 8581015.1
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Naples Tap to Payne 138kV Rebuild | Current Study | Rebuild the existing Naples Tap to Payne 138kV 8.9 mile line to achieve a minimum summer/emergency rating of 185 MVA | 1247070.9082 | 14.53% | 8581015.1
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Naples Tap to Payne 138kV Rebuild | Current Study | Rebuild the existing Naples Tap to Payne 138kV 8.9 mile line to achieve a minimum summer/emergency rating of 185 MVA | 1015337.1538 | 11.83% | 8581015.1
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Naples Tap to Payne 138kV Rebuild | Current Study | Rebuild the existing Naples Tap to Payne 138kV 8.9 mile line to achieve a minimum summer/emergency rating of 185 MVA | 2731883.483 | 31.84% | 8581015.1
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Naples Tap to Payne 138kV Rebuild | Current Study | Rebuild the existing Naples Tap to Payne 138kV 8.9 mile line to achieve a minimum summer/emergency rating of 185 MVA | 40338.8387 | 0.4701% | 8581015.1
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Naples Tap to Payne 138kV Rebuild | Current Study | Rebuild the existing Naples Tap to Payne 138kV 8.9 mile line to achieve a minimum summer/emergency rating of 185 MVA | 43771.9314 | 0.5101% | 8581015.1
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Naples Tap to Payne 138kV Rebuild | Current Study | Rebuild the existing Naples Tap to Payne 138kV 8.9 mile line to achieve a minimum summer/emergency rating of 185 MVA | 70378.3995 | 0.8202% | 8581015.1
GEN-2016-005 | 03 - Spearville |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 207937.6187 | 0.16% | 130000000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 3469959.0123 | 2.669% | 130000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 415875.2374 | 0.3199% | 130000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 779766.0702 | 0.5998% | 130000000
GEN-2016-107 | 01 - Woodward |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 1377586.724 | 1.06% | 130000000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 3197040.8877 | 2.459% | 130000000
GEN-2017-011 | 01 - Woodward |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 948715.3854 | 0.7298% | 130000000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 1273617.9146 | 0.9797% | 130000000
GEN-2017-018 | 03 - Spearville |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 636808.9573 | 0.4899% | 130000000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 1572528.2415 | 1.21% | 130000000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 909727.0819 | 0.6998% | 130000000
GEN-2017-028 | 01 - Woodward |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 597820.6538 | 0.4599% | 130000000
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 22028391.4826 | 16.94% | 130000000
GEN-2017-032 | 03 - Spearville |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 142957.1129 | 0.11% | 130000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 1728481.4556 | 1.33% | 130000000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 1208637.4088 | 0.9297% | 130000000
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 22028391.4826 | 16.94% | 130000000
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 22028391.4826 | 16.94% | 130000000
GEN-2017-047 | 02 - Hitchland |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 545836.2491 | 0.4199% | 130000000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 4522643.207 | 3.479% | 130000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 584824.5526 | 0.4499% | 130000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 1728481.4556 | 1.33% | 130000000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 1923422.9731 | 1.48% | 130000000
GEN-2017-067 | 01 - Woodward |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 2469259.2222 | 1.899% | 130000000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 363890.8328 | 0.2799% | 130000000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 1546536.0392 | 1.19% | 130000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 1533539.938 | 1.18% | 130000000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 3378986.3041 | 2.599% | 130000000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 1117664.7006 | 0.8597% | 130000000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 2599220.2339 | 1.999% | 130000000
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 22028391.4826 | 16.94% | 130000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 558832.3503 | 0.4299% | 130000000
GEN-2017-100 | 02 - Hitchland |  | NRIS | Nashua to Sibley 345kV New Build | Current Study | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | 545836.2491 | 0.4199% | 130000000
GEN-2016-005 | 03 - Spearville |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 574002.7992 | 0.8497% | 67550000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 2005633.31 | 2.969% | 67550000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 303883.8348 | 0.4499% | 67550000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 560496.8509 | 0.8298% | 67550000
GEN-2016-107 | 01 - Woodward |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 1046710.9867 | 1.55% | 67550000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 2363540.9377 | 3.499% | 67550000
GEN-2017-011 | 01 - Woodward |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 898145.5563 | 1.33% | 67550000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 5078236.529 | 7.518% | 67550000
GEN-2017-018 | 03 - Spearville |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 1242547.2358 | 1.839% | 67550000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 580755.7733 | 0.8597% | 67550000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 344401.6795 | 0.5098% | 67550000
GEN-2017-028 | 01 - Woodward |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 384919.5241 | 0.5698% | 67550000
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 7678131.5605 | 11.37% | 67550000
GEN-2017-032 | 03 - Spearville |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 33764.8705 | 0.04999% | 67550000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 1161511.5465 | 1.719% | 67550000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 675297.4108 | 0.9997% | 67550000
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 7678131.5605 | 11.37% | 67550000
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 7678131.5605 | 11.37% | 67550000
GEN-2017-047 | 02 - Hitchland |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 432190.3429 | 0.6398% | 67550000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 4679811.0567 | 6.928% | 67550000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 1708502.4493 | 2.529% | 67550000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 1161511.5465 | 1.719% | 67550000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 1127746.676 | 1.669% | 67550000
GEN-2017-067 | 01 - Woodward |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 1499160.2519 | 2.219% | 67550000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 1222288.3135 | 1.809% | 67550000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 898145.5563 | 1.33% | 67550000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 891392.5822 | 1.32% | 67550000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 1411371.5885 | 2.089% | 67550000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 506473.0581 | 0.7498% | 67550000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 1526172.1484 | 2.259% | 67550000
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 7678131.5605 | 11.37% | 67550000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 2086668.9993 | 3.089% | 67550000
GEN-2017-100 | 02 - Hitchland |  | NRIS | Nashua to St. Joe 345kV Rebuild | Current Study | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | 432190.3429 | 0.6398% | 67550000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 132991 | ERIS | Needmore 230 kV Substation GEN-2017-039 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-039 (200.1 MW/Wind), into the Point of Interconnection (POI) at Needmore 230 kV Substation. | 693659 | 100% | 693659
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 132990 | ERIS | Needmore 230 kV Substation GEN-2017-039 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-039 (200.1 MW/Wind), into the Point of Interconnection (POI) at Needmore 230 kV Substation. | 933132 | 100% | 933132
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 132947 | ERIS | Neosho - Caney River 345 kV GEN-2017-009 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-009 (302.5 MW/Wind), into the Point of Interconnection (POI) at Neosho - Caney River 345 kV. | 14319701 | 100% | 14319701
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas | 132946 | ERIS | Neosho - Caney River 345 kV GEN-2017-009 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-009 (302.5 MW/Wind), into the Point of Interconnection (POI) at Neosho - Caney River 345 kV. | 1522073 | 100% | 1522073
GEN-2017-050 | 12 - Northwest Arkansas | 133003 | ERIS | Neosho - Crawford 69 kV GEN-2017-050 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-050 (25 MW/Solar), into the Point of Interconnection (POI) at Neosho - Crawford 69 kV. | 4976423 | 100% | 4976423
GEN-2017-050 | 12 - Northwest Arkansas | 133002 | ERIS | Neosho - Crawford 69 kV GEN-2017-050 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-050 (25 MW/Solar), into the Point of Interconnection (POI) at Neosho - Crawford 69 kV. | 824356 | 100% | 824356
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Neosho South to Tipton Ford 161kV Rebuild | Current Study | Rebuild the existing Neosho South to Tipton Ford 161kV 10.6 mile line to achieve a minimum summer/emergency rating of 241 MVA | 1406368.5 | 8.49% | 16565000
GEN-2016-107 | 01 - Woodward |  | NRIS | Neosho South to Tipton Ford 161kV Rebuild | Current Study | Rebuild the existing Neosho South to Tipton Ford 161kV 10.6 mile line to achieve a minimum summer/emergency rating of 241 MVA | 525110.5 | 3.17% | 16565000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Neosho South to Tipton Ford 161kV Rebuild | Current Study | Rebuild the existing Neosho South to Tipton Ford 161kV 10.6 mile line to achieve a minimum summer/emergency rating of 241 MVA | 1142985 | 6.9% | 16565000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Neosho South to Tipton Ford 161kV Rebuild | Current Study | Rebuild the existing Neosho South to Tipton Ford 161kV 10.6 mile line to achieve a minimum summer/emergency rating of 241 MVA | 602966 | 3.64% | 16565000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Neosho South to Tipton Ford 161kV Rebuild | Current Study | Rebuild the existing Neosho South to Tipton Ford 161kV 10.6 mile line to achieve a minimum summer/emergency rating of 241 MVA | 354491 | 2.14% | 16565000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Neosho South to Tipton Ford 161kV Rebuild | Current Study | Rebuild the existing Neosho South to Tipton Ford 161kV 10.6 mile line to achieve a minimum summer/emergency rating of 241 MVA | 740455.5 | 4.47% | 16565000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Neosho South to Tipton Ford 161kV Rebuild | Current Study | Rebuild the existing Neosho South to Tipton Ford 161kV 10.6 mile line to achieve a minimum summer/emergency rating of 241 MVA | 495293.5 | 2.99% | 16565000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Neosho South to Tipton Ford 161kV Rebuild | Current Study | Rebuild the existing Neosho South to Tipton Ford 161kV 10.6 mile line to achieve a minimum summer/emergency rating of 241 MVA | 742112 | 4.48% | 16565000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Neosho South to Tipton Ford 161kV Rebuild | Current Study | Rebuild the existing Neosho South to Tipton Ford 161kV 10.6 mile line to achieve a minimum summer/emergency rating of 241 MVA | 778555 | 4.7% | 16565000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Neosho South to Tipton Ford 161kV Rebuild | Current Study | Rebuild the existing Neosho South to Tipton Ford 161kV 10.6 mile line to achieve a minimum summer/emergency rating of 241 MVA | 3142380.5 | 18.97% | 16565000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Neosho South to Tipton Ford 161kV Rebuild | Current Study | Rebuild the existing Neosho South to Tipton Ford 161kV 10.6 mile line to achieve a minimum summer/emergency rating of 241 MVA | 2110381 | 12.74% | 16565000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Neosho South to Tipton Ford 161kV Rebuild | Current Study | Rebuild the existing Neosho South to Tipton Ford 161kV 10.6 mile line to achieve a minimum summer/emergency rating of 241 MVA | 4523901.5 | 27.31% | 16565000
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Neosho to Riverton 161kV Rebuild | Current Study | Rebuild the existing Neosho to Riverton 161kV 28.4 mile line to achieve a minimum winter/normal rating of 324 MVA | 36383821.1598 | 77.15% | 47161402
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Neosho to Riverton 161kV Rebuild | Current Study | Rebuild the existing Neosho to Riverton 161kV 28.4 mile line to achieve a minimum winter/normal rating of 324 MVA | 10777580.8402 | 22.85% | 47161402
GEN-2017-048 | 16 - Western North Dakota | 132999 | ERIS | Neset 230 kV Substation GEN-2017-048 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-048 (300 MW/Wind), into the Point of Interconnection (POI) at Neset 230 kV Substation. | 1362742 | 100% | 1362742
GEN-2017-048 | 16 - Western North Dakota | 132998 | ERIS | Neset 230 kV Substation GEN-2017-048 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-048 (300 MW/Wind), into the Point of Interconnection (POI) at Neset 230 kV Substation. | 1617104 | 100% | 1617104
GEN-2017-048 | 16 - Western North Dakota |  | ERIS | Neset to Tioga 230kV Rebuild | Current Study | Rebuild the existing Neset to Tioga 230kV 1 mile line to achieve a minimum summer/emergency rating of 712 MVA | 950000 | 100% | 950000
GEN-2017-014 | 17 - Western South Dakota |  | ERIS | New Underwood 230kV Reactive Support | Current Study | Install a new 75 MVAR capacitor bank at New Underwood 230kV Substation | 2228921.7337 | 36.54% | 6100000
GEN-2017-064 | 17 - Western South Dakota |  | ERIS | New Underwood 230kV Reactive Support | Current Study | Install a new 75 MVAR capacitor bank at New Underwood 230kV Substation | 2452249.624 | 40.2% | 6100000
GEN-2017-097 | 17 - Western South Dakota |  | ERIS | New Underwood 230kV Reactive Support | Current Study | Install a new 75 MVAR capacitor bank at New Underwood 230kV Substation | 1418828.6423 | 23.26% | 6100000
GEN-2016-159 | 09 - Nebraska |  | NRIS | New Underwood to Wicksville 115kV Rebuild | Current Study | Rebuild the existing New Underwood to Wicksville 115kV 12.42 mile line to achieve a minimum summer/emergency rating of 150 MVA | 173800 | 3.16% | 5500000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | New Underwood to Wicksville 115kV Rebuild | Current Study | Rebuild the existing New Underwood to Wicksville 115kV 12.42 mile line to achieve a minimum summer/emergency rating of 150 MVA | 3850 | 0.07% | 5500000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | New Underwood to Wicksville 115kV Rebuild | Current Study | Rebuild the existing New Underwood to Wicksville 115kV 12.42 mile line to achieve a minimum summer/emergency rating of 150 MVA | 966350 | 17.57% | 5500000
GEN-2017-055 | 09 - Nebraska |  | NRIS | New Underwood to Wicksville 115kV Rebuild | Current Study | Rebuild the existing New Underwood to Wicksville 115kV 12.42 mile line to achieve a minimum summer/emergency rating of 150 MVA | 54450 | 0.99% | 5500000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | New Underwood to Wicksville 115kV Rebuild | Current Study | Rebuild the existing New Underwood to Wicksville 115kV 12.42 mile line to achieve a minimum summer/emergency rating of 150 MVA | 1326600 | 24.12% | 5500000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | New Underwood to Wicksville 115kV Rebuild | Current Study | Rebuild the existing New Underwood to Wicksville 115kV 12.42 mile line to achieve a minimum summer/emergency rating of 150 MVA | 12100 | 0.22% | 5500000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | New Underwood to Wicksville 115kV Rebuild | Current Study | Rebuild the existing New Underwood to Wicksville 115kV 12.42 mile line to achieve a minimum summer/emergency rating of 150 MVA | 7700 | 0.14% | 5500000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | New Underwood to Wicksville 115kV Rebuild | Current Study | Rebuild the existing New Underwood to Wicksville 115kV 12.42 mile line to achieve a minimum summer/emergency rating of 150 MVA | 2955150 | 53.73% | 5500000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico | 132953 | ERIS | Newhart - Potter County 230 kV GEN-2017-012 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-012 (201.6 MW/Wind), into the Point of Interconnection (POI) at Newhart - Potter County 230 kV. | 7433790 | 100% | 7433790
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico | 132952 | ERIS | Newhart - Potter County 230 kV GEN-2017-012 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-012 (201.6 MW/Wind), into the Point of Interconnection (POI) at Newhart - Potter County 230 kV. | 958427 | 100% | 958427
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico | 133061 | ERIS | Newhart - Swisher 230 kV GEN-2017-084 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-084 (89.3 MW/Solar), into the Point of Interconnection (POI) at Newhart - Swisher 230 kV. | 7415347 | 100% | 7415347
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico | 133060 | ERIS | Newhart - Swisher 230 kV GEN-2017-084 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-084 (89.3 MW/Solar), into the Point of Interconnection (POI) at Newhart - Swisher 230 kV. | 956616 | 100% | 956616
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 132931 | ERIS | Newhart 115 kV Substation GEN-2016-172 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-172 (231 MW/Wind), into the Point of Interconnection (POI) at Newhart 115 kV Substation. | 705336 | 100% | 705336
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 132930 | ERIS | Newhart 115 kV Substation GEN-2016-172 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-172 (231 MW/Wind), into the Point of Interconnection (POI) at Newhart 115 kV Substation. | 627807 | 100% | 627807
GEN-2016-005 | 03 - Spearville |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 233123.3123 | 1.26% | 18500000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 1905690.5691 | 10.3% | 18500000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 366336.6337 | 1.98% | 18500000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 679017.9018 | 3.67% | 18500000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 986148.6149 | 5.331% | 18500000
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 190569.0569 | 1.03% | 18500000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 31453.1453 | 0.17% | 18500000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 791879.1879 | 4.28% | 18500000
GEN-2017-018 | 03 - Spearville |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 340434.0434 | 1.84% | 18500000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 1361736.1736 | 7.361% | 18500000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 775227.5228 | 4.19% | 18500000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 1415391.5392 | 7.651% | 18500000
GEN-2017-032 | 03 - Spearville |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 242374.2374 | 1.31% | 18500000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 1556005.6006 | 8.411% | 18500000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 579107.9108 | 3.13% | 18500000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 233123.3123 | 1.26% | 18500000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 1557855.7856 | 8.421% | 18500000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 388538.8539 | 2.1% | 18500000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 246074.6075 | 1.33% | 18500000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 257175.7176 | 1.39% | 18500000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 2869636.9637 | 15.51% | 18500000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 53655.3655 | 0.29% | 18500000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 462546.2546 | 2.5% | 18500000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 660516.0516 | 3.57% | 18500000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Northwest Texarkana 345kV Reactive Support | Current Study | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | 316381.6382 | 1.71% | 18500000
GEN-2016-005 | 03 - Spearville |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 2159784.0216 | 1.2% | 180000000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 19006099.3901 | 10.56% | 180000000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 10258974.1026 | 5.699% | 180000000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 107989.2011 | 0.05999% | 180000000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 9413058.6941 | 5.229% | 180000000
GEN-2017-018 | 03 - Spearville |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 3221677.8322 | 1.79% | 180000000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 15802419.758 | 8.779% | 180000000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 8963103.6896 | 4.98% | 180000000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 14326567.3433 | 7.959% | 180000000
GEN-2017-032 | 03 - Spearville |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 2141785.8214 | 1.19% | 180000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 15820417.9582 | 8.789% | 180000000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 6443355.6644 | 3.58% | 180000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 2843715.6284 | 1.58% | 180000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 15838416.1584 | 8.799% | 180000000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 3941605.8394 | 2.19% | 180000000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 2573742.6257 | 1.43% | 180000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 2699730.027 | 1.5% | 180000000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 28581141.8858 | 15.88% | 180000000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 467953.2047 | 0.26% | 180000000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 4859514.0486 | 2.7% | 180000000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 6731326.8673 | 3.74% | 180000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Northwest Texarkana to Wilkes 345kV New Build | Current Study | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | 3797620.238 | 2.11% | 180000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 132959 | ERIS | Norton 115 kV Switching Station GEN-2017-016 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-016 (33 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | 1069895 | 100% | 1069895
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 132958 | ERIS | Norton 115 kV Switching Station GEN-2017-016 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-016 (33 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | 617431 | 100% | 617431
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 133033 | ERIS | Norton 115 kV Switching Station GEN-2017-069 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-069 (3.6 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | 1069895 | 100% | 1069895
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 133032 | ERIS | Norton 115 kV Switching Station GEN-2017-069 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-069 (3.6 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | 617431 | 100% | 617431
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Norton to Pleasant Hills 115kV Rebuild | Current Study | Rebuild the existing Norton to Pleasant Hills 115kV 54.54 mile line to achieve a minimum spring/emergency rating of 150 MVA | 135245.9 | 90.16% | 150000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Norton to Pleasant Hills 115kV Rebuild | Current Study | Rebuild the existing Norton to Pleasant Hills 115kV 54.54 mile line to achieve a minimum spring/emergency rating of 150 MVA | 14754.1 | 9.836% | 150000
GEN-2016-034 | 09 - Nebraska |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2016-093 | 09 - Nebraska |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2016-103 | 15 - Eastern South Dakota |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2016-109 | 09 - Nebraska |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2016-159 | 09 - Nebraska |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-001 | 09 - Nebraska |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-004 | 04 - Northwest Kansas |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-006 | 09 - Nebraska |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-008 | 09 - Nebraska |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-010 | 16 - Western North Dakota |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-013 | 04 - Northwest Kansas |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-014 | 17 - Western South Dakota |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-031 | 09 - Nebraska |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-037 | 09 - Nebraska |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-048 | 16 - Western North Dakota |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-055 | 09 - Nebraska |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-064 | 17 - Western South Dakota |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-083 | 04 - Northwest Kansas |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-085 | 09 - Nebraska |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-094 | 15 - Eastern South Dakota |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2017-097 | 17 - Western South Dakota |  |  | NTC 200220 (Rplan) | Contingent | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | 0 | 0 | 412074343
GEN-2016-107 | 01 - Woodward | 132921 | ERIS | Okeene - Cedardale 138 kV GEN-2016-107 Interconnection (NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-107 (141.75 MW/Wind), into the Point of Interconnection (POI) at Okeene - Cedardale 138 kV. | 4750000 | 100% | 4750000
GEN-2016-107 | 01 - Woodward | 132920 | ERIS | Okeene - Cedardale 138 kV GEN-2016-107 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-107 (141.75 MW/Wind), into the Point of Interconnection (POI) at Okeene - Cedardale 138 kV. | 400000 | 100% | 400000
GEN-2016-107 | 01 - Woodward |  | ERIS | Okeene to G16-107-Tap 138kV Rebuild | Current Study | Rebuild the existing Okeene to G16-107-Tap 138kV 16.975 mile line to achieve a minimum summer/normal rating of 170 MVA | 16366599.025 | 100% | 16366599.025
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 132983 | ERIS | Oklaunion 345 kV Substation GEN-2017-033 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-033 (200 MW/Wind), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | 3877147.5 | 100% | 3877147.5
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico | 132982 | ERIS | Oklaunion 345 kV Substation GEN-2017-033 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-033 (200 MW/Wind), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | 1373275 | 100% | 1373275
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 133025 | ERIS | Oklaunion 345 kV Substation GEN-2017-065 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-065 (200.3 MW/Solar), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | 3877147.5 | 100% | 3877147.5
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico | 133024 | ERIS | Oklaunion 345 kV Substation GEN-2017-065 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-065 (200.3 MW/Solar), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | 1373275 | 100% | 1373275
GEN-2017-066 | 14 - South Central Oklahoma | 133027 | ERIS | Oney 138 kV Substation GEN-2017-066 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-066 (150.8 MW/Solar), into the Point of Interconnection (POI) at Oney 138 kV Substation. | 4750000 | 100% | 4750000
GEN-2017-066 | 14 - South Central Oklahoma | 133026 | ERIS | Oney 138 kV Substation GEN-2017-066 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-066 (150.8 MW/Solar), into the Point of Interconnection (POI) at Oney 138 kV Substation. | 400000 | 100% | 400000
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Oronogo Jct. to Joplin Fir Road 161kV Rebuild | Current Study | Rebuild the existing Oronogo Jct. to Fir Road 161kV 2.86 mile line to achieve a minimum winter/emergency rating of 312 MVA | 1830800 | 39.8% | 4600000
GEN-2017-082 | 12 - Northwest Arkansas |  | ERIS | Oronogo Jct. to Joplin Fir Road 161kV Rebuild | Current Study | Rebuild the existing Oronogo Jct. to Fir Road 161kV 2.86 mile line to achieve a minimum winter/emergency rating of 312 MVA | 2769200 | 60.2% | 4600000
GEN-2017-049 | 03 - Spearville | 133001 | ERIS | Pawnee Valley - Hanston 69 kV GEN-2017-049 Interconnection (Non-Shared NU) (MIDW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-049 (50 MW/Solar), into the Point of Interconnection (POI) at Pawnee Valley - Hanston 69 kV. | 3967218 | 100% | 3967218
GEN-2017-049 | 03 - Spearville | 133000 | ERIS | Pawnee Valley - Hanston 69 kV GEN-2017-049 Interconnection (TOIF) (MIDW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-049 (50 MW/Solar), into the Point of Interconnection (POI) at Pawnee Valley - Hanston 69 kV. | 908569 | 100% | 908569
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Phillip to Wall 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wall 115kV 26.95 mile line to achieve a minimum summer/emergency rating of 137 MVA | 2209200 | 18.41% | 12000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Phillip to Wall 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wall 115kV 26.95 mile line to achieve a minimum summer/emergency rating of 137 MVA | 3033600 | 25.28% | 12000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Phillip to Wall 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wall 115kV 26.95 mile line to achieve a minimum summer/emergency rating of 137 MVA | 6757200 | 56.31% | 12000000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 270425.9148 | 1.47% | 18400000
GEN-2016-107 | 01 - Woodward |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 115896.8206 | 0.6299% | 18400000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 139812.0376 | 0.7598% | 18400000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 196840.6319 | 1.07% | 18400000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 13296860.6279 | 72.27% | 18400000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 42311.5377 | 0.23% | 18400000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 25754.849 | 0.14% | 18400000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 134293.1414 | 0.7299% | 18400000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 86462.7075 | 0.4699% | 18400000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 49670.066 | 0.2699% | 18400000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 134293.1414 | 0.7299% | 18400000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 126934.6131 | 0.6899% | 18400000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 101179.764 | 0.5499% | 18400000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 38632.2735 | 0.21% | 18400000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 38632.2735 | 0.21% | 18400000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 117736.4527 | 0.6399% | 18400000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 31273.7453 | 0.17% | 18400000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 68066.3867 | 0.3699% | 18400000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Phillip to Wanblee 115kV Rebuild | Current Study | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | 3384923.0154 | 18.4% | 18400000
GEN-2016-005 | 03 - Spearville |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 1324831.7103 | 2.14% | 61900000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 4741409.7607 | 7.66% | 61900000
GEN-2016-107 | 01 - Woodward |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 3138283.6837 | 5.07% | 61900000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 2408807.959 | 3.891% | 61900000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 307077.5757 | 0.4961% | 61900000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 3349273.7535 | 5.411% | 61900000
GEN-2017-018 | 03 - Spearville |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 2046050.266 | 3.305% | 61900000
GEN-2017-028 | 01 - Woodward |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 1542389.8552 | 2.492% | 61900000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 3430156.9894 | 5.541% | 61900000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 798795.5943 | 1.29% | 61900000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 2786020.1364 | 4.501% | 61900000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 957905.2754 | 1.548% | 61900000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 3435302.2183 | 5.55% | 61900000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 2273841.0243 | 3.673% | 61900000
GEN-2017-067 | 01 - Woodward |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 3433262.429 | 5.546% | 61900000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 1311317.7178 | 2.118% | 61900000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 423751.314 | 0.6846% | 61900000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 351413.965 | 0.5677% | 61900000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 18914865.6357 | 30.56% | 61900000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 497406.9973 | 0.8036% | 61900000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 520503.5949 | 0.8409% | 61900000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 2578816.8136 | 4.166% | 61900000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Pittsburg to Seminole 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | 1328515.7305 | 2.146% | 61900000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Pittsburg to Valiant 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Valiant 345kV 70.2 mile line to achieve a minimum winter/emergency rating of 1147 MVA | 30321500 | 16.39% | 185000000
GEN-2016-107 | 01 - Woodward |  | NRIS | Pittsburg to Valiant 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Valiant 345kV 70.2 mile line to achieve a minimum winter/emergency rating of 1147 MVA | 11266500 | 6.09% | 185000000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Pittsburg to Valiant 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Valiant 345kV 70.2 mile line to achieve a minimum winter/emergency rating of 1147 MVA | 34595000 | 18.7% | 185000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Pittsburg to Valiant 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Valiant 345kV 70.2 mile line to achieve a minimum winter/emergency rating of 1147 MVA | 26936000 | 14.56% | 185000000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Pittsburg to Valiant 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Valiant 345kV 70.2 mile line to achieve a minimum winter/emergency rating of 1147 MVA | 8510000 | 4.6% | 185000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Pittsburg to Valiant 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Valiant 345kV 70.2 mile line to achieve a minimum winter/emergency rating of 1147 MVA | 26973000 | 14.58% | 185000000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Pittsburg to Valiant 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Valiant 345kV 70.2 mile line to achieve a minimum winter/emergency rating of 1147 MVA | 13542000 | 7.32% | 185000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Pittsburg to Valiant 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Valiant 345kV 70.2 mile line to achieve a minimum winter/emergency rating of 1147 MVA | 10508000 | 5.68% | 185000000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Pittsburg to Valiant 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Valiant 345kV 70.2 mile line to achieve a minimum winter/emergency rating of 1147 MVA | 3626000 | 1.96% | 185000000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Pittsburg to Valiant 345kV Rebuild | Current Study | Rebuild the existing Pittsburg to Valiant 345kV 70.2 mile line to achieve a minimum winter/emergency rating of 1147 MVA | 18722000 | 10.12% | 185000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 132943 | ERIS | Pleasant Hill 230 kV Substation GEN-2017-007 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-007 (297.5 MW/Wind), into the Point of Interconnection (POI) at Pleasant Hill 230 kV Substation. | 1865013 | 100% | 1865013
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 132942 | ERIS | Pleasant Hill 230 kV Substation GEN-2017-007 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-007 (297.5 MW/Wind), into the Point of Interconnection (POI) at Pleasant Hill 230 kV Substation. | 1074589 | 100% | 1074589
GEN-2017-027 | 14 - South Central Oklahoma | 132973 | ERIS | Pooleville - Ratliff 138 kV GEN-2017-027 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-027 (140 MW/Wind), into the Point of Interconnection (POI) at Pooleville - Ratliff 138 kV. | 1396000 | 100% | 1396000
GEN-2017-027 | 14 - South Central Oklahoma | 132972 | ERIS | Pooleville - Ratliff 138 kV GEN-2017-027 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-027 (140 MW/Wind), into the Point of Interconnection (POI) at Pooleville - Ratliff 138 kV. | 515000 | 100% | 515000
GEN-2016-049 | 03 - Spearville | 132907 | ERIS | Post Rock - Spearville 345 kV GEN-2016-049 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-049 (310.2 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | 15081109 | 100% | 15081109
GEN-2016-049 | 03 - Spearville | 132906 | ERIS | Post Rock - Spearville 345 kV GEN-2016-049 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-049 (310.2 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | 1054767 | 100% | 1054767
GEN-2017-021 | 03 - Spearville | 132963 | ERIS | Post Rock - Spearville 345 kV GEN-2017-021 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-021 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | 15081109 | 100% | 15081109
GEN-2017-021 | 03 - Spearville | 132962 | ERIS | Post Rock - Spearville 345 kV GEN-2017-021 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-021 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | 1054767 | 100% | 1054767
GEN-2017-099 | 03 - Spearville | 133079 | ERIS | Post Rock - Spearville 345 kV GEN-2017-099 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-099 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | 15081109 | 100% | 15081109
GEN-2017-099 | 03 - Spearville | 133078 | ERIS | Post Rock - Spearville 345 kV GEN-2017-099 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-099 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | 1054767 | 100% | 1054767
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County 345/230kV New Transformer CKT 2 | Current Study | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | 518445.6384 | 4.12% | 12583632
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County 345/230kV New Transformer CKT 2 | Current Study | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | 256706.0928 | 2.04% | 12583632
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County 345/230kV New Transformer CKT 2 | Current Study | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | 1555336.9152 | 12.36% | 12583632
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County 345/230kV New Transformer CKT 2 | Current Study | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | 2059940.5584 | 16.37% | 12583632
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County 345/230kV New Transformer CKT 2 | Current Study | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | 737400.8352 | 5.86% | 12583632
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County 345/230kV New Transformer CKT 2 | Current Study | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | 168620.6688 | 1.34% | 12583632
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County 345/230kV New Transformer CKT 2 | Current Study | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | 13841.9952 | 0.11% | 12583632
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County 345/230kV New Transformer CKT 2 | Current Study | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | 483211.4688 | 3.84% | 12583632
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County 345/230kV New Transformer CKT 2 | Current Study | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | 313332.4368 | 2.49% | 12583632
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County 345/230kV New Transformer CKT 2 | Current Study | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | 2048615.2896 | 16.28% | 12583632
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County 345/230kV New Transformer CKT 2 | Current Study | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | 2567060.928 | 20.4% | 12583632
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County 345/230kV New Transformer CKT 2 | Current Study | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | 611564.5152 | 4.86% | 12583632
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County 345/230kV New Transformer CKT 2 | Current Study | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | 548646.3552 | 4.36% | 12583632
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County 345/230kV New Transformer CKT 2 | Current Study | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | 142195.0416 | 1.13% | 12583632
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County 345/230kV New Transformer CKT 2 | Current Study | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | 558713.2608 | 4.44% | 12583632
GEN-2016-005 | 03 - Spearville |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 1168400 | 1.27% | 92000000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 1895200 | 2.06% | 92000000
GEN-2016-049 | 03 - Spearville |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 2162000 | 2.35% | 92000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 892400 | 0.97% | 92000000
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 1794000 | 1.95% | 92000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 1637600 | 1.78% | 92000000
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 1039600 | 1.13% | 92000000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 3946800 | 4.29% | 92000000
GEN-2017-004 | 04 - Northwest Kansas |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 1462800 | 1.59% | 92000000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 4894400 | 5.32% | 92000000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 3606400 | 3.92% | 92000000
GEN-2017-013 | 04 - Northwest Kansas |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 2769200 | 3.01% | 92000000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 542800 | 0.59% | 92000000
GEN-2017-018 | 03 - Spearville |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 2171200 | 2.36% | 92000000
GEN-2017-021 | 03 - Spearville |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 892400 | 0.97% | 92000000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 3827200 | 4.16% | 92000000
GEN-2017-032 | 03 - Spearville |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 3266000 | 3.55% | 92000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 2594400 | 2.82% | 92000000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 3275200 | 3.56% | 92000000
GEN-2017-047 | 02 - Hitchland |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 1067200 | 1.16% | 92000000
GEN-2017-049 | 03 - Spearville |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 414000 | 0.45% | 92000000
GEN-2017-052 | 03 - Spearville |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 423200 | 0.46% | 92000000
GEN-2017-058 | 02 - Hitchland |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 3615600 | 3.93% | 92000000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 1518000 | 1.65% | 92000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 2603600 | 2.83% | 92000000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 55200 | 0.06% | 92000000
GEN-2017-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 4627600 | 5.03% | 92000000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 846400 | 0.92% | 92000000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 8611200 | 9.36% | 92000000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 5142800 | 5.59% | 92000000
GEN-2017-083 | 04 - Northwest Kansas |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 1380000 | 1.5% | 92000000
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 1527200 | 1.66% | 92000000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 2106800 | 2.29% | 92000000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 441600 | 0.48% | 92000000
GEN-2017-099 | 03 - Spearville |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 892400 | 0.97% | 92000000
GEN-2017-100 | 02 - Hitchland |  | ERIS | Potter County to Grapevine 345kV New Build | Current Study | Build a new 65 mile 345kV line from Potter County to Grapevine | 12889200 | 14.01% | 92000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 133041 | ERIS | Pryor Junction 138 kV Substation GEN-2017-074 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-074 (72.5 MW/Solar), into the Point of Interconnection (POI) at Pryor Junction 138 kV Substation. | 1365027 | 100% | 1365027
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas | 133040 | ERIS | Pryor Junction 138 kV Substation GEN-2017-074 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-074 (72.5 MW/Solar), into the Point of Interconnection (POI) at Pryor Junction 138 kV Substation. | 1146800 | 100% | 1146800
GEN-2016-005 | 03 - Spearville |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 1163850.3935 | 1.51% | 77076185
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 1734214.1625 | 2.25% | 77076185
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 393088.5435 | 0.51% | 77076185
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 724516.139 | 0.94% | 77076185
GEN-2016-107 | 01 - Woodward |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 1156142.775 | 1.5% | 77076185
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 1703383.6885 | 2.21% | 77076185
GEN-2016-159 | 09 - Nebraska |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 23215346.922 | 30.12% | 77076185
GEN-2017-011 | 01 - Woodward |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 1264049.434 | 1.64% | 77076185
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 13912251.3925 | 18.05% | 77076185
GEN-2017-018 | 03 - Spearville |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 1603184.648 | 2.08% | 77076185
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 300597.1215 | 0.39% | 77076185
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 177275.2255 | 0.23% | 77076185
GEN-2017-028 | 01 - Woodward |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 385380.925 | 0.5% | 77076185
GEN-2017-032 | 03 - Spearville |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 1248634.197 | 1.62% | 77076185
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 1433617.041 | 1.86% | 77076185
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 562656.1505 | 0.73% | 77076185
GEN-2017-047 | 02 - Hitchland |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 616609.48 | 0.8% | 77076185
GEN-2017-055 | 09 - Nebraska |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 7576588.9855 | 9.83% | 77076185
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 3699656.88 | 4.8% | 77076185
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 1433617.041 | 1.86% | 77076185
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 917206.6015 | 1.19% | 77076185
GEN-2017-067 | 01 - Woodward |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 1479862.752 | 1.92% | 77076185
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 1171558.012 | 1.52% | 77076185
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 562656.1505 | 0.73% | 77076185
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 562656.1505 | 0.73% | 77076185
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 855545.6535 | 1.11% | 77076185
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 292889.503 | 0.38% | 77076185
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 971159.931 | 1.26% | 77076185
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 5341379.6205 | 6.93% | 77076185
GEN-2017-100 | 02 - Hitchland |  | NRIS | Raun to S3451 345kV Rebuild | Current Study | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | 616609.48 | 0.8% | 77076185
GEN-2016-005 | 03 - Spearville |  | NRIS | Raun to Tekamah 161kV Rebuild | Current Study | Rebuild the existing Raun to Tekamah 37.07 mile line to achieve a minimum winter/emergency rating of 382 MVA | 1214954.208 | 3.45% | 35216064
GEN-2016-159 | 09 - Nebraska |  | NRIS | Raun to Tekamah 161kV Rebuild | Current Study | Rebuild the existing Raun to Tekamah 37.07 mile line to achieve a minimum winter/emergency rating of 382 MVA | 10033056.6336 | 28.49% | 35216064
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Raun to Tekamah 161kV Rebuild | Current Study | Rebuild the existing Raun to Tekamah 37.07 mile line to achieve a minimum winter/emergency rating of 382 MVA | 11681168.4288 | 33.17% | 35216064
GEN-2017-018 | 03 - Spearville |  | NRIS | Raun to Tekamah 161kV Rebuild | Current Study | Rebuild the existing Raun to Tekamah 37.07 mile line to achieve a minimum winter/emergency rating of 382 MVA | 1507247.5392 | 4.28% | 35216064
GEN-2017-032 | 03 - Spearville |  | NRIS | Raun to Tekamah 161kV Rebuild | Current Study | Rebuild the existing Raun to Tekamah 37.07 mile line to achieve a minimum winter/emergency rating of 382 MVA | 1574158.0608 | 4.47% | 35216064
GEN-2017-047 | 02 - Hitchland |  | NRIS | Raun to Tekamah 161kV Rebuild | Current Study | Rebuild the existing Raun to Tekamah 37.07 mile line to achieve a minimum winter/emergency rating of 382 MVA | 647975.5776 | 1.84% | 35216064
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Raun to Tekamah 161kV Rebuild | Current Study | Rebuild the existing Raun to Tekamah 37.07 mile line to achieve a minimum winter/emergency rating of 382 MVA | 2912368.4928 | 8.27% | 35216064
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Raun to Tekamah 161kV Rebuild | Current Study | Rebuild the existing Raun to Tekamah 37.07 mile line to achieve a minimum winter/emergency rating of 382 MVA | 566978.6304 | 1.61% | 35216064
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Raun to Tekamah 161kV Rebuild | Current Study | Rebuild the existing Raun to Tekamah 37.07 mile line to achieve a minimum winter/emergency rating of 382 MVA | 4426659.2448 | 12.57% | 35216064
GEN-2017-100 | 02 - Hitchland |  | NRIS | Raun to Tekamah 161kV Rebuild | Current Study | Rebuild the existing Raun to Tekamah 37.07 mile line to achieve a minimum winter/emergency rating of 382 MVA | 651497.184 | 1.85% | 35216064
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas | 132909 | ERIS | Renfrow 345 kV Substation GEN-2016-072 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-072 (300 MW/Wind), into the Point of Interconnection (POI) at Renfrow 345 kV Substation. | 1430000 | 100% | 1430000
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas | 143114 | ERIS | Renfrow 345 kV Substation GEN-2016-072 Interconnection (Non-Shared NU) (WERE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2016-072 (300 MW/Wind), into the Point of Interconnection (POI) at Renfrow 345 kV Substation. | 8866 | 100% | 8866
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas | 132908 | ERIS | Renfrow 345 kV Substation GEN-2016-072 Interconnection (TOIF) (OKGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-072 (300 MW/Wind), into the Point of Interconnection (POI) at Renfrow 345 kV Substation. | 915000 | 100% | 915000
GEN-2017-010 | 16 - Western North Dakota | 132949 | ERIS | Rhame 230 kV Substation GEN-2017-010 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-010 (200.1 MW/Wind), into the Point of Interconnection (POI) at Rhame 230 kV Substation. | 1189064 | 100% | 1189064
GEN-2017-010 | 16 - Western North Dakota | 132948 | ERIS | Rhame 230 kV Substation GEN-2017-010 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-010 (200.1 MW/Wind), into the Point of Interconnection (POI) at Rhame 230 kV Substation. | 1608232 | 100% | 1608232
GEN-2016-005 | 03 - Spearville |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 18853.94 | 0.3475% | 5425000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 200805.8504 | 3.701% | 5425000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 24042.18 | 0.4432% | 5425000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 44522.5601 | 0.8207% | 5425000
GEN-2016-107 | 01 - Woodward |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 27906.1101 | 0.5144% | 5425000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 1818.16 | 0.03351% | 5425000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 30893.2101 | 0.5695% | 5425000
GEN-2017-018 | 03 - Spearville |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 22730.74 | 0.419% | 5425000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 188577.2903 | 3.476% | 5425000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 215949.5804 | 3.981% | 5425000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 3576009.9966 | 65.92% | 5425000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 219584.0804 | 4.048% | 5425000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 48308.5001 | 0.8905% | 5425000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 8495.63 | 0.1566% | 5425000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 219913.4504 | 4.054% | 5425000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 31514.7101 | 0.5809% | 5425000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 7993.62 | 0.1473% | 5425000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 9661.7 | 0.1781% | 5425000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 488536.7109 | 9.005% | 5425000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 10434.64 | 0.1923% | 5425000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 16429.28 | 0.3028% | 5425000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Russett to Stirling 138kV Rebuild | Current Study | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | 12018.06 | 0.2215% | 5425000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 1284585.143 | 2.15% | 59754121
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 12033276.6417 | 20.14% | 59754121
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 31517147.1128 | 52.74% | 59754121
GEN-2016-107 | 01 - Woodward |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 573582.2034 | 0.9599% | 59754121
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 3489291.7372 | 5.839% | 59754121
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 1284585.143 | 2.15% | 59754121
GEN-2017-018 | 03 - Spearville |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 824524.4174 | 1.38% | 59754121
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 394337.7648 | 0.6599% | 59754121
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 233017.7701 | 0.39% | 59754121
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 346539.2479 | 0.5799% | 59754121
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 460060.7256 | 0.7699% | 59754121
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 466035.5402 | 0.7799% | 59754121
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 346539.2479 | 0.5799% | 59754121
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 705028.125 | 1.18% | 59754121
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 1416031.0646 | 2.37% | 59754121
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 1326408.8453 | 2.22% | 59754121
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 221068.1409 | 0.37% | 59754121
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 2288353.9989 | 3.83% | 59754121
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Seminole to Cunningham 230kV New Build | Current Study | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | 543708.1303 | 0.9099% | 59754121
GEN-2016-109 | 09 - Nebraska |  |  | Seneca to Bailyville to Smittyville to Marshall County 115kV CKT 1 Rebuild | Contingent | NTC 210542 | 0 | 0 | 14861868.53
GEN-2017-049 | 03 - Spearville |  | ERIS | Seward to Zook 69kV Rebuild | Current Study | Rebuild the existing Seward to Zook 69kV 16.89 mile line to achieve a minimum winter/emergency rating of 51 MVA | 15352148.61 | 100% | 15352148.61
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 52715.8147 | 0.3101% | 17000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 3401.0203 | 0.02001% | 17000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 6802.0406 | 0.04001% | 17000000
GEN-2016-107 | 01 - Woodward |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 3401.0203 | 0.02001% | 17000000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 197259.1778 | 1.16% | 17000000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 1700.5102 | 0.01% | 17000000
GEN-2017-011 | 01 - Woodward |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 64619.3858 | 0.3801% | 17000000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 618985.6957 | 3.641% | 17000000
GEN-2017-018 | 03 - Spearville |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 81624.4873 | 0.4801% | 17000000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 25507.6523 | 0.15% | 17000000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 15304.5914 | 0.09003% | 17000000
GEN-2017-028 | 01 - Woodward |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 8502.5508 | 0.05002% | 17000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 5101.5305 | 0.03001% | 17000000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 11903.5711 | 0.07002% | 17000000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 435330.5992 | 2.561% | 17000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 10555066.52 | 62.09% | 17000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 5101.5305 | 0.03001% | 17000000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 17005.1015 | 0.1% | 17000000
GEN-2017-067 | 01 - Woodward |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 39111.7335 | 0.2301% | 17000000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 71421.4264 | 0.4201% | 17000000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 88426.528 | 0.5202% | 17000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 86726.0178 | 0.5102% | 17000000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 39111.7335 | 0.2301% | 17000000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 17005.1015 | 0.1% | 17000000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 147944.3833 | 0.8703% | 17000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Shannon 230/115kV New Transformer | Current Study | Build a new 230/115kV transformer at Shannon | 4400920.2761 | 25.89% | 17000000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Shell Creek to Grand Island 345kV New Build | Current Study | Build a new 72 mile 345kV line from Shell Creek to Grand Island | 3967003.2997 | 2.39% | 166000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Shell Creek to Grand Island 345kV New Build | Current Study | Build a new 72 mile 345kV line from Shell Creek to Grand Island | 713728.6271 | 0.43% | 166000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Shell Creek to Grand Island 345kV New Build | Current Study | Build a new 72 mile 345kV line from Shell Creek to Grand Island | 1311268.8731 | 0.7899% | 166000000
GEN-2016-159 | 09 - Nebraska |  | NRIS | Shell Creek to Grand Island 345kV New Build | Current Study | Build a new 72 mile 345kV line from Shell Creek to Grand Island | 97316068.3932 | 58.62% | 166000000
GEN-2017-001 | 09 - Nebraska |  | NRIS | Shell Creek to Grand Island 345kV New Build | Current Study | Build a new 72 mile 345kV line from Shell Creek to Grand Island | 43886011.3989 | 26.44% | 166000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Shell Creek to Grand Island 345kV New Build | Current Study | Build a new 72 mile 345kV line from Shell Creek to Grand Island | 2207579.2421 | 1.33% | 166000000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Shell Creek to Grand Island 345kV New Build | Current Study | Build a new 72 mile 345kV line from Shell Creek to Grand Island | 1228277.1723 | 0.7399% | 166000000
GEN-2017-047 | 02 - Hitchland |  | NRIS | Shell Creek to Grand Island 345kV New Build | Current Study | Build a new 72 mile 345kV line from Shell Creek to Grand Island | 3020897.9102 | 1.82% | 166000000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Shell Creek to Grand Island 345kV New Build | Current Study | Build a new 72 mile 345kV line from Shell Creek to Grand Island | 7037696.2304 | 4.24% | 166000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Shell Creek to Grand Island 345kV New Build | Current Study | Build a new 72 mile 345kV line from Shell Creek to Grand Island | 2207579.2421 | 1.33% | 166000000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Shell Creek to Grand Island 345kV New Build | Current Study | Build a new 72 mile 345kV line from Shell Creek to Grand Island | 49795.0205 | 0.03% | 166000000
GEN-2017-100 | 02 - Hitchland |  | NRIS | Shell Creek to Grand Island 345kV New Build | Current Study | Build a new 72 mile 345kV line from Shell Creek to Grand Island | 3054094.5905 | 1.84% | 166000000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas | 132925 | ERIS | Shidler 138 kV Substation GEN-2016-127 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-127 (200.1 MW/Wind), into the Point of Interconnection (POI) at Shidler 138 kV Substation. | 1300000 | 100% | 1300000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas | 132924 | ERIS | Shidler 138 kV Substation GEN-2016-127 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-127 (200.1 MW/Wind), into the Point of Interconnection (POI) at Shidler 138 kV Substation. | 1146800 | 100% | 1146800
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Shilder to Remington 138kV Rebuild | Current Study | Rebuild the existing Shidler to Remington 138kV 5.0 mile line to achieve a minimum summer/emergency rating of 178 MVA | 4975698 | 98.14% | 5070000
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Shilder to Remington 138kV Rebuild | Current Study | Rebuild the existing Shidler to Remington 138kV 5.0 mile line to achieve a minimum summer/emergency rating of 178 MVA | 94302 | 1.86% | 5070000
GEN-2016-005 | 03 - Spearville |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 163216.3216 | 0.32% | 51000000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 2325832.5833 | 4.56% | 51000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 265226.5227 | 0.5201% | 51000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 489648.9649 | 0.9601% | 51000000
GEN-2016-093 | 09 - Nebraska |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 515151.5152 | 1.01% | 51000000
GEN-2016-107 | 01 - Woodward |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 841584.1584 | 1.65% | 51000000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 2004500.45 | 3.93% | 51000000
GEN-2016-159 | 09 - Nebraska |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 4881188.1188 | 9.571% | 51000000
GEN-2017-001 | 09 - Nebraska |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 2341134.1134 | 4.59% | 51000000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 209120.9121 | 0.41% | 51000000
GEN-2017-011 | 01 - Woodward |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 591659.1659 | 1.16% | 51000000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 4014101.4101 | 7.871% | 51000000
GEN-2017-018 | 03 - Spearville |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 586558.6559 | 1.15% | 51000000
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 800780.078 | 1.57% | 51000000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 668166.8167 | 1.31% | 51000000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 392739.2739 | 0.7701% | 51000000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 1076207.6208 | 2.11% | 51000000
GEN-2017-028 | 01 - Woodward |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 341734.1734 | 0.6701% | 51000000
GEN-2017-031 | 09 - Nebraska |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 739573.9574 | 1.45% | 51000000
GEN-2017-032 | 03 - Spearville |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 311131.1131 | 0.6101% | 51000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 1050705.0705 | 2.06% | 51000000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 785478.5479 | 1.54% | 51000000
GEN-2017-037 | 09 - Nebraska |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 147914.7915 | 0.29% | 51000000
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 2055505.5506 | 4.03% | 51000000
GEN-2017-047 | 02 - Hitchland |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 438643.8644 | 0.8601% | 51000000
GEN-2017-048 | 16 - Western North Dakota |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 3483648.3648 | 6.831% | 51000000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 3498949.895 | 6.861% | 51000000
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 555955.5956 | 1.09% | 51000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 1402640.264 | 2.75% | 51000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 1050705.0705 | 2.06% | 51000000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 1035403.5404 | 2.03% | 51000000
GEN-2017-067 | 01 - Woodward |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 1366936.6937 | 2.68% | 51000000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 510051.0051 | 1% | 51000000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 994599.4599 | 1.95% | 51000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 989498.9499 | 1.94% | 51000000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 1535253.5254 | 3.01% | 51000000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 719171.9172 | 1.41% | 51000000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 1657665.7666 | 3.25% | 51000000
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 2055505.5506 | 4.03% | 51000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 1667866.7867 | 3.27% | 51000000
GEN-2017-100 | 02 - Hitchland |  | NRIS | Sibley 161kV Reactive Support | Current Study | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | 438643.8644 | 0.8601% | 51000000
GEN-2017-031 | 09 - Nebraska |  | NRIS | Sidney to G16-034 Tap 345kV New Build CKT 2 | Current Study | Build a new 345kV line from Sidney to G16-034 Tap as a second circuit | 18837000 | 21% | 89700000
GEN-2016-093 | 09 - Nebraska |  | NRIS | Sidney to G16-034 Tap 345kV New Build CKT 2 | Current Study | Build a new 345kV line from Sidney to G16-034 Tap as a second circuit | 26084760 | 29.08% | 89700000
GEN-2016-034 | 09 - Nebraska |  | NRIS | Sidney to G16-034 Tap 345kV New Build CKT 2 | Current Study | Build a new 345kV line from Sidney to G16-034 Tap as a second circuit | 37333140 | 41.62% | 89700000
GEN-2017-037 | 09 - Nebraska |  | NRIS | Sidney to G16-034 Tap 345kV New Build CKT 2 | Current Study | Build a new 345kV line from Sidney to G16-034 Tap as a second circuit | 3722550 | 4.15% | 89700000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Sidney to G16-034 Tap 345kV New Build CKT 2 | Current Study | Build a new 345kV line from Sidney to G16-034 Tap as a second circuit | 3722550 | 4.15% | 89700000
GEN-2016-107 | 01 - Woodward |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 1203.6108 | 0.02006% | 6000000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 71013.0391 | 1.184% | 6000000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 601.8054 | 0.01003% | 6000000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 222066.1986 | 3.701% | 6000000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 9628.8867 | 0.1605% | 6000000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 5416.2487 | 0.09027% | 6000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 1805.4162 | 0.03009% | 6000000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 4212.6379 | 0.07021% | 6000000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 155867.6028 | 2.598% | 6000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 3781745.2357 | 63.03% | 6000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 1805.4162 | 0.03009% | 6000000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 6018.0542 | 0.1003% | 6000000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 25877.6329 | 0.4313% | 6000000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 31293.8816 | 0.5216% | 6000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 31293.8816 | 0.5216% | 6000000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 14443.33 | 0.2407% | 6000000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 6018.0542 | 0.1003% | 6000000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 52958.8766 | 0.8826% | 6000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Sioux City 230kV Substation Upgrade | Current Study | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | 1576730.1906 | 26.28% | 6000000
GEN-2016-034 | 09 - Nebraska |  | ERIS | Smoky Hill to Summit 230kV Rebuild | Current Study | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA | 2154435.6114 | 4.748% | 45375000
GEN-2016-049 | 03 - Spearville |  | ERIS | Smoky Hill to Summit 230kV Rebuild | Current Study | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA | 12905678.39 | 28.44% | 45375000
GEN-2016-093 | 09 - Nebraska |  | ERIS | Smoky Hill to Summit 230kV Rebuild | Current Study | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA | 1575672.9057 | 3.473% | 45375000
GEN-2017-001 | 09 - Nebraska |  | ERIS | Smoky Hill to Summit 230kV Rebuild | Current Study | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA | 5083131.4443 | 11.2% | 45375000
GEN-2017-008 | 09 - Nebraska |  | ERIS | Smoky Hill to Summit 230kV Rebuild | Current Study | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA | 4161636.5214 | 9.172% | 45375000
GEN-2017-021 | 03 - Spearville |  | ERIS | Smoky Hill to Summit 230kV Rebuild | Current Study | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA | 5592912.3014 | 12.33% | 45375000
GEN-2017-031 | 09 - Nebraska |  | ERIS | Smoky Hill to Summit 230kV Rebuild | Current Study | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA | 2289121.4657 | 5.045% | 45375000
GEN-2017-032 | 03 - Spearville |  | ERIS | Smoky Hill to Summit 230kV Rebuild | Current Study | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA | 4082160.6257 | 8.996% | 45375000
GEN-2017-037 | 09 - Nebraska |  | ERIS | Smoky Hill to Summit 230kV Rebuild | Current Study | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA | 450192.2543 | 0.9922% | 45375000
GEN-2017-049 | 03 - Spearville |  | ERIS | Smoky Hill to Summit 230kV Rebuild | Current Study | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA | 991920.0186 | 2.186% | 45375000
GEN-2017-052 | 03 - Spearville |  | ERIS | Smoky Hill to Summit 230kV Rebuild | Current Study | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA | 495226.16 | 1.091% | 45375000
GEN-2017-099 | 03 - Spearville |  | ERIS | Smoky Hill to Summit 230kV Rebuild | Current Study | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA | 5592912.3014 | 12.33% | 45375000
GEN-2017-036 | 07 - Southwestern Oklahoma | 132985 | ERIS | Snyder - Cache 138 kV GEN-2017-036 Interconnection (Non-Shared NU) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-036 (100 MW/Solar), into the Point of Interconnection (POI) at Snyder 138 kV Substation. | 8198087 | 100% | 8198087
GEN-2017-036 | 07 - Southwestern Oklahoma | 132984 | ERIS | Snyder - Cahce 138 kV GEN-2017-036 Interconnection (TOIF) (AEPW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-036 (100 MW/Solar), into the Point of Interconnection (POI) at Snyder 138 kV Substation. | 1337068 | 100% | 1337068
GEN-2016-034 | 09 - Nebraska |  | ERIS | South Hays to Great Bend 230kV Rebuild | Current Study | Rebuild the existing South Hays to Great Bend 230kV 39.2 mile line to achieve a minimum spring/normal rating of 336 MVA | 4345802.4901 | 12.48% | 34834000
GEN-2016-093 | 09 - Nebraska |  | ERIS | South Hays to Great Bend 230kV Rebuild | Current Study | Rebuild the existing South Hays to Great Bend 230kV 39.2 mile line to achieve a minimum spring/normal rating of 336 MVA | 3217308.4551 | 9.236% | 34834000
GEN-2017-001 | 09 - Nebraska |  | ERIS | South Hays to Great Bend 230kV Rebuild | Current Study | Rebuild the existing South Hays to Great Bend 230kV 39.2 mile line to achieve a minimum spring/normal rating of 336 MVA | 11168683.1148 | 32.06% | 34834000
GEN-2017-008 | 09 - Nebraska |  | ERIS | South Hays to Great Bend 230kV Rebuild | Current Study | Rebuild the existing South Hays to Great Bend 230kV 39.2 mile line to achieve a minimum spring/normal rating of 336 MVA | 10521147.9837 | 30.2% | 34834000
GEN-2017-031 | 09 - Nebraska |  | ERIS | South Hays to Great Bend 230kV Rebuild | Current Study | Rebuild the existing South Hays to Great Bend 230kV 39.2 mile line to achieve a minimum spring/normal rating of 336 MVA | 4661826.9686 | 13.38% | 34834000
GEN-2017-037 | 09 - Nebraska |  | ERIS | South Hays to Great Bend 230kV Rebuild | Current Study | Rebuild the existing South Hays to Great Bend 230kV 39.2 mile line to achieve a minimum spring/normal rating of 336 MVA | 919230.9877 | 2.639% | 34834000
GEN-2016-005 | 03 - Spearville |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 96240.376 | 0.7699% | 12500000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 1141135.8864 | 9.129% | 12500000
GEN-2016-107 | 01 - Woodward |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 401209.879 | 3.21% | 12500000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 13748.6251 | 0.11% | 12500000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 1216128.3872 | 9.729% | 12500000
GEN-2017-018 | 03 - Spearville |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 166233.3767 | 1.33% | 12500000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 1064893.5106 | 8.519% | 12500000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 608689.1311 | 4.87% | 12500000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 429957.0043 | 3.44% | 12500000
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 286221.3779 | 2.29% | 12500000
GEN-2017-057 | 10 - Southeast Oklahoma/Northeast Texas |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 2169783.0217 | 17.36% | 12500000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 392460.7539 | 3.14% | 12500000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 608689.1311 | 4.87% | 12500000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 654934.5065 | 5.239% | 12500000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 89991.0009 | 0.7199% | 12500000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 2208529.1471 | 17.67% | 12500000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 29997.0003 | 0.24% | 12500000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 136236.3764 | 1.09% | 12500000
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 286221.3779 | 2.29% | 12500000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Southwest Shreveport 345kV Reactive Support | Current Study | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | 498700.13 | 3.99% | 12500000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 843165.6131 | 1.96% | 43010050
GEN-2016-107 | 01 - Woodward |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 266715.6531 | 0.6201% | 43010050
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 2150932.6865 | 5.001% | 43010050
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 877580.5361 | 2.04% | 43010050
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 8169242.3435 | 18.99% | 43010050
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 731317.1134 | 1.7% | 43010050
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 400073.4797 | 0.9302% | 43010050
GEN-2017-032 | 03 - Spearville |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 1045353.2857 | 2.43% | 43010050
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 378564.1528 | 0.8802% | 43010050
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 232300.7301 | 0.5401% | 43010050
GEN-2017-055 | 09 - Nebraska |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 5609632.4465 | 13.04% | 43010050
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 2649949.0698 | 6.161% | 43010050
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 378564.1528 | 0.8802% | 43010050
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 374262.2875 | 0.8702% | 43010050
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 3226399.0298 | 7.502% | 43010050
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 4297563.5077 | 9.992% | 43010050
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 998032.7666 | 2.32% | 43010050
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 757128.3057 | 1.76% | 43010050
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 6259214.1178 | 14.55% | 43010050
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | Current Study | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | 3364058.7217 | 7.822% | 43010050
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 490310.9689 | 5.329% | 9200000
GEN-2016-103 | 15 - Eastern South Dakota |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 236416.3584 | 2.57% | 9200000
GEN-2016-107 | 01 - Woodward |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 197780.222 | 2.15% | 9200000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 356924.3076 | 3.88% | 9200000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 938306.1694 | 10.2% | 9200000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 137986.2014 | 1.5% | 9200000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 80951.9048 | 0.8799% | 9200000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 250214.9785 | 2.72% | 9200000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 164663.5336 | 1.79% | 9200000
GEN-2017-048 | 16 - Western North Dakota |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 3810258.9741 | 41.42% | 9200000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 493990.6009 | 5.369% | 9200000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 251134.8865 | 2.73% | 9200000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 239176.0824 | 2.6% | 9200000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 130626.9373 | 1.42% | 9200000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 103029.697 | 1.12% | 9200000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 225377.4623 | 2.45% | 9200000
GEN-2017-094 | 15 - Eastern South Dakota |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 421317.8682 | 4.58% | 9200000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Stanton to Beulah 115kV Rebuild | Current Study | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | 671532.8467 | 7.299% | 9200000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 181201.8798 | 5.329% | 3400000
GEN-2016-103 | 15 - Eastern South Dakota |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 87371.2629 | 2.57% | 3400000
GEN-2016-107 | 01 - Woodward |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 73092.6907 | 2.15% | 3400000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 131906.8093 | 3.88% | 3400000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 346765.3235 | 10.2% | 3400000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 50994.9005 | 1.5% | 3400000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 29917.0083 | 0.8799% | 3400000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 92470.7529 | 2.72% | 3400000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 60853.9146 | 1.79% | 3400000
GEN-2017-048 | 16 - Western North Dakota |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 1408139.1861 | 41.42% | 3400000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 182561.7438 | 5.369% | 3400000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 92810.7189 | 2.73% | 3400000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 88391.1609 | 2.6% | 3400000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 48275.1725 | 1.42% | 3400000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 38076.1924 | 1.12% | 3400000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 83291.6708 | 2.45% | 3400000
GEN-2017-094 | 15 - Eastern South Dakota |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 155704.4296 | 4.58% | 3400000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Stanton to Pick City 115kV Rebuild | Current Study | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | 248175.1825 | 7.299% | 3400000
GEN-2016-034 | 09 - Nebraska |  | ERIS | Stegall 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Stegall 345kV Substation | 7420009.6127 | 26.5% | 28000000
GEN-2016-093 | 09 - Nebraska |  | ERIS | Stegall 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Stegall 345kV Substation | 10513987.5038 | 37.55% | 28000000
GEN-2017-031 | 09 - Nebraska |  | ERIS | Stegall 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Stegall 345kV Substation | 7062006.4525 | 25.22% | 28000000
GEN-2017-037 | 09 - Nebraska |  | ERIS | Stegall 345kV Reactive Support | Current Study | Install a new 150 MVAR capacitor bank at Stegall 345kV Substation | 3003996.4311 | 10.73% | 28000000
GEN-2016-034 | 09 - Nebraska |  | ERIS | Stegall to GEN-2016-034 Tap New Build | Current Study | Build a new 345kV 26 mile line from Stegall to GEN-2016-034 Tap | 25480828.0828 | 45.66% | 55800000
GEN-2016-093 | 09 - Nebraska |  | ERIS | Stegall to GEN-2016-034 Tap New Build | Current Study | Build a new 345kV 26 mile line from Stegall to GEN-2016-034 Tap | 17974977.4977 | 32.21% | 55800000
GEN-2017-031 | 09 - Nebraska |  | ERIS | Stegall to GEN-2016-034 Tap New Build | Current Study | Build a new 345kV 26 mile line from Stegall to GEN-2016-034 Tap | 7210081.0081 | 12.92% | 55800000
GEN-2017-037 | 09 - Nebraska |  | ERIS | Stegall to GEN-2016-034 Tap New Build | Current Study | Build a new 345kV 26 mile line from Stegall to GEN-2016-034 Tap | 5134113.4113 | 9.201% | 55800000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 11118.8881 | 2.78% | 400000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 1919.808 | 0.48% | 400000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 3519.648 | 0.8799% | 400000
GEN-2016-107 | 01 - Woodward |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 5919.4081 | 1.48% | 400000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 11958.8041 | 2.99% | 400000
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 3119.688 | 0.7799% | 400000
GEN-2017-011 | 01 - Woodward |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 6399.3601 | 1.6% | 400000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 15918.4082 | 3.98% | 400000
GEN-2017-018 | 03 - Spearville |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 9039.0961 | 2.26% | 400000
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 3999.6 | 0.9999% | 400000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 1679.832 | 0.42% | 400000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 999.9 | 0.25% | 400000
GEN-2017-028 | 01 - Woodward |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 1919.808 | 0.48% | 400000
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 60073.9926 | 15.02% | 400000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 6919.3081 | 1.73% | 400000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 3599.64 | 0.8999% | 400000
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 60073.9926 | 15.02% | 400000
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 60073.9926 | 15.02% | 400000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 9079.0921 | 2.27% | 400000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 4879.512 | 1.22% | 400000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 6919.3081 | 1.73% | 400000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 4839.516 | 1.21% | 400000
GEN-2017-067 | 01 - Woodward |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 7439.2561 | 1.86% | 400000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 8999.1001 | 2.25% | 400000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 3719.628 | 0.9299% | 400000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 1079.892 | 0.27% | 400000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 6439.3561 | 1.61% | 400000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 11918.8081 | 2.98% | 400000
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 60073.9926 | 15.02% | 400000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 6359.3641 | 1.59% | 400000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 729677.0323 | 2.78% | 26250000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 125987.4013 | 0.48% | 26250000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 230976.9023 | 0.8799% | 26250000
GEN-2016-107 | 01 - Woodward |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 388461.1539 | 1.48% | 26250000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 784796.5203 | 2.99% | 26250000
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 204729.527 | 0.7799% | 26250000
GEN-2017-011 | 01 - Woodward |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 419958.0042 | 1.6% | 26250000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 1044645.5354 | 3.98% | 26250000
GEN-2017-018 | 03 - Spearville |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 593190.6809 | 2.26% | 26250000
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 262473.7526 | 0.9999% | 26250000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 110238.9761 | 0.42% | 26250000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 65618.4382 | 0.25% | 26250000
GEN-2017-028 | 01 - Woodward |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 125987.4013 | 0.48% | 26250000
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 3942355.7644 | 15.02% | 26250000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 454079.592 | 1.73% | 26250000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 236226.3774 | 0.8999% | 26250000
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 3942355.7644 | 15.02% | 26250000
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 3942355.7644 | 15.02% | 26250000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 595815.4185 | 2.27% | 26250000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 320217.9782 | 1.22% | 26250000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 454079.592 | 1.73% | 26250000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 317593.2407 | 1.21% | 26250000
GEN-2017-067 | 01 - Woodward |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 488201.1799 | 1.86% | 26250000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 590565.9434 | 2.25% | 26250000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 244100.5899 | 0.9299% | 26250000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 70867.9132 | 0.27% | 26250000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 422582.7417 | 1.61% | 26250000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 782171.7828 | 2.98% | 26250000
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 3942355.7644 | 15.02% | 26250000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | Current Study | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | 417333.2667 | 1.59% | 26250000
GEN-2017-001 | 09 - Nebraska | 132935 | ERIS | Sweetwater 345 kV Substation GEN-2017-001 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-001 (250 MW/Wind), into the Point of Interconnection (POI) at Sweetwater 345 kV Substation. | 2600000 | 100% | 2600000
GEN-2017-001 | 09 - Nebraska | 132934 | ERIS | Sweetwater 345 kV Substation GEN-2017-001 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-001 (250 MW/Wind), into the Point of Interconnection (POI) at Sweetwater 345 kV Substation. | 2600000 | 100% | 2600000
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 132905 | ERIS | Swisher 115 kV Substation GEN-2016-039 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-039 (112 MW/Solar), into the Point of Interconnection (POI) at Swisher 115 kV Substation. | 5147608 | 100% | 5147608
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 132904 | ERIS | Swisher 115 kV Substation GEN-2016-039 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-039 (112 MW/Solar), into the Point of Interconnection (POI) at Swisher 115 kV Substation. | 587191 | 100% | 587191
GEN-2016-005 | 03 - Spearville |  | NRIS | Tekamah to S1226 161kV Rebuild | Current Study | Rebuild the existing Tekamah to S1226 161kV 20.87 mile line to achieve a minimum winter/emergency rating of 429 MVA | 311562.6575 | 1.5% | 20774998
GEN-2016-159 | 09 - Nebraska |  | NRIS | Tekamah to S1226 161kV Rebuild | Current Study | Rebuild the existing Tekamah to S1226 161kV 20.87 mile line to achieve a minimum winter/emergency rating of 429 MVA | 9294952.6145 | 44.74% | 20774998
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Tekamah to S1226 161kV Rebuild | Current Study | Rebuild the existing Tekamah to S1226 161kV 20.87 mile line to achieve a minimum winter/emergency rating of 429 MVA | 4552968.9678 | 21.92% | 20774998
GEN-2017-018 | 03 - Spearville |  | NRIS | Tekamah to S1226 161kV Rebuild | Current Study | Rebuild the existing Tekamah to S1226 161kV 20.87 mile line to achieve a minimum winter/emergency rating of 429 MVA | 475652.3237 | 2.29% | 20774998
GEN-2017-032 | 03 - Spearville |  | NRIS | Tekamah to S1226 161kV Rebuild | Current Study | Rebuild the existing Tekamah to S1226 161kV 20.87 mile line to achieve a minimum winter/emergency rating of 429 MVA | 257558.4635 | 1.24% | 20774998
GEN-2017-047 | 02 - Hitchland |  | NRIS | Tekamah to S1226 161kV Rebuild | Current Study | Rebuild the existing Tekamah to S1226 161kV 20.87 mile line to achieve a minimum winter/emergency rating of 429 MVA | 168243.835 | 0.8098% | 20774998
GEN-2017-055 | 09 - Nebraska |  | NRIS | Tekamah to S1226 161kV Rebuild | Current Study | Rebuild the existing Tekamah to S1226 161kV 20.87 mile line to achieve a minimum winter/emergency rating of 429 MVA | 2000232.2609 | 9.628% | 20774998
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Tekamah to S1226 161kV Rebuild | Current Study | Rebuild the existing Tekamah to S1226 161kV 20.87 mile line to achieve a minimum winter/emergency rating of 429 MVA | 1260790.2206 | 6.069% | 20774998
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Tekamah to S1226 161kV Rebuild | Current Study | Rebuild the existing Tekamah to S1226 161kV 20.87 mile line to achieve a minimum winter/emergency rating of 429 MVA | 193168.8476 | 0.9298% | 20774998
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Tekamah to S1226 161kV Rebuild | Current Study | Rebuild the existing Tekamah to S1226 161kV 20.87 mile line to achieve a minimum winter/emergency rating of 429 MVA | 336487.6701 | 1.62% | 20774998
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Tekamah to S1226 161kV Rebuild | Current Study | Rebuild the existing Tekamah to S1226 161kV 20.87 mile line to achieve a minimum winter/emergency rating of 429 MVA | 1755136.3037 | 8.448% | 20774998
GEN-2017-100 | 02 - Hitchland |  | NRIS | Tekamah to S1226 161kV Rebuild | Current Study | Rebuild the existing Tekamah to S1226 161kV 20.87 mile line to achieve a minimum winter/emergency rating of 429 MVA | 168243.835 | 0.8098% | 20774998
GEN-2017-100 | 02 - Hitchland | 133081 | ERIS | Texas County 115 kV Substation GEN-2017-100 Inteconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-100 (102.6 MW/Solar), into the Point of Interconnection (POI) at Texas County 115 kV Substation. | 17186637 | 100% | 17186637
GEN-2017-100 | 02 - Hitchland | 133080 | ERIS | Texas County 115 kV Substation GEN-2017-100 Inteconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-100 (102.6 MW/Solar), into the Point of Interconnection (POI) at Texas County 115 kV Substation. | 781840 | 100% | 781840
GEN-2017-018 | 03 - Spearville | 132961 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | 1412092 | 100% | 1412092
GEN-2017-018 | 03 - Spearville | 143117 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | 30000 | 100% | 30000
GEN-2017-018 | 03 - Spearville | 143118 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (WERE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | 13260 | 100% | 13260
GEN-2017-018 | 03 - Spearville | 132960 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | 918132 | 100% | 918132
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 132971 | ERIS | Tolk 230 kV Substation GEN-2017-026 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-026 (235 MW/Wind), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | 1543568 | 100% | 1543568
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 132970 | ERIS | Tolk 230 kV Substation GEN-2017-026 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-026 (235 MW/Wind), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | 901002 | 100% | 901002
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 133053 | ERIS | Tolk 230 kV Substation GEN-2017-080 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-080 (525 MW/Solar), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | 2141174 | 100% | 2141174
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 133052 | ERIS | Tolk 230 kV Substation GEN-2017-080 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-080 (525 MW/Solar), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | 840720 | 100% | 840720
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2016-171 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico | 122568 |  | Tolk 345/230kV Transformer CKT 2 | Contingent | Install a new 345/230kV transformer at Tolk substation | 0 | 0 | 14055360
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tolk to Tuco 230kV Rebuild | Current Study | Rebuild the existing Tolk to Tuco 230kV 54.58 mile line to achieve a minimum light/emergency rating of 555 MVA | 2582313.8005 | 5.224% | 49432000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tolk to Tuco 230kV Rebuild | Current Study | Rebuild the existing Tolk to Tuco 230kV 54.58 mile line to achieve a minimum light/emergency rating of 555 MVA | 8942070.4318 | 18.09% | 49432000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tolk to Tuco 230kV Rebuild | Current Study | Rebuild the existing Tolk to Tuco 230kV 54.58 mile line to achieve a minimum light/emergency rating of 555 MVA | 962015.9202 | 1.946% | 49432000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tolk to Tuco 230kV Rebuild | Current Study | Rebuild the existing Tolk to Tuco 230kV 54.58 mile line to achieve a minimum light/emergency rating of 555 MVA | 8298334.1517 | 16.79% | 49432000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tolk to Tuco 230kV Rebuild | Current Study | Rebuild the existing Tolk to Tuco 230kV 54.58 mile line to achieve a minimum light/emergency rating of 555 MVA | 6267595.2513 | 12.68% | 49432000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tolk to Tuco 230kV Rebuild | Current Study | Rebuild the existing Tolk to Tuco 230kV 54.58 mile line to achieve a minimum light/emergency rating of 555 MVA | 104947.19 | 0.2123% | 49432000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tolk to Tuco 230kV Rebuild | Current Study | Rebuild the existing Tolk to Tuco 230kV 54.58 mile line to achieve a minimum light/emergency rating of 555 MVA | 18538831.6138 | 37.5% | 49432000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tolk to Tuco 230kV Rebuild | Current Study | Rebuild the existing Tolk to Tuco 230kV 54.58 mile line to achieve a minimum light/emergency rating of 555 MVA | 3735891.6408 | 7.558% | 49432000
GEN-2016-107 | 01 - Woodward |  | NRIS | Tonnece to Tontitown 345kV New Build | Current Study | Build a new 18 mile 345kV line from Tonnece to Tontitown | 1941030 | 2.73% | 71100000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Tonnece to Tontitown 345kV New Build | Current Study | Build a new 18 mile 345kV line from Tonnece to Tontitown | 490590 | 0.69% | 71100000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Tonnece to Tontitown 345kV New Build | Current Study | Build a new 18 mile 345kV line from Tonnece to Tontitown | 4763700 | 6.7% | 71100000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Tonnece to Tontitown 345kV New Build | Current Study | Build a new 18 mile 345kV line from Tonnece to Tontitown | 2808450 | 3.95% | 71100000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Tonnece to Tontitown 345kV New Build | Current Study | Build a new 18 mile 345kV line from Tonnece to Tontitown | 3611880 | 5.08% | 71100000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Tonnece to Tontitown 345kV New Build | Current Study | Build a new 18 mile 345kV line from Tonnece to Tontitown | 5474700 | 7.7% | 71100000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Tonnece to Tontitown 345kV New Build | Current Study | Build a new 18 mile 345kV line from Tonnece to Tontitown | 7053120 | 9.92% | 71100000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Tonnece to Tontitown 345kV New Build | Current Study | Build a new 18 mile 345kV line from Tonnece to Tontitown | 35201610 | 49.51% | 71100000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Tonnece to Tontitown 345kV New Build | Current Study | Build a new 18 mile 345kV line from Tonnece to Tontitown | 9754920 | 13.72% | 71100000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 133017 | ERIS | Tuco 230 kV Substation GEN-2017-059 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-059 (90 MW/Solar), into the Point of Interconnection (POI) at Tuco 230 kV Substation. | 849034 | 100% | 849034
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico | 133016 | ERIS | Tuco 230 kV Substation GEN-2017-059 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-059 (90 MW/Solar), into the Point of Interconnection (POI) at Tuco 230 kV Substation. | 1231645 | 100% | 1231645
GEN-2016-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 34387.5409 | 4.298% | 800000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 20587.4205 | 2.573% | 800000
GEN-2016-078 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 27481.9707 | 3.435% | 800000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 36464.9509 | 4.558% | 800000
GEN-2016-172 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 62279.8316 | 7.785% | 800000
GEN-2017-007 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 68771.4917 | 8.596% | 800000
GEN-2017-012 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 39597.411 | 4.95% | 800000
GEN-2017-016 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 7631.1602 | 0.9539% | 800000
GEN-2017-026 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 54897.5714 | 6.862% | 800000
GEN-2017-039 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 50749.5913 | 6.344% | 800000
GEN-2017-059 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 46951.1812 | 5.869% | 800000
GEN-2017-069 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 832.49 | 0.1041% | 800000
GEN-2017-079 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 13960.2903 | 1.745% | 800000
GEN-2017-080 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 122643.5131 | 15.33% | 800000
GEN-2017-081 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 71987.7518 | 8.998% | 800000
GEN-2017-084 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 24730.3506 | 3.091% | 800000
GEN-2017-087 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 29593.3007 | 3.699% | 800000
GEN-2017-091 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 7874.0102 | 0.9843% | 800000
GEN-2017-104 | 06 - South Texas Panhandle/New Mexico |  | ERIS | Tuco to Crawfish Draw 345kV Rebuild | Current Study | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | 78578.172 | 9.822% | 800000
GEN-2016-005 | 03 - Spearville |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 14875.9507 | 1.308% | 1137707.62
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 345872.5845 | 30.4% | 1137707.62
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 5463.0366 | 0.4802% | 1137707.62
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 9971.6934 | 0.8765% | 1137707.62
GEN-2016-107 | 01 - Woodward |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 4163.3586 | 0.3659% | 1137707.62
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 2974.8622 | 0.2615% | 1137707.62
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 6030.8782 | 0.5301% | 1137707.62
GEN-2017-011 | 01 - Woodward |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 13348.1036 | 1.173% | 1137707.62
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 5003.9755 | 0.4398% | 1137707.62
GEN-2017-018 | 03 - Spearville |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 15294.7605 | 1.344% | 1137707.62
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 9123.191 | 0.8019% | 1137707.62
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 6436.2709 | 0.5657% | 1137707.62
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 15331.0181 | 1.348% | 1137707.62
GEN-2017-032 | 03 - Spearville |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 23787.0103 | 2.091% | 1137707.62
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 60374.0472 | 5.307% | 1137707.62
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 174830.9089 | 15.37% | 1137707.62
GEN-2017-055 | 09 - Nebraska |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 4387.5106 | 0.3856% | 1137707.62
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 2532.8118 | 0.2226% | 1137707.62
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 60464.6088 | 5.315% | 1137707.62
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 192559.5634 | 16.93% | 1137707.62
GEN-2017-067 | 01 - Woodward |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 144171.1874 | 12.67% | 1137707.62
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 2589.5559 | 0.2276% | 1137707.62
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 2326.5728 | 0.2045% | 1137707.62
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 2326.5728 | 0.2045% | 1137707.62
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 761.4716 | 0.06693% | 1137707.62
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 1514.2496 | 0.1331% | 1137707.62
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 4069.5409 | 0.3577% | 1137707.62
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 4732.0163 | 0.4159% | 1137707.62
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Tupelo to Stonewall 138kV Rebuild | Current Study | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | 2390.308 | 0.2101% | 1137707.62
GEN-2016-159 | 09 - Nebraska | 132927 | ERIS | Turtle Creek 345 kV Substation GEN-2016-159 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-159 (427.8 MW/Wind), into the Point of Interconnection (POI) at Hoskins 345 kV Substation. | 2900000 | 100% | 2900000
GEN-2016-159 | 09 - Nebraska | 132926 | ERIS | Turtle Creek 345 kV Substation GEN-2016-159 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-159 (427.8 MW/Wind), into the Point of Interconnection (POI) at Hoskins 345 kV Substation. | 2900000 | 100% | 2900000
GEN-2017-014 | 17 - Western South Dakota | 132957 | ERIS | Underwood - Philip 230 kV GEN-2017-014 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-014 (300 MW/Wind), into the Point of Interconnection (POI) at Underwood - Philip 230 kV. | 4604916.8086 | 100% | 4604916.8086
GEN-2017-014 | 17 - Western South Dakota | 132956 | ERIS | Underwood - Philip 230 kV GEN-2017-014 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-014 (300 MW/Wind), into the Point of Interconnection (POI) at Underwood - Philip 230 kV. | 1000000 | 100% | 1000000
GEN-2017-097 | 17 - Western South Dakota | 133077 | ERIS | Underwood 115 kV Substation GEN-2017-097 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-097 (128 MW/Solar), into the Point of Interconnection (POI) at Underwood 115 kV Substation. | 1208190 | 100% | 1208190
GEN-2017-097 | 17 - Western South Dakota | 133076 | ERIS | Underwood 115 kV Substation GEN-2017-097 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-097 (128 MW/Solar), into the Point of Interconnection (POI) at Underwood 115 kV Substation. | 1208190 | 100% | 1208190
GEN-2017-064 | 17 - Western South Dakota | 133023 | ERIS | Underwoord - Wayside 230 kV GEN-2017-064 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-064 (110 MW/Solar), into the Point of Interconnection (POI) at Underwood - Wayside 230 kV. | 7350000 | 100% | 7350000
GEN-2017-064 | 17 - Western South Dakota | 133022 | ERIS | Underwoord - Wayside 230 kV GEN-2017-064 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-064 (110 MW/Solar), into the Point of Interconnection (POI) at Underwood - Wayside 230 kV. | 7350000 | 100% | 7350000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 84157.9158 | 0.8901% | 9455000
GEN-2016-103 | 15 - Eastern South Dakota |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 1870386.0386 | 19.78% | 9455000
GEN-2016-107 | 01 - Woodward |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 57681.2681 | 0.6101% | 9455000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 148458.3458 | 1.57% | 9455000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 9455.9456 | 0.1% | 9455000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 1521461.6462 | 16.09% | 9455000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 52953.2953 | 0.5601% | 9455000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 30259.0259 | 0.32% | 9455000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 80375.5376 | 0.8501% | 9455000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 31204.6205 | 0.33% | 9455000
GEN-2017-048 | 16 - Western North Dakota |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 2042484.2484 | 21.6% | 9455000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 347033.2033 | 3.67% | 9455000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 311100.6101 | 3.29% | 9455000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 80375.5376 | 0.8501% | 9455000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 56735.6736 | 0.6001% | 9455000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 101178.6179 | 1.07% | 9455000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 45388.5389 | 0.48% | 9455000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 46334.1334 | 0.49% | 9455000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 110634.5635 | 1.17% | 9455000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 21748.6749 | 0.23% | 9455000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 80375.5376 | 0.8501% | 9455000
GEN-2017-094 | 15 - Eastern South Dakota |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 1792847.2847 | 18.96% | 9455000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | Current Study | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | 532369.737 | 5.631% | 9455000
GEN-2016-005 | 03 - Spearville |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 430543.0543 | 1.23% | 35000000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 3545854.5855 | 10.13% | 35000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 707070.7071 | 2.02% | 35000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 1316131.6132 | 3.76% | 35000000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 2023202.3202 | 5.781% | 35000000
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 392039.2039 | 1.12% | 35000000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 91009.1009 | 0.26% | 35000000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 1337133.7134 | 3.82% | 35000000
GEN-2017-018 | 03 - Spearville |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 630063.0063 | 1.8% | 35000000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 2551755.1755 | 7.291% | 35000000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 1452645.2645 | 4.15% | 35000000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 2579757.9758 | 7.371% | 35000000
GEN-2017-032 | 03 - Spearville |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 451545.1545 | 1.29% | 35000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 2978797.8798 | 8.511% | 35000000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 1053605.3605 | 3.01% | 35000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 388538.8539 | 1.11% | 35000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 2985798.5799 | 8.531% | 35000000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 822582.2582 | 2.35% | 35000000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 532053.2053 | 1.52% | 35000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 553055.3055 | 1.58% | 35000000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 5173517.3517 | 14.78% | 35000000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 119011.9012 | 0.34% | 35000000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 987098.7099 | 2.82% | 35000000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 1365136.5137 | 3.9% | 35000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Valiant to Huge 138kV Rebuild | Current Study | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | 532053.2053 | 1.52% | 35000000
GEN-2017-023 | 14 - South Central Oklahoma |  | ERIS | Valiant to Hugo 138kV Rebuild | Current Study | Rebuild the existing 138kV 17.81 mile line from Valiant to Hugo to achieve a minimum normal/emergency rating of 325 MVA | 11446647.2038 | 64.61% | 17715217
GEN-2017-024 | 14 - South Central Oklahoma |  | ERIS | Valiant to Hugo 138kV Rebuild | Current Study | Rebuild the existing 138kV 17.81 mile line from Valiant to Hugo to achieve a minimum normal/emergency rating of 325 MVA | 6268569.7962 | 35.39% | 17715217
GEN-2016-005 | 03 - Spearville |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 1691419.1419 | 1.23% | 137500000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 13930143.0143 | 10.13% | 137500000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 2777777.7778 | 2.02% | 137500000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 5170517.0517 | 3.76% | 137500000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 7948294.8295 | 5.781% | 137500000
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 1540154.0154 | 1.12% | 137500000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 357535.7536 | 0.26% | 137500000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 5253025.3025 | 3.82% | 137500000
GEN-2017-018 | 03 - Spearville |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 2475247.5248 | 1.8% | 137500000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 10024752.4752 | 7.291% | 137500000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 5706820.6821 | 4.15% | 137500000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 10134763.4763 | 7.371% | 137500000
GEN-2017-032 | 03 - Spearville |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 1773927.3927 | 1.29% | 137500000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 11702420.242 | 8.511% | 137500000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 4139163.9164 | 3.01% | 137500000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 1526402.6403 | 1.11% | 137500000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 11729922.9923 | 8.531% | 137500000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 3231573.1573 | 2.35% | 137500000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 2090209.0209 | 1.52% | 137500000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 2172717.2717 | 1.58% | 137500000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 20324532.4532 | 14.78% | 137500000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 467546.7547 | 0.34% | 137500000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 3877887.7888 | 2.82% | 137500000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 5363036.3036 | 3.9% | 137500000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Valiant to Lydia 345kV New Build CKT 2 | Current Study | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | 2090209.0209 | 1.52% | 137500000
GEN-2016-005 | 03 - Spearville |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 2767776.7777 | 1.23% | 225000000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 22794779.4779 | 10.13% | 225000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 4545454.5455 | 2.02% | 225000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 8460846.0846 | 3.76% | 225000000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 13006300.6301 | 5.781% | 225000000
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 2520252.0252 | 1.12% | 225000000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 585058.5059 | 0.26% | 225000000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 8595859.586 | 3.82% | 225000000
GEN-2017-018 | 03 - Spearville |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 4050405.0405 | 1.8% | 225000000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 16404140.414 | 7.291% | 225000000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 9338433.8434 | 4.15% | 225000000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 16584158.4158 | 7.371% | 225000000
GEN-2017-032 | 03 - Spearville |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 2902790.279 | 1.29% | 225000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 19149414.9415 | 8.511% | 225000000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 6773177.3177 | 3.01% | 225000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 2497749.775 | 1.11% | 225000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 19194419.4419 | 8.531% | 225000000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 5288028.8029 | 2.35% | 225000000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 3420342.0342 | 1.52% | 225000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 3555355.5356 | 1.58% | 225000000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 33258325.8326 | 14.78% | 225000000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 765076.5077 | 0.34% | 225000000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 6345634.5635 | 2.82% | 225000000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 8775877.5878 | 3.9% | 225000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | Current Study | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | 3420342.0342 | 1.52% | 225000000
GEN-2016-005 | 03 - Spearville |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 3611277.7445 | 1.29% | 280000000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 29590081.9836 | 10.57% | 280000000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 5486902.6195 | 1.96% | 280000000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 10189962.0076 | 3.639% | 280000000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 14053189.3621 | 5.019% | 280000000
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 335932.8134 | 0.12% | 280000000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 12933413.3173 | 4.619% | 280000000
GEN-2017-018 | 03 - Spearville |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 5290941.8116 | 1.89% | 280000000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 21079784.0432 | 7.528% | 280000000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 12009598.0804 | 4.289% | 280000000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 22339532.0936 | 7.978% | 280000000
GEN-2017-032 | 03 - Spearville |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 3751249.75 | 1.34% | 280000000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 23515296.9406 | 8.398% | 280000000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 9126174.765 | 3.259% | 280000000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 3863227.3545 | 1.38% | 280000000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 23543291.3417 | 8.408% | 280000000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 5374925.015 | 1.92% | 280000000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 3303339.3321 | 1.18% | 280000000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 3499300.14 | 1.25% | 280000000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 45574885.023 | 16.28% | 280000000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 699860.028 | 0.25% | 280000000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 6326734.6531 | 2.26% | 280000000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 9322135.5729 | 3.329% | 280000000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Valiant to Turk 345kV New Build | Current Study | Build a new 84 mile 345kV line from Valiant to Turk | 5178964.2072 | 1.85% | 280000000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 596.6448 | 0.21% | 284145
GEN-2016-107 | 01 - Woodward |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 937.5847 | 0.33% | 284145
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 4403.8071 | 1.55% | 284145
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 596.6448 | 0.21% | 284145
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 123278.1877 | 43.39% | 284145
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 681.8798 | 0.24% | 284145
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 397.7632 | 0.14% | 284145
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 596.6448 | 0.21% | 284145
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 113.6466 | 0.04% | 284145
GEN-2017-055 | 09 - Nebraska |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 5312.9802 | 1.87% | 284145
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 72307.6717 | 25.45% | 284145
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 596.6448 | 0.21% | 284145
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 56.8233 | 0.02% | 284145
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 1619.4646 | 0.5699% | 284145
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 1875.1695 | 0.6599% | 284145
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 1875.1695 | 0.6599% | 284145
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 1193.2897 | 0.42% | 284145
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 340.9399 | 0.12% | 284145
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 3210.5174 | 1.13% | 284145
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Victory Hill 230kV Reactive Support | Current Study | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | 64153.5256 | 22.58% | 284145
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 143125 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (Non-Shared NU) (OKGE) | Interconnection | Potential interconnection impacts from the following generating facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | 20000 | 100% | 20000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 133065 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | 38569 | 100% | 38569
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas | 133064 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | 1593919 | 100% | 1593919
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Viola 345/138kV New Transformer CKT 2 | Current Study | Build a new 345/138kV transformer as a second circuit | 624383.1936 | 7.52% | 8302968
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Viola 345/138kV New Transformer CKT 2 | Current Study | Build a new 345/138kV transformer as a second circuit | 7678584.8064 | 92.48% | 8302968
GEN-2017-055 | 09 - Nebraska | 133011 | ERIS | Wagener 115 kV Substation GEN-2017-055 Interconnection (Non-Shared NU) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-055 (228.3 MW/Solar), into the Point of Interconnection (POI) at Wagener 115 kV Substation. | 1080000 | 100% | 1080000
GEN-2017-055 | 09 - Nebraska | 133010 | ERIS | Wagener 115 kV Substation GEN-2017-055 Interconnection (TOIF) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-055 (228.3 MW/Solar), into the Point of Interconnection (POI) at Wagener 115 kV Substation. | 250000 | 100% | 250000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Wall to Wicksville 115kV Rebuild | Current Study | Rebuild the existing Wall to Wicksville 115kV 18.29 mile line to achieve a minimum summer/emergency rating of 145 MVA | 1493971.5 | 18.41% | 8115000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Wall to Wicksville 115kV Rebuild | Current Study | Rebuild the existing Wall to Wicksville 115kV 18.29 mile line to achieve a minimum summer/emergency rating of 145 MVA | 2051472 | 25.28% | 8115000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Wall to Wicksville 115kV Rebuild | Current Study | Rebuild the existing Wall to Wicksville 115kV 18.29 mile line to achieve a minimum summer/emergency rating of 145 MVA | 4569556.5 | 56.31% | 8115000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Watertown to Appledorn 230kV Rebuild | Current Study | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | 243695.6304 | 6.769% | 3600000
GEN-2016-107 | 01 - Woodward |  | NRIS | Watertown to Appledorn 230kV Rebuild | Current Study | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | 114108.5891 | 3.17% | 3600000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Watertown to Appledorn 230kV Rebuild | Current Study | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | 197620.238 | 5.489% | 3600000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Watertown to Appledorn 230kV Rebuild | Current Study | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | 88551.1449 | 2.46% | 3600000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Watertown to Appledorn 230kV Rebuild | Current Study | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | 51834.8165 | 1.44% | 3600000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Watertown to Appledorn 230kV Rebuild | Current Study | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | 151544.8455 | 4.21% | 3600000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Watertown to Appledorn 230kV Rebuild | Current Study | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | 83151.6848 | 2.31% | 3600000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Watertown to Appledorn 230kV Rebuild | Current Study | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | 151904.8095 | 4.22% | 3600000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Watertown to Appledorn 230kV Rebuild | Current Study | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | 127067.2933 | 3.53% | 3600000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Watertown to Appledorn 230kV Rebuild | Current Study | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | 83151.6848 | 2.31% | 3600000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Watertown to Appledorn 230kV Rebuild | Current Study | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | 77392.2608 | 2.15% | 3600000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Watertown to Appledorn 230kV Rebuild | Current Study | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | 51474.8525 | 1.43% | 3600000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Watertown to Appledorn 230kV Rebuild | Current Study | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | 132826.7173 | 3.69% | 3600000
GEN-2017-094 | 15 - Eastern South Dakota |  | NRIS | Watertown to Appledorn 230kV Rebuild | Current Study | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | 2045675.4325 | 56.82% | 3600000
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 193777.2587 | 0.31% | 62515044
GEN-2016-107 | 01 - Woodward |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 12501.7586 | 0.02% | 62515044
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 737603.7588 | 1.18% | 62515044
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 6250.8793 | 0.009999% | 62515044
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 2306574.4662 | 3.69% | 62515044
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 100014.069 | 0.16% | 62515044
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 56257.9138 | 0.08999% | 62515044
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 18752.6379 | 0.03% | 62515044
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 43756.1552 | 0.06999% | 62515044
GEN-2017-055 | 09 - Nebraska |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 1618977.7418 | 2.59% | 62515044
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 39280525.597 | 62.83% | 62515044
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 18752.6379 | 0.03% | 62515044
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 62508.7931 | 0.09999% | 62515044
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 268787.8104 | 0.43% | 62515044
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 325045.7242 | 0.5199% | 62515044
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 325045.7242 | 0.5199% | 62515044
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 150021.1035 | 0.24% | 62515044
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 62508.7931 | 0.09999% | 62515044
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 550077.3795 | 0.8799% | 62515044
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Wayside to Shannon 230kV New Build | Current Study | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | 16377303.7976 | 26.2% | 62515044
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | ERIS | West Pawhuska to Shidler 138kV Rebuild | Current Study | Rebuild the existing West Pawhuska to Shidler 138kV 16.11 mile line to achieve a minimum winter/emergency rating of 246 MVA | 20239443 | 100% | 20239443
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | ERIS | West Pawhuska to Western Walls 138kV Rebuild | Current Study | Rebuild the existing West Pawhuska to Western Walls 138kV 5.98 mile line to achieve a minimum spring/emergency rating of 244 MVA | 10183861 | 100% | 10183861
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 133031 | ERIS | Wichita 345 kV Substation GEN-2017-068 Interconnection (Non-Shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-068 (103.5 MW/Solar), into the Point of Interconnection (POI) at Wichita 345 kV Substation. | 22332748 | 100% | 22332748
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas | 133030 | ERIS | Wichita 345 kV Substation GEN-2017-068 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-068 (103.5 MW/Solar), into the Point of Interconnection (POI) at Wichita 345 kV Substation. | 1593919 | 100% | 1593919
GEN-2016-005 | 03 - Spearville |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 2036492.59 | 7.988% | 25493115
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 435845.0975 | 1.71% | 25493115
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 114696.0783 | 0.4499% | 25493115
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 209001.7427 | 0.8198% | 25493115
GEN-2016-107 | 01 - Woodward |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 558187.581 | 2.19% | 25493115
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 843653.3758 | 3.309% | 25493115
GEN-2017-004 | 04 - Northwest Kansas |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 2719571.4562 | 10.67% | 25493115
GEN-2017-011 | 01 - Woodward |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 1292242.482 | 5.069% | 25493115
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 581126.7966 | 2.28% | 25493115
GEN-2017-018 | 03 - Spearville |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 3183453.3728 | 12.49% | 25493115
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 145281.6992 | 0.5699% | 25493115
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 84110.4574 | 0.3299% | 25493115
GEN-2017-028 | 01 - Woodward |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 56073.6383 | 0.22% | 25493115
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 173318.5183 | 0.6799% | 25493115
GEN-2017-032 | 03 - Spearville |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 1980418.9517 | 7.768% | 25493115
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 249782.5705 | 0.9798% | 25493115
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 112147.2765 | 0.4399% | 25493115
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 173318.5183 | 0.6799% | 25493115
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 173318.5183 | 0.6799% | 25493115
GEN-2017-047 | 02 - Hitchland |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 790128.5393 | 3.099% | 25493115
GEN-2017-055 | 09 - Nebraska |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 364478.6488 | 1.43% | 25493115
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 338990.6314 | 1.33% | 25493115
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 249782.5705 | 0.9798% | 25493115
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 127440.087 | 0.4999% | 25493115
GEN-2017-067 | 01 - Woodward |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 193708.9322 | 0.7598% | 25493115
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 2951512.4145 | 11.58% | 25493115
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 410357.0801 | 1.61% | 25493115
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 400161.8731 | 1.57% | 25493115
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 300758.6053 | 1.18% | 25493115
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 675432.461 | 2.649% | 25493115
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 2293921.5657 | 8.998% | 25493115
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 173318.5183 | 0.6799% | 25493115
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 298209.8035 | 1.17% | 25493115
GEN-2017-100 | 02 - Hitchland |  | NRIS | Wichita to Benton 345kV New Build CKT 2 | Current Study | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | 802872.548 | 3.149% | 25493115
GEN-2016-037 | 07 - Southwestern Oklahoma |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 754624.0752 | 2.27% | 33250000
GEN-2016-107 | 01 - Woodward |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 967381.5237 | 2.909% | 33250000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 1462707.4585 | 4.399% | 33250000
GEN-2017-011 | 01 - Woodward |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 2237277.5445 | 6.729% | 33250000
GEN-2017-018 | 03 - Spearville |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 5515071.9856 | 16.59% | 33250000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 252649.4701 | 0.7598% | 33250000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 142946.4107 | 0.4299% | 33250000
GEN-2017-028 | 01 - Woodward |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 96405.7189 | 0.2899% | 33250000
GEN-2017-030 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 302514.4971 | 0.9098% | 33250000
GEN-2017-032 | 03 - Spearville |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 3430713.8572 | 10.32% | 33250000
GEN-2017-033 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 432163.5673 | 1.3% | 33250000
GEN-2017-036 | 07 - Southwestern Oklahoma |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 192811.4377 | 0.5799% | 33250000
GEN-2017-038 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 302514.4971 | 0.9098% | 33250000
GEN-2017-041 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 302514.4971 | 0.9098% | 33250000
GEN-2017-047 | 02 - Hitchland |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 1369626.0748 | 4.119% | 33250000
GEN-2017-055 | 09 - Nebraska |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 631623.6753 | 1.9% | 33250000
GEN-2017-065 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 432163.5673 | 1.3% | 33250000
GEN-2017-066 | 14 - South Central Oklahoma |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 219406.1188 | 0.6599% | 33250000
GEN-2017-067 | 01 - Woodward |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 335757.8484 | 1.01% | 33250000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 5112827.4345 | 15.38% | 33250000
GEN-2017-073 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 711407.7185 | 2.14% | 33250000
GEN-2017-074 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 691461.7077 | 2.08% | 33250000
GEN-2017-076 | 12 - Northwest Arkansas |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 521920.6159 | 1.57% | 33250000
GEN-2017-077 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 1166841.6317 | 3.509% | 33250000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 3972580.4839 | 11.95% | 33250000
GEN-2017-095 | 13 - Northeast Kansas/Northwest Missouri |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 302514.4971 | 0.9098% | 33250000
GEN-2017-100 | 02 - Hitchland |  | NRIS | Wichita to Benton 345kV Rebuild | Current Study | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | 1389572.0856 | 4.179% | 33250000
GEN-2017-031 | 09 - Nebraska | 132979 | ERIS | Wildhorse - Covalt 115 kV GEN-2017-031 Interconnection (Non-Shared NU) (TSGT) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-031 (100 MW/Wind), into the Point of Interconnection (POI) at Wildhorse - Covalt 115 kV. | 736000 | 100% | 736000
GEN-2017-031 | 09 - Nebraska | 132978 | ERIS | Wildhorse - Covalt 115 kV GEN-2017-031 Interconnection (TOIF) (TSGT) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-031 (100 MW/Wind), into the Point of Interconnection (POI) at Wildhorse - Covalt 115 kV. | 3271000 | 100% | 3271000
GEN-2016-005 | 03 - Spearville |  | NRIS | Wilkes to Diana 345kV New Build | Current Study | Build a new 12.5 mile 345kV line from Wilkes to Diana | 1370250 | 2.03% | 67500000
GEN-2016-077 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Wilkes to Diana 345kV New Build | Current Study | Build a new 12.5 mile 345kV line from Wilkes to Diana | 5859000 | 8.68% | 67500000
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico |  | NRIS | Wilkes to Diana 345kV New Build | Current Study | Build a new 12.5 mile 345kV line from Wilkes to Diana | 10847250 | 16.07% | 67500000
GEN-2017-014 | 17 - Western South Dakota |  | NRIS | Wilkes to Diana 345kV New Build | Current Study | Build a new 12.5 mile 345kV line from Wilkes to Diana | 1498500 | 2.22% | 67500000
GEN-2017-018 | 03 - Spearville |  | NRIS | Wilkes to Diana 345kV New Build | Current Study | Build a new 12.5 mile 345kV line from Wilkes to Diana | 1998000 | 2.96% | 67500000
GEN-2017-023 | 14 - South Central Oklahoma |  | NRIS | Wilkes to Diana 345kV New Build | Current Study | Build a new 12.5 mile 345kV line from Wilkes to Diana | 8086500 | 11.98% | 67500000
GEN-2017-024 | 14 - South Central Oklahoma |  | NRIS | Wilkes to Diana 345kV New Build | Current Study | Build a new 12.5 mile 345kV line from Wilkes to Diana | 4596750 | 6.81% | 67500000
GEN-2017-027 | 14 - South Central Oklahoma |  | NRIS | Wilkes to Diana 345kV New Build | Current Study | Build a new 12.5 mile 345kV line from Wilkes to Diana | 7425000 | 11% | 67500000
GEN-2017-064 | 17 - Western South Dakota |  | NRIS | Wilkes to Diana 345kV New Build | Current Study | Build a new 12.5 mile 345kV line from Wilkes to Diana | 236250 | 0.35% | 67500000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | NRIS | Wilkes to Diana 345kV New Build | Current Study | Build a new 12.5 mile 345kV line from Wilkes to Diana | 11340000 | 16.8% | 67500000
GEN-2017-075 | 14 - South Central Oklahoma |  | NRIS | Wilkes to Diana 345kV New Build | Current Study | Build a new 12.5 mile 345kV line from Wilkes to Diana | 13709250 | 20.31% | 67500000
GEN-2017-097 | 17 - Western South Dakota |  | NRIS | Wilkes to Diana 345kV New Build | Current Study | Build a new 12.5 mile 345kV line from Wilkes to Diana | 533250 | 0.79% | 67500000
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas |  |  | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC: 210540) | 0 | 0 | 142601178
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  |  | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC: 210540) | 0 | 0 | 142601178
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas |  |  | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC: 210540) | 0 | 0 | 142601178
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas |  |  | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC: 210540) | 0 | 0 | 142601178
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas |  |  | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC: 210540) | 0 | 0 | 142601178
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas |  |  | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC: 210540) | 0 | 0 | 142601178
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas |  |  | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC: 210540) | 0 | 0 | 142601178
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  |  | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC: 210540) | 0 | 0 | 142601178
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas |  |  | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC: 210540) | 0 | 0 | 142601178
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas |  |  | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC: 210540) | 0 | 0 | 142601178
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  |  | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC: 210540) | 0 | 0 | 142601178
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas |  |  | Wolf Creek to Blackberry 345kV | Contingent | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC: 210540) | 0 | 0 | 142601178
GEN-2016-072 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Wolf Creek to West Gardner 345kV New Build | Current Study | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA | 22140993.8917 | 17.4% | 127250000
GEN-2016-127 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Wolf Creek to West Gardner 345kV New Build | Current Study | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA | 14282869.8311 | 11.22% | 127250000
GEN-2016-173 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Wolf Creek to West Gardner 345kV New Build | Current Study | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA | 4037282.1203 | 3.173% | 127250000
GEN-2017-005 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Wolf Creek to West Gardner 345kV New Build | Current Study | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA | 4139352.2003 | 3.253% | 127250000
GEN-2017-009 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Wolf Creek to West Gardner 345kV New Build | Current Study | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA | 25018001.272 | 19.66% | 127250000
GEN-2017-022 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Wolf Creek to West Gardner 345kV New Build | Current Study | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA | 5164276.5404 | 4.058% | 127250000
GEN-2017-040 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Wolf Creek to West Gardner 345kV New Build | Current Study | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA | 11162111.2909 | 8.772% | 127250000
GEN-2017-068 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Wolf Creek to West Gardner 345kV New Build | Current Study | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA | 7424929.2706 | 5.835% | 127250000
GEN-2017-071 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Wolf Creek to West Gardner 345kV New Build | Current Study | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA | 8030918.9206 | 6.311% | 127250000
GEN-2017-072 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Wolf Creek to West Gardner 345kV New Build | Current Study | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA | 3361780.0103 | 2.642% | 127250000
GEN-2017-086 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Wolf Creek to West Gardner 345kV New Build | Current Study | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA | 11330951.6209 | 8.904% | 127250000
GEN-2017-092 | 08 - North Oklahoma/South Central Kansas |  | ERIS | Wolf Creek to West Gardner 345kV New Build | Current Study | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA | 11156533.0309 | 8.767% | 127250000
ASGI-2016-001 | 06 - South Texas Panhandle/New Mexico | 143142 | ERIS | Wolfforth 115 kV Substation ASGI-2016-001 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, ASGI-2016-001 (2.5 MW/Wind), into the Point of Interconnection (POI) at Wolfforth 115 kV Substation. | 4382573.1852 | 100% | 4382573.1852
ASGI-2016-001 | 06 - South Texas Panhandle/New Mexico | 143141 | ERIS | Wolfforth 151 kV Substation ASGI-2016-001 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, ASGI-2016-001 (2.5 MW/Wind), into the Point of Interconnection (POI) at Wolfforth 115 kV Substation. | 883481 | 100% | 883481
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico | 132915 | ERIS | Yoakum - Seagraves 115 kV GEN-2016-090 Interconnection (Non-Shared NU) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-090 (100 MW/Solar), into the Point of Interconnection (POI) at Yoakum - Seagraves 115 kV. | 6622279 | 100% | 6622279
GEN-2016-090 | 06 - South Texas Panhandle/New Mexico | 132914 | ERIS | Yoakum - Seagraves 115 kV GEN-2016-090 Interconnection (TOIF) (SWPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-090 (100 MW/Solar), into the Point of Interconnection (POI) at Yoakum - Seagraves 115 kV. | 606770 | 100% | 606770
GEN-2017-067 | 01 - Woodward |  | ERIS | Northwest to Matthewson 138kV Rebuild | Current Study | Substation and terminal equipment upgrades requred at Northwest 345kV substation to achieve a minimum light/emergency rating of 1301 MVA | 7347911.9107 | 39.87% | 18427752
GEN-2017-011 | 01 - Woodward |  | ERIS | Northwest to Matthewson 138kV Rebuild | Current Study | Substation and terminal equipment upgrades requred at Northwest 345kV substation to achieve a minimum light/emergency rating of 1301 MVA | 11079840.0893 | 60.13% | 18427752

## Upgrade Summary
Upgrade Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time (months) | Total Upgrade Cost | Column1 | Column2
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P1 | ERIS | Adrian 161 kV Substation GEN-2017-090 Interconnection (Non-Shared NU) (KCPL) | 133069 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-090 (150 MW/Solar), into the Point of Interconnection (POI) at Adrian 161 kV Substation. | Evergy | TBD | 9955939 | 9955939 | TRUE
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P1 | ERIS | Adrian 161 kV Substation GEN-2017-090 Interconnection (TOIF) (KCPL) | 133068 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-090 (150 MW/Solar), into the Point of Interconnection (POI) at Adrian 161 kV Substation. | Evergy | TBD | 824356 | 824356 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Altoona - Parson 138 kV GEN-2017-022 Interconnection (Non-Shared NU) (WERE) | 132965 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-022 (65 MW/Solar), into the Point of Interconnection (POI) at Altoona - Parson 138 kV. | Evergy | TBD | 4790295 | 4790295 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Altoona - Parson 138 kV GEN-2017-022 Interconnection (TOIF) (WERE) | 132964 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-022 (65 MW/Solar), into the Point of Interconnection (POI) at Altoona - Parson 138 kV. | Evergy | TBD | 696118 | 696118 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Amarillo South - Swisher 230 kV GEN-2017-081 Interconnection (Non-Shared NU) (SWPS) | 133055 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-081 (300 MW/Solar), into the Point of Interconnection (POI) at Amarillo South - Swisher 230 kV. | SWPS | TBD | 7473582 | 7473582 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Amarillo South - Swisher 230 kV GEN-2017-081 Interconnection (TOIF) (SWPS) | 133054 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-081 (300 MW/Solar), into the Point of Interconnection (POI) at Amarillo South - Swisher 230 kV. | SWPS | TBD | 956616 | 956616 | TRUE
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P1 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (Non-Shared NU) (EDE) | 133057 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-082 (149.4 MW/Solar), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | EMDE | TBD | 3400000 | 3400000 | TRUE
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P1 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (Non-Shared NU) (WERE) | 143123 | Potential interconnection impacts from the following generating facility, GEN-2017-082 (149.4 MW/Wind), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | Evergy | TBD | 6649 | 6649 | TRUE
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P1 | ERIS | Asbury Plant 161 kV Substation GEN-2017-082 Interconnection (TOIF) (EDE) | 133056 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-082 (149.4 MW/Solar), into the Point of Interconnection (POI) at Asbury Plant 161 kV Substation. | EMDE | TBD | 800000 | 800000 | TRUE
Interconnection | 01 - Woodward | DISIS-2017-001-P1 | ERIS | Badger - Woodward 345 kV GEN-2017-011 Interconnection (Non-Shared NU) (OKGE) | 132951 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-011 (151.8 MW/Solar), into the Point of Interconnection (POI) at Badger - Woodward 345 kV. | OKGE | TBD | 15000 | 15000 | TRUE
Interconnection | 01 - Woodward | DISIS-2017-001-P1 | ERIS | Badger - Woodward 345 kV GEN-2017-011 Interconnection (TOIF) (OKGE) | 132950 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-011 (151.8 MW/Solar), into the Point of Interconnection (POI) at Badger - Woodward 345 kV. | OKGE | TBD | 689661 | 689661 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Bailey County 115 kV Substation GEN-2016-078 Interconnection (Non-Shared NU) (SWPS) | 132913 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-078 (108 MW/Solar), into the Point of Interconnection (POI) at Bailey County 115 kV Substation. | SWPS | TBD | 1719092 | 1719092 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Bailey County 115 kV Substation GEN-2016-078 Interconnection (TOIF) (SWPS) | 132912 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-078 (108 MW/Solar), into the Point of Interconnection (POI) at Bailey County 115 kV Substation. | SWPS | TBD | 575012 | 575012 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Bear Creek - Johnson Corner 115 kV GEN-2017-052 Interconnection (Non-Shared NU) (SUNC) | 133007 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-052 (25 MW/Solar), into the Point of Interconnection (POI) at Bear Creek - Johnson Corner 115 kV. | SUNC | TBD | 3372070 | 3372070 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Bear Creek - Johnson Corner 115 kV GEN-2017-052 Interconnection (TOIF) (SUNC) | 133006 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-052 (25 MW/Solar), into the Point of Interconnection (POI) at Bear Creek - Johnson Corner 115 kV. | SUNC | TBD | 1662749 | 1662749 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Bobcat 115 kV Substation GEN-2016-093 Interconnection (Non-Shared NU) (NPPD) | 132917 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-093 (70 MW/Solar), into the Point of Interconnection (POI) at Stegall 115 kV Substation. | NPPD | TBD | 525000 | 525000 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Bobcat 115 kV Substation GEN-2016-093 Interconnection (TOIF) (NPPD) | 132916 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-093 (70 MW/Solar), into the Point of Interconnection (POI) at Stegall 115 kV Substation. | NPPD | TBD | 525000 | 525000 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Bobcat 115 kV Substation GEN-2017-037 Interconnection (NU) (NPPD) | 132987 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-037 (20 MW/Solar), into the Point of Interconnection (POI) at Stegall 115 kV Substation. | NPPD | TBD | 525000 | 525000 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Bobcat 115 kV Substation GEN-2017-037 Interconnection (TOIF) (NPPD) | 132986 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-037 (20 MW/Solar), into the Point of Interconnection (POI) at Stegall 115 kV Substation. | NPPD | TBD | 525000 | 525000 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-040 Interconnection (Non-Shared NU) (OKGE) | 132993 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-040 (200.1 MW/Wind), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole 345 kV. | OKGE | TBD | 5741321 | 5741321 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-040 Interconnection (TOIF) (OKGE) | 132992 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-040 (200.1 MW/Wind), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole 345 kV. | OKGE | TBD | 599979 | 599979 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-092 Interconnection (Non-Shared NU) (OKGE) | 133073 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-092 (200 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole | OKGE | TBD | 5741321 | 5741321 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Canadian River - Muskogee - Seminole 345 kV GEN-2017-092 Interconnection (TOIF) (OKGE) | 133072 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-092 (200 MW/Solar), into the Point of Interconnection (POI) at Canadian River - Muskogee - Seminole | OKGE | TBD | 599979 | 599979 | TRUE
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P1 | ERIS | Chamber Springs 161 kV Substation GEN-2017-076 Interconnection (Non-Shared NU) (AEPW) | 133045 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-076 (52.2 MW/Solar), into the Point of Interconnection (POI) at Chamber Springs 161 kV Substation. | AEPW | TBD | 1406646 | 1406646 | TRUE
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P1 | ERIS | Chamber Springs 161 kV Substation GEN-2017-076 Interconnection (TOIF) (AEPW) | 133044 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-076 (52.2 MW/Solar), into the Point of Interconnection (POI) at Chamber Springs 161 kV Substation. | AEPW | TBD | 1193983 | 1193983 | TRUE
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P1 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (Non-Shared NU) (AEPW) | 132903 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | AEPW | TBD | 20639740 | 20639740 | TRUE
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P1 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (Non-Shared NU) (OKGE) | 143127 | Potential interconnection impacts from the following generating facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | OKGE | TBD | 15000 | 15000 | TRUE
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P1 | ERIS | Chisholm - Gracemont 345 kV GEN-2016-037 Interconnection (TOIF) (AEPW) | 132902 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-037 (300 MW/Wind), into the Point of Interconnection (POI) at Chisholm - Gracemont 345 kV. | AEPW | TBD | 1146800 | 1146800 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Clark - Thistle 345 kV GEN-2016-005 Interconnection (Non-Shared NU) (ITCGP) | 132899 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-005 (150 MW/Wind), into the Point of Interconnection (POI) at Clark - Thristle 345 kV. | ITCGP | TBD | 15081109 | 15081109 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Clark - Thistle 345 kV GEN-2016-005 Interconnection (TOIF) (ITCGP) | 132898 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-005 (150 MW/Wind), into the Point of Interconnection (POI) at Clark - Thirstle 234 kV. | ITCGP | TBD | 1054767 | 1054767 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Clovis Interchange 115 kV Substation GEN-2017-087 Interconnection (Non-Shared NU) (SWPS) | 133067 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-087 (128 MW/Solar), into the Point of Interconnection (POI) at Clovis Interchange 115 kV Substation. | SWPS | TBD | 3610830 | 3610830 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Clovis Interchange 115 kV Substation GEN-2017-087 Interconnection (TOIF) (SWPS) | 133066 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-087 (128 MW/Solar), into the Point of Interconnection (POI) at Clovis Interchange 115 kV Substation. | SWPS | TBD | 634734 | 634734 | TRUE
Interconnection | 02 - Hitchland | DISIS-2017-001-P1 | ERIS | Cole 115 kV Substation GEN-2017-047 Interconnection (Non-Shared NU) (SWPS) | 132997 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-047 (102 MW/Wind), into the Point of Interconnection (POI) at Cole 115 kV Substation. | SWPS | TBD | 13148764 | 13148764 | TRUE
Interconnection | 02 - Hitchland | DISIS-2017-001-P1 | ERIS | Cole 115 kV Substation GEN-2017-047 Interconnection (TOIF) (SWPS) | 132996 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-047 (102 MW/Wind), into the Point of Interconnection (POI) at Cole 115 kV Substation. | SWPS | TBD | 759404 | 759404 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Creswell 69 kV Substation GEN-2016-173 Interconnection (Non-Shared NU) (WERE) | 132933 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-173 (42 MW/Solar), into the Point of Interconnection (POI) at Creswell 69 kV Substation. | Evergy | TBD | 16242935.8 | 16242935.8 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Creswell 69 kV Substation GEN-2016-173 Interconnection (TOIF) (WERE) | 132932 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-173 (42 MW/Solar), into the Point of Interconnection (POI) at Creswell 69 kV Substation. | Evergy | TBD | 605450.91 | 605450.91 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Dry Gulch 161 kV Substation GEN-2017-073 Interconnection (Non-Shared NU) (GRDA) | 133039 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-073 (72.5 MW/Solar), into the Point of Interconnection (POI) at Dry Gulch 161 kV Substation. | GRDA | TBD | 42000 | 42000 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Dry Gulch 161 kV Substation GEN-2017-073 Interconnection (TOIF) (GRDA) | 133038 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-073 (72.5 MW/Solar), into the Point of Interconnection (POI) at Dry Gulch 161 kV Substation. | GRDA | TBD | 1100000 | 1100000 | TRUE
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P1 | ERIS | Eastown - Iatan 345 kV GEN-2017-030 Interconnection (Non-Shared NU) (KCPL) | 132977 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-030 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | Evergy | TBD | 3081098 | 3081098 | TRUE
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P1 | ERIS | Eastown - Iatan 345 kV GEN-2017-030 Interconnection (TOIF) (KCPL) | 132976 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-030 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | Evergy | TBD | 11083 | 11083 | TRUE
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P1 | ERIS | Eastown - Iatan 345 kV GEN-2017-038 Interconnection (Non-Shared NU) (KCPL) | 132989 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-038 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | Evergy | TBD | 3081098 | 3081098 | TRUE
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P1 | ERIS | Eastown - Iatan 345 kV GEN-2017-038 Interconnection (TOIF) (KCPL) | 132988 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-038 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | Evergy | TBD | 11083 | 11083 | TRUE
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P1 | ERIS | Eastown - Iatan 345 kV GEN-2017-041 Interconnection (Non-Shared NU) (KCPL) | 132995 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-041 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | Evergy | TBD | 3081098 | 3081098 | TRUE
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P1 | ERIS | Eastown - Iatan 345 kV GEN-2017-041 Interconnection (TOIF) (KCPL) | 132994 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-041 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | Evergy | TBD | 11083 | 11083 | TRUE
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P1 | ERIS | Eastown - Iatan 345 kV GEN-2017-095 Interconnection (Non-Shared NU) (KCPL) | 133075 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-095 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | Evergy | TBD | 3081098 | 3081098 | TRUE
Interconnection | 13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P1 | ERIS | Eastown - Iatan 345 kV GEN-2017-095 Interconnection (TOIF) (KCPL) | 133074 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-095 (200 MW/Wind), into the Point of Interconnection (POI) at Eastown - Iatan 345 kV. | Evergy | TBD | 11083 | 11083 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Eddy County - Tolk 345 kV GEN-2017-078 Interconnection (Non-Shared NU) (SWPS) | 133049 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-078 (300 MW/Wind), into the Point of Interconnection (POI) at Eddy County - Tolk 345 kV. | SWPS | TBD | 1098575 | 1098575 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Eddy County - Tolk 345 kV GEN-2017-078 Interconnection (TOIF) (SWPS) | 133048 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-078 (300 MW/Wind), into the Point of Interconnection (POI) at Eddy County - Tolk 345 kV. | SWPS | TBD | 1644416 | 1644416 | TRUE
Interconnection | 01 - Woodward | DISIS-2017-001-P1 | ERIS | El Reno 138 kV Switching Station GEN-2017-028 Interconnection (Non-Shared NU) (OKGE) | 143119 | Potential interconnection impacts from the following generating facility, GEN-2017-028 (50 MW/Solar), into the Point of Interconnection (POI) at El Reno 138 kV Substation. | OKGE | TBD | 15000 | 15000 | TRUE
Interconnection | 01 - Woodward | DISIS-2017-001-P1 | ERIS | El Reno 138 kV Switching Station GEN-2017-028 Interconnection (TOIF) (WFEC) | 132974 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-028 (50 MW/Solar), into the Point of Interconnection (POI) at El Reno 138 kV Switching Station. | WFEC | TBD | 400000 | 400000 | TRUE
Interconnection | 04 - Northwest Kansas | DISIS-2017-001-P1 | ERIS | Elm Creek - Summit 345 kV GEN-2017-004 Interconnection (Non-Shared NU) (ITCGP) | 132937 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-004 (201.6 MW/Wind), into the Point of Interconnection (POI) at Elm Creek - Summit 345 kV. | ITCGP | TBD | 15081109 | 15081109 | TRUE
Interconnection | 04 - Northwest Kansas | DISIS-2017-001-P1 | ERIS | Elm Creek - Summit 345 kV GEN-2017-004 Interconnection (TOIF) (ITCGP) | 132936 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-004 (201.6 MW/Wind), into the Point of Interconnection (POI) at Elm Creek - Summit 345 kV. | ITCGP | TBD | 1054767 | 1054767 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Erskine 69 kV Substation ASGI-2017-007 Interconnection (Non-Shared NU) (SWPS) | 132897 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, ASGI-2017-007 (4.2 MW/Wind), into the Point of Interconnection (POI) at Erskine 69 kV Substation. | SWPS | TBD | 4382573.1852 | 4382573.1852 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Erskine 69 kV Substation ASGI-2017-007 Interconnection (TOIF) (SWPS) | 132896 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, ASGI-2017-007 (4.2 MW/Wind), into the Point of Interconnection (POI) at Erskine 69 kV Substation. | SWPS | TBD | 883481 | 883481 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Explorer - Claremore 69 kV GEN-2017-077 Interconnection (Non-Shared NU) (AEPW) | 133047 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-077 (124.7 MW/Solar), into the Point of Interconnection (POI) at Explorer - Claremore 69 kV. | AEPW | TBD | 10334726 | 10334726 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Explorer - Claremore 69 kV GEN-2017-077 Interconnection (TOIF) (AEPW) | 133046 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-077 (124.7 MW/Solar), into the Point of Interconnection (POI) at Explorer - Claremore 69 kV. | AEPW | TBD | 1146800 | 1146800 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Fairbury 115 kV Substation GEN-2016-109 Interconnection (Non-Shared NU) (NPPD) | 132923 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-109 (102 MW/Wind), into the Point of Interconnection (POI) at Fairbury 115 kV Substation. | NPPD | TBD | 3650000 | 3650000 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Fairbury 115 kV Substation GEN-2016-109 Interconnection (TOIF) (NPPD) | 132922 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-109 (102 MW/Wind), into the Point of Interconnection (POI) at Fairbury 115 kV Substation. | NPPD | TBD | 3650000 | 3650000 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Finney - Lamar 345 kV GEN-2017-032 Interconnection (Non-Shared NU) (SWPS) | 132981 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-032 (200 MW/Wind), into the Point of Interconnection (POI) at Finney - Lamar 345 kV. | SWPS | TBD | 12750261 | 12750261 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Finney - Lamar 345 kV GEN-2017-032 Interconnection (TOIF) (SWPS) | 132980 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-032 (200 MW/Wind), into the Point of Interconnection (POI) at Finney - Lamar 345 kV. | SWPS | TBD | 1708037 | 1708037 | TRUE
Interconnection | 15 - Eastern South Dakota | DISIS-2017-001-P1 | ERIS | Fort Thompson - Huron 230 kV GEN-2017-094 Interconnection (Non-Shared NU) (WAPA) | 122574 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-094 (200 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Huron 230 kV. | WAPA | TBD | 4500000 | 4500000 | TRUE
Interconnection | 15 - Eastern South Dakota | DISIS-2017-001-P1 | ERIS | Fort Thompson - Huron 230 kV GEN-2017-094 Interconnection (TOIF) (WAPA) | 122573 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-094 (200 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Huron 230 kV. | WAPA | TBD | 4500000 | 4500000 | TRUE
Interconnection | 15 - Eastern South Dakota | DISIS-2017-001-P1 | ERIS | Fort Thompson - Leland Olds 345 kV GEN-2016-103 Interconnection (Non-Shared NU) (BEPC) | 132919 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-103 (250.7 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Leland Olds 345 kV. | BEPC | TBD | 1552831 | 1552831 | TRUE
Interconnection | 15 - Eastern South Dakota | DISIS-2017-001-P1 | ERIS | Fort Thompson - Leland Olds 345 kV GEN-2016-103 Interconnection (TOIF) (BEPC) | 132918 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-103 (250.7 MW/Wind), into the Point of Interconnection (POI) at Fort Thompson - Leland Olds 345 kV. | BEPC | TBD | 1145002 | 1145002 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Friend 115 kV Substation GEN-2017-085 Interconnection (Non-Shared NU) (NPPD) | 133063 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-085 (.6 MW/Wind), into the Point of Interconnection (POI) at Friend 115 kV Substation. | NPPD | TBD | 0 | 0 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Friend 115 kV Substation GEN-2017-085 Interconnection (TOIF) (NPPD) | 133062 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-085 (.6 MW/Wind), into the Point of Interconnection (POI) at Friend 115 kV Substation. | NPPD | TBD | 0 | 0 | TRUE
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P1 | ERIS | Frogville 138 kV Substation GEN-2017-024 Interconnection (Non-Shared NU) (WFEC) | 132969 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-024 (50 MW/Solar), into the Point of Interconnection (POI) at Frogville 138 kV Substation. | WFEC | TBD | 4750000 | 4750000 | TRUE
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P1 | ERIS | Frogville 138 kV Substation GEN-2017-024 Interconnection (TOIF) (WFEC) | 132968 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-024 (50 MW/Solar), into the Point of Interconnection (POI) at Frogville 138 kV Substation. | WFEC | TBD | 400000 | 400000 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | GRDA1 - CLARMR5 161 kV GEN-2017-061 Interconnection (Non-Shared NU) (GRDA) | 133021 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-061 (101.5 MW/Solar), into the Point of Interconnection (POI) at GRDA1 - CLARMR5 161 kV. | GRDA | TBD | 2135000 | 2135000 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | GRDA1 - CLARMR5 161 kV GEN-2017-061 Interconnection (TOIF) (GRDA) | 133020 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-061 (101.5 MW/Solar), into the Point of Interconnection (POI) at GRDA1 - CLARMR5 161 kV. | GRDA | TBD | 2135000 | 2135000 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Greenwood 138 kV Substation GEN-2017-071 Interconnection (Non-Shared NU) (OKGE) | 133035 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-071 (124.7 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | OKGE | TBD | 1721000 | 1721000 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Greenwood 138 kV Substation GEN-2017-071 Interconnection (TOIF) (OKGE) | 133034 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-071 (124.7 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | OKGE | TBD | 515000 | 515000 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Greenwood 138 kV Substation GEN-2017-072 Interconnection (Non-Shared NU) (OKGE) | 133037 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-072 (52.2 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | OKGE | TBD | 1721000 | 1721000 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Greenwood 138 kV Substation GEN-2017-072 Interconnection (TOIF) (OKGE) | 133036 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-072 (52.2 MW/Solar), into the Point of Interconnection (POI) at Greenwood 138 kV Substation. | OKGE | TBD | 515000 | 515000 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Hart Industrial 115 kV Substation GEN-2017-079 Interconnection (Non-Shared NU) (SWPS) | 133051 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-079 (49.875 MW/Solar), into the Point of Interconnection (POI) at Hart Industrial 115 kV Substation. | SWPS | TBD | 7124292 | 7124292 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Hart Industrial 115 kV Substation GEN-2017-079 Interconnection (TOIF) (SWPS) | 133050 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-079 (49.875 MW/Solar), into the Point of Interconnection (POI) at Hart Industrial 115 kV Substation. | SWPS | TBD | 583974 | 583974 | TRUE
Interconnection | 02 - Hitchland | DISIS-2017-001-P1 | ERIS | Hereford Northeast 115 kV Substation GEN-2017-058 Interconnection (Non-Shared NU) (SWPS) | 133015 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-058 (135 MW/Solar), into the Point of Interconnection (POI) at Hereford Northeast 115 kV Substation. | SWPS | TBD | 1419861 | 1419861 | TRUE
Interconnection | 02 - Hitchland | DISIS-2017-001-P1 | ERIS | Hereford Northeast 115 kV Substation GEN-2017-058 Interconnection (TOIF) (SWPS) | 133014 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-058 (135 MW/Solar), into the Point of Interconnection (POI) at Hereford Northeast 115 kV Substation. | SWPS | TBD | 701784 | 701784 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Hobbs - Yoakum 230 kV GEN-2016-171 Interconnection (Non-Shared NU) (SWPS) | 132929 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-171 (64 MW/Solar), into the Point of Interconnection (POI) at Hobbs - Yoakum 230 kV. | SWPS | TBD | 7126227 | 7126227 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Hobbs - Yoakum 230 kV GEN-2016-171 Interconnection (TOIF) (SWPS) | 132928 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-171 (64 MW/Solar), into the Point of Interconnection (POI) at Hobbs - Yoakum 230 kV. | SWPS | TBD | 927894 | 927894 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Hobbs 230 kV Substation GEN-2017-104 Interconnection (Non-Shared NU) (SWPS) | 133083 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-104 (240 MW/Solar), into the Point of Interconnection (POI) at Hobbs 230 kV Substation. | SWPS | TBD | 2530072 | 2530072 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Hobbs 230 kV Substation GEN-2017-104 Interconnection (TOIF) (SWPS) | 133082 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-104 (240 MW/Solar), into the Point of Interconnection (POI) at Hobbs 230 kV Substation. | SWPS | TBD | 1324666 | 1324666 | TRUE
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P1 | ERIS | Holister SW - PSO Walters 69 kV GEN-2017-053 Interconnection (Non-Shared NU) (WFEC) | 133009 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-053 (50 MW/Solar), into the Point of Interconnection (POI) at Holister SW - PSO Walters 69 kV. | WFEC | TBD | 4750000 | 4750000 | TRUE
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P1 | ERIS | Holister SW - PSO Walters 69 kV GEN-2017-053 Interconnection (TOIF) (WFEC) | 133008 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-053 (50 MW/Solar), into the Point of Interconnection (POI) at Holister SW - PSO Walters 69 kV. | WFEC | TBD | 400000 | 400000 | TRUE
Interconnection | 10 - Southeast Oklahoma/Northeast Texas | DISIS-2017-001-P1 | ERIS | Hosston 69 kV Substation GEN-2017-057 Interconnection (Non-Shared NU) (AEPW) | 133013 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-057 (72.5 MW/Solar), into the Point of Interconnection (POI) at Houston 69 kV Substation. | AEPW | TBD | 17032809 | 17032809 | TRUE
Interconnection | 10 - Southeast Oklahoma/Northeast Texas | DISIS-2017-001-P1 | ERIS | Hosston 69 kV Substation GEN-2017-057 Interconnection (TOIF) (AEPW) | 133012 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-057 (72.5 MW/Solar), into the Point of Interconnection (POI) at Houston 69 kV Substation. | AEPW | TBD | 1120262 | 1120262 | TRUE
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P1 | ERIS | Hugo - Sunnyside 345 kV GEN-2017-075 Interconnection (Non-Shared NU) (OKGE) | 133043 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-075 (200 MW/Solar), into the Point of Interconnection (POI) at Hugo - Sunnyside 345 kV. | OKGE | TBD | 1430000 | 1430000 | TRUE
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P1 | ERIS | Hugo - Sunnyside 345 kV GEN-2017-075 Interconnection (TOIF) (OKGE) | 133042 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-075 (200 MW/Solar), into the Point of Interconnection (POI) at Hugo - Sunnyside 345 kV. | OKGE | TBD | 915000 | 915000 | TRUE
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P1 | ERIS | Hugo 138 kV Substation GEN-2017-023 Interconnection (Non-Shared NU) (WFEC) | 132967 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-023 (85 MW/Solar), into the Point of Interconnection (POI) at Hugo 138 kV Substaion. | WFEC | TBD | 0 | 0 | TRUE
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P1 | ERIS | Hugo 138 kV Substation GEN-2017-023 Interconnection (TOIF) (WFEC) | 132966 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-023 (85 MW/Solar), into the Point of Interconnection (POI) at Hugo 138 kV Substaion. | WFEC | TBD | 750000 | 750000 | TRUE
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P1 | ERIS | Lake Creek SW - Russell SW 69 kV GEN-2017-051 Interconnection (Non-Shared NU) (WFEC) | 133005 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-051 (30 MW/Solar), into the Point of Interconnection (POI) at Lake Creek SW - Russell SW 69 kV. | WFEC | TBD | 4750000 | 4750000 | TRUE
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P1 | ERIS | Lake Creek SW - Russell SW 69 kV GEN-2017-051 Interconnection (TOIF) (WFEC) | 133004 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-051 (30 MW/Solar), into the Point of Interconnection (POI) at Lake Creek SW - Russell SW 69 kV. | WFEC | TBD | 400000 | 400000 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Lakeview - Brownfield 69 kV GEN-2016-077 Interconnection (Non-Shared NU) (SWPS) | 132911 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-077 (54 MW/Solar), into the Point of Interconnection (POI) at Lakefield - Brownfield 69 kV. | SWPS | TBD | 5040642 | 5040642 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Lakeview - Brownfield 69 kV GEN-2016-077 Interconnection (TOIF) (SWPS) | 132910 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-077 (54 MW/Solar), into the Point of Interconnection (POI) at Lakefield - Brownfield 69 kV. | SWPS | TBD | 868751 | 868751 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Lamton 115 kV Substation GEN-2017-091 Interconnection (Non-Shared NU) (SWPS) | 133071 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-091 (26.3 MW/Solar), into the Point of Interconnection (POI) at Lamton 115 kV Substation. | SWPS | TBD | 1544043 | 1544043 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Lamton 115 kV Substation GEN-2017-091 Interconnection (TOIF) (SWPS) | 133070 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-091 (26.3 MW/Solar), into the Point of Interconnection (POI) at Lamton 115 kV Substation. | SWPS | TBD | 667159 | 667159 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Laramie River - Sidney 345 kV GEN-2016-034 Interconnection (Non-Shared NU) (BEPC) | 132901 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-034 (90 MW/Wind), into the Point of Interconnection (POI) at Laramie River - Sidney 345 kV. | BEPC | TBD | 19121943 | 19121943 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Laramie River - Sidney 345 kV GEN-2016-034 Interconnection (TOIF) (BEPC) | 132900 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-034 (90 MW/Wind), into the Point of Interconnection (POI) at Laramie River - Sidney 345 kV. | BEPC | TBD | 1365130 | 1365130 | TRUE
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P1 | ERIS | LaRussell Energy Center 161 kV Substation GEN-2017-060 Interconnection (Non-Shared NU) (EDE) | 133019 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-060 (149.4 MW/Wind), into the Point of Interconnection (POI) at LaRussell Energy Center 161 kV Substation. | EMDE | TBD | 2400000 | 2400000 | TRUE
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P1 | ERIS | LaRussell Energy Center 161 kV Substation GEN-2017-060 Interconnection (TOIF) (EDE) | 133018 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-060 (149.4 MW/Wind), into the Point of Interconnection (POI) at LaRussell Energy Center 161 kV Substation. | EMDE | TBD | 800000 | 800000 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Marmaton - Litchfield 161 kV GEN-2017-005 Interconnection (Non-Shared NU) (WERE) | 132939 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-005 (195 MW/Wind), into the Point of Interconnection (POI) at Marmaton - Litchfield 161 kV. | Evergy | TBD | 11434128 | 11434128 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Marmaton - Litchfield 161 kV GEN-2017-005 Interconnection (TOIF) (WERE) | 132938 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-005 (195 MW/Wind), into the Point of Interconnection (POI) at Marmaton - Litchfield 161 kV. | Evergy | TBD | 1216477 | 1216477 | TRUE
Interconnection | 01 - Woodward | DISIS-2017-001-P1 | ERIS | Minco 345 kV Substation GEN-2017-067 Interconnection (Non-Shared NU) (OKGE) | 133029 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-067 (200.25 MW/Solar), into the Point of Interconnection (POI) at Minco 345 kV Substation. | OKGE | TBD | 1082665 | 1082665 | TRUE
Interconnection | 01 - Woodward | DISIS-2017-001-P1 | ERIS | Minco 345 kV Substation GEN-2017-067 Interconnection (TOIF) (OKGE) | 133028 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-067 (200.25 MW/Solar), into the Point of Interconnection (POI) at Minco 345 kV Substation. | OKGE | TBD | 942335 | 942335 | TRUE
Interconnection | 04 - Northwest Kansas | DISIS-2017-001-P1 | ERIS | Mingo 115 kV Substation GEN-2017-083 Interconnection (Non-Shared NU) (SUNC) | 133059 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-083 (100 MW/Wind), into the Point of Interconnection (POI) at Mingo 115 kV Substation. | SUNC | TBD | 6236939.02 | 6236939.02 | TRUE
Interconnection | 04 - Northwest Kansas | DISIS-2017-001-P1 | ERIS | Mingo 115 kV Substation GEN-2017-083 Interconnection (TOIF) (SUNC) | 133058 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-083 (100 MW/Wind), into the Point of Interconnection (POI) at Mingo 115 kV Substation. | SUNC | TBD | 2136559.42 | 2136559.42 | TRUE
Interconnection | 04 - Northwest Kansas | DISIS-2017-001-P1 | ERIS | Mingo 345 kV Substation GEN-2017-013 Interconnection (Non-Shared NU) (SUNC) | 132955 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-013 (200 MW/Wind), into the Point of Interconnection (POI) at Mingo 345 kV Substation. | SUNC | TBD | 3204601.9 | 3204601.9 | TRUE
Interconnection | 04 - Northwest Kansas | DISIS-2017-001-P1 | ERIS | Mingo 345 kV Substation GEN-2017-013 Interconnection (TOIF) (SUNC) | 132954 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-013 (200 MW/Wind), into the Point of Interconnection (POI) at Mingo 345 kV Substation. | SUNC | TBD | 2312184.97 | 2312184.97 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Moore - Pauline 345 kV GEN-2017-006 Interconnection (Non-Shared NU) (NPPD) | 132941 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-006 (73.6 MW/Wind), into the Point of Interconnection (POI) at Moore - Pauline 345 kV. | NPPD | TBD | 3150000 | 3150000 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Moore - Pauline 345 kV GEN-2017-006 Interconnection (TOIF) (NPPD) | 132940 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-006 (73.6 MW/Wind), into the Point of Interconnection (POI) at Moore - Pauline 345 kV. | NPPD | TBD | 3150000 | 3150000 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Moore - Pauline 345 kV GEN-2017-008 Interconnection (Non-Shared NU) (NPPD) | 132945 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-008 (305 MW/Solar), into the Point of Interconnection (POI) at Moore - Pauline 345 kV Substation. | NPPD | TBD | 1200000 | 1200000 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Moore - Pauline 345 kV GEN-2017-008 Interconnection (TOIF) (NPPD) | 132944 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-008 (305 MW/Solar), into the Point of Interconnection (POI) at Moore - Pauline 345 kV Substation. | NPPD | TBD | 1200000 | 1200000 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Needmore 230 kV Substation GEN-2017-039 Interconnection (Non-Shared NU) (SWPS) | 132991 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-039 (200.1 MW/Wind), into the Point of Interconnection (POI) at Needmore 230 kV Substation. | SWPS | TBD | 693659 | 693659 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Needmore 230 kV Substation GEN-2017-039 Interconnection (TOIF) (SWPS) | 132990 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-039 (200.1 MW/Wind), into the Point of Interconnection (POI) at Needmore 230 kV Substation. | SWPS | TBD | 933132 | 933132 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Neosho - Caney River 345 kV GEN-2017-009 Interconnection (Non-Shared NU) (WERE) | 132947 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-009 (302.5 MW/Wind), into the Point of Interconnection (POI) at Neosho - Caney River 345 kV. | Evergy | TBD | 14319701 | 14319701 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Neosho - Caney River 345 kV GEN-2017-009 Interconnection (TOIF) (WERE) | 132946 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-009 (302.5 MW/Wind), into the Point of Interconnection (POI) at Neosho - Caney River 345 kV. | Evergy | TBD | 1522073 | 1522073 | TRUE
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P1 | ERIS | Neosho - Crawford 69 kV GEN-2017-050 Interconnection (Non-Shared NU) (WERE) | 133003 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-050 (25 MW/Solar), into the Point of Interconnection (POI) at Neosho - Crawford 69 kV. | Evergy | TBD | 4976423 | 4976423 | TRUE
Interconnection | 12 - Northwest Arkansas | DISIS-2017-001-P1 | ERIS | Neosho - Crawford 69 kV GEN-2017-050 Interconnection (TOIF) (WERE) | 133002 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-050 (25 MW/Solar), into the Point of Interconnection (POI) at Neosho - Crawford 69 kV. | Evergy | TBD | 824356 | 824356 | TRUE
Interconnection | 16 - Western North Dakota | DISIS-2017-001-P1 | ERIS | Neset 230 kV Substation GEN-2017-048 Interconnection (Non-Shared NU) (BEPC) | 132999 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-048 (300 MW/Wind), into the Point of Interconnection (POI) at Neset 230 kV Substation. | BEPC | TBD | 1362742 | 1362742 | TRUE
Interconnection | 16 - Western North Dakota | DISIS-2017-001-P1 | ERIS | Neset 230 kV Substation GEN-2017-048 Interconnection (TOIF) (BEPC) | 132998 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-048 (300 MW/Wind), into the Point of Interconnection (POI) at Neset 230 kV Substation. | BEPC | TBD | 1617104 | 1617104 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Newhart - Potter County 230 kV GEN-2017-012 Interconnection (Non-Shared NU) (SWPS) | 132953 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-012 (201.6 MW/Wind), into the Point of Interconnection (POI) at Newhart - Potter County 230 kV. | SWPS | TBD | 7433790 | 7433790 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Newhart - Potter County 230 kV GEN-2017-012 Interconnection (TOIF) (SWPS) | 132952 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-012 (201.6 MW/Wind), into the Point of Interconnection (POI) at Newhart - Potter County 230 kV. | SWPS | TBD | 958427 | 958427 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Newhart - Swisher 230 kV GEN-2017-084 Interconnection (Non-Shared NU) (SWPS) | 133061 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-084 (89.3 MW/Solar), into the Point of Interconnection (POI) at Newhart - Swisher 230 kV. | SWPS | TBD | 7415347 | 7415347 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Newhart - Swisher 230 kV GEN-2017-084 Interconnection (TOIF) (SWPS) | 133060 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-084 (89.3 MW/Solar), into the Point of Interconnection (POI) at Newhart - Swisher 230 kV. | SWPS | TBD | 956616 | 956616 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Newhart 115 kV Substation GEN-2016-172 Interconnection (Non-Shared NU) (SWPS) | 132931 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-172 (231 MW/Wind), into the Point of Interconnection (POI) at Newhart 115 kV Substation. | SWPS | TBD | 705336 | 705336 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Newhart 115 kV Substation GEN-2016-172 Interconnection (TOIF) (SWPS) | 132930 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-172 (231 MW/Wind), into the Point of Interconnection (POI) at Newhart 115 kV Substation. | SWPS | TBD | 627807 | 627807 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Norton 115 kV Switching Station GEN-2017-016 Interconnection (Non-Shared NU) (SWPS) | 132959 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-016 (33 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | SWPS | TBD | 1069895 | 1069895 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Norton 115 kV Switching Station GEN-2017-016 Interconnection (TOIF) (SWPS) | 132958 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-016 (33 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | SWPS | TBD | 617431 | 617431 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Norton 115 kV Switching Station GEN-2017-069 Interconnection (Non-Shared NU) (SWPS) | 133033 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-069 (3.6 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | SWPS | TBD | 1069895 | 1069895 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Norton 115 kV Switching Station GEN-2017-069 Interconnection (TOIF) (SWPS) | 133032 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-069 (3.6 MW/Solar), into the Point of Interconnection (POI) at Norton 115 kV Switching Station. | SWPS | TBD | 617431 | 617431 | TRUE
Interconnection | 01 - Woodward | DISIS-2017-001-P1 | ERIS | Okeene - Cedardale 138 kV GEN-2016-107 Interconnection (NU) (WFEC) | 132921 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-107 (141.75 MW/Wind), into the Point of Interconnection (POI) at Okeene - Cedardale 138 kV. | WFEC | TBD | 4750000 | 4750000 | TRUE
Interconnection | 01 - Woodward | DISIS-2017-001-P1 | ERIS | Okeene - Cedardale 138 kV GEN-2016-107 Interconnection (TOIF) (WFEC) | 132920 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-107 (141.75 MW/Wind), into the Point of Interconnection (POI) at Okeene - Cedardale 138 kV. | WFEC | TBD | 400000 | 400000 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Oklaunion 345 kV Substation GEN-2017-033 Interconnection (Non-Shared NU) (AEPW) | 132983 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-033 (200 MW/Wind), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | AEPW | TBD | 3877147.5 | 3877147.5 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Oklaunion 345 kV Substation GEN-2017-033 Interconnection (TOIF) (AEPW) | 132982 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-033 (200 MW/Wind), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | AEPW | TBD | 1373275 | 1373275 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Oklaunion 345 kV Substation GEN-2017-065 Interconnection (Non-Shared NU) (AEPW) | 133025 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-065 (200.3 MW/Solar), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | AEPW | TBD | 3877147.5 | 3877147.5 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Oklaunion 345 kV Substation GEN-2017-065 Interconnection (TOIF) (AEPW) | 133024 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-065 (200.3 MW/Solar), into the Point of Interconnection (POI) at Oklaunion 345 kV Substation. | AEPW | TBD | 1373275 | 1373275 | TRUE
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P1 | ERIS | Oney 138 kV Substation GEN-2017-066 Interconnection (Non-Shared NU) (WFEC) | 133027 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-066 (150.8 MW/Solar), into the Point of Interconnection (POI) at Oney 138 kV Substation. | WFEC | TBD | 4750000 | 4750000 | TRUE
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P1 | ERIS | Oney 138 kV Substation GEN-2017-066 Interconnection (TOIF) (WFEC) | 133026 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-066 (150.8 MW/Solar), into the Point of Interconnection (POI) at Oney 138 kV Substation. | WFEC | TBD | 400000 | 400000 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Pawnee Valley - Hanston 69 kV GEN-2017-049 Interconnection (Non-Shared NU) (MIDW) | 133001 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-049 (50 MW/Solar), into the Point of Interconnection (POI) at Pawnee Valley - Hanston 69 kV. | MIDW | TBD | 3967218 | 3967218 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Pawnee Valley - Hanston 69 kV GEN-2017-049 Interconnection (TOIF) (MIDW) | 133000 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-049 (50 MW/Solar), into the Point of Interconnection (POI) at Pawnee Valley - Hanston 69 kV. | MIDW | TBD | 908569 | 908569 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Pleasant Hill 230 kV Substation GEN-2017-007 Interconnection (Non-Shared NU) (SWPS) | 132943 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-007 (297.5 MW/Wind), into the Point of Interconnection (POI) at Pleasant Hill 230 kV Substation. | SWPS | TBD | 1865013 | 1865013 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Pleasant Hill 230 kV Substation GEN-2017-007 Interconnection (TOIF) (SWPS) | 132942 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-007 (297.5 MW/Wind), into the Point of Interconnection (POI) at Pleasant Hill 230 kV Substation. | SWPS | TBD | 1074589 | 1074589 | TRUE
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P1 | ERIS | Pooleville - Ratliff 138 kV GEN-2017-027 Interconnection (Non-Shared NU) (OKGE) | 132973 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-027 (140 MW/Wind), into the Point of Interconnection (POI) at Pooleville - Ratliff 138 kV. | OKGE | TBD | 1396000 | 1396000 | TRUE
Interconnection | 14 - South Central Oklahoma | DISIS-2017-001-P1 | ERIS | Pooleville - Ratliff 138 kV GEN-2017-027 Interconnection (TOIF) (OKGE) | 132972 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-027 (140 MW/Wind), into the Point of Interconnection (POI) at Pooleville - Ratliff 138 kV. | OKGE | TBD | 515000 | 515000 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Post Rock - Spearville 345 kV GEN-2016-049 Interconnection (Non-Shared NU) (ITCGP) | 132907 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-049 (310.2 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | ITCGP | TBD | 15081109 | 15081109 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Post Rock - Spearville 345 kV GEN-2016-049 Interconnection (TOIF) (ITCGP) | 132906 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-049 (310.2 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | ITCGP | TBD | 1054767 | 1054767 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Post Rock - Spearville 345 kV GEN-2017-021 Interconnection (Non-Shared NU) (ITCGP) | 132963 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-021 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | ITCGP | TBD | 15081109 | 15081109 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Post Rock - Spearville 345 kV GEN-2017-021 Interconnection (TOIF) (ITCGP) | 132962 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-021 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | ITCGP | TBD | 1054767 | 1054767 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Post Rock - Spearville 345 kV GEN-2017-099 Interconnection (Non-Shared NU) (ITCGP) | 133079 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-099 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | ITCGP | TBD | 15081109 | 15081109 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Post Rock - Spearville 345 kV GEN-2017-099 Interconnection (TOIF) (ITCGP) | 133078 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-099 (200 MW/Wind), into the Point of Interconnection (POI) at Post Rock - Spearville 345 kV. | ITCGP | TBD | 1054767 | 1054767 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Pryor Junction 138 kV Substation GEN-2017-074 Interconnection (Non-Shared NU) (AEPW) | 133041 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-074 (72.5 MW/Solar), into the Point of Interconnection (POI) at Pryor Junction 138 kV Substation. | AEPW | TBD | 1365027 | 1365027 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Pryor Junction 138 kV Substation GEN-2017-074 Interconnection (TOIF) (AEPW) | 133040 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-074 (72.5 MW/Solar), into the Point of Interconnection (POI) at Pryor Junction 138 kV Substation. | AEPW | TBD | 1146800 | 1146800 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Renfrow 345 kV Substation GEN-2016-072 Interconnection (Non-Shared NU) (OKGE) | 132909 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-072 (300 MW/Wind), into the Point of Interconnection (POI) at Renfrow 345 kV Substation. | OKGE | TBD | 1430000 | 1430000 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Renfrow 345 kV Substation GEN-2016-072 Interconnection (Non-Shared NU) (WERE) | 143114 | Potential interconnection impacts from the following generating facility, GEN-2016-072 (300 MW/Wind), into the Point of Interconnection (POI) at Renfrow 345 kV Substation. | Evergy | TBD | 8866 | 8866 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Renfrow 345 kV Substation GEN-2016-072 Interconnection (TOIF) (OKGE) | 132908 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-072 (300 MW/Wind), into the Point of Interconnection (POI) at Renfrow 345 kV Substation. | OKGE | TBD | 915000 | 915000 | TRUE
Interconnection | 16 - Western North Dakota | DISIS-2017-001-P1 | ERIS | Rhame 230 kV Substation GEN-2017-010 Interconnection (Non-Shared NU) (BEPC) | 132949 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-010 (200.1 MW/Wind), into the Point of Interconnection (POI) at Rhame 230 kV Substation. | BEPC | TBD | 1189064 | 1189064 | TRUE
Interconnection | 16 - Western North Dakota | DISIS-2017-001-P1 | ERIS | Rhame 230 kV Substation GEN-2017-010 Interconnection (TOIF) (BEPC) | 132948 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-010 (200.1 MW/Wind), into the Point of Interconnection (POI) at Rhame 230 kV Substation. | BEPC | TBD | 1608232 | 1608232 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Shidler 138 kV Substation GEN-2016-127 Interconnection (Non-Shared NU) (AEPW) | 132925 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-127 (200.1 MW/Wind), into the Point of Interconnection (POI) at Shidler 138 kV Substation. | AEPW | TBD | 1300000 | 1300000 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Shidler 138 kV Substation GEN-2016-127 Interconnection (TOIF) (AEPW) | 132924 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-127 (200.1 MW/Wind), into the Point of Interconnection (POI) at Shidler 138 kV Substation. | AEPW | TBD | 1146800 | 1146800 | TRUE
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P1 | ERIS | Snyder - Cache 138 kV GEN-2017-036 Interconnection (Non-Shared NU) (AEPW) | 132985 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-036 (100 MW/Solar), into the Point of Interconnection (POI) at Snyder 138 kV Substation. | AEPW | TBD | 8198087 | 8198087 | TRUE
Interconnection | 07 - Southwestern Oklahoma | DISIS-2017-001-P1 | ERIS | Snyder - Cahce 138 kV GEN-2017-036 Interconnection (TOIF) (AEPW) | 132984 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-036 (100 MW/Solar), into the Point of Interconnection (POI) at Snyder 138 kV Substation. | AEPW | TBD | 1337068 | 1337068 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Sweetwater 345 kV Substation GEN-2017-001 Interconnection (Non-Shared NU) (NPPD) | 132935 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-001 (250 MW/Wind), into the Point of Interconnection (POI) at Sweetwater 345 kV Substation. | NPPD | TBD | 2600000 | 2600000 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Sweetwater 345 kV Substation GEN-2017-001 Interconnection (TOIF) (NPPD) | 132934 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-001 (250 MW/Wind), into the Point of Interconnection (POI) at Sweetwater 345 kV Substation. | NPPD | TBD | 2600000 | 2600000 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Swisher 115 kV Substation GEN-2016-039 Interconnection (Non-Shared NU) (SWPS) | 132905 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-039 (112 MW/Solar), into the Point of Interconnection (POI) at Swisher 115 kV Substation. | SWPS | TBD | 5147608 | 5147608 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Swisher 115 kV Substation GEN-2016-039 Interconnection (TOIF) (SWPS) | 132904 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-039 (112 MW/Solar), into the Point of Interconnection (POI) at Swisher 115 kV Substation. | SWPS | TBD | 587191 | 587191 | TRUE
Interconnection | 02 - Hitchland | DISIS-2017-001-P1 | ERIS | Texas County 115 kV Substation GEN-2017-100 Inteconnection (Non-Shared NU) (SWPS) | 133081 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-100 (102.6 MW/Solar), into the Point of Interconnection (POI) at Texas County 115 kV Substation. | SWPS | TBD | 17186637 | 17186637 | TRUE
Interconnection | 02 - Hitchland | DISIS-2017-001-P1 | ERIS | Texas County 115 kV Substation GEN-2017-100 Inteconnection (TOIF) (SWPS) | 133080 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-100 (102.6 MW/Solar), into the Point of Interconnection (POI) at Texas County 115 kV Substation. | SWPS | TBD | 781840 | 781840 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (ITCGP) | 132961 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | ITCGP | TBD | 1412092 | 1412092 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (OKGE) | 143117 | Potential interconnection impacts from the following generating facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | OKGE | TBD | 30000 | 30000 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (Non-Shared NU) (WERE) | 143118 | Potential interconnection impacts from the following generating facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | Evergy | TBD | 13260 | 13260 | TRUE
Interconnection | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Thistle 345 kV Substation GEN-2017-018 Interconnection (TOIF) (ITCGP) | 132960 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-018 (190 MW/Solar), into the Point of Interconnection (POI) at Thistle 345 kV Substation. | ITCGP | TBD | 918132 | 918132 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Tolk 230 kV Substation GEN-2017-026 Interconnection (Non-Shared NU) (SWPS) | 132971 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-026 (235 MW/Wind), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | SWPS | TBD | 1543568 | 1543568 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Tolk 230 kV Substation GEN-2017-026 Interconnection (TOIF) (SWPS) | 132970 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-026 (235 MW/Wind), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | SWPS | TBD | 901002 | 901002 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Tolk 230 kV Substation GEN-2017-080 Interconnection (Non-Shared NU) (SWPS) | 133053 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-080 (525 MW/Solar), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | SWPS | TBD | 2141174 | 2141174 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Tolk 230 kV Substation GEN-2017-080 Interconnection (TOIF) (SWPS) | 133052 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-080 (525 MW/Solar), into the Point of Interconnection (POI) at Tolk 230 kV Substation. | SWPS | TBD | 840720 | 840720 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Tuco 230 kV Substation GEN-2017-059 Interconnection (Non-Shared NU) (SWPS) | 133017 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-059 (90 MW/Solar), into the Point of Interconnection (POI) at Tuco 230 kV Substation. | SWPS | TBD | 849034 | 849034 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Tuco 230 kV Substation GEN-2017-059 Interconnection (TOIF) (SWPS) | 133016 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-059 (90 MW/Solar), into the Point of Interconnection (POI) at Tuco 230 kV Substation. | SWPS | TBD | 1231645 | 1231645 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Turtle Creek 345 kV Substation GEN-2016-159 Interconnection (Non-Shared NU) (NPPD) | 132927 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-159 (427.8 MW/Wind), into the Point of Interconnection (POI) at Hoskins 345 kV Substation. | NPPD | TBD | 2900000 | 2900000 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Turtle Creek 345 kV Substation GEN-2016-159 Interconnection (TOIF) (NPPD) | 132926 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-159 (427.8 MW/Wind), into the Point of Interconnection (POI) at Hoskins 345 kV Substation. | NPPD | TBD | 2900000 | 2900000 | TRUE
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P1 | ERIS | Underwood - Philip 230 kV GEN-2017-014 Interconnection (Non-Shared NU) (WAPA) | 132957 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-014 (300 MW/Wind), into the Point of Interconnection (POI) at Underwood - Philip 230 kV. | WAPA | TBD | 4604916.8086 | 4604916.8086 | TRUE
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P1 | ERIS | Underwood - Philip 230 kV GEN-2017-014 Interconnection (TOIF) (WAPA) | 132956 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-014 (300 MW/Wind), into the Point of Interconnection (POI) at Underwood - Philip 230 kV. | WAPA | TBD | 1000000 | 1000000 | TRUE
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P1 | ERIS | Underwood 115 kV Substation GEN-2017-097 Interconnection (Non-Shared NU) (WAPA) | 133077 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-097 (128 MW/Solar), into the Point of Interconnection (POI) at Underwood 115 kV Substation. | WAPA | TBD | 1208190 | 1208190 | TRUE
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P1 | ERIS | Underwood 115 kV Substation GEN-2017-097 Interconnection (TOIF) (WAPA) | 133076 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-097 (128 MW/Solar), into the Point of Interconnection (POI) at Underwood 115 kV Substation. | WAPA | TBD | 1208190 | 1208190 | TRUE
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P1 | ERIS | Underwoord - Wayside 230 kV GEN-2017-064 Interconnection (Non-Shared NU) (WAPA) | 133023 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-064 (110 MW/Solar), into the Point of Interconnection (POI) at Underwood - Wayside 230 kV. | WAPA | TBD | 7350000 | 7350000 | TRUE
Interconnection | 17 - Western South Dakota | DISIS-2017-001-P1 | ERIS | Underwoord - Wayside 230 kV GEN-2017-064 Interconnection (TOIF) (WAPA) | 133022 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-064 (110 MW/Solar), into the Point of Interconnection (POI) at Underwood - Wayside 230 kV. | WAPA | TBD | 7350000 | 7350000 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (Non-Shared NU) (OKGE) | 143125 | Potential interconnection impacts from the following generating facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | OKGE | TBD | 20000 | 20000 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (Non-Shared NU) (WERE) | 133065 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | Evergy | TBD | 38569 | 38569 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Viola 345 kV Substation GEN-2017-086 Interconnection (TOIF) (WERE) | 133064 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-086 (150 MW/Wind), into the Point of Interconnection (POI) at Viola 345 kV Substation. | Evergy | TBD | 1593919 | 1593919 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Wagener 115 kV Substation GEN-2017-055 Interconnection (Non-Shared NU) (LES) | 133011 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-055 (228.3 MW/Solar), into the Point of Interconnection (POI) at Wagener 115 kV Substation. | LES | TBD | 1080000 | 1080000 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Wagener 115 kV Substation GEN-2017-055 Interconnection (TOIF) (LES) | 133010 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-055 (228.3 MW/Solar), into the Point of Interconnection (POI) at Wagener 115 kV Substation. | LES | TBD | 250000 | 250000 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Wichita 345 kV Substation GEN-2017-068 Interconnection (Non-Shared NU) (WERE) | 133031 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-068 (103.5 MW/Solar), into the Point of Interconnection (POI) at Wichita 345 kV Substation. | Evergy | TBD | 22332748 | 22332748 | TRUE
Interconnection | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Wichita 345 kV Substation GEN-2017-068 Interconnection (TOIF) (WERE) | 133030 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-068 (103.5 MW/Solar), into the Point of Interconnection (POI) at Wichita 345 kV Substation. | Evergy | TBD | 1593919 | 1593919 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Wildhorse - Covalt 115 kV GEN-2017-031 Interconnection (Non-Shared NU) (TSGT) | 132979 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-031 (100 MW/Wind), into the Point of Interconnection (POI) at Wildhorse - Covalt 115 kV. | TSGT | TBD | 736000 | 736000 | TRUE
Interconnection | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Wildhorse - Covalt 115 kV GEN-2017-031 Interconnection (TOIF) (TSGT) | 132978 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-031 (100 MW/Wind), into the Point of Interconnection (POI) at Wildhorse - Covalt 115 kV. | TSGT | TBD | 3271000 | 3271000 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Wolfforth 115 kV Substation ASGI-2016-001 Interconnection (Non-Shared NU) (SWPS) | 143142 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, ASGI-2016-001 (2.5 MW/Wind), into the Point of Interconnection (POI) at Wolfforth 115 kV Substation. | SWPS | TBD | 4382573.1852 | 4382573.1852 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Wolfforth 151 kV Substation ASGI-2016-001 Interconnection (TOIF) (SWPS) | 143141 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, ASGI-2016-001 (2.5 MW/Wind), into the Point of Interconnection (POI) at Wolfforth 115 kV Substation. | SWPS | TBD | 883481 | 883481 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Yoakum - Seagraves 115 kV GEN-2016-090 Interconnection (Non-Shared NU) (SWPS) | 132915 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-090 (100 MW/Solar), into the Point of Interconnection (POI) at Yoakum - Seagraves 115 kV. | SWPS | TBD | 6622279 | 6622279 | TRUE
Interconnection | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Yoakum - Seagraves 115 kV GEN-2016-090 Interconnection (TOIF) (SWPS) | 132914 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2016-090 (100 MW/Solar), into the Point of Interconnection (POI) at Yoakum - Seagraves 115 kV. | SWPS | TBD | 606770 | 606770 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | 2nd Circle 230/115kV New Transformer | TBD | Build a new 230/115kV transformer at 2nd Circle | Evergy | TBD | 33000000 | 33000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Albion to Petersburg 115kV Rebuild | TBD | Rebuild the existing Albion to Petersburg 115kV 12.13 mile line to achieve a minimum winter/emergency rating of 151 MVA | NPPD | TBD | 4000000 | 4000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Altoona to Neodesha Jct. 69kV Rebuild | TBD | Rebuild the existing Altoona to Neodesha Jct. 69kV 2.2 mile line to achieve a minimum summer/emergency rating of 42 MVA | Evergy | TBD | 100000 | 100000 | TRUE
Current Study | 07 - Southwestern Oklahoma | DISIS-2017-001-P1 | ERIS | Anadark to Cherry Road 138kV Rebuild | TBD | Rebuild the existing Anadark to Cherry Road 138kV 25.15 mile line to achieve a minimum light/emergency rating of 189 MVA | WFEC | TBD | 24248598.85 | 24248598.85 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Arbuckle to Millcreek Tap 138kV Rebuild | TBD | Rebuild the existing Arbuckle to Mill Creek Tap 138kV 13.16 mile line to achieve a minimum winter/emergency rating of 212 MVA | OKGE | TBD | 8200000 | 8200000 | TRUE
Current Study | 08 - North Okahoma/South Central Kansas/12 - Northwest Arkansas | DISIS-2017-001-P1 | ERIS | Asbury Plant to Carl Junction NE 161kV Rebuild | TBD | Rebuild the existing Asbury Plant to Carl Junction NE 161kV 12.3 mile line to achieve a minimum winter/emergency rating of 342 MVA | EMDE | TBD | 19468000 | 19468000 | TRUE
Current Study | 08 - North Okahoma/South Central Kansas/12 - Northwest Arkansas | DISIS-2017-001-P1 | ERIS | Asbury Plant to Purcell Switch 161kV Rebuild | TBD | Rebuild the existing Asbury Plant to Purcell Switch 161kV 11.94 mile line to achieve a minimum winter/emergency rating of 329 MVA | EMDE | TBD | 21196000 | 21196000 | TRUE
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Batesville Comanche to Mound Road 138kV Rebuild | TBD | Rebuild the existing Batesville Comanche to Mound Road 138kV 3.8 mile line to achieve a minimum spring/emergency rating of 136 MVA | AEPW | TBD | 5889657 | 5889657 | TRUE
Current Study | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Beatrice to Harbine 115kV Rebuild | TBD | Rebuild the existing Beatrice to Harbine 115kV 14.08 mile line to achieve a minimum light/emergency rating of 144 MVA. | NPPD | TBD | 5520000 | 5520000 | TRUE
Current Study | 02 - Hitchland/03 - Spearville/ 04 - Northwest Kansas | DISIS-2017-001-P1 | ERIS | Beaver County to Clark County 345kV New Line | TBD | Build approximately 125 miles of new 345kV from Beaver County to Clark County to achieve a minimum light/emergency rating of 1195 MVA | OKGE | TBD | 165200000 | 165200000 | TRUE
Current Study | 02 - Hitchland/03 - Spearville/04 - Northwest Kansas/06 SoutjTexas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Beaver County to Grapevine New Build | TBD | Build a new 90 mile 345kV line from Beaver County to Grapevine | OKGE | TBD | 119700000 | 119700000 | TRUE
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Beaver to Eureka 161kV Rebuild | TBD | Rebuild the existing Beaver to Eureka 161kV 7.22 mile line to achieve a minimum winter/emergency rating of 417 MVA | AEPW, SWPA | TBD | 8000000 | 8000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Benton to Rose Hill 345kV New Build CKT 2 | TBD | Build a new 15 mile 345kV line from Benton to Rose Hill as a second circuit | Evergy | TBD | 45000000 | 45000000 | TRUE
Current Study | 16 - Western North Dakota | DISIS-2017-001-P1 | ERIS | Broadland 345/230kV Transformer Replacement | TBD | Replace the existing Broadland 345/230kV transformer to achieve a minimum rating of 450 MVA | BEPC | TBD | 6000000 | 6000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Brown to South Brown 138kV Rebuild | TBD | Rebuild the existing Brown to South Brown 138kV .12 mile line to achieve a minimum winter/emergency rating of 158 MVA | OKGE, SWPA | TBD | 345000 | 345000 | TRUE
Current Study | 14 - South Central Oklahoma | DISIS-2017-001-P1 | ERIS | Carter to Chicksaw 138kV Rebuild | TBD | Rebuild the existing Carter to Chicksaw 138kV 2.73 mile line to achieve a minimum summer/emergency rating of 217 MVA | OKGE | TBD | 1285000 | 1285000 | TRUE
Current Study | 08 - North Okahoma/South Central Kansas/12 - Northwest Arkansas | DISIS-2017-001-P1 | ERIS | Carthage to Car 395 161kV Rebuild | TBD | Rebuild the existing Carthage to Car 395 161kV 4.14 mile line to achieve a minimum winter/emergency rating of 305 MVA | SWPA, EMDE | TBD | 7700000 | 7700000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Carthage to Joplin Atlas Jct. 161kV Rebuild | TBD | Rebuild the existing Cartahage to Joplin Atlas Jct. 161kV 8.2 mile line to achieve a minimum summer/emergency rating of 262 MVA | SWPA, EMDE | TBD | 14830000 | 14830000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Carthage to LaRussell Energy Center 161kV Rebuild | TBD | Rebuild the existing Carthage to LaRussell Energy Center 161kV 11.5 mile line to achieve a minimum winter/emergency rating of 242 MVA | SWPA, EMDE | TBD | 12196500 | 12196500 | TRUE
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Carthage to Purcell Switch 161kV Rebuild | TBD | Rebuild the existing Carthage to Purcell Switch 161kV 7.89 mile line to achieve a minimum winter/emergency rating of 317 MVA | EMDE | TBD | 10856000 | 10856000 | TRUE
Current Study | 15 - Eastern South Dakota | DISIS-2017-001-P1 | ERIS | Chappelle Creek to Ft. Thompson 345k New Build CKT 2 | TBD | Build a new 30 mile 345kV line from Chappelle Creek to Ft. Thompson as a second circuit | WAPA, BEPC | TBD | 65900000 | 65900000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Cimarron 345/138kV New Transformer CKT3 | TBD | Build a new 345/138kV transformer at Cimarron as a third circuit | OKGE | TBD | 26000000 | 26000000 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico/08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | NRIS | Cleveland 138kV Substation Upgrade | TBD | Uprate terminal equipment at Cleveland 138kV to achieve a minimum rating of 460 MVA | GRDA | TBD | 146888 | 146888 | TRUE
Current Study | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Cooper 345kV New Substation | TBD | Build a new 345kV substation at Cooper | NPPD | TBD | 51000000 | 51000000 | TRUE
Current Study | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Cooper 345kV Reactive Support | TBD | Install a 200 MVAR capacitor bank at Cooper 345kV Substation | NPPD | TBD | 5000000 | 5000000 | TRUE
Current Study | 13 - Northeast Kansas/Northwest Missouri/ 15 - Eastern South Dakota | DISIS-2017-001-P1 | ERIS | Cooper to Holt 345kV New Build | TBD | Build a new 32 mile 345kV line from Cooper to Holt | TMO, NPPD | TBD | 62750000 | 62750000 | TRUE
Current Study | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Cooper to Hoyt 345kV New Build | TBD | Build a new 95 mile 345kV line from Cooper to Hoyt | NPPD, Evergy | TBD | 148250000 | 148250000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Council Bluffs to S3456 345kV Rebuild | TBD | Rebuild the existing Council Bluffs to S3456 8 mile line to achieve a minimum winter/emergency rating of 1203 MVA | OPPD | TBD | 2510992 | 2510992 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Crawfish Draw 345/230kV New Transformer | 122548 | Build a new 345/230kV transformer at Crawfish Draw with a minimum normal/emergency rating of 559/643 MVA | SWPS | TBD | 8764205 | 8764205 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico/08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to Border) | TBD | Reroute Tuco to Border line through Crawfish Draw (Tuco to Crawfish Draw to Border 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | SWPS | TBD | 8000000 | 8000000 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Crawfish Draw 345/230kV New Transformer (Tuco to OKU) | TBD | Reroute Tuco to OKU line through Crawfish Draw (Tuco to Crawfish Draw to OKU 345kV line) and build a new 345/230kV transformer at Crawfish Draw to Tuco | SWPS | TBD | 8000000 | 8000000 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Crawfish Draw 765/345kV New Substation | TBD | Build a new 345/765kV substation at Crawfish Draw | SWPS | TBD | 20000000 | 20000000 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Crawfish Draw 765/345kV New Transformer | TBD | Build a new 345/765kV transformer at Crawfish Draw | SWPS | TBD | 20000000 | 20000000 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico/08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Crawfish Draw to Crossroads 765kV New Build | TBD | Build a new 95 mile 765kV line from Crawfish Draw to Crossroads | SWPS | TBD | 380000000 | 380000000 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Crawfish Draw to Grapevine 345kV New Build | TBD | Build a new 193 mile 345kV line from Crawfish Draw to Grapevine | SWPS | TBD | 245600000 | 245600000 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Crawfish Draw to Lawton Eastside 345kV New Build | 122545 | Build a new 250 mile 345kV line from Crawfish Draw to Lawton Eastside | AEPW | TBD | 560956277 | 560956277 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico/08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Crawfish Draw to Seminole 765kV New Build | TBD | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole | OKGE, SWPS | TBD | 662000000 | 662000000 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico/08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Crawfish Draw to Seminole 765kV New Build CKT 2 | TBD | Build a new 165.5 mile 765kV line from Crawfish Draw to Seminole as a second circuit | OKGE, SWPS | TBD | 662000000 | 662000000 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico/08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Crossroads 765/345kV New Transformer | TBD | Build a new 765/345kV Transformer at Crossroads | SWPS | TBD | 20000000 | 20000000 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico/08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Crossroads 765/345kV New Transformer CKT 2 | TBD | Build a new 765/345kV Transformer at Crossroads as a second circuit | SWPS | TBD | 20000000 | 20000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Diana 345kV Substation Upgrade | TBD | Update breaker configuration at Diana 345kV | AEPW | TBD | 18427752 | 18427752 | TRUE
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Domes to Elizack 138kV Rebuild | TBD | Rebuild the existing Domes to Elizack 138kV 13.59 mile line to achieve a minimum winter/emergency rating of 231 MVA | AEPW | TBD | 21063272 | 21063272 | TRUE
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Domes to Western Walls 138kV Rebuild | TBD | Rebuild the existing Domes to Western Walls 138kV 5.74 mile line to achieve a minimum winter/emergency rating of 236 MVA | AEPW | TBD | 8271597 | 8271597 | TRUE
Current Study | 09 - Nebraska/13 - Northeast Kansas/Northwest Missouri | DISIS-2017-001-P1 | ERIS | Double Circuit Stranger Creek Creek to 87th to Craig 345kV | TBD | Rebuild 30 miles of line with one circuit bypassing 87th Street as Stranger Creek Creek-Craig 345kV to achieve a minimum spring/emergency rating of 1792 MVA | Evergy | TBD | 81000000 | 81000000 | TRUE
Current Study | 01 - Woodward | DISIS-2017-001-P1 | ERIS | Dover Switch to Okeene 138kV Rebuild | TBD | Rebuild the existing Dover Switch to Okeene 138kV 27.24 mile line to acieve a minimum winter/normal rating of 121 MVA | WFEC | TBD | 26263691.16 | 26263691.16 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Dover to Okeene 138kV Rebuild | TBD | Rebuild the existing Dover to Okeene 138kV 27.24 mile line to achieve a minimum winter/emergency rating of 121 MVA | WFEC | TBD | 26263691.16 | 26263691.16 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Dripping Spring to Springdale 138kV Rebuild | TBD | Rebuild the existing Dripping Spring to Springdale 138kV 1.25 mile line to achieve a minimum winter/emergency rating of 203 MVA | OKGE | TBD | 450000 | 450000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Dripping Spring to Stirling 138kV Rebuild | TBD | Rebuild the existings Dripping Spring to Stirling 138kV 2.23 mile line to achieve a minimum winter/emergency rating of 197 MVA | OKGE | TBD | 1400000 | 1400000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Eastowne 161kV Reactive Support | TBD | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | Evergy | TBD | 50000000 | 50000000 | TRUE
Current Study | 01 - Woodward | DISIS-2017-001-P1 | ERIS | El Reno to Scott Switch 138kV Rebuild | TBD | Rebuild the existing El Reno to Scott Switch 138kV 6.45 mile line to achieve a minimum spring/emergency rating of 146 MVA | WFEC | TBD | 6218825.55 | 6218825.55 | TRUE
Current Study | 07 - Southwestern Oklahoma | DISIS-2017-001-P1 | ERIS | Essaquandale Jct. to Walters 69kV Rebuild | TBD | Rebuild the existing Essaquandale Jct. to Walters 69kV 1.19 mile line to achieve a minimum light/emergency rating of 66 MVA | AEPW, WFEC | TBD | 2350861 | 2350861 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Eureka to Grandview 161kV Rebuild | TBD | Rebuild the existing Eureka to Grandview 161kV 10.56 mile line to achieve a minimum winter/emergency rating of 274 MVA | AEPW, SWPA | TBD | 12500000 | 12500000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Eureka to Osage 161kV Rebuild | TBD | Rebuild the existing Eureka to Osage 161kV 6.55 mile line to achieve a minimum winter/emergency rating of 332 MVA | AEPW | TBD | 11500000 | 11500000 | TRUE
Current Study | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Fairbury to Hebron N 115kV Rebuild | TBD | Rebuild the existing Fairbury to Hebron 115kV 22 mile line to achieve a minimum emergency rating of 101 MVA | NPPD | TBD | 5500000 | 5500000 | TRUE
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Farber to Belle Plaine 138kV Rebuild | TBD | Rebuild the existing Farber to Belle Plain 138kV 10.33 mile line to achieve a minimum summer/emergency rating of 172 MVA | Evergy | TBD | 14679632.18 | 14679632.18 | TRUE
Current Study | 03 - Spearville/04 - Northwest Kansas | DISIS-2017-001-P1 | ERIS | Finney 345kV Reactive Support | TBD | Install a new 250 MVAR capacitor bank at Finney 345kV Substation | SWPS | TBD | 8500000 | 8500000 | TRUE
Current Study | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Finney to G17-032-Tap 345kV Rebuild | TBD | Rebuild the existing Finney to G17-032-Tap 345kV 75.75 mile line to achieve a minimum summer/emergency rating of 444 MVA | SWPS | TBD | 150000 | 150000 | TRUE
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Franklin 161/69kV New Transformer CKT 2 | TBD | Build a new 161/69kV Transformer at Franklin as a second circuit | Evergy | TBD | 3200000 | 3200000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Ft. Randall to Lake Platte 230kV Rebuild | TBD | Rebuild the existing Ft. Randall to Lake Platte 230kV 43.34 mile line to achieve a minimum summer/emergency rating of 353 MVA | WAPA, EREC | TBD | 2000000 | 2000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Ft. Smith 345/161kV New Transformer CKT 2 | TBD | Build a new 345/161kV transformer at Ft. Smith as a second circuit | OKGE | TBD | 7400000 | 7400000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Ft. Thompson to Ft. Randall 230kV Rebuild | TBD | Rebuild the existing Ft. Thompson to Ft. Randall 230kV 87.32 mile line to achieve a minimum summer/emergency rating of 367 MVA | WAPA | TBD | 2800000 | 2800000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Ft. Thompson to Lake Platte 230kV Rebuild | TBD | Rebuild the existing Ft. Thompson to Lake Platte 230kV 43.98 mile line to achieve a minimum summer/emergency rating of 368 MVA | WAPA, BEPC | TBD | 38856725.82 | 38856725.82 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | G17-030 Tap to Iatan 345kV Rebuild | TBD | Rebuild the existing G17-30 Tap to Iatan 345kV 15.0 mile line to achieve a minimum winter/emergency rating of 1575 MVA | Evergy | TBD | 26250000 | 26250000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | G17-064 Tap to Wayside 230kV Rebuild | TBD | Rebuild the existing G16-074 Tap to Wayside 230kV 38.05 mile line to achieve a summer/emergency rating of 434 MVA | WAPA | TBD | 39500000 | 39500000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Gaines to Johnson Draw 115kV New Build | TBD | Build a new 13.99 mile 115kV line from Gaines to Johnson Draw as a second circuit | SWPS | TBD | 21293000 | 21293000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Garrison to Pick City 115kV Rebuild | TBD | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | WAPA, BEPC | TBD | 2400000 | 2400000 | TRUE
Current Study | 07 - Southwestern Oklahoma | DISIS-2017-001-P1 | ERIS | Geronimo Jct. to Essaquanadable Jct. 69kV Rebuild | TBD | Rebuild the existing Geronimo Jct. to Essaquanadale Jct. 69kV 3.83 mile line to achieve a minimum light/emergency rating of 67 MVA | WFEC | TBD | 3481274.67 | 3481274.67 | TRUE
Current Study | 07 - Southwestern Oklahoma | DISIS-2017-001-P1 | ERIS | Geronimo Jct. to Granfield 69kV Rebuild | TBD | Rebuild the existing Geronimo Jct. to Granfield 69kV 14.93 mile line to achieve a minimum light/emergency rating of 71 MVA | WFEC | TBD | 13570608.57 | 13570608.57 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Gilliam to Superior 69kV Rebuild | TBD | Rebuild the existing Gilliam to Superior 69kV 6.0 mile line to achieve a minimum summer/emergency rating of 41 MVA | AEPW | TBD | 16000000 | 16000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Gracemont to Anadark 138kV New Build CKT 2 | TBD | Build a new 5 mile 138kV line from Gracemont to Anadark as a second circuit | OKGE, WFEC | TBD | 5950000 | 5950000 | TRUE
Current Study | 01 - Woodward | DISIS-2017-001-P1 | ERIS | Gracemont to Anadark 138kV Rebuild | TBD | Rebuild the existing Gracemont to Anadark 138kV 5.09 mile line to achieve a minimum winter/emergency rating of 451 MVA | OKGE, WFEC | TBD | 4907569.31 | 4907569.31 | TRUE
Current Study | 02 - Hitchland/03 - Spearville/04 - Northwest Kansas/06 SoutjTexas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Grapevine 345kV New Substation | TBD | Build a new 345kV substation at Grapevine | SWPS | TBD | 18427752 | 18427752 | TRUE
Current Study | 02 - Hitchland/03 - Spearville/04 - Northwest Kansas/06 SoutjTexas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Grapevine to Chisholm 345kV New Build | 122551 | Build a new 75 mile 345kV line from Grapevine to Chisholm | AEPW, SWPS | TBD | 153145988 | 153145988 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Hale County to Tuco 115kV Rebuild | TBD | Rebuild the existing Hale County to Tuco 115kV 20.73 mile line to achieve a minimum spring/normal rating of 107 MVA | SWPS | TBD | 14500000 | 14500000 | TRUE
Current Study | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Hanston to Kinsley 69kV Rebuild | TBD | Rebuild the existing Hanston to Kinsley 69kV 18.75 mile line to achieve a minimum winter/emergency rating of 53 MVA | MIDW | TBD | 17042793.75 | 17042793.75 | TRUE
Current Study | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Harbine to Fairbury 115kV Rebuild | TBD | Rebuild the existing Harbine to Fairbury 115kV 9 mile line to achieve a minimum spring/emergency rating of 134 MVA | NPPD | TBD | 2250000 | 2250000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Hawthorne 345/161kV New Transformer CKT3 | TBD | Build a new 345/161kV transformer at Hawthorne as a third circuit | Evergy | TBD | 22000000 | 22000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Hawthorne to Craig 345kV New Build | TBD | Build a new 25 mile 345kV line from Hawthorn to Craig | Evergy | TBD | 37489875 | 37489875 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Hoskins 345/230kV New Transformer CKT3 | TBD | Build a new 345/230kV transformer at Hoskins as a third circuit | NPPD | TBD | 10000000 | 10000000 | TRUE
Current Study | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Hoskins 345/230kV Transformer Replacement | TBD | Replace the existing Hoskins 345/230kV transformer to achieve a minimum rating of 400 MVA | NPPD | TBD | 8302968 | 8302968 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Hoskins to Shell Creek 345kV New Build CKT 2 | TBD | Build a new 40 mile 345kV line from Hoskins to Shell Creek as a second circuit | NPPD | TBD | 82000000 | 82000000 | TRUE
Current Study | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Kelly to Goff 115kV Rebuild | TBD | Rebuild the existing Kelly to Goff 115kV 9.6 mile line to achieve a minimum spring/emergency rating of 90 MVA | Evergy | TBD | 150000 | 150000 | TRUE
Current Study | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Kelly to Tecumseh Hill 161kV Rebuild | TBD | Rebuild the existing Kelly to Tecumseh Hill 161kV 52.64 mile line to achieve a minimum spring/emergency rating of 152 MVA | Evergy | TBD | 87500000 | 87500000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Kenzie to Kenzie GR 138kV Rebuild | TBD | Rebuild the existing Kenzie to Kenzie GR 138kV .001 mile line to achieve a minimum summer/emergency rating of 348 MVA | OKGE | TBD | 115000 | 115000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Kenzie to University 138kV Rebuild | TBD | Rebuild the existing Kenzie to University 138kV .70 mile line to achieve a minimum summer/emergency rating of 232 MVA | OKGE | TBD | 1100000 | 1100000 | TRUE
Current Study | 09 - Nebraska/17 - Western South Dakota | DISIS-2017-001-P1 | ERIS | Keystone to Sidney 345kV New Build CKT 2 | TBD | Build a new 80 mile 345kV line from Keystone to Sidney as a second circuit | BEPC, NPPD | TBD | 119967600 | 119967600 | TRUE
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Kildare to White Eagle 138kV Rebuild | TBD | Rebuild the existing Kildare to While Eagle 138 kV 11.22 mile line to achieve a minimm light/emergency rating of 298 MVA | OKGE | TBD | 5123000 | 5123000 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Lampton to Hale County 115kV Rebuild | TBD | Rebuild the existing Lampton to Hale Coutny 115kV 20.06 mile line to achieve a minimum summer/emergency rating of 98 MVA | SWPS | TBD | 30000 | 30000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Lawrence to Sioux Falls 115kV Rebuild | TBD | Rebuild the existing Lawrence to Sioux Falls 115kV 1.0 mile line to achieve a minimum winter/emergency rating of 295 MVA | WAPA | TBD | 92000 | 92000 | TRUE
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Litchfield to Asbury Plant 161kV Rebuild | TBD | Rebuild the existing Litchfield to Asbury Plant 161kV 6.8 mile line to achieve a minimum winter/emergency rating of 329 MVA | Evergy, EMDE | TBD | 16610000 | 16610000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Logan 230/115kV New Transformer CKT3 | TBD | Build a new 230/115kV transformer at Logan as a third circuit | BEPC | TBD | 6621188 | 6621188 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Longwood 345kV Reactive Support | TBD | Install a new 150 MVAR capacitor bank at Longwood 345kV Substation | AEPW | TBD | 12500000 | 12500000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Lydia 345kV Reactive Support | TBD | Install a new 300 MVAR capacitor bank at Lydia 345kV Substation | AEPW | TBD | 15000000 | 15000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Madison to Norfolk 115kV Rebuild | TBD | Rebuild the existing Madison to Norfolk 115kV 13.88 mile line to achieve a minimum summer/emergency rating of 164 MVA | NPPD | TBD | 500000 | 500000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Mark Moore 161kV Reactive Support | TBD | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | NPPD | TBD | 7232700 | 7232700 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Mark Moore to Elm Creek 345kV New Build | TBD | Build a new 102 mile 345kV line from Mark Moore to Elm Creek | NPPD, ITCGP, SUNC | TBD | 206200000 | 206200000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Martin to Wanblee 115kV Rebuild | TBD | Rebuild the existing Martin to Wanblee 115kV 20.86 mile line to achieve a minimum summer/emergency rating of 135 MVA | WAPA | TBD | 8800000 | 8800000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | McElroy to University 138kV Rebuild | TBD | Rebuild the existing McElroy to University 138kV 1.27 mile line to achieve a minimum summer/emergency rating of 246 MVA | OKGE | TBD | 1300000 | 1300000 | TRUE
Current Study | 07 - Southwestern Oklahoma | DISIS-2017-001-P1 | ERIS | Minco to Cimarron 345kV Rebuild | TBD | Rebuild the existing Minco to Cimarron 345kV 20.90 mile line to achieve a minimum winter/emergency rating of 1240 MVA | OKGE | TBD | 1682485 | 1682485 | TRUE
Current Study | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Mingo to Post Rock 345kV New Build | TBD | Build a new 100 mile 345kV line from Mingo to Post Rock | ITC GP, SUNC | TBD | 177500000 | 177500000 | TRUE
Current Study | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Moore to Monolith 345kV Rebuild | TBD | Rebuild the existing Moore to Monolith 345kV 0.75 mile line to achieve a minimum winter/emergency rating of 982 MVA | NPPD | TBD | 2000000 | 2000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Mt. Vernon to Storla 115kV Rebuild | TBD | Rebuild the existing Mt. Vernon to Storla 115kV 15.0 mile line to achieve a minimum summer/emergency rating of 128 MVA | WAPA, BEPC | TBD | 7700000 | 7700000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Mustang to SW 5th St. 138kV Rebuild | TBD | Rebuild the existing Mustang to SW 5th St. 138kV 6.75 mile line to achieve a minimum summer/emergency rating of 307 MVA | OKGE | TBD | 420000 | 420000 | TRUE
Current Study | 07 - Southwestern Oklahoma | DISIS-2017-001-P1 | ERIS | Naples Tap to Cornville Tap 138kV Rebuild | TBD | Rebuild the existing Naples Tap to Cornville Tap 138kV 11 mile line to achieve a minimum winter/emergency rating of 203 MVA | WFEC | TBD | 10605749 | 10605749 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Naples Tap to Payne 138kV Rebuild | TBD | Rebuild the existing Naples Tap to Payne 138kV 8.9 mile line to achieve a minimum summer/emergency rating of 185 MVA | WFEC | TBD | 8581015.1 | 8581015.1 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Nashua to Sibley 345kV New Build | TBD | Build a new 20 mile 345kV line from Nashua to Sidney to achieve a minimum normal/emergency rating of 1792 MVA | Evergy | TBD | 130000000 | 130000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Nashua to St. Joe 345kV Rebuild | TBD | Rebuild the existing Nashua to St. Joe 345kV 38.6 mile line to achieve a minimum winter/emergency rating of 1273 MVA | Evergy | TBD | 67550000 | 67550000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Neosho South to Tipton Ford 161kV Rebuild | TBD | Rebuild the existing Neosho South to Tipton Ford 161kV 10.6 mile line to achieve a minimum summer/emergency rating of 241 MVA | EMDE, SWPA | TBD | 16565000 | 16565000 | TRUE
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Neosho to Riverton 161kV Rebuild | TBD | Rebuild the existing Neosho to Riverton 161kV 28.4 mile line to achieve a minimum winter/normal rating of 324 MVA | Evergy, EMDE, | TBD | 47161402 | 47161402 | TRUE
Current Study | 16 - Western North Dakota | DISIS-2017-001-P1 | ERIS | Neset to Tioga 230kV Rebuild | TBD | Rebuild the existing Neset to Tioga 230kV 1 mile line to achieve a minimum summer/emergency rating of 712 MVA | BEPC, MDU, | TBD | 950000 | 950000 | TRUE
Current Study | 17 - Western South Dakota | DISIS-2017-001-P1 | ERIS | New Underwood 230kV Reactive Support | TBD | Install a new 75 MVAR capacitor bank at New Underwood 230kV Substation | WAPA | TBD | 6100000 | 6100000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | New Underwood to Wicksville 115kV Rebuild | TBD | Rebuild the existing New Underwood to Wicksville 115kV 12.42 mile line to achieve a minimum summer/emergency rating of 150 MVA | WAPA | TBD | 5500000 | 5500000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Northwest Texarkana 345kV Reactive Support | TBD | Install a 350 MVAR capacitor bank at Northwest Texarkana 345kV Substation | AEPW | TBD | 18500000 | 18500000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Northwest Texarkana to Wilkes 345kV New Build | TBD | Build a new 60 mile 345kV line from Northwest Texarkana to Wilkes | AEPW | TBD | 180000000 | 180000000 | TRUE
Current Study | 02 - Hitchland/07 - Southwestern Oklahoma | DISIS-2017-001-P1 | NRIS | Northwest to Matthewson 138kV Rebuild | TBD | Substation and terminal equipment upgrades requred at Northwest 345kV substation to achieve a minimum light/emergency rating of 1301 MVA | OKGE | TBD | 18427752 | 18427752 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Norton to Pleasant Hills 115kV Rebuild | TBD | Rebuild the existing Norton to Pleasant Hills 115kV 54.54 mile line to achieve a minimum spring/emergency rating of 150 MVA | SWPS | TBD | 150000 | 150000 | TRUE
Current Study | 01 - Woodward | DISIS-2017-001-P1 | ERIS | Okeene to G16-107-Tap 138kV Rebuild | TBD | Rebuild the existing Okeene to G16-107-Tap 138kV 16.975 mile line to achieve a minimum summer/normal rating of 170 MVA | WFEC | TBD | 16366599.025 | 16366599.025 | TRUE
Current Study | 08 - North Okahoma/South Central Kansas/12 - Northwest Arkansas | DISIS-2017-001-P1 | ERIS | Oronogo Jct. to Joplin Fir Road 161kV Rebuild | TBD | Rebuild the existing Oronogo Jct. to Fir Road 161kV 2.86 mile line to achieve a minimum winter/emergency rating of 312 MVA | EMDE | TBD | 4600000 | 4600000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Phillip to Wall 115kV Rebuild | TBD | Rebuild the existing Phillip to Wall 115kV 26.95 mile line to achieve a minimum summer/emergency rating of 137 MVA | WAPA | TBD | 12000000 | 12000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Phillip to Wanblee 115kV Rebuild | TBD | Rebuild the existing Phillip to Wanblee 115kV 40 mile line to achieve a minimum summer/emergency rating of 139 MVA | WAPA | TBD | 18400000 | 18400000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Pittsburg to Seminole 345kV Rebuild | TBD | Rebuild the existing Pittsburg to Seminole 345kV 51.27 mile line to achieve a minimum light/emergency rating of 1248 MVA | AEPW, OKGE | TBD | 61900000 | 61900000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Pittsburg to Valiant 345kV Rebuild | TBD | Rebuild the existing Pittsburg to Valiant 345kV 70.2 mile line to achieve a minimum winter/emergency rating of 1147 MVA | AEPW | TBD | 185000000 | 185000000 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Potter County 345/230kV New Transformer CKT 2 | TBD | Build a new 345/230kV transformer at Potter County to achieve a minimum rating of 559 MVA | SWPS | TBD | 12583632 | 12583632 | TRUE
Current Study | 02 - Hitchland/03 - Spearville/04 - Northwest Kansas/06 SoutjTexas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Potter County to Grapevine 345kV New Build | 122552 | Build a new 65 mile 345kV line from Potter County to Grapevine | SWPS | TBD | 92000000 | 92000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Raun to S3451 345kV Rebuild | TBD | Rebuild the existing Raun to S3451 345kV 64.16 mile line to achieve a minimum winter/emergency rating of 1536 MVA | OPPD | TBD | 77076185 | 77076185 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Raun to Tekamah 161kV Rebuild | TBD | Rebuild the existing Raun to Tekamah 37.07 mile line to achieve a minimum winter/emergency rating of 382 MVA | OPPD | TBD | 35216064 | 35216064 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Russett to Stirling 138kV Rebuild | TBD | Rebuild the existing Russett to Stirling 138kV 12.1 mile line to achieve a minimum winter/emergency rating of 190 MVA | OKGE | TBD | 5425000 | 5425000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Seminole to Cunningham 230kV New Build | TBD | Build a new 53 mile 230kV line from Seminole to Cunningham to achieve a minimum normal/emergency rating of 478/545 MVA | SWPS | TBD | 59754121 | 59754121 | TRUE
Current Study | 03 - Spearville | DISIS-2017-001-P1 | ERIS | Seward to Zook 69kV Rebuild | TBD | Rebuild the existing Seward to Zook 69kV 16.89 mile line to achieve a minimum winter/emergency rating of 51 MVA | MIDW | TBD | 15352148.61 | 15352148.61 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Shannon 230/115kV New Transformer | TBD | Build a new 230/115kV transformer at Shannon | BEPC | TBD | 17000000 | 17000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Shell Creek to Grand Island 345kV New Build | TBD | Build a new 72 mile 345kV line from Shell Creek to Grand Island | NPPD, WAPA | TBD | 166000000 | 166000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Shilder to Remington 138kV Rebuild | TBD | Rebuild the existing Shidler to Remington 138kV 5.0 mile line to achieve a minimum summer/emergency rating of 178 MVA | AEPW | TBD | 5070000 | 5070000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Sibley 161kV Reactive Support | TBD | Install a 100 MVAR capacitor bank at Sibley 161kV Substation | Evergy | TBD | 51000000 | 51000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Sidney to G16-034 Tap 345kV New Build CKT 2 | TBD | Build a new 345kV line from Sidney to G16-034 Tap as a second circuit | BEPC | TBD | 89700000 | 89700000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Sioux City 230kV Substation Upgrade | TBD | Upgrade terminal equipment at Sioux City 230kV to achieve a minimum rating of 700 MVA | WAPA | TBD | 6000000 | 6000000 | TRUE
Current Study | 03 - Spearville/09 - Nebraska | DISIS-2017-001-P1 | ERIS | Smoky Hill to Summit 230kV Rebuild | TBD | Rebuild the existing Smoky Hill to Summit 230kV 35.56 mile line to achieve a minimum light/normal rating of 388 MVA | MIDW | TBD | 45375000 | 45375000 | TRUE
Current Study | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | South Hays to Great Bend 230kV Rebuild | TBD | Rebuild the existing South Hays to Great Bend 230kV 39.2 mile line to achieve a minimum spring/normal rating of 336 MVA | MIDW, SUNC, | TBD | 34834000 | 34834000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Southwest Shreveport 345kV Reactive Support | TBD | Install a 150 MVAR capacitor bank at Southwest Shreveport 345kV Substation | AEPW | TBD | 12500000 | 12500000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Springfield to LaRussell Energy Center 161kV Rebuild | TBD | Rebuild the existing Springfield to LaRussell Energy Center 161kV 43.0 mile line to achieve a minimum summer/emergency rating of 201 MVA | SWPA, EMDE | TBD | 43010050 | 43010050 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Stanton to Beulah 115kV Rebuild | TBD | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | WAPA, BEPC, MDU | TBD | 9200000 | 9200000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Stanton to Pick City 115kV Rebuild | TBD | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | WAPA, BEPC | TBD | 3400000 | 3400000 | TRUE
Current Study | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Stegall 345kV Reactive Support | TBD | Install a new 150 MVAR capacitor bank at Stegall 345kV Substation | BEPC | TBD | 28000000 | 28000000 | TRUE
Current Study | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Stegall to GEN-2016-034 Tap New Build | TBD | Build a new 345kV 26 mile line from Stegall to GEN-2016-034 Tap | BEPC | TBD | 55800000 | 55800000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 1 | TBD | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | Evergy | TBD | 400000 | 400000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Stranger Creek to Iatan 345kV Rebuild CKT 2 | TBD | Rebuild the existing Stranger Creek to Iatan 345kV 18.0 mile line to achieve a minimum summer/emergency rating of 1271 MVA | Evergy | TBD | 26250000 | 26250000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Tekamah to S1226 161kV Rebuild | TBD | Rebuild the existing Tekamah to S1226 161kV 20.87 mile line to achieve a minimum winter/emergency rating of 429 MVA | OPPD | TBD | 20774998 | 20774998 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Tolk to Tuco 230kV Rebuild | TBD | Rebuild the existing Tolk to Tuco 230kV 54.58 mile line to achieve a minimum light/emergency rating of 555 MVA | SWPS | TBD | 49432000 | 49432000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Tonnece to Tontitown 345kV New Build | TBD | Build a new 18 mile 345kV line from Tonnece to Tontitown | AEPW, GRDA | TBD | 71100000 | 71100000 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | ERIS | Tuco to Crawfish Draw 345kV Rebuild | TBD | Rebuild the existing Tuco to Crawfish Draw 345kV 1.54 mile line to achieve a minimum light/emergency rating of 1392 MVA | SWPS | TBD | 800000 | 800000 | TRUE
Current Study | 06 - South Texas Panhandle/New Mexico | DISIS-2017-001-P1 | NRIS | Tupelo to Stonewall 138kV Rebuild | TBD | Rebuild the existing Tupelo to Stonewall 138kV 1.18 mile line to achieve a minimum light/emergency rating of 242 MVA | SWPA, WFEC | TBD | 1137707.62 | 1137707.62 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Utica Jct. to Napa Jct. 115kV Rebuild | TBD | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | WAPA, NWPS | TBD | 9455000 | 9455000 | TRUE
Current Study | 01 - Woodward/02 - Hitchland/06 - South Texas Panhandle/New Mexico/07 - Southwestern Oklahoma/10 - Southeast Oklahoma/Northeast Texas/12 - Northwest Arkansas/14 - South Central Oklahoma | DISIS-2017-001-P1 | NRIS | Valiant to Huge 138kV Rebuild | TBD | Rebuild the existing Valiant to Huge 138kV 138kV 17.81 mile line to achieve a minimum light/emergency rating of 442 MVA | AEPW | TBD | 35000000 | 35000000 | TRUE
Current Study | 14 - South Central Oklahoma | DISIS-2017-001-P1 | ERIS | Valiant to Hugo 138kV Rebuild | TBD | Rebuild the existing 138kV 17.81 mile line from Valiant to Hugo to achieve a minimum normal/emergency rating of 325 MVA | AEPW, WFEC | TBD | 17715217 | 17715217 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Valiant to Lydia 345kV New Build CKT 2 | TBD | Build a new 43 mile 345kV line from Valiant to Lydia as a second circuit | AEPW | TBD | 137500000 | 137500000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Valiant to Petersburg 345kV New Build CKT 2 | TBD | Build a new 70.2 mile 345kV line from Valiant to Petersburg as a second circuit | AEPW | TBD | 225000000 | 225000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Valiant to Turk 345kV New Build | TBD | Build a new 84 mile 345kV line from Valiant to Turk | AEPW | TBD | 280000000 | 280000000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Victory Hill 230kV Reactive Support | TBD | Insall a 15 MVAR capacitor bank at Victory Hill 230kV Substation | NPPD | TBD | 284145 | 284145 | TRUE
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Viola 345/138kV New Transformer CKT 2 | TBD | Build a new 345/138kV transformer as a second circuit | Evergy | TBD | 8302968 | 8302968 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Wall to Wicksville 115kV Rebuild | TBD | Rebuild the existing Wall to Wicksville 115kV 18.29 mile line to achieve a minimum summer/emergency rating of 145 MVA | WAPA | TBD | 8115000 | 8115000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Watertown to Appledorn 230kV Rebuild | TBD | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | WAPA | TBD | 3600000 | 3600000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Wayside to Shannon 230kV New Build | TBD | Build a new 54 mile line from Wayside to Shannon 230kV to achieve a minimum normal/emergency rating of 319/341 MVA | NPPD | TBD | 62515044 | 62515044 | TRUE
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | West Pawhuska to Shidler 138kV Rebuild | TBD | Rebuild the existing West Pawhuska to Shidler 138kV 16.11 mile line to achieve a minimum winter/emergency rating of 246 MVA | AEPW | TBD | 20239443 | 20239443 | TRUE
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | West Pawhuska to Western Walls 138kV Rebuild | TBD | Rebuild the existing West Pawhuska to Western Walls 138kV 5.98 mile line to achieve a minimum spring/emergency rating of 244 MVA | AEPW | TBD | 10183861 | 10183861 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Wichita to Benton 345kV New Build CKT 2 | TBD | Build a new 17 mile 345kV line from Wichita to Benton as a second circuit | Evergy | TBD | 25493115 | 25493115 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Wichita to Benton 345kV Rebuild | TBD | Rebuild the existing Wichita to Benton 345kV 19.76 mile line to achieve a minimum winter/emergency rating of 1203 MVA | Evergy | TBD | 33250000 | 33250000 | TRUE
Current Study | NRIS (Multiple) | DISIS-2017-001-P1 | NRIS | Wilkes to Diana 345kV New Build | TBD | Build a new 12.5 mile 345kV line from Wilkes to Diana | AEPW | TBD | 67500000 | 67500000 | TRUE
Current Study | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 | ERIS | Wolf Creek to West Gardner 345kV New Build | TBD | Build a new 345kV line from Wolf Creek to West Gardner to achieve a summer/emergency rating of 1792 MVA | Evergy | TBD | 127250000 | 127250000 | TRUE
Contingent | 09 - Nebraska | DISIS-2017-001-P1 | ERIS | Seneca to Bailyville to Smittyville to Marshall County 115kV CKT 1 Rebuild | TBD | NTC 210542 | Evergy | TBD | 14861868.53 | 0 | FALSE
Contingent | 06 - South Texas Panhandle/New Mexico/08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 |  | Tolk 345/230kV Transformer CKT 2 | 122568 | Install a new 345/230kV transformer at Tolk substation | SWPS | TBD | 14055360 | 0 | FALSE
Contingent | 08 - North Oklahoma/South Central Kansas | DISIS-2017-001-P1 |  | Wolf Creek to Blackberry 345kV |  | Build a new 86 mile 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC: 210540) | Evergy | TBD | 142601178 | 0 | FALSE
Contingent | 04 - Northwest Kansas/09 - Nebraska/15 - Eastern South Dakota/16 - Western North Dakota/17 - Western South Dakota | DISIS-2017-001-P1 |  | NTC 200220 (Rplan) |  | Build new 222 mile, 345 kV line from Gentleman - Cherry Co - Holt Co. Build new 345 kV substations at Cherry Co and Holt Co. Terminal upgrades at Gentleman. | NPPD | 40 | 412074343 | 0 | FALSE

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05211 | 199.77 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.0311 | 199.77 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.77 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.77 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05536 | 199.77 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05211 | 199.77 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.0311 | 199.77 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.77 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.77 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05536 | 199.77 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05211 | 199.77 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.0311 | 199.77 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.77 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.77 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05536 | 199.77 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05211 | 199.61 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.0311 | 199.61 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.61 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.61 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05536 | 199.61 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05211 | 199.61 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.0311 | 199.61 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.61 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.61 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05536 | 199.61 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05211 | 199.61 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.0311 | 199.61 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.61 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.61 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05536 | 199.61 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05211 | 199.61 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.0311 | 199.61 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.61 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.61 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05536 | 199.61 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05211 | 199.61 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.0311 | 199.61 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.61 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.61 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05536 | 199.61 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05211 | 199.61 | P23:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.0311 | 199.61 | P23:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.61 | P23:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 1 | 199.61 | P23:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.05536 | 199.61 | P23:345:OPPD:S3451-RAUN
Thermal | 15NR | 2 | 20G | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.03287 | 188.58 | P23:345:MEC:RAUN 0270
Thermal | 00NR | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.04079 | 186.79 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.04079 | 186.79 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.04079 | 186.79 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.04079 | 186.79 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.27643 | 181.66 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.27643 | 181.66 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.3328 | 181.66 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20182 | 181.66 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.0323 | 175.78 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.03132 | 175.78 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.05272 | 175.78 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.0681 | 175.78 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.07364 | 175.78 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.03837 | 175.78 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.11888 | 175.78 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.05516 | 175.78 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.07711 | 175.78 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.03929 | 175.78 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.0323 | 175.78 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.03132 | 175.78 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.05272 | 175.78 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.0681 | 175.78 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.07364 | 175.78 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.03837 | 175.78 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.11888 | 175.78 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.05516 | 175.78 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.07711 | 175.78 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.03929 | 175.78 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.0323 | 175.78 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.03132 | 175.78 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.05272 | 175.78 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.0681 | 175.78 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.07364 | 175.78 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.03837 | 175.78 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.11888 | 175.78 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.05516 | 175.78 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.07711 | 175.78 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.03929 | 175.78 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.0323 | 175.78 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.03132 | 175.78 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.05272 | 175.78 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.0681 | 175.78 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.07364 | 175.78 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.03837 | 175.78 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.11888 | 175.78 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.05516 | 175.78 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.07711 | 175.78 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.03929 | 175.78 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.0323 | 175.78 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.03132 | 175.78 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.05272 | 175.78 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.0681 | 175.78 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.07364 | 175.78 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.03837 | 175.78 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.11888 | 175.78 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.05516 | 175.78 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.07711 | 175.78 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.03929 | 175.78 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.27643 | 175.74 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.27643 | 175.74 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.3328 | 175.74 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20182 | 175.74 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05026 | 167.31 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.31 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.31 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05026 | 167.31 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.31 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.31 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05026 | 167.31 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.31 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.31 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05026 | 167.31 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.31 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.31 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05026 | 167.31 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.31 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.31 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05026 | 167.31 | P23:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.31 | P23:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.31 | P23:345:OPPD:S3451-RAUN
Thermal | 09ALL | 2 | 20G | GEN-2017-031 | 'FROM -> TO' | B.SPRGS7 - BRULE 7 115 |  | 109 | 0.50455 | 167.21 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.04975 | 167.04 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.04 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.04 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.04975 | 167.04 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.04 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 1 | 167.04 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.27439 | 163.57 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.27439 | 163.57 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.33752 | 163.57 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.0323 | 163.45 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.0527 | 163.45 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05272 | 163.45 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.0681 | 163.45 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.07364 | 163.45 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.03837 | 163.45 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.11888 | 163.45 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05516 | 163.45 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.07711 | 163.45 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.03929 | 163.45 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.0323 | 163.45 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.0527 | 163.45 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05272 | 163.45 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.0681 | 163.45 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.07364 | 163.45 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.03837 | 163.45 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.11888 | 163.45 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05516 | 163.45 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.07711 | 163.45 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.03929 | 163.45 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.0323 | 163.45 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.0527 | 163.45 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05272 | 163.45 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.0681 | 163.45 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.07364 | 163.45 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.03837 | 163.45 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.11888 | 163.45 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05516 | 163.45 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.07711 | 163.45 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.03929 | 163.45 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.0323 | 163.45 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.0527 | 163.45 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05272 | 163.45 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.0681 | 163.45 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.07364 | 163.45 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.03837 | 163.45 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.11888 | 163.45 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05516 | 163.45 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.07711 | 163.45 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.03929 | 163.45 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.0323 | 163.45 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.0527 | 163.45 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05272 | 163.45 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.0681 | 163.45 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.07364 | 163.45 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.03837 | 163.45 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.11888 | 163.45 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05516 | 163.45 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.07711 | 163.45 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.03929 | 163.45 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.03635 | 163.43 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.03635 | 163.43 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.03635 | 163.43 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.03635 | 163.43 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.03635 | 162.6 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.03635 | 162.6 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.03635 | 162.6 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.03635 | 162.6 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 06ALL | 2 | 19WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.35636 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.35636 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.26671 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.32722 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.28363 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.31974 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.31514 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.2558 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.29058 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.28738 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.295 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.29834 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.38045 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.28738 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.26458 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.295 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.21355 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.2551 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.28778 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.28121 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.31373 | 162.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 09ALL | 2 | 19WP | GEN-2017-031 | 'FROM -> TO' | B.SPRGS7 - BRULE 7 115 |  | 109 | 0.50416 | 161.59 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.26137 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.26137 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.17435 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.13483 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.12207 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.08609 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.05023 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.1457 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.09968 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.10142 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.10081 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.11012 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.10317 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.33265 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.10081 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.15116 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.11012 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.1331 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.15306 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.10045 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.1615 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.03683 | 160.99 | System Intact
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.27439 | 160.88 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.27439 | 160.88 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.33752 | 160.88 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.25904 | 160.63 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 1 | 160.63 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 1 | 160.63 | P42:345:NPPD:BKR-HOS-3308
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.26137 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.26137 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.17435 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.13483 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.12207 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.08609 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.05023 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.1457 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.09968 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.10142 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.10081 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.11012 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.10317 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.33265 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.10081 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.15116 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.11012 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.1331 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.15306 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.10045 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.1615 | 159.57 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.03683 | 159.57 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.19802 | 159.45 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 1 | 159.45 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 1 | 159.45 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.19991 | 158.61 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 1 | 158.61 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 1 | 158.61 | P42:345:NPPD:BKR-HOS-3322
Thermal | 09ALL | 2 | 24WP | GEN-2017-031 | 'FROM -> TO' | B.SPRGS7 - BRULE 7 115 |  | 109 | 0.5057 | 157.96 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.2409 | 157.95 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.2409 | 157.95 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.29002 | 157.95 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.05561 | 157.88 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.07562 | 157.88 | System Intact
Thermal | 09ALL | 2 | 20SP | GEN-2016-034 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.54389 | 156.77 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20SP | GEN-2016-093 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.48961 | 156.77 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20SP | GEN-2017-031 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24038 | 156.77 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20SP | GEN-2017-037 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.48961 | 156.77 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20SP | GEN-2016-034 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.53784 | 155.79 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2016-093 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.48387 | 155.79 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2017-031 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.23269 | 155.79 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2017-037 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.48387 | 155.79 | P42:345:NPPD:BKR-KEY-3310
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.05512 | 155.11 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.07512 | 155.11 | System Intact
Thermal | 06ALL | 2 | 19WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.35636 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.35636 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.26671 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.32722 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.28363 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.31974 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.31514 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.2558 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.29058 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.28738 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.295 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.29834 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.38045 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.28738 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.26458 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.295 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.21355 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.2551 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.28778 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.28121 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.31373 | 154.87 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.0323 | 154.54 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.20994 | 154.54 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.05272 | 154.54 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.0681 | 154.54 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.07364 | 154.54 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.03837 | 154.54 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.11888 | 154.54 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.05516 | 154.54 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.07711 | 154.54 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.03929 | 154.54 | P42:345:NPPD:BKR-SC-3306
Thermal | 09ALL | 2 | 20G | GEN-2016-034 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.54494 | 153.93 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20G | GEN-2016-093 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.49066 | 153.93 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20G | GEN-2017-031 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24144 | 153.93 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20G | GEN-2017-037 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.49066 | 153.93 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.07615 | 153.79 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.07498 | 153.79 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.10752 | 153.79 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.07243 | 153.79 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-094 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.09134 | 153.79 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.0761 | 153.79 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.07615 | 153.79 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.07498 | 153.79 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.10752 | 153.79 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.07243 | 153.79 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-094 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.09134 | 153.79 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.0761 | 153.79 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.07615 | 153.79 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.07498 | 153.79 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.10752 | 153.79 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.07243 | 153.79 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-094 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.09134 | 153.79 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.0761 | 153.79 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.07615 | 153.79 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.07498 | 153.79 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.10752 | 153.79 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.07243 | 153.79 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-094 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.09134 | 153.79 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.0761 | 153.79 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.07615 | 153.79 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.07498 | 153.79 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.10752 | 153.79 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.07243 | 153.79 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-094 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.09134 | 153.79 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z |  | 341 | 0.0761 | 153.79 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 09ALL | 2 | 24SP | GEN-2016-034 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.54747 | 153.79 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24SP | GEN-2016-093 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.49276 | 153.79 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24SP | GEN-2017-031 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24445 | 153.79 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24SP | GEN-2017-037 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.49276 | 153.79 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.0323 | 153.43 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.21201 | 153.43 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.05272 | 153.43 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.0681 | 153.43 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.07364 | 153.43 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.03837 | 153.43 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.11888 | 153.43 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.05516 | 153.43 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.07711 | 153.43 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 |  | 956 | 0.03929 | 153.43 | P42:345:NPPD:BKR-HOS-3322
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.2409 | 153.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.2409 | 153.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.29002 | 153.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | ASB349 5 - CJ 366 5 161 |  | 223 | 0.31557 | 153.21 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | ASB349 5 - LITCH 5 161 |  | 223 | 0.31557 | 153.21 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 09ALL | 2 | 19WP | GEN-2016-034 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.54413 | 153.03 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 19WP | GEN-2016-093 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.48985 | 153.03 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 19WP | GEN-2017-031 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24062 | 153.03 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 19WP | GEN-2017-037 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.48985 | 153.03 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24SP | GEN-2016-034 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.54124 | 152.85 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24SP | GEN-2016-093 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.48685 | 152.85 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24SP | GEN-2017-031 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.23644 | 152.85 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24SP | GEN-2017-037 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.48685 | 152.85 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2016-034 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.53803 | 152.23 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2016-093 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.48406 | 152.23 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2017-031 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.23288 | 152.23 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2017-037 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.48406 | 152.23 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 29SP | GEN-2016-034 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.54757 | 151.77 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 29SP | GEN-2016-093 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.49285 | 151.77 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 29SP | GEN-2017-031 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24454 | 151.77 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 29SP | GEN-2017-037 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.49285 | 151.77 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 152 | 0.2516 | 151.76 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 152 | 0.2516 | 151.76 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | ASB349 5 - CJ 366 5 161 |  | 223 | 0.31523 | 151.35 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | ASB349 5 - LITCH 5 161 |  | 223 | 0.31523 | 151.35 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04384 | 150.79 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04384 | 150.79 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04384 | 150.79 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 09ALL | 2 | 24WP | GEN-2016-034 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.5479 | 150.62 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24WP | GEN-2016-093 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.49319 | 150.62 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24WP | GEN-2017-031 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24488 | 150.62 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24WP | GEN-2017-037 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.49319 | 150.62 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 29SP | GEN-2016-034 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.54133 | 150.59 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 29SP | GEN-2016-093 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.48694 | 150.59 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 29SP | GEN-2017-031 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.23653 | 150.59 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 29SP | GEN-2017-037 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.48694 | 150.59 | P42:345:NPPD:BKR-KEY-3310
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 152 | 0.2516 | 150.57 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 152 | 0.2516 | 150.57 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 09ALL | 2 | 20G | GEN-2017-031 | 'FROM -> TO' | BRULE 7 - OGALALA_-TS7115 |  | 120 | 0.50455 | 150.52 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05054 | 150.4 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.05054 | 150.4 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 152 | 0.25126 | 150.26 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 152 | 0.25126 | 150.26 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 09ALL | 2 | 24WP | GEN-2016-034 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.5416 | 149.76 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24WP | GEN-2016-093 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.48721 | 149.76 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24WP | GEN-2017-031 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.2368 | 149.76 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24WP | GEN-2017-037 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.48721 | 149.76 | P42:345:NPPD:BKR-KEY-3310
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.05425 | 149.53 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-022 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.07426 | 149.53 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 152 | 0.25126 | 148.99 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 152 | 0.25126 | 148.99 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.3282 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.3282 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.25134 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.22418 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.23729 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.23313 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.23014 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.22895 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.24465 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.23162 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.38457 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.22895 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.2402 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.24465 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.20395 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.23614 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.22886 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.25359 | 148.58 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 09ALL | 2 | 20SP | GEN-2017-031 | 'FROM -> TO' | B.SPRGS7 - BRULE 7 115 |  | 109 | 0.5041 | 148.34 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.03748 | 148.32 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | ASB349 5 - PUR421 5 161 |  | 223 | 0.29249 | 147.48 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04759 | 146.21 | P12:161:EES-EAI:GRANVW:EUREKASP:1
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04759 | 146.21 | P12:161:EES-EAI-AEPW:5GDVIEW:EUREKA5
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04759 | 146.21 | P12:HV:EES::5GRANDVIEW%:EUREKA 5!:1
Thermal | 09ALL | 2 | 24L | GEN-2016-109 | 'FROM -> TO' | BEATRCE7 - HARBINE7 115 |  | 99 | 0.57792 | 145.43 | P12:115:WERE:KNOB-NPPD_115::
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 152 | 0.25187 | 145.2 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.3282 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.3282 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.25134 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.22418 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.23729 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.23313 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.23014 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.22895 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.24465 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.23162 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.38457 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.22895 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.2402 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.24465 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.20395 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.23614 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.22886 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.25359 | 145.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | ASB349 5 - PUR421 5 161 |  | 223 | 0.29219 | 145.1 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 16NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.08568 | 145.08 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 16NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.20801 | 145.08 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 16NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.13079 | 145.08 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03936 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03919 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.05468 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.07912 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03373 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.04146 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03006 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.065 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.08082 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.07991 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.08464 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.11586 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.04138 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.05441 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.11586 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.11586 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.49605 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.07887 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.04138 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.33445 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.05868 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03907 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03103 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03036 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03135 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.11586 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.0481 | 144.98 | P23:345:WERE:87TH_345_BKRS::
Thermal | 09ALL | 2 | 24SP | GEN-2017-031 | 'FROM -> TO' | B.SPRGS7 - BRULE 7 115 |  | 109 | 0.50557 | 144.51 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.11618 | 144.44 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.11618 | 144.44 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.11618 | 144.44 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.11618 | 144.44 | P23:345:WERE:87TH_345_BKRS::
Thermal | 16NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.08466 | 144.05 | P42:345:NPPD:BKR-KEY-3310
Thermal | 16NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.20561 | 144.05 | P42:345:NPPD:BKR-KEY-3310
Thermal | 16NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.12926 | 144.05 | P42:345:NPPD:BKR-KEY-3310
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 152 | 0.25187 | 144 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 152 | 0.25156 | 143.61 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.31936 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.31936 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24248 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.21548 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22838 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22423 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22123 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22005 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23576 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22272 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.37567 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22005 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23126 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23576 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22725 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.21996 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24458 | 143.12 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 08ALL | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 152 | 0.25235 | 142.96 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 152 | 0.25235 | 142.96 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0323 | 142.9 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.24635 | 142.9 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.21069 | 142.9 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05272 | 142.9 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0681 | 142.9 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07112 | 142.9 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.2589 | 142.9 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11888 | 142.9 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.2589 | 142.9 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.1939 | 142.9 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11642 | 142.9 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18973 | 142.9 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.19591 | 142.9 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07711 | 142.9 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0323 | 142.9 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.24635 | 142.9 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.21069 | 142.9 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05272 | 142.9 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0681 | 142.9 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07112 | 142.9 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.2589 | 142.9 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11888 | 142.9 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.2589 | 142.9 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.1939 | 142.9 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11642 | 142.9 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18973 | 142.9 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.19591 | 142.9 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07711 | 142.9 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.03166 | 142.75 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.03105 | 142.75 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.03105 | 142.75 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.03166 | 142.75 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.03105 | 142.75 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.03105 | 142.75 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03936 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.05491 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.07673 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.07912 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03373 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03006 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.065 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.08082 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.07991 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.04138 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.05441 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.07887 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.04138 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.33445 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03907 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03103 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03036 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03135 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.0481 | 142.46 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.12051 | 142.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.12051 | 142.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.12051 | 142.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.12051 | 142.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 152 | 0.25156 | 142.35 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.23912 | 142.31 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.23912 | 142.31 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.29414 | 142.31 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | BV-COM-4 - MOUNDRD4 138 1 | 106 |  | 0.17854 | 142.2 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.26625 | 142.15 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.23008 | 142.15 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 152 | 0.2516 | 142.07 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 152 | 0.2516 | 142.07 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 09ALL | 2 | 19WP | GEN-2017-031 | 'FROM -> TO' | BRULE 7 - OGALALA_-TS7115 |  | 120 | 0.50416 | 141.75 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 06ALL | 2 | 19WP | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 |  | 559 | 0.26625 | 141.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 19WP | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 |  | 559 | 0.23008 | 141.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 08ALL | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 152 | 0.25235 | 141.64 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 152 | 0.25235 | 141.64 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.08568 | 141.64 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.20801 | 141.64 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.1308 | 141.64 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0323 | 141.46 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.24542 | 141.46 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20944 | 141.46 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05272 | 141.46 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0681 | 141.46 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07158 | 141.46 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.25808 | 141.46 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11888 | 141.46 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.25808 | 141.46 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.1925 | 141.46 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.1174 | 141.46 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18831 | 141.46 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.19452 | 141.46 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07711 | 141.46 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0323 | 141.46 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.24542 | 141.46 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20944 | 141.46 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05272 | 141.46 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0681 | 141.46 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07158 | 141.46 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.25808 | 141.46 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11888 | 141.46 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.25808 | 141.46 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.1925 | 141.46 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.1174 | 141.46 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18831 | 141.46 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.19452 | 141.46 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07711 | 141.46 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.10403 | 141.18 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.10403 | 141.18 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.10403 | 141.18 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.10403 | 141.18 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0323 | 141.04 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.24543 | 141.04 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20947 | 141.04 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05272 | 141.04 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0681 | 141.04 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07171 | 141.04 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.25808 | 141.04 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11888 | 141.04 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.25808 | 141.04 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.19254 | 141.04 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11742 | 141.04 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18833 | 141.04 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.19456 | 141.04 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07711 | 141.04 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 06ALL | 2 | 19WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.31056 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.31056 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.23243 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.28516 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.24718 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.27864 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.27463 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.22292 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.25323 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.25044 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.25708 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.25999 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.33155 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.25044 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.23057 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.25708 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.22231 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.25079 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.24506 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.2734 | 141.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 09ALL | 2 | 29SP | GEN-2017-031 | 'FROM -> TO' | B.SPRGS7 - BRULE 7 115 |  | 109 | 0.5056 | 140.79 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.12822 | 140.67 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 1 | 140.67 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 1 | 140.67 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0323 | 140.62 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.24423 | 140.62 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20837 | 140.62 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05272 | 140.62 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0681 | 140.62 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07151 | 140.62 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.25685 | 140.62 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11888 | 140.62 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.25685 | 140.62 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.19148 | 140.62 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11711 | 140.62 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18729 | 140.62 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.1935 | 140.62 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07711 | 140.62 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0323 | 140.62 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.24423 | 140.62 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20837 | 140.62 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05272 | 140.62 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0681 | 140.62 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07151 | 140.62 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.25685 | 140.62 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11888 | 140.62 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.25685 | 140.62 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.19148 | 140.62 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11711 | 140.62 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18729 | 140.62 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.1935 | 140.62 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07711 | 140.62 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 16ALL | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | NESET___-BE4 - TIOGA4 4 230 |  | 506 | 0.88904 | 140.58 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | NESET___-BE4 - TIOGA4 4 230 |  | 506 | 0.88904 | 140.58 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 152 | 0.25126 | 140.43 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 152 | 0.25126 | 140.43 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.08466 | 140.39 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.20561 | 140.39 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.12927 | 140.39 | P42:345:NPPD:BKR-KEY-3310
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.23912 | 140.28 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.23912 | 140.28 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.29414 | 140.28 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.22777 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.22777 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.15194 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.1175 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.10638 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.07503 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.04378 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.12697 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.08687 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.08838 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.08785 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.09596 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.08991 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.2899 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.08785 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.13173 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.09596 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.11599 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.13338 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.08754 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.14074 | 140.09 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.0321 | 140.09 | System Intact
Thermal | 16ALL | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | NESET___-BE4 - TIOGA4 4 230 |  | 506 | 0.88905 | 139.86 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | NESET___-BE4 - TIOGA4 4 230 |  | 506 | 0.88905 | 139.86 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 16ALL | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | NESET___-BE4 - TIOGA4 4 230 |  | 506 | 0.88908 | 139.66 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | NESET___-BE4 - TIOGA4 4 230 |  | 506 | 0.88908 | 139.66 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | ORO110 5 - FIR417 5 161 |  | 223 | 0.31523 | 139.63 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | BV-COM-4 - MOUNDRD4 138 1 | 106 |  | 0.17828 | 139.54 | System Intact
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.29509 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.29509 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.20102 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.28474 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.22623 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.28637 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.28876 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.23696 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.23319 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.2387 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.24624 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.31123 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.23319 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.20124 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.2387 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.23373 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.21895 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.28991 | 139.51 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.05499 | 139.43 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.0625 | 139.43 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.0567 | 139.43 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.06423 | 139.43 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.05548 | 139.43 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.06655 | 139.43 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.05499 | 139.43 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.0625 | 139.43 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.0567 | 139.43 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.06423 | 139.43 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.05548 | 139.43 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.06655 | 139.43 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 16ALL | 2 | 24L | GEN-2017-048 | 'FROM -> TO' | NESET___-BE4 - TIOGA4 4 230 |  | 506 | 0.889 | 139.33 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 24L | GEN-2017-048 | 'FROM -> TO' | NESET___-BE4 - TIOGA4 4 230 |  | 506 | 0.889 | 139.33 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.31936 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.31936 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24248 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.21548 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22838 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22423 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22123 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22005 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23576 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22272 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.37567 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22005 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23126 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23576 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22725 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.21996 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24458 | 139.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.22777 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.22777 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.15194 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.1175 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.10638 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.07503 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.04378 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.12697 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.08687 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.08838 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.08785 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.09596 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.08991 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.2899 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.08785 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.13173 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.09596 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.11599 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.13338 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.08754 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.14074 | 139.08 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.0321 | 139.08 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.05211 | 139 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.03139 | 139 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 1 | 139 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 1 | 139 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.05536 | 139 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | MTVERN 7 - STORLA__-BE7 115 1 |  | 92 | 0.0341 | 138.85 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.72587 | 138.63 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.72587 | 138.61 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04848 | 138.5 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 06NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.03249 | 138.5 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05634 | 138.5 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05634 | 138.5 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 00NR | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.05499 | 138.46 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.0625 | 138.46 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.0567 | 138.46 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.06423 | 138.46 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.05548 | 138.46 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.06655 | 138.46 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.05499 | 138.46 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.0625 | 138.46 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.0567 | 138.46 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.06423 | 138.46 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.05548 | 138.46 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.06655 | 138.46 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 09ALL | 2 | 24WP | GEN-2017-031 | 'FROM -> TO' | BRULE 7 - OGALALA_-TS7115 |  | 120 | 0.5057 | 138.24 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 152 | 0.2516 | 138.21 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 152 | 0.2516 | 138.21 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 16ALL | 2 | 20G | GEN-2017-048 | 'FROM -> TO' | NESET___-BE4 - TIOGA4 4 230 |  | 506 | 0.88894 | 138.07 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 20G | GEN-2017-048 | 'FROM -> TO' | NESET___-BE4 - TIOGA4 4 230 |  | 506 | 0.88894 | 138.07 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | BV-COM-4 - MOUNDRD4 138 1 |  | 131 | 0.24194 | 137.89 | P12:138:GRDA:FAIRFAX-PAWNSW
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | ORO110 5 - FIR417 5 161 |  | 223 | 0.31557 | 137.63 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 01ALL | 2 | 24SP | GEN-2016-107 | 'FROM -> TO' | DOVERSW4 - OKEENE 4 138 |  | 83 | 0.36851 | 137.4 | P12:138:WFEC:OKEENE_WATONGA:2024+
Thermal | 01ALL | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | DOVERSW4 - OKEENE 4 138 |  | 83 | 0.36811 | 137.22 | P12:138:WFEC:OKEENE_WATONGA:2024+
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | CARTHAG5 - CAR395 5 161 |  | 222 | 0.29219 | 137.08 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.03936 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.05999 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.07912 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.03373 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.0675 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.08082 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.07991 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.04138 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.05441 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.06171 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.06923 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.04138 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.33445 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.03103 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.03036 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.03135 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.06048 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.07155 | 137.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.03936 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.05999 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.07912 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.03373 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.0675 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.08082 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.07991 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.04138 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.05441 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.06171 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.06923 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.04138 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.33445 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.03103 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.03036 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.03135 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.06048 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.07155 | 137.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.73054 | 136.7 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.73054 | 136.65 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.08325 | 136.52 | P42:345:NPPD:BKR-HOS-3308
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 152 | 0.25126 | 136.47 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 152 | 0.25126 | 136.47 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.03443 | 136.44 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.03443 | 136.44 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.03443 | 136.44 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.03443 | 136.44 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.0323 | 136.16 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.13561 | 136.16 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.05272 | 136.16 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.0681 | 136.16 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.07364 | 136.16 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.03837 | 136.16 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.11888 | 136.16 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.05516 | 136.16 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.07711 | 136.16 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.03929 | 136.16 | System Intact
Thermal | 06ALL | 2 | 24WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.31916 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.31916 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.24408 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.21935 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.22382 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.20406 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.20386 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.22744 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.21209 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.38229 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.20386 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.2304 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.22744 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.22788 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.20346 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.24286 | 136.15 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | CARTHAG5 - CAR395 5 161 |  | 222 | 0.29249 | 136.12 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.33247 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.33247 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.25562 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22845 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24156 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.2374 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23441 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23322 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24892 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23589 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.38884 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23322 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24448 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24892 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20822 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24041 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23313 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.25786 | 136.1 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.03936 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.05999 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.07912 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.03373 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.0675 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.08082 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.07991 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.04138 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.05441 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.06171 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.06923 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.04138 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.33445 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.03907 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.03103 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.03036 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.03135 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.06048 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.07155 | 136.08 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.03936 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.05999 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.07912 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.03373 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.0675 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.08082 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.07991 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.04138 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.05441 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.06171 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.06923 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.04138 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.33445 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.03907 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.03103 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.03036 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.03135 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.06048 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.07155 | 136.08 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.03919 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.05468 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.07912 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.04146 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.03006 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.065 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.08082 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.07991 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.08464 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.0343 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.05441 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.0343 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.0343 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.49605 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.07887 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.33445 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.05868 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.03907 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.0343 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.0481 | 136.06 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 08ALL | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 152 | 0.25262 | 136.01 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.30147 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.30147 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.21446 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.17493 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.16218 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.1262 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.09034 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.1858 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.13978 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.14152 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.14092 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.15022 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.14327 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.37276 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.14092 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.19126 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.15022 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.17321 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.19316 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.14055 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.2016 | 135.99 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.07693 | 135.99 | System Intact
Thermal | 06ALL | 2 | 19WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.33538 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.33538 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.25142 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.26251 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.24292 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.23474 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.23536 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.23221 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.23121 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.25493 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.25105 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.37814 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.23121 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.24291 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.25493 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.20229 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.2373 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.23094 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 699 | 0.2572 | 135.87 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.72712 | 135.63 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 152 | 0.25187 | 135.53 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 19WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.31056 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.31056 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.23243 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.28516 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.24718 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.27864 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.27463 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.22292 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.25323 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.25044 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.25708 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.25999 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.33155 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.25044 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.23057 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.25708 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.22231 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.25079 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.24506 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.2734 | 135.26 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.30147 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.30147 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.21446 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.17493 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.16218 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.1262 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.09034 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.1858 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.13978 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.14152 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.14092 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.15022 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.14327 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.37276 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.14092 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.19126 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.15022 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.17321 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.19316 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.14055 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.2016 | 135.12 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.07693 | 135.12 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2016-109 | 'FROM -> TO' | FAIRBRY7 - HARBINE7115 |  | 99 | 0.62615 | 134.93 | P42:345:NPPD:BKR-MOR-3306
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.08461 | 134.84 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 1 | 134.84 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 1 | 134.84 | P42:345:NPPD:BKR-HOS-3308
Thermal | 06ALL | 2 | 24WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.31916 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.31916 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.24408 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.21935 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.22382 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.20406 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.20386 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.22744 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.21209 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.38229 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.20386 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.2304 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.22744 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.22788 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.20346 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.24286 | 134.75 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.03443 | 134.69 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.03443 | 134.69 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.03443 | 134.69 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.03443 | 134.69 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.03919 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.05468 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.07912 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.04146 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.03006 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.065 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.08082 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.07991 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.08464 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.0343 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.05441 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.0343 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.0343 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.49605 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.07887 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.33445 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.05868 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.03907 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.0343 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.0481 | 134.25 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08667 | 134.09 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08667 | 134.09 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08667 | 134.09 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08667 | 134.09 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.13728 | 134.06 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2016-173 | 'FROM -> TO' | KILDARE4 - WHEAGLE4 138 1 |  | 222 | 0.26217 | 134 | P42:345:OKGE:SB_WONG7383
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.72785 | 134 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.72785 | 133.97 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 08ALL | 2 | 24L | GEN-2016-173 | 'FROM -> TO' | KILDARE4 - WHEAGLE4 138 1 |  | 222 | 0.26311 | 133.88 | P12:345:OKGE:BKRBKR400
Thermal | 08ALL | 2 | 24L | GEN-2016-173 | 'FROM -> TO' | KILDARE4 - WHEAGLE4 138 1 |  | 222 | 0.26311 | 133.88 | P42:345:OKGE:SB_WONG7313
Thermal | 01ALL | 2 | 20SP | GEN-2016-107 | 'FROM -> TO' | DOVERSW4 - OKEENE 4 138 |  | 83 | 0.36748 | 133.82 | P12:138:WFEC:OKEENE_WATONGA:2024+
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 152 | 0.25156 | 133.81 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.72385 | 133.51 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 09ALL | 2 | 24WP | GEN-2016-109 | 'FROM -> TO' | BEATRCE7 - HARBINE7 115 |  | 99 | 0.57784 | 133.46 | P12:115:WERE:KNOB-NPPD_115::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0323 | 133.36 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.23083 | 133.36 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20054 | 133.36 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05272 | 133.36 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0681 | 133.36 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05416 | 133.36 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.2401 | 133.36 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11888 | 133.36 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.2401 | 133.36 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18495 | 133.36 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0628 | 133.36 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18116 | 133.36 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.1869 | 133.36 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07711 | 133.36 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0323 | 133.36 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.23083 | 133.36 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20054 | 133.36 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05272 | 133.36 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0681 | 133.36 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05416 | 133.36 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.2401 | 133.36 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11888 | 133.36 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.2401 | 133.36 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18495 | 133.36 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0628 | 133.36 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18116 | 133.36 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.1869 | 133.36 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07711 | 133.36 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.09206 | 133.32 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-078 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.05729 | 133.32 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.0666 | 133.32 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-012 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.0361 | 133.32 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-079 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.09475 | 133.32 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-081 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.03446 | 133.32 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-084 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.0439 | 133.32 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.14801 | 133.32 | System Intact
Thermal | 13NR | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.0443 | 133.3 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 13NR | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.0443 | 133.3 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 13NR | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.0443 | 133.3 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 13NR | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.0443 | 133.3 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0323 | 133.19 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.23544 | 133.19 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.20749 | 133.19 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05272 | 133.19 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0681 | 133.19 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05619 | 133.19 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.24529 | 133.19 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.11888 | 133.19 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.24529 | 133.19 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.1942 | 133.19 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.09077 | 133.19 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19078 | 133.19 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19582 | 133.19 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07711 | 133.19 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0323 | 133.19 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.23544 | 133.19 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.20749 | 133.19 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05272 | 133.19 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0681 | 133.19 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05619 | 133.19 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.24529 | 133.19 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.11888 | 133.19 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.24529 | 133.19 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.1942 | 133.19 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.09077 | 133.19 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19078 | 133.19 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19582 | 133.19 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07711 | 133.19 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 08ALL | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 152 | 0.25235 | 132.92 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 152 | 0.25235 | 132.92 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08667 | 132.87 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08667 | 132.87 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08667 | 132.87 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08667 | 132.87 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 06ALL | 2 | 19WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.31266 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.31266 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.21688 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.22488 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.1754 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.19568 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.16272 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.19084 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.15627 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.14321 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.15685 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.16452 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.1681 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.36762 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.15685 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.19696 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.16452 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.17326 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.19678 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.15661 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.20855 | 132.84 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 615 |  | 0.14238 | 132.84 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0323 | 132.82 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.23421 | 132.82 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.20657 | 132.82 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05272 | 132.82 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0681 | 132.82 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0556 | 132.82 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.24395 | 132.82 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.11888 | 132.82 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.24395 | 132.82 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.1934 | 132.82 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.08977 | 132.82 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19002 | 132.82 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19501 | 132.82 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07711 | 132.82 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0323 | 132.82 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.23421 | 132.82 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.20657 | 132.82 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05272 | 132.82 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0681 | 132.82 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0556 | 132.82 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.24395 | 132.82 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.11888 | 132.82 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.24395 | 132.82 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.1934 | 132.82 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.08977 | 132.82 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19002 | 132.82 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19501 | 132.82 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07711 | 132.82 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.03157 | 132.78 | System Intact
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.33247 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.33247 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.25562 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22845 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24156 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.2374 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23441 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23322 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24892 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23589 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.38884 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23322 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24448 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24892 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20822 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24041 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23313 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.25786 | 132.59 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 09ALL | 2 | 20G | GEN-2016-109 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 | 112 |  | 0.04786 | 132.54 | System Intact
Thermal | 06ALL | 2 | 19WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.33538 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.33538 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.25142 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.26251 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.24292 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.23474 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.23536 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.23221 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.23121 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.25493 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.25105 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.37814 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.23121 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.24291 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.25493 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.20229 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.2373 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.23094 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 699 | 0.2572 | 132.45 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 00NR | 2 | 20SP | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.06038 | 132.12 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03936 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03919 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.05468 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.07912 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03373 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03006 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.065 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.08082 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.07991 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.04138 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.05441 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.07887 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.04138 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.33445 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.0561 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03907 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03103 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03036 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03135 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.0481 | 131.9 | P42:345:OKGE:SB_CION7382
Thermal | 09ALL | 2 | 19WP | GEN-2016-109 | 'FROM -> TO' | BEATRCE7 - HARBINE7 115 |  | 99 | 0.57088 | 131.89 | P12:115:WERE:KNOB-NPPD_115::
Thermal | 16ALL | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | NESET___-BE4 - TIOGA4 4 230 |  | 526 | 0.88902 | 131.82 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | NESET___-BE4 - TIOGA4 4 230 |  | 526 | 0.88902 | 131.82 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05931 | 131.27 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05931 | 131.27 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05931 | 131.27 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.04116 | 131.21 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | MTVERN 7 - STORLA__-BE7 115 1 |  | 92 | 0.04085 | 131.19 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | MTVERN 7 - STORLA__-BE7 115 1 |  | 92 | 0.03777 | 131.19 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | MTVERN 7 - STORLA__-BE7 115 1 |  | 92 | 0.04635 | 131.19 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 13NR | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.0443 | 131.14 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 13NR | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.0443 | 131.14 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 13NR | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.0443 | 131.14 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 13NR | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.0443 | 131.14 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0323 | 131.13 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.23432 | 131.13 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.20666 | 131.13 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05272 | 131.13 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0681 | 131.13 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05564 | 131.13 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.24407 | 131.13 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.11888 | 131.13 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.24407 | 131.13 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19349 | 131.13 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.08983 | 131.13 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.1901 | 131.13 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.1951 | 131.13 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07711 | 131.13 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 09ALL | 2 | 20SP | GEN-2017-031 | 'FROM -> TO' | BRULE 7 - OGALALA_-TS7115 |  | 120 | 0.5041 | 131.09 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08849 | 130.96 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08849 | 130.96 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08849 | 130.96 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08849 | 130.96 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.07585 | 130.81 | P23:345:MEC:RAUN 0270
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.18234 | 130.81 | P23:345:MEC:RAUN 0270
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.11512 | 130.81 | P23:345:MEC:RAUN 0270
Thermal | 16ALL | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | NESET___-BE4 - TIOGA4 4 230 |  | 526 | 0.88887 | 130.69 | P12:345:UMZ:# 5868 #: IN . PROPER N-1 (LINE) FOR 659336-659427-Z
Thermal | 16ALL | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | NESET___-BE4 - TIOGA4 4 230 |  | 526 | 0.88887 | 130.69 | P23:345:UMZB:# 3708 #: JDM IN ND. BREAKER FAULT JUDSON (696)
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.15588 | 130.51 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.09689 | 130.51 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16804 | 130.51 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16804 | 130.51 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06NR | 2 | 24L | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.06289 | 130.51 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05477 | 130.51 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06NR | 2 | 24L | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.06371 | 130.51 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.15588 | 130.51 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.09689 | 130.51 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16804 | 130.51 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16804 | 130.51 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06NR | 2 | 24L | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.06289 | 130.51 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05477 | 130.51 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06NR | 2 | 24L | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.06371 | 130.51 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.04187 | 130.29 | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.04187 | 130.29 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5!:1
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.04187 | 130.29 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5:1
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.06416 | 130.13 | P42:345:NPPD:BKR-SC-3306
Thermal | 06ALL | 2 | 19WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.31266 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.31266 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.21688 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.22488 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.1754 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.19568 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.16272 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.19084 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.15627 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.14321 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.15685 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.16452 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.1681 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.36762 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.15685 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.19696 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.16452 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.17326 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.19678 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.15661 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.20855 | 130.1 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 615 |  | 0.14238 | 130.1 | System Intact
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04523 | 130.05 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05289 | 130.05 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05289 | 130.05 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04523 | 130.05 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05289 | 130.05 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05289 | 130.05 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.03364 | 130.02 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.03364 | 130.02 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.03364 | 130.02 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 1 | 130.02 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.03364 | 130.02 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.05676 | 129.99 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07334 | 129.87 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07334 | 129.87 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07334 | 129.87 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07334 | 129.87 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 152 | 0.25156 | 129.86 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 07ALL | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | ANADARK4 - CHERRYRD 4 138 | 145 | 169 | 0.57306 | 129.84 | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4
Thermal | 07ALL | 2 | 24L | GEN-2017-053 | 'FROM -> TO' | ANADARK4 - CHERRYRD 4 138 | 145 | 169 | 0.4654 | 129.84 | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4
Thermal | 08ALL | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 189 | 0.25036 | 129.8 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 189 | 0.25036 | 129.8 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08849 | 129.69 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08849 | 129.69 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08849 | 129.69 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08849 | 129.69 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.16214 | 129.52 | P42:345:OKGE:SB_CION7384
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.243 | 129.52 | P42:345:OKGE:SB_CION7384
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.26863 | 129.52 | P42:345:OKGE:SB_CION7384
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.26815 | 129.52 | P42:345:OKGE:SB_CION7384
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.09643 | 129.52 | P42:345:OKGE:SB_CION7384
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.25528 | 129.52 | P42:345:OKGE:SB_CION7384
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.09643 | 129.52 | P42:345:OKGE:SB_CION7384
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.41337 | 129.52 | P42:345:OKGE:SB_CION7384
Thermal | 06ALL | 2 | 24WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.28601 | 129.49 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.28601 | 129.49 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.21904 | 129.49 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.20679 | 129.49 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.20316 | 129.49 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.20056 | 129.49 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.21321 | 129.49 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.20185 | 129.49 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.33514 | 129.49 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.20933 | 129.49 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.21321 | 129.49 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.20579 | 129.49 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.221 | 129.49 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 189 | 0.24951 | 129.43 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 189 | 0.24951 | 129.43 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 12ALL | 2 | 24WP | GEN-2017-082 | 'FROM -> TO' | ASB349 5 - CJ 366 5 161 |  | 223 | 0.62017 | 129.21 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 17ALL | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24752 | 129.2 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07859 | 129.11 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07859 | 129.11 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07859 | 129.11 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07859 | 129.11 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 08ALL | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 189 | 0.24977 | 128.99 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 189 | 0.24977 | 128.99 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.18202 | 128.89 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 1 | 128.89 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 1 | 128.89 | P42:345:NPPD:BKR-HOS-3322
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.31153 | 128.88 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.31153 | 128.88 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23641 | 128.88 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.21164 | 128.88 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.21612 | 128.88 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.21974 | 128.88 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20439 | 128.88 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.37459 | 128.88 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22265 | 128.88 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.21974 | 128.88 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22019 | 128.88 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23502 | 128.88 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.16214 | 128.79 | P12:345:OKGE:BKRBKR24
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.243 | 128.79 | P12:345:OKGE:BKRBKR24
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.26863 | 128.79 | P12:345:OKGE:BKRBKR24
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.26815 | 128.79 | P12:345:OKGE:BKRBKR24
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.09643 | 128.79 | P12:345:OKGE:BKRBKR24
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.25528 | 128.79 | P12:345:OKGE:BKRBKR24
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.09643 | 128.79 | P12:345:OKGE:BKRBKR24
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.41337 | 128.79 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.04931 | 128.74 | P13:115-345:NPPD:NUCOR-2
Thermal | 08ALL | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 152 | 0.25235 | 128.72 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 152 | 0.25235 | 128.72 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 189 | 0.24951 | 128.69 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 189 | 0.24951 | 128.69 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 189 | 0.25036 | 128.68 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 189 | 0.25036 | 128.68 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03936 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03919 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05468 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07912 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03373 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.0497 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.04146 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03006 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.065 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.08082 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07991 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.08464 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.04138 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05441 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07887 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.04138 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.33445 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05868 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03907 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03103 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03036 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03135 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.0481 | 128.65 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 | 220 |  | 0.03659 | 128.52 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.07788 | 128.23 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.24372 | 128.23 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.1392 | 128.23 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.04872 | 128.21 | P13:115-345:NPPD:NUCOR-2
Thermal | 17ALL | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24428 | 128.13 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07859 | 128.02 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07859 | 128.02 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07859 | 128.02 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07859 | 128.02 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.29454 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.29454 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.20749 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.16816 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.15516 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.11961 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.08331 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.17877 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.13277 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.1345 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.1339 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.14322 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.13626 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.36576 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.1339 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.18416 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.14322 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.16625 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.18616 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.13354 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.19436 | 127.94 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.06986 | 127.94 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 189 | 0.24977 | 127.87 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 189 | 0.24977 | 127.87 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.03364 | 127.85 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.03364 | 127.85 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.03364 | 127.85 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 1 | 127.85 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.03364 | 127.85 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07334 | 127.82 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07334 | 127.82 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07334 | 127.82 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07334 | 127.82 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07969 | 127.66 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07969 | 127.66 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07969 | 127.66 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07969 | 127.66 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.7365 | 127.61 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.7365 | 127.61 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 09ALL | 2 | 24SP | GEN-2017-031 | 'FROM -> TO' | BRULE 7 - OGALALA_-TS7115 |  | 120 | 0.50557 | 127.49 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 243 | 0.03352 | 127.43 | P12:345:WERE:N345-AECI_345::
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 243 | 0.03487 | 127.43 | P12:345:WERE:N345-AECI_345::
Thermal | 12ALL | 2 | 19WP | GEN-2017-082 | 'FROM -> TO' | ASB349 5 - CJ 366 5 161 |  | 223 | 0.62001 | 127.4 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.18646 | 127.38 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.0323 | 127.37 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.06543 | 127.37 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.24255 | 127.37 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.0681 | 127.37 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.07364 | 127.37 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03837 | 127.37 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05516 | 127.37 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03929 | 127.37 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.06066 | 127.35 | P42:345:NPPD:BKR-HOS-3322
Thermal | 09ALL | 2 | 19WP | GEN-2016-034 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 |  | 320 | 0.52062 | 127.34 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2016-093 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 |  | 320 | 0.48391 | 127.34 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2017-031 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 |  | 320 | 0.51608 | 127.34 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2017-037 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 |  | 320 | 0.48391 | 127.34 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.08325 | 127.3 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.0317 | 127.21 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.37885 | 127.21 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.5058 | 127.21 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.36593 | 127.21 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.05499 | 127.13 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.0625 | 127.13 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.0567 | 127.13 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.06423 | 127.13 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.05548 | 127.13 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.06655 | 127.13 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.05499 | 127.13 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.0625 | 127.13 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.0567 | 127.13 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.06423 | 127.13 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.05548 | 127.13 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.06655 | 127.13 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.12949 | 126.97 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.73168 | 126.87 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.31153 | 126.83 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.31153 | 126.83 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23641 | 126.83 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.21164 | 126.83 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.21612 | 126.83 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.21974 | 126.83 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20439 | 126.83 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.37459 | 126.83 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22265 | 126.83 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.21974 | 126.83 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22019 | 126.83 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23502 | 126.83 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 16NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | B.SPRGS7 - BRULE 7 115 1 |  | 109 | 0.03215 | 126.75 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 16NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | B.SPRGS7 - BRULE 7 115 1 |  | 109 | 0.07626 | 126.75 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 16NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | B.SPRGS7 - BRULE 7 115 1 |  | 109 | 0.04841 | 126.75 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 16NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 1 |  | 320 | 0.08796 | 126.75 | P42:345:NPPD:BKR-KEY-3310
Thermal | 16NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 1 |  | 320 | 0.21248 | 126.75 | P42:345:NPPD:BKR-KEY-3310
Thermal | 16NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 1 |  | 320 | 0.13389 | 126.75 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.06038 | 126.7 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.0324 | 126.62 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.14178 | 126.62 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.4024 | 126.62 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.23817 | 126.62 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07969 | 126.55 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07969 | 126.55 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07969 | 126.55 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07969 | 126.55 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 06ALL | 2 | 24WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.28601 | 126.5 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.28601 | 126.5 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.21904 | 126.5 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.20679 | 126.5 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.20316 | 126.5 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.20056 | 126.5 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.21321 | 126.5 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.20185 | 126.5 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.33514 | 126.5 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.20933 | 126.5 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.21321 | 126.5 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.20579 | 126.5 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.221 | 126.5 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.29454 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.29454 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.20749 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.16816 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.15516 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.11961 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.08331 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.17877 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.13277 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.1345 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.1339 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.14322 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.13626 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.36576 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.1339 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.18416 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.14322 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.16625 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.18616 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.13354 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.19436 | 126.44 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.06986 | 126.44 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.06361 | 126.38 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 1 | 126.38 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 1 | 126.38 | P42:345:NPPD:BKR-SC-3306
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | B.SPRGS7 - BRULE 7 115 1 |  | 109 | 0.03215 | 126.36 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | B.SPRGS7 - BRULE 7 115 1 |  | 109 | 0.07626 | 126.36 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | B.SPRGS7 - BRULE 7 115 1 |  | 109 | 0.04841 | 126.36 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.18018 | 126.34 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2016-103 | 'FROM -> TO' | MTVERN 7 - STORLA__-BE7 115 1 |  | 92 | 0.0322 | 126.3 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | MTVERN 7 - STORLA__-BE7 115 1 |  | 92 | 0.05211 | 126.3 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | MTVERN 7 - STORLA__-BE7 115 1 |  | 92 | 1 | 126.3 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | MTVERN 7 - STORLA__-BE7 115 1 |  | 92 | 1 | 126.3 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | MTVERN 7 - STORLA__-BE7 115 1 |  | 92 | 0.05536 | 126.3 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 24WP | GEN-2017-094 | 'FROM -> TO' | MTVERN 7 - STORLA__-BE7 115 1 |  | 92 | 0.0377 | 126.3 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.0323 | 126.28 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.06543 | 126.28 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.24255 | 126.28 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.0681 | 126.28 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.07364 | 126.28 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03837 | 126.28 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05516 | 126.28 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03929 | 126.28 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03936 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03919 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.05468 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.07912 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03373 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03006 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.065 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.08082 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.07991 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.04138 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.05441 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.07887 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.04138 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.33445 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.0561 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03907 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03103 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03036 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03135 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.0481 | 126.14 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.0323 | 126.02 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.06461 | 126.02 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.23573 | 126.02 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.0681 | 126.02 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.07364 | 126.02 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03837 | 126.02 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05516 | 126.02 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03929 | 126.02 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.08163 | 126 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.20301 | 126 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.1264 | 126 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 08ALL | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 152 | 0.25262 | 126 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 20SP | GEN-2017-011 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03053 | 125.99 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.09382 | 125.99 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-011 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03053 | 125.99 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.09382 | 125.99 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03936 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03919 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05468 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07912 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03373 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.04146 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03006 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.065 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08082 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07991 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08464 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07846 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.04138 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05441 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07846 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07846 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.49605 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07887 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.04138 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.33445 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05868 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03907 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03103 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03036 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03135 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07846 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.0481 | 125.95 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05211 | 125.94 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04861 | 125.94 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.06194 | 125.94 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.0558 | 125.94 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04086 | 125.94 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 125.94 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.11509 | 125.94 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.26313 | 125.94 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 125.94 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05536 | 125.94 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04554 | 125.94 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07828 | 125.94 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07315 | 125.94 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05211 | 125.94 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04861 | 125.94 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.06194 | 125.94 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.0558 | 125.94 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04086 | 125.94 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 125.94 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.11509 | 125.94 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.26313 | 125.94 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 125.94 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05536 | 125.94 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04554 | 125.94 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07828 | 125.94 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07315 | 125.94 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05211 | 125.94 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04861 | 125.94 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.06194 | 125.94 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.0558 | 125.94 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04086 | 125.94 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 125.94 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.11509 | 125.94 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.26313 | 125.94 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 125.94 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05536 | 125.94 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07828 | 125.94 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07315 | 125.94 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.08461 | 125.85 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 1 | 125.85 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 1 | 125.85 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.06438 | 125.82 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 19WP | GEN-2016-107 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.04921 | 125.82 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 19WP | GEN-2017-011 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.10222 | 125.82 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05785 | 125.82 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 19WP | GEN-2017-028 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03447 | 125.82 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.0703 | 125.82 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05791 | 125.82 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03586 | 125.82 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05791 | 125.82 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 19WP | GEN-2017-067 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03536 | 125.82 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.20919 | 125.82 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 19WP | GEN-2017-086 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.07874 | 125.82 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03672 | 125.82 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07925 | 125.79 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07925 | 125.79 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07925 | 125.79 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07925 | 125.79 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.07585 | 125.77 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.18234 | 125.77 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.11512 | 125.77 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.07585 | 125.77 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.18234 | 125.77 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | RAUN 5 - TEKAMAH5 161 1 |  | 217 | 0.11512 | 125.77 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.0323 | 125.74 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03789 | 125.74 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.0681 | 125.74 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.07364 | 125.74 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03837 | 125.74 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03014 | 125.74 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.05516 | 125.74 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03929 | 125.74 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.0323 | 125.74 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03789 | 125.74 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.0681 | 125.74 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.07364 | 125.74 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03837 | 125.74 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03014 | 125.74 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.05516 | 125.74 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03929 | 125.74 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 17ALL | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24815 | 125.68 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.08163 | 125.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.20301 | 125.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.1264 | 125.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03936 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03919 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.05468 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.07912 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03373 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03491 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.04146 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03006 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.065 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.08082 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.07991 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.08464 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.04138 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.05441 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.07887 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.04138 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.33445 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.05868 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03103 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03036 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03135 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.0481 | 125.65 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03936 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03919 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.05468 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.07912 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03373 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03491 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.04146 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03006 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.065 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.08082 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.07991 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.08464 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.04138 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.05441 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.07887 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.04138 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.33445 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.05868 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03103 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03036 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03135 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.0481 | 125.65 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05951 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-011 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.10084 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-018 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05404 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-028 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03382 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03171 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-032 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.06683 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05288 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03171 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03171 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-047 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03267 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05288 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-067 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.035 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.18597 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.04602 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03171 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 20SP | GEN-2017-100 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03352 | 125.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06212 | 125.51 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06212 | 125.51 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06212 | 125.51 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06212 | 125.51 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06098 | 125.49 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06098 | 125.49 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06098 | 125.49 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06098 | 125.49 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08004 | 125.43 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08004 | 125.43 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08004 | 125.43 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08004 | 125.43 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.03936 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.07912 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.03373 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.07947 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.08082 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.07991 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.04138 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.05441 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.24613 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.04138 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.33445 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.03907 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.03103 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.03036 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.03135 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.14114 | 125.36 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 17ALL | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24812 | 125.28 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.18202 | 125.23 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 1 | 125.23 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 1 | 125.23 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.08201 | 125.22 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.23229 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.19692 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-173 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0325 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05211 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04861 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0751 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.06944 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07118 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04086 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.245 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11509 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.245 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17985 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11694 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17564 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18187 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03082 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07315 | 125.21 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.23229 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.19692 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-173 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0325 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05211 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04861 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0751 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.06944 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07118 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04086 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.245 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11509 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.245 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17985 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11694 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17564 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18187 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03082 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07315 | 125.21 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.18646 | 125.19 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.04872 | 125.18 | P13:115-345:NPPD:NUCOR-2
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 189 | 0.24976 | 125.15 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.0323 | 125.11 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.08578 | 125.11 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05272 | 125.11 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.0681 | 125.11 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.07364 | 125.11 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03837 | 125.11 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.11888 | 125.11 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05516 | 125.11 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.07711 | 125.11 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03929 | 125.11 | P42:345:NPPD:BKR-HOS-3308
Thermal | 17ALL | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24498 | 125.09 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06212 | 125.07 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06212 | 125.07 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06212 | 125.07 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06212 | 125.07 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06098 | 125.05 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06098 | 125.05 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06098 | 125.05 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06098 | 125.05 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07925 | 125 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07925 | 125 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07925 | 125 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07925 | 125 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.0323 | 124.95 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.06461 | 124.95 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.23573 | 124.95 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.0681 | 124.95 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.07364 | 124.95 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03837 | 124.95 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05516 | 124.95 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03929 | 124.95 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.0323 | 124.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.0768 | 124.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.12217 | 124.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.0681 | 124.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.07364 | 124.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03837 | 124.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05516 | 124.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03929 | 124.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03936 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03919 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.05468 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.07912 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03373 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.0497 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.04146 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03006 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.065 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.08082 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.07991 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.08464 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.04138 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.05441 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.07887 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.04138 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.33445 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.05868 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03907 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03103 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03036 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03135 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.0481 | 124.89 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.03936 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.05999 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.07912 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.03373 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.0675 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.08082 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.07991 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.04138 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.05441 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.06171 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.06923 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.04138 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.33445 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.03103 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.03036 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.03135 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.06048 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.07155 | 124.89 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.03936 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.05999 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.07912 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.03373 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.0675 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.08082 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.07991 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.04138 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.05441 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.06171 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.06923 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.04138 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.33445 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.03103 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.03036 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.03135 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.06048 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.07155 | 124.89 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03936 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03919 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05468 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.07912 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03373 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.04146 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03006 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.065 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.08082 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.07991 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.08464 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0613 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.04138 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05441 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0613 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0613 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.49605 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.07887 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.04138 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.33445 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05868 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03907 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03103 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03036 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03135 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0613 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0481 | 124.86 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03919 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05468 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.07912 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.04146 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03006 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.065 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.08082 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.07991 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.08464 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06246 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05441 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06246 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06246 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.49605 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.07887 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.33445 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05868 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03907 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06246 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0481 | 124.86 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.05676 | 124.85 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.04968 | 124.82 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.04968 | 124.82 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.23148 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.1958 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-173 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03274 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05211 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04861 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07243 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.06711 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07163 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04086 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.24431 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11509 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.24431 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17858 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11791 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17435 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18061 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03105 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07315 | 124.74 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.23148 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.1958 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-173 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03274 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05211 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04861 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07243 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.06711 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07163 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04086 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.24431 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11509 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.24431 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17858 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11791 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17435 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18061 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03105 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07315 | 124.74 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.29097 | 124.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.29097 | 124.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.20049 | 124.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.24924 | 124.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.20414 | 124.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.23652 | 124.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.21473 | 124.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.21806 | 124.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.22092 | 124.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.32077 | 124.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.21806 | 124.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.21141 | 124.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 08ALL | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 189 | 0.25036 | 124.7 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 189 | 0.25036 | 124.7 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03936 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03919 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05468 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07912 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03373 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.04146 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03006 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.065 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08082 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07991 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08464 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07846 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.04138 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05441 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07846 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07846 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.49605 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07887 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.04138 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.33445 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05868 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03907 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03103 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03036 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03135 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07846 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.0481 | 124.68 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 06ALL | 2 | 24WP | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.2729 | 124.64 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.23749 | 124.64 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03936 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03919 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05468 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07912 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03373 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.04146 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03006 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.065 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08082 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07991 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08464 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07957 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.04138 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05441 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07957 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07957 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.49605 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07887 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.04138 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.33445 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05868 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03907 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03103 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03036 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03135 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07957 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.0481 | 124.57 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03936 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03919 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05468 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.07912 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03373 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.04146 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03006 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.065 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.08082 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.07991 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.08464 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0613 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.04138 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05441 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0613 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0613 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.49605 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.07887 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.04138 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.33445 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05868 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03907 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03103 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03036 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03135 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0613 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0481 | 124.55 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03919 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05468 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.07912 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.04146 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03006 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.065 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.08082 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.07991 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.08464 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06246 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05441 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06246 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06246 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.49605 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.07887 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.33445 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05868 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03907 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06246 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0481 | 124.54 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.04931 | 124.49 | P13:115-345:NPPD:NUCOR-2
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 189 | 0.24976 | 124.41 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.0323 | 124.4 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05272 | 124.4 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.0681 | 124.4 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.09012 | 124.4 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07364 | 124.4 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.09012 | 124.4 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.09012 | 124.4 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03837 | 124.4 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 1 | 124.4 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.11888 | 124.4 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05516 | 124.4 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.09012 | 124.4 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07711 | 124.4 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03929 | 124.4 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 06ALL | 2 | 24WP | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 |  | 559 | 0.2729 | 124.4 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24WP | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 |  | 559 | 0.23749 | 124.4 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.27831 | 124.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.27831 | 124.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.21132 | 124.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20545 | 124.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.32739 | 124.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20154 | 124.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20545 | 124.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.21314 | 124.36 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 08ALL | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | BV-COM-4 - MOUNDRD4 138 1 | 106 |  | 0.17918 | 124.34 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.23148 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.19582 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2016-173 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03273 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05211 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04861 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0755 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.06982 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07176 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04086 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.2443 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11509 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.2443 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17861 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11794 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17437 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18064 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03104 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07315 | 124.33 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 17ALL | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24489 | 124.33 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03053 | 124.15 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.09382 | 124.15 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03053 | 124.15 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.09382 | 124.15 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03936 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03919 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05468 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.07912 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03373 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.04146 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03006 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.065 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.08082 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.07991 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.08464 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06055 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.04138 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05441 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06055 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06055 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.49605 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.07887 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.04138 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.33445 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05868 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03907 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03103 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03036 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03135 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06055 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0481 | 124.1 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 08ALL | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 189 | 0.25007 | 124.09 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03936 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03547 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.05227 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.07912 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03373 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03006 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.065 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.08082 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.07991 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.04138 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.05441 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.07887 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.04138 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.33445 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03907 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03103 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03036 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03135 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.0481 | 124.06 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03936 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.04929 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.06783 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.07912 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03373 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03006 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.065 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.08082 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.07991 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.04138 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.05441 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.07887 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.04138 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.33445 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03907 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03103 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03036 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03135 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.0481 | 124.04 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0323 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16921 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2016-107 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.24802 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11772 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05272 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0681 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.17275 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.25749 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11888 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.17275 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-066 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.25746 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.08777 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05516 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0798 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.08865 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07711 | 124.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0323 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16921 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2016-107 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.24802 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11772 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05272 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0681 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.17275 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.25749 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11888 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.17275 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-066 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.25746 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.08777 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05516 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0798 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.08865 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07711 | 124.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 08ALL | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | BV-COM-4 - MOUNDRD4 138 1 | 131 |  | 0.1778 | 124.03 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.03569 | 123.97 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.03919 | 123.97 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.05468 | 123.97 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.08961 | 123.97 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.03006 | 123.97 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.065 | 123.97 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.10998 | 123.97 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.10908 | 123.97 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.07526 | 123.97 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.07887 | 123.97 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.29384 | 123.97 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.04487 | 123.97 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.03907 | 123.97 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.0481 | 123.97 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.23033 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.19477 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-173 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03262 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05211 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04861 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07518 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.06953 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07155 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04086 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.24311 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11509 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.24311 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17761 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11761 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17338 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17964 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03094 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07315 | 123.94 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.23033 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.19477 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-173 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03262 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05211 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04861 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07518 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.06953 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07155 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04086 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.24311 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11509 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.24311 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17761 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11761 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17338 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17964 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03094 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07315 | 123.94 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.0323 | 123.92 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.0768 | 123.92 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.12217 | 123.92 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.0681 | 123.92 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.07364 | 123.92 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03837 | 123.92 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05516 | 123.92 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03929 | 123.92 | P42:345:NPPD:BKR-HOS-3308
Thermal | 09ALL | 2 | 29SP | GEN-2017-031 | 'FROM -> TO' | BRULE 7 - OGALALA_-TS7115 |  | 120 | 0.5056 | 123.9 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 08ALL | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 189 | 0.24977 | 123.84 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 189 | 0.24977 | 123.84 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03936 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.0407 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.07912 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03373 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03006 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.065 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.08082 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.07991 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.04138 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.05441 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.07887 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.04138 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.33445 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03907 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03103 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03036 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03135 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.0481 | 123.83 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03936 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03919 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05468 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.07912 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03373 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.04146 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03006 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.065 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.08082 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.07991 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.08464 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06055 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.04138 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05441 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06055 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06055 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.49605 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.07887 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.04138 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.33445 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05868 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03907 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03103 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03036 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03135 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06055 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0481 | 123.79 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 189 | 0.24951 | 123.77 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 189 | 0.24951 | 123.77 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 09ALL | 2 | 24WP | GEN-2016-034 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 |  | 320 | 0.5254 | 123.7 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24WP | GEN-2016-093 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 |  | 320 | 0.48808 | 123.7 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24WP | GEN-2017-031 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 |  | 320 | 0.52135 | 123.7 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24WP | GEN-2017-037 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 |  | 320 | 0.48808 | 123.7 | P42:345:NPPD:BKR-KEY-3310
Thermal | 08ALL | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 189 | 0.25064 | 123.69 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.32264 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.32264 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24756 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20309 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22283 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.2273 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20754 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20734 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23092 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.21557 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.38577 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20734 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23389 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23092 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20181 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23136 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20694 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24634 | 123.67 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.04951 | 123.64 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 1 | 123.64 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 1 | 123.64 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.18018 | 123.53 | P42:345:NPPD:BKR-HOS-3322
Thermal | 09NR | 2 | 20G | GEN-2016-109 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 1 |  | 123 | 0.0329 | 123.53 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 09NR | 2 | 20G | GEN-2016-159 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 1 |  | 123 | 0.00123 | 123.53 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03919 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05468 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07912 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.04146 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03006 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.065 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08082 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07991 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08464 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07992 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05441 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07992 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07992 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.49605 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07887 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.33445 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05868 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03907 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07992 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.0481 | 123.46 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.06014 | 123.3 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 1 | 123.3 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 1 | 123.3 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03936 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03919 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05468 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07912 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03373 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.04146 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03006 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.065 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08082 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07991 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08464 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07957 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.04138 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05441 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07957 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07957 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.49605 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07887 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.04138 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.33445 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05868 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03907 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03103 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03036 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03135 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07957 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.0481 | 123.29 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03936 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03919 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05468 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07912 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03373 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.0307 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03006 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.065 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.08082 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07991 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.04138 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05441 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07887 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.04138 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.33445 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05207 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03103 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03036 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03135 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.0481 | 123.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03936 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03919 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05468 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07912 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03373 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.0307 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03006 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.065 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.08082 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07991 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.04138 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05441 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07887 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.04138 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.33445 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05207 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03103 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03036 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03135 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.0481 | 123.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03936 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03919 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.05468 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.07912 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03373 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.18293 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.04146 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03006 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.065 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.08082 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.07991 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.08464 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.04138 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.05441 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.07887 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.04138 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.33445 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.05868 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03907 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03103 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03036 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03135 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.0481 | 123.14 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03088 | 123.13 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.0524 | 123.13 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03088 | 123.13 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.0524 | 123.13 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08263 | 123.11 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08263 | 123.11 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08263 | 123.11 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08263 | 123.11 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 08ALL | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | BV-COM-4 - MOUNDRD4 138 1 | 131 |  | 0.17735 | 123.11 | System Intact
Thermal | 01ALL | 2 | 20G | GEN-2016-107 | 'FROM -> TO' | DOVERSW4 - OKEENE 4 138 |  | 83 | 0.36967 | 123.08 | P12:138:WFEC:OKEENE_WATONGA:2024+
Thermal | 08ALL | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 189 | 0.25007 | 122.97 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07059 | 122.96 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07059 | 122.96 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07059 | 122.96 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07059 | 122.96 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 | 151 |  | 0.24853 | 122.93 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2016-173 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.03179 | 122.91 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.0301 | 122.91 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.03265 | 122.91 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.71197 | 122.9 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.71197 | 122.9 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.71197 | 122.9 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.71197 | 122.9 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07059 | 122.68 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07059 | 122.68 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07059 | 122.68 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07059 | 122.68 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 08ALL | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | BV-COM-4 - MOUNDRD4 138 1 |  | 131 | 0.24659 | 122.66 | P12:138:GRDA:FAIRFAX-PAWNSW
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05921 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-011 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.10029 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-018 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05667 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-028 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03314 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03176 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-032 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.06487 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05266 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03176 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03176 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-047 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03144 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05266 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-067 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03467 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.18519 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.04531 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03176 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24SP | GEN-2017-100 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03228 | 122.64 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.03936 | 122.61 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.07912 | 122.61 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.03373 | 122.61 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.08082 | 122.61 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.07991 | 122.61 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.04138 | 122.61 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.05441 | 122.61 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.03414 | 122.61 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.04138 | 122.61 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.33445 | 122.61 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.03907 | 122.61 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.03103 | 122.61 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.03036 | 122.61 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.03135 | 122.61 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.0323 | 122.5 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05272 | 122.5 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.0681 | 122.5 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.09012 | 122.5 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07364 | 122.5 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.09012 | 122.5 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.09012 | 122.5 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03837 | 122.5 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 1 | 122.5 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.11888 | 122.5 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05516 | 122.5 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.09012 | 122.5 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07711 | 122.5 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03929 | 122.5 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0323 | 122.46 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05272 | 122.46 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0681 | 122.46 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.04808 | 122.46 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.07364 | 122.46 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.04808 | 122.46 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.04808 | 122.46 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03837 | 122.46 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 1 | 122.46 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.11888 | 122.46 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05516 | 122.46 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.04808 | 122.46 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.07711 | 122.46 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03929 | 122.46 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05766 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-011 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.09963 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-018 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05666 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.06194 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.0558 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-028 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03248 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.0313 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.06653 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05111 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.0313 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.0313 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-047 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.0331 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 1 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05111 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-067 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03401 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.20273 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 1 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.06285 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.0313 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 24WP | GEN-2017-100 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03394 | 122.45 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 12ALL | 2 | 24WP | GEN-2017-082 | 'FROM -> TO' | ASB349 5 - PUR421 5 161 |  | 223 | 0.57126 | 122.39 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 17ALL | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24851 | 122.35 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0323 | 122.29 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05272 | 122.29 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0681 | 122.29 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.04942 | 122.29 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.07364 | 122.29 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.04942 | 122.29 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.04942 | 122.29 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03837 | 122.29 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 1 | 122.29 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.11888 | 122.29 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05516 | 122.29 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.04942 | 122.29 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.07711 | 122.29 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03929 | 122.29 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 1 |  | 320 | 0.08797 | 122.26 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 1 |  | 320 | 0.21248 | 122.26 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 1 |  | 320 | 0.13391 | 122.26 | P42:345:NPPD:BKR-KEY-3310
Thermal | 06ALL | 2 | 20SP | GEN-2017-091 | 'FROM -> TO' | LAMTON 3 - HALE_CNTY 3 115 1 |  | 79.7 | 0.33343 | 122.24 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.32264 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.32264 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24756 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20309 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22283 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.2273 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20754 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20734 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23092 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.21557 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.38577 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20734 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23389 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23092 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20181 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23136 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20694 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24634 | 122.23 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03919 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05468 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07912 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.04146 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03006 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.065 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08082 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07991 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.08464 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07992 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05441 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07992 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07992 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.49605 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07887 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.33445 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05868 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03907 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07992 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.0481 | 122.18 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0323 | 122.18 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05272 | 122.18 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0681 | 122.18 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.04808 | 122.18 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.07364 | 122.18 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.04808 | 122.18 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.04808 | 122.18 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03837 | 122.18 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 1 | 122.18 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.11888 | 122.18 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05516 | 122.18 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.04808 | 122.18 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.07711 | 122.18 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03929 | 122.18 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.03507 | 122.1 | P42:345:NPPD:BKR-CE-3306
Thermal | 17ALL | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24822 | 122.08 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0323 | 122.02 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05272 | 122.02 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0681 | 122.02 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.04942 | 122.02 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.07364 | 122.02 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.04942 | 122.02 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.04942 | 122.02 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03837 | 122.02 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 1 | 122.02 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.11888 | 122.02 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05516 | 122.02 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.04942 | 122.02 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.07711 | 122.02 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03929 | 122.02 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.04536 | 121.91 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.04861 | 121.91 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.06194 | 121.91 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.0558 | 121.91 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.03613 | 121.91 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 1 | 121.91 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.11509 | 121.91 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.26313 | 121.91 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 1 | 121.91 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.05536 | 121.91 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.07828 | 121.91 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.07315 | 121.91 | P11:RENO-G16-111-TAP
Thermal | 09ALL | 2 | 24L | GEN-2016-109 | 'FROM -> TO' | FAIRBRY7 - HARBINE7115 |  | 99 | 0.62884 | 121.91 | P42:345:NPPD:BKR-MOR-3310
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | PLSNT_HILL 3 - E_CLOVIS 3 115 1 |  | 123.1 | 0.36649 | 121.9 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | PLSNT_HILL 3 - E_CLOVIS 3 115 1 |  | 123.1 | 0.36649 | 121.9 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | PLSNT_HILL 3 - E_CLOVIS 3 115 1 |  | 123.1 | 0.27961 | 121.9 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.25916 | 121.87 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.22341 | 121.87 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | BENTON 4 - BENT TX-2 138 1 |  | 440 | 0.03936 | 121.78 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | BENTON 4 - BENT TX-2 138 1 |  | 440 | 0.07912 | 121.78 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | BENTON 4 - BENT TX-2 138 1 |  | 440 | 0.03373 | 121.78 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | BENTON 4 - BENT TX-2 138 1 |  | 440 | 0.08082 | 121.78 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | BENTON 4 - BENT TX-2 138 1 |  | 440 | 0.07991 | 121.78 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | BENTON 4 - BENT TX-2 138 1 |  | 440 | 0.04138 | 121.78 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | BENTON 4 - BENT TX-2 138 1 |  | 440 | 0.05441 | 121.78 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | BENTON 4 - BENT TX-2 138 1 |  | 440 | 0.04138 | 121.78 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | BENTON 4 - BENT TX-2 138 1 |  | 440 | 0.33445 | 121.78 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | BENTON 4 - BENT TX-2 138 1 |  | 440 | 0.03927 | 121.78 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | BENTON 4 - BENT TX-2 138 1 |  | 440 | 0.03103 | 121.78 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | BENTON 4 - BENT TX-2 138 1 |  | 440 | 0.03036 | 121.78 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | BENTON 4 - BENT TX-2 138 1 |  | 440 | 0.03135 | 121.78 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0323 | 121.77 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05272 | 121.77 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0681 | 121.77 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0471 | 121.77 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.07364 | 121.77 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0471 | 121.77 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0471 | 121.77 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03837 | 121.77 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 1 | 121.77 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.11888 | 121.77 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05516 | 121.77 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.0471 | 121.77 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.07711 | 121.77 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.03929 | 121.77 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03936 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03919 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.05468 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.07912 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03373 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.04146 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03006 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.065 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.08082 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.07991 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.08464 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.12115 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.04138 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.05441 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.12115 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.12115 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.49605 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.07887 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.04138 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.33445 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.05868 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03907 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03103 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03036 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.03135 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.12115 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1136 | 0.0481 | 121.76 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 08ALL | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 189 | 0.25036 | 121.7 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 189 | 0.25036 | 121.7 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05211 | 121.62 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04861 | 121.62 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.06194 | 121.62 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.0558 | 121.62 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04086 | 121.62 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 121.62 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.11509 | 121.62 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.26313 | 121.62 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 121.62 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05536 | 121.62 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.03897 | 121.62 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07828 | 121.62 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07315 | 121.62 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05211 | 121.62 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04861 | 121.62 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.06194 | 121.62 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.0558 | 121.62 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04086 | 121.62 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 121.62 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.11509 | 121.62 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.26313 | 121.62 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 121.62 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05536 | 121.62 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.03897 | 121.62 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07828 | 121.62 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07315 | 121.62 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.0404 | 121.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03691 | 121.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03691 | 121.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.0404 | 121.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03691 | 121.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03691 | 121.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.0404 | 121.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03691 | 121.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03691 | 121.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 | 151 |  | 0.2483 | 121.57 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.03936 | 121.54 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.07912 | 121.54 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.03373 | 121.54 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.08082 | 121.54 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.07991 | 121.54 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.04138 | 121.54 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.05441 | 121.54 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.04138 | 121.54 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.33445 | 121.54 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.03927 | 121.54 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.03103 | 121.54 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.03036 | 121.54 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.03135 | 121.54 | P23:345:WERE:BENT_345-50::
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.27831 | 121.53 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.27831 | 121.53 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.21132 | 121.53 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20545 | 121.53 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.32739 | 121.53 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20154 | 121.53 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20545 | 121.53 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.21314 | 121.53 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0323 | 121.49 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05272 | 121.49 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0681 | 121.49 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0471 | 121.49 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.07364 | 121.49 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0471 | 121.49 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0471 | 121.49 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03837 | 121.49 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 1 | 121.49 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.11888 | 121.49 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05516 | 121.49 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.0471 | 121.49 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.07711 | 121.49 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.03929 | 121.49 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 01ALL | 2 | 19WP | GEN-2016-107 | 'FROM -> TO' | DOVERSW4 - OKEENE 4 138 |  | 99 | 0.3499 | 121.48 | P12:138:OKGE:BKRBKR87
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 189 | 0.24951 | 121.44 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 189 | 0.24951 | 121.44 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07273 | 121.43 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07273 | 121.43 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07273 | 121.43 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07273 | 121.43 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 09ALL | 2 | 24L | GEN-2016-034 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 |  | 0.0409 | 121.33 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2016-093 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 |  | 0.03852 | 121.33 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2017-001 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 |  | 0.03664 | 121.33 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2017-031 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 |  | 0.03967 | 121.33 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2017-037 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 |  | 0.03852 | 121.33 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.09229 | 121.32 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.05811 | 121.32 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.06697 | 121.32 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-012 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.0363 | 121.32 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-079 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.09516 | 121.32 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-081 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.03457 | 121.32 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-084 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.0442 | 121.32 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.1485 | 121.32 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.0323 | 121.31 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05272 | 121.31 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.0681 | 121.31 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.09322 | 121.31 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07364 | 121.31 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.09322 | 121.31 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.09322 | 121.31 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03837 | 121.31 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 1 | 121.31 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.11888 | 121.31 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05516 | 121.31 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.09322 | 121.31 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07711 | 121.31 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03929 | 121.31 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.0323 | 121.24 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.06674 | 121.24 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05272 | 121.24 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.0681 | 121.24 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.07364 | 121.24 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03837 | 121.24 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.11888 | 121.24 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05516 | 121.24 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.07711 | 121.24 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03929 | 121.24 | P42:345:NPPD:BKR-SC-3306
Thermal | 06ALL | 2 | 20G | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 |  | 559 | 0.25916 | 121.24 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20G | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 |  | 559 | 0.22341 | 121.24 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.0323 | 121.23 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05272 | 121.23 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.0681 | 121.23 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.09323 | 121.23 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07364 | 121.23 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.09323 | 121.23 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.09323 | 121.23 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03837 | 121.23 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 1 | 121.23 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.11888 | 121.23 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05516 | 121.23 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.09323 | 121.23 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07711 | 121.23 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03929 | 121.23 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07273 | 121.19 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07273 | 121.19 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07273 | 121.19 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07273 | 121.19 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 20SP | GEN-2017-071 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.09348 | 121.18 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 20SP | GEN-2017-072 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.09348 | 121.18 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 20SP | GEN-2017-071 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.09348 | 121.18 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 20SP | GEN-2017-072 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.09348 | 121.18 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.03335 | 121.14 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.03278 | 121.14 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.03278 | 121.14 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.03335 | 121.14 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.03278 | 121.14 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.03278 | 121.14 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05833 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.07912 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.09968 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05467 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.08082 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.07991 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.0326 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03173 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-032 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.06599 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05177 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05441 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03173 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03173 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-047 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03257 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.49605 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05177 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.33445 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03411 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.18403 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.04416 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03173 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 00NR | 2 | 29SP | GEN-2017-100 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03341 | 121.01 | P23:345:KCPL-WERE:WGARDNER_R8-13::WGARD-CRAIG-SWISSVALE
Thermal | 17ALL | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24502 | 121 | P42:345:NPPD:BKR-KEY-3310
Thermal | 17ALL | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 |  | 320 | 0.24525 | 120.92 | P42:345:NPPD:BKR-KEY-3310
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 | 152 |  | 0.24853 | 120.91 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.04536 | 120.9 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.04861 | 120.9 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.06194 | 120.9 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.0558 | 120.9 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.03613 | 120.9 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 1 | 120.9 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.11509 | 120.9 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.26313 | 120.9 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 1 | 120.9 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.05536 | 120.9 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.07828 | 120.9 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.07315 | 120.9 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03919 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05468 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07912 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.04146 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03006 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.065 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08082 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07991 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08464 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07046 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05441 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07046 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07046 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.49605 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07887 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.33445 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05868 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03907 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07046 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.0481 | 120.9 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.06416 | 120.86 | P42:345:NPPD:BKR-SC-3306
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.73193 | 120.84 | P12:345:WERE:WAVS-LACY_345::
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04083 | 120.82 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03737 | 120.82 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03737 | 120.82 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04083 | 120.82 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03737 | 120.82 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03737 | 120.82 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0323 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16921 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-107 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.24802 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11772 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05272 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0681 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.17275 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.25749 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11888 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.17275 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-066 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.25746 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.08777 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05516 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0798 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.08865 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07711 | 120.82 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0323 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16921 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-107 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.24802 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11772 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05272 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0681 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.17275 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.25749 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11888 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.17275 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-066 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.25746 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.08777 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05516 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0798 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.08865 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07711 | 120.82 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0323 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16921 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-107 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.24802 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11772 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05272 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0681 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.17275 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.25749 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11888 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.17275 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-066 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.25746 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.08777 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05516 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0798 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.08865 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07711 | 120.82 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0323 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16921 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-107 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.24802 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11772 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05272 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0681 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.17275 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.25749 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11888 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.17275 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-066 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.25746 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.08777 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05516 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.0798 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.08865 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07711 | 120.82 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.73193 | 120.81 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0323 | 120.68 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.23817 | 120.68 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.21319 | 120.68 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05272 | 120.68 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0681 | 120.68 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05024 | 120.68 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.24698 | 120.68 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.11888 | 120.68 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.24698 | 120.68 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.20131 | 120.68 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.08111 | 120.68 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19825 | 120.68 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.20277 | 120.68 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07711 | 120.68 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0323 | 120.68 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.23817 | 120.68 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.21319 | 120.68 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05272 | 120.68 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0681 | 120.68 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05024 | 120.68 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.24698 | 120.68 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.11888 | 120.68 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.24698 | 120.68 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.20131 | 120.68 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.08111 | 120.68 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19825 | 120.68 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.20277 | 120.68 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07711 | 120.68 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 189 | 0.24977 | 120.68 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 189 | 0.24977 | 120.68 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.0323 | 120.66 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03442 | 120.66 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.18808 | 120.66 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.0681 | 120.66 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.07364 | 120.66 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03837 | 120.66 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03046 | 120.66 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.05516 | 120.66 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03929 | 120.66 | P42:345:NPPD:BKR-HOS-3322
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | HOLT.CO3 - GRPRAR1-LNX3 345 | 720 |  | 0.25565 | 120.64 | System Intact
Thermal | 15ALL | 2 | 24L | GEN-2017-094 | 'FROM -> TO' | HOLT.CO3 - GRPRAR1-LNX3 345 | 720 |  | 0.17638 | 120.64 | System Intact
Thermal | 07ALL | 2 | 24L | GEN-2017-053 | 'FROM -> TO' | GEROJCT2 - GRANFLD2 69 | 58 | 68 | 0.33052 | 120.62 | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.03343 | 120.6 | P42:345:NPPD:BKR-CE-3306
Thermal | 09ALL | 2 | 24WP | GEN-2016-109 | 'FROM -> TO' | FAIRBRY7 - HARBINE7115 |  | 99 | 0.62895 | 120.59 | P42:345:NPPD:BKR-MOR-3310
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03919 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05468 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07912 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.04146 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03006 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.065 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.08082 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07991 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.08464 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07046 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05441 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07046 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07046 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.49605 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07887 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.33445 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05868 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03907 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07046 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.0481 | 120.57 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.07585 | 120.5 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.18234 | 120.5 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.11512 | 120.5 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.07585 | 120.5 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.18234 | 120.5 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | TEKAMAH5 - S1226 5 161 1 |  | 256 | 0.11512 | 120.5 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.03936 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.03919 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.05468 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.07912 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.03373 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.18293 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.04146 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.03006 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.065 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.08082 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.07991 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.08464 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.04138 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.05441 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.07887 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.04138 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.33445 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.05868 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.03907 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.03103 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.03036 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.03135 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.0481 | 120.46 | P42:345:NPPD:BKR-HOS-3322
Thermal | 15ALL | 2 | 24L | GEN-2016-103 | 'FROM -> TO' | GR PRAIRIE 3 - GRPRAR1-LNX3 345 | 720 |  | 0.25565 | 120.42 | System Intact
Thermal | 15ALL | 2 | 24L | GEN-2017-094 | 'FROM -> TO' | GR PRAIRIE 3 - GRPRAR1-LNX3 345 | 720 |  | 0.17638 | 120.42 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04691 | 120.3 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05272 | 120.3 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03091 | 120.3 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.11888 | 120.3 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05516 | 120.3 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07711 | 120.3 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.0464 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.0464 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.08891 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-077 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.07129 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-078 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.18706 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.06456 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-171 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.04529 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.11883 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.21235 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-012 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.09129 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.20761 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.25847 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.22856 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.20761 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-079 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.12282 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.25847 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-081 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.07287 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-084 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.10707 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.20748 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.13038 | 120.26 | System Intact
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.38395 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.38395 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.28988 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.3736 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.31509 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.37523 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.37762 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.28075 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.32582 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.21467 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.32205 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.32756 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.33509 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.40009 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.32205 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.2901 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.32756 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.23455 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.27909 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.32259 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.30781 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.37877 | 120.23 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.04897 | 120.21 | P12:161:EMDE:::AUR124_RDS424
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07239 | 120.2 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07239 | 120.2 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07239 | 120.2 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07239 | 120.2 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 12ALL | 2 | 19WP | GEN-2017-082 | 'FROM -> TO' | ASB349 5 - PUR421 5 161 |  | 223 | 0.57115 | 120.03 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 00NR | 2 | 24SP | GEN-2016-077 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.06003 | 119.99 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 24SP | GEN-2016-090 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.08182 | 119.99 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 06ALL | 2 | 19WP | ASGI-2016-001 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.06266 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | ASGI-2017-007 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.06266 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.15014 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-077 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.07479 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.11676 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-090 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.07603 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-171 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.07277 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.1601 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.10131 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.23997 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.10589 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.09696 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.09398 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.04756 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.10589 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.03187 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-079 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.14985 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.09696 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.20094 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-084 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.16262 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.10528 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.13045 | 119.97 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-104 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.06903 | 119.97 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07239 | 119.93 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07239 | 119.93 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07239 | 119.93 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07239 | 119.93 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.04671 | 119.88 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.06235 | 119.88 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.07912 | 119.88 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03006 | 119.88 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.065 | 119.88 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.08082 | 119.88 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.07991 | 119.88 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.05441 | 119.88 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.07887 | 119.88 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.33445 | 119.88 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03907 | 119.88 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.0481 | 119.88 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | ASGI-2016-001 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.06266 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | ASGI-2017-007 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.06266 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.15014 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-077 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.07479 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.11676 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-090 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.07603 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-171 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.07277 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.1601 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.10131 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.23997 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.10589 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.09696 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.09398 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.04756 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.10589 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-078 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.03187 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-079 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.14985 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.09696 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.20094 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-084 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.16262 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.10528 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.13045 | 119.86 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-104 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.06903 | 119.86 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2016-173 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.03451 | 119.84 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.05211 | 119.84 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.04861 | 119.84 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.7131 | 119.84 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.7131 | 119.84 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.7131 | 119.84 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 1 | 119.84 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.11509 | 119.84 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.03295 | 119.84 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 1 | 119.84 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.05536 | 119.84 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.03534 | 119.84 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.7131 | 119.84 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.07315 | 119.84 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | BV-COM-4 - MOUNDRD4 138 1 | 131 |  | 0.17728 | 119.84 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03936 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03919 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.05468 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.07912 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03373 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03026 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03006 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.065 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.08082 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.07991 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.04138 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.05441 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.07887 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.04138 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.33445 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.10685 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03103 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03036 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03135 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.0481 | 119.82 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03936 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03919 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.05468 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.07912 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03373 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03026 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03006 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.065 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.08082 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.07991 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.04138 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.05441 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.07887 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.04138 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.33445 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.10685 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03103 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03036 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03135 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.0481 | 119.82 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.03936 | 119.8 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.07912 | 119.8 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.03373 | 119.8 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.08082 | 119.8 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.07991 | 119.8 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.04138 | 119.8 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.05441 | 119.8 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.04138 | 119.8 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.33445 | 119.8 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.03103 | 119.8 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.03036 | 119.8 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.03135 | 119.8 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.03936 | 119.8 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.07912 | 119.8 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.03373 | 119.8 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.08082 | 119.8 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.07991 | 119.8 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.04138 | 119.8 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.05441 | 119.8 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.04138 | 119.8 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.33445 | 119.8 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.03103 | 119.8 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.03036 | 119.8 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.03135 | 119.8 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.07912 | 119.8 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.08082 | 119.8 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.07991 | 119.8 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.05441 | 119.8 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.33445 | 119.8 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.03936 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.03919 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.05468 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.07912 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.03373 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.04146 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.03006 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.065 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.08082 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.07991 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.08464 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.71194 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.04138 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.05441 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.71194 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.71194 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.49605 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.07887 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.04138 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.33445 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.05868 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.03907 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.03103 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.03036 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.03135 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.71194 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.0481 | 119.76 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24SP | GEN-2017-071 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.09347 | 119.74 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24SP | GEN-2017-072 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.09347 | 119.74 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24SP | GEN-2017-071 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.09347 | 119.74 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24SP | GEN-2017-072 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.09347 | 119.74 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08ALL | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 189 | 0.25064 | 119.74 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | PLSNT_HILL 3 - E_CLOVIS 3 115 1 |  | 123.1 | 0.36925 | 119.69 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | PLSNT_HILL 3 - E_CLOVIS 3 115 1 |  | 123.1 | 0.36925 | 119.69 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | PLSNT_HILL 3 - E_CLOVIS 3 115 1 |  | 123.1 | 0.28232 | 119.69 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05272 | 119.69 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 07NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.03265 | 119.69 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.2862 | 119.69 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.26646 | 119.69 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.06083 | 119.69 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.06083 | 119.69 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04153 | 119.67 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.07912 | 119.67 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.08082 | 119.67 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.07991 | 119.67 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03806 | 119.67 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.05441 | 119.67 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03806 | 119.67 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.33445 | 119.67 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04153 | 119.67 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.07912 | 119.67 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.08082 | 119.67 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.07991 | 119.67 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03806 | 119.67 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.05441 | 119.67 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03806 | 119.67 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.33445 | 119.67 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04153 | 119.67 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.07912 | 119.67 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.08082 | 119.67 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.07991 | 119.67 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03806 | 119.67 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.05441 | 119.67 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03806 | 119.67 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.33445 | 119.67 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04153 | 119.67 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.07912 | 119.67 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.08082 | 119.67 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.07991 | 119.67 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03806 | 119.67 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.05441 | 119.67 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03806 | 119.67 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.33445 | 119.67 | P42:345:GRDA:CLEVLND CB13280
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.09141 | 119.62 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-078 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.05587 | 119.62 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.06556 | 119.62 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-012 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.03516 | 119.62 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-079 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.09342 | 119.62 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-081 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.03357 | 119.62 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-084 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.04296 | 119.62 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.14614 | 119.62 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 | 152 |  | 0.2483 | 119.5 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03919 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05468 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07912 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.04146 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03006 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.065 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08082 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07991 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08464 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07261 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05441 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07261 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07261 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.49605 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07887 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.33445 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05868 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03907 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07261 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.0481 | 119.46 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.73122 | 119.4 | P23:345:WERE:WOLF_345-120::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.0323 | 119.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05272 | 119.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.0681 | 119.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.09322 | 119.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07364 | 119.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.09322 | 119.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.09322 | 119.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03837 | 119.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 1 | 119.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.11888 | 119.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05516 | 119.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.09322 | 119.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07711 | 119.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03929 | 119.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.0464 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.0464 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.08891 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-077 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.07129 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-078 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.18706 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.06456 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-171 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.04529 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.11883 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.21235 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-012 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.09129 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.20761 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.25847 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.22856 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.20761 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-079 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.12282 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.25847 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-081 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.07287 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-084 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.10707 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.20748 | 119.34 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.13038 | 119.34 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.0323 | 119.29 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05272 | 119.29 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.0681 | 119.29 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.09323 | 119.29 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07364 | 119.29 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.09323 | 119.29 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.09323 | 119.29 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03837 | 119.29 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 1 | 119.29 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.11888 | 119.29 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05516 | 119.29 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.09323 | 119.29 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07711 | 119.29 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03929 | 119.29 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | PLSNT_HILL 3 - E_CLOVIS 3 115 1 |  | 123.1 | 0.36655 | 119.25 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | PLSNT_HILL 3 - E_CLOVIS 3 115 1 |  | 123.1 | 0.36655 | 119.25 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | PLSNT_HILL 3 - E_CLOVIS 3 115 1 |  | 123.1 | 0.27967 | 119.25 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.73028 | 119.2 | P12:345:WERE:WAVS-LACY_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04149 | 119.18 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.07912 | 119.18 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.08082 | 119.18 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.07991 | 119.18 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03801 | 119.18 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.05441 | 119.18 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03801 | 119.18 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.33445 | 119.18 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04149 | 119.18 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.07912 | 119.18 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.08082 | 119.18 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.07991 | 119.18 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03801 | 119.18 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.05441 | 119.18 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03801 | 119.18 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.33445 | 119.18 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.73028 | 119.17 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03919 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05468 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07912 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.04146 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03006 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.065 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.08082 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07991 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.08464 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07261 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05441 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07261 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07261 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.49605 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07887 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.33445 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05868 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03907 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07261 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.0481 | 119.16 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.72808 | 119.16 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 01NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.2861 | 119.04 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 01NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.26636 | 119.04 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 01NR | 2 | 24L | GEN-2017-027 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05348 | 119.04 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 01NR | 2 | 24L | GEN-2017-075 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.13873 | 119.04 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.04951 | 118.94 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 1 | 118.94 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 1 | 118.94 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03936 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03919 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.05468 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.07912 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03373 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03026 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03006 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.065 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.08082 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.07991 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.04138 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.05441 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.07887 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.04138 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.33445 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.10685 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03103 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03036 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03135 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.0481 | 118.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03936 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03919 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.05468 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.07912 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03373 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03026 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03006 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.065 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.08082 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.07991 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.04138 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.05441 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.07887 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.04138 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.33445 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.10685 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03103 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03036 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03135 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.0481 | 118.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.0323 | 118.92 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.05264 | 118.92 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.05272 | 118.92 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.0681 | 118.92 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.04884 | 118.92 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.06119 | 118.92 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.11888 | 118.92 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.06119 | 118.92 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.07876 | 118.92 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.07711 | 118.92 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.0323 | 118.92 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.05264 | 118.92 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.05272 | 118.92 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.0681 | 118.92 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.04884 | 118.92 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.06119 | 118.92 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.11888 | 118.92 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.06119 | 118.92 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.07876 | 118.92 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.07711 | 118.92 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.0323 | 118.86 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.06321 | 118.86 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05272 | 118.86 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.0681 | 118.86 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.07364 | 118.86 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03837 | 118.86 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.11888 | 118.86 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05516 | 118.86 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.07711 | 118.86 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03929 | 118.86 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.03507 | 118.8 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.03936 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.07912 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.03373 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.08364 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.08082 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.07991 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.04138 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.05441 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.20644 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.04138 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.33445 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.03907 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.03103 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.03036 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.03135 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.12899 | 118.7 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.03936 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.07912 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.03373 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.08364 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.08082 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.07991 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.04138 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.05441 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.20644 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.04138 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.33445 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.03907 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.03103 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.03036 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.03135 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.12899 | 118.67 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.03964 | 118.66 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 24SP | GEN-2016-107 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.06087 | 118.66 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 24SP | GEN-2017-023 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.08127 | 118.66 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.08038 | 118.66 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.03383 | 118.66 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 24SP | GEN-2017-036 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.04656 | 118.66 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.03383 | 118.66 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 24SP | GEN-2017-066 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.26513 | 118.66 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 24SP | GEN-2017-067 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.04487 | 118.66 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 06ALL | 2 | 24WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.27814 | 118.66 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.27814 | 118.66 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.21271 | 118.66 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.33315 | 118.66 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.20079 | 118.66 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.21165 | 118.66 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 03NR | 2 | 24L | GEN-2016-077 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.04648 | 118.65 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 03NR | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.0678 | 118.65 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.28974 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.28974 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.22276 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.21051 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20689 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20428 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20324 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.21693 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20557 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.33886 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20324 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.21305 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.21693 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20951 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20317 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.22472 | 118.61 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03936 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03919 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.05468 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.07912 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03373 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03006 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.065 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.08082 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.07991 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.04138 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.05441 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.07887 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.04138 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.33445 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03907 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-071 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.09318 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-072 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.09318 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03103 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03036 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03135 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.0481 | 118.59 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03936 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03919 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.05468 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.07912 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03373 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03006 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.065 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.08082 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.07991 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.04138 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.05441 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.07887 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.04138 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.33445 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03907 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-071 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.09318 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-072 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.09318 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03103 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03036 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03135 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.0481 | 118.59 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24SP | GEN-2017-011 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03041 | 118.56 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.10798 | 118.56 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-011 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03041 | 118.56 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.10798 | 118.56 | P23:345:WERE:BENT_345-110::
Thermal | 06ALL | 2 | 24WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.26272 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.26272 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.18689 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.15245 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.14133 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.10998 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.07872 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.16192 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.12182 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.12333 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.1228 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.13091 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.12486 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.32485 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.1228 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.16668 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.13091 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.15094 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.16833 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.12249 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.17569 | 118.52 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.06705 | 118.52 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05211 | 118.49 | P12:161:EES-EAI:GRANVW:EUREKASP:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04861 | 118.49 | P12:161:EES-EAI:GRANVW:EUREKASP:1
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.06194 | 118.49 | P12:161:EES-EAI:GRANVW:EUREKASP:1
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.0558 | 118.49 | P12:161:EES-EAI:GRANVW:EUREKASP:1
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04086 | 118.49 | P12:161:EES-EAI:GRANVW:EUREKASP:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 118.49 | P12:161:EES-EAI:GRANVW:EUREKASP:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.11509 | 118.49 | P12:161:EES-EAI:GRANVW:EUREKASP:1
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.26313 | 118.49 | P12:161:EES-EAI:GRANVW:EUREKASP:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 118.49 | P12:161:EES-EAI:GRANVW:EUREKASP:1
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05536 | 118.49 | P12:161:EES-EAI:GRANVW:EUREKASP:1
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04936 | 118.49 | P12:161:EES-EAI:GRANVW:EUREKASP:1
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07828 | 118.49 | P12:161:EES-EAI:GRANVW:EUREKASP:1
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07315 | 118.49 | P12:161:EES-EAI:GRANVW:EUREKASP:1
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05211 | 118.49 | P12:161:EES-EAI-AEPW:5GDVIEW:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04861 | 118.49 | P12:161:EES-EAI-AEPW:5GDVIEW:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.06194 | 118.49 | P12:161:EES-EAI-AEPW:5GDVIEW:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.0558 | 118.49 | P12:161:EES-EAI-AEPW:5GDVIEW:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04086 | 118.49 | P12:161:EES-EAI-AEPW:5GDVIEW:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 118.49 | P12:161:EES-EAI-AEPW:5GDVIEW:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.11509 | 118.49 | P12:161:EES-EAI-AEPW:5GDVIEW:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.26313 | 118.49 | P12:161:EES-EAI-AEPW:5GDVIEW:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 118.49 | P12:161:EES-EAI-AEPW:5GDVIEW:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05536 | 118.49 | P12:161:EES-EAI-AEPW:5GDVIEW:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04936 | 118.49 | P12:161:EES-EAI-AEPW:5GDVIEW:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07828 | 118.49 | P12:161:EES-EAI-AEPW:5GDVIEW:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07315 | 118.49 | P12:161:EES-EAI-AEPW:5GDVIEW:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05211 | 118.49 | P12:HV:EES::5GRANDVIEW%:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04861 | 118.49 | P12:HV:EES::5GRANDVIEW%:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.06194 | 118.49 | P12:HV:EES::5GRANDVIEW%:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.0558 | 118.49 | P12:HV:EES::5GRANDVIEW%:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04086 | 118.49 | P12:HV:EES::5GRANDVIEW%:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 118.49 | P12:HV:EES::5GRANDVIEW%:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.11509 | 118.49 | P12:HV:EES::5GRANDVIEW%:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.26313 | 118.49 | P12:HV:EES::5GRANDVIEW%:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 1 | 118.49 | P12:HV:EES::5GRANDVIEW%:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05536 | 118.49 | P12:HV:EES::5GRANDVIEW%:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04936 | 118.49 | P12:HV:EES::5GRANDVIEW%:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07828 | 118.49 | P12:HV:EES::5GRANDVIEW%:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07315 | 118.49 | P12:HV:EES::5GRANDVIEW%:EUREKA 5!:1
Thermal | 08NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.03424 | 118.38 | P12:345:OKGE:BKRBKR295
Thermal | 08NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.03424 | 118.38 | P41:345:OKGE:SB_MUGE7385
Thermal | 08NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.03425 | 118.38 | P42:345:OKGE:SB_FTTH7385
Thermal | 08NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.03425 | 118.37 | P42:345:OKGE:SB_FTTH7386
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05943 | 118.29 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-107 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.04629 | 118.29 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-011 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.09664 | 118.29 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05969 | 118.29 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-028 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03283 | 118.29 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.06287 | 118.29 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05345 | 118.29 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03329 | 118.29 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05345 | 118.29 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-067 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03363 | 118.29 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.23428 | 118.29 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-086 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.10722 | 118.29 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03409 | 118.29 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.03944 | 118.27 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 24WP | GEN-2016-173 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.035 | 118.27 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.05211 | 118.27 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.04861 | 118.27 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.7123 | 118.27 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.7123 | 118.27 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.7123 | 118.27 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 1 | 118.27 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.11509 | 118.27 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.03336 | 118.27 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 1 | 118.27 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.05536 | 118.27 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.03579 | 118.27 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.7123 | 118.27 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.07315 | 118.27 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 20SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03102 | 118.24 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05946 | 118.24 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03102 | 118.24 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05946 | 118.24 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03919 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05468 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07912 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.04146 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03006 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.065 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08082 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07991 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08464 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07229 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05441 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07229 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07229 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.49605 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07887 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.33445 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05868 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03907 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07229 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.0481 | 118.21 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24SP | GEN-2017-011 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03088 | 118.19 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.0524 | 118.19 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-011 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03088 | 118.19 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.0524 | 118.19 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.06066 | 118.19 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03936 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03919 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05468 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07912 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03373 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.0497 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.04146 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03006 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.065 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.08082 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07991 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.08464 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.04138 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05441 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07887 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.04138 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.33445 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05868 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03907 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03103 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03036 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03135 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.0481 | 118.17 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 20SP | GEN-2017-004 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03141 | 118.12 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06743 | 118.12 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06743 | 118.12 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06743 | 118.12 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06743 | 118.12 | P12:345:WERE:87TH-STRA_345::
Thermal | 06ALL | 2 | 19WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.29227 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.29227 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.2191 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.22877 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.21169 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.20456 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.20511 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.20236 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.20149 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.22216 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.21878 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.32953 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.20149 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.21169 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.22216 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.2068 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.20126 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 699 | 0.22414 | 118.11 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.32904 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.32904 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.25216 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22516 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23805 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23391 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23091 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22972 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24543 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.2324 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.38535 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22972 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24094 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24543 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20478 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23693 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22964 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.25425 | 117.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05483 | 117.96 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-011 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.09468 | 117.96 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-018 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05642 | 117.96 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-028 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03163 | 117.96 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-032 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05957 | 117.96 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.0487 | 117.96 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-047 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03027 | 117.96 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.0487 | 117.96 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-067 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.0327 | 117.96 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.21574 | 117.96 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.07943 | 117.96 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-100 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03106 | 117.96 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03919 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05468 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07912 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.04146 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03006 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.065 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.08082 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07991 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.08464 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07229 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05441 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07229 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07229 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.49605 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07887 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.33445 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05868 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03907 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07229 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.0481 | 117.87 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.30547 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.30547 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.21846 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.17893 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.16618 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.1302 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.09434 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.1898 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.14378 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.14552 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.14492 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.15422 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.14727 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.37676 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.14492 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.19526 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.15422 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.17721 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.19716 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.14455 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.2056 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 | 559 |  | 0.08093 | 117.78 | System Intact
Thermal | 06ALL | 2 | 24WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.26272 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.26272 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.18689 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.15245 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.14133 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.10998 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.07872 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.16192 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.12182 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.12333 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.1228 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.13091 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.12486 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.32485 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.1228 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.16668 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.13091 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.15094 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.16833 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.12249 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.17569 | 117.75 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.06705 | 117.75 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.72954 | 117.75 | P23:345:WERE:WOLF_345-120::
Thermal | 00NR | 2 | 24SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03041 | 117.74 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.10798 | 117.74 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03041 | 117.74 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.10798 | 117.74 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 20SP | GEN-2017-004 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.0346 | 117.72 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 20SP | GEN-2017-032 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.03627 | 117.72 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.0323 | 117.65 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.03442 | 117.65 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.18808 | 117.65 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.0681 | 117.65 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.07364 | 117.65 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.03837 | 117.65 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.03046 | 117.65 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.05516 | 117.65 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.03929 | 117.65 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2016-103 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05215 | 117.64 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.16931 | 117.64 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05211 | 117.64 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 1 | 117.64 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 1 | 117.64 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05536 | 117.64 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.04872 | 117.64 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CARTHAG5 - ATL109 5 161 1 |  | 222 | 0.03936 | 117.62 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CARTHAG5 - ATL109 5 161 1 |  | 222 | 0.07912 | 117.62 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CARTHAG5 - ATL109 5 161 1 |  | 222 | 0.03373 | 117.62 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CARTHAG5 - ATL109 5 161 1 |  | 222 | 0.08082 | 117.62 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CARTHAG5 - ATL109 5 161 1 |  | 222 | 0.07991 | 117.62 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CARTHAG5 - ATL109 5 161 1 |  | 222 | 0.04138 | 117.62 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CARTHAG5 - ATL109 5 161 1 |  | 222 | 0.05441 | 117.62 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CARTHAG5 - ATL109 5 161 1 |  | 222 | 0.04138 | 117.62 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CARTHAG5 - ATL109 5 161 1 |  | 222 | 0.33445 | 117.62 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CARTHAG5 - ATL109 5 161 1 |  | 222 | 0.03103 | 117.62 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CARTHAG5 - ATL109 5 161 1 |  | 222 | 0.03036 | 117.62 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CARTHAG5 - ATL109 5 161 1 |  | 222 | 0.03135 | 117.62 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.0323 | 117.62 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05008 | 117.62 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05272 | 117.62 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.0681 | 117.62 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07364 | 117.62 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03837 | 117.62 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.11888 | 117.62 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05516 | 117.62 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07711 | 117.62 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03929 | 117.62 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.06091 | 117.56 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.03343 | 117.54 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.71197 | 117.5 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.71197 | 117.5 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.71197 | 117.5 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1136 | 0.71197 | 117.5 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04054 | 117.5 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.0479 | 117.5 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.0479 | 117.5 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05661 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.07912 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.09876 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05936 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.08082 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.07991 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03215 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2017-032 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.06245 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05024 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05441 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2017-047 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03189 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.05024 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.33445 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03364 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.21459 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.07146 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 00NR | 2 | 29SP | GEN-2017-100 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03272 | 117.47 | P12:138:WERE:GORD-MAIZ_138::
Thermal | 16ALL | 2 | 24SP | GEN-2017-010 | 'FROM -> TO' | BROADLND-BE3 - BD KU2A 345/230 | 400 |  | 0.1049 | 117.45 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | BROADLND-BE3 - BD KU2A 345/230 | 400 |  | 0.13344 | 117.45 | System Intact
Thermal | 06ALL | 2 | 24WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.27814 | 117.43 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.27814 | 117.43 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.21271 | 117.43 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.33315 | 117.43 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.20079 | 117.43 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.21165 | 117.43 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 00NR | 2 | 20SP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04184 | 117.4 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.08019 | 117.4 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03162 | 117.4 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.08019 | 117.4 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.08019 | 117.4 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.08019 | 117.4 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.06361 | 117.37 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 1 | 117.37 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 1 | 117.37 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.04931 | 117.32 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04677 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04861 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06194 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0558 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07012 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03092 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07012 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07012 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 1 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.11509 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.26313 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 1 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05536 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07828 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07012 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07315 | 117.29 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 01ALL | 2 | 24WP | GEN-2016-107 | 'FROM -> TO' | DOVERSW4 - OKEENE 4 138 |  | 99 | 0.36799 | 117.29 | P12:138:WFEC:OKEENE_WATONGA:2024+
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03936 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03919 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05468 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07912 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03373 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.0307 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03006 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.065 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.08082 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07991 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.04138 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05441 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07887 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.04138 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.33445 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05207 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03103 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03036 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03135 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.0481 | 117.25 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03936 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03919 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05468 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07912 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03373 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.0307 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03006 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.065 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.08082 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07991 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.04138 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05441 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07887 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.04138 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.33445 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05207 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03103 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03036 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03135 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.0481 | 117.25 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03173 | 117.25 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.06934 | 117.25 | P23:345:WERE:WICH_345-50::
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 189 | 0.24976 | 117.2 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.21802 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.1879 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-173 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0312 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05211 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04861 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03643 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03493 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05373 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04086 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.22749 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11509 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.22749 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17207 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.06263 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.16824 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17402 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07315 | 117.17 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.21802 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.1879 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-173 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.0312 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05211 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04861 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03643 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.03493 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.05373 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.04086 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.22749 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.11509 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.22749 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 1 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17207 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.06263 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.16824 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.17402 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.07315 | 117.17 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.73322 | 117.1 | P12:345:WERE:WAVS-LACY_345::
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.73322 | 117.08 | P23:345:KCPL-WERE:LACYGNE_R4-9::LACYGNE-WAVERLY-LACYGT7
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.30547 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.30547 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.21846 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.17893 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.16618 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.1302 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.09434 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.1898 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.14378 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.14552 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.14492 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.15422 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.14727 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.37676 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.14492 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.19526 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.15422 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.17721 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.19716 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.14455 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.2056 | 117.02 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 | 559 |  | 0.08093 | 117.02 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05046 | 116.97 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.16809 | 116.97 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2016-103 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.0525 | 116.93 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.11396 | 116.93 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05211 | 116.93 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 1 | 116.93 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 1 | 116.93 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05536 | 116.93 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2016-103 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.0525 | 116.93 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.11396 | 116.93 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05211 | 116.93 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 1 | 116.93 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 1 | 116.93 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05536 | 116.93 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.03567 | 116.92 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 20SP | GEN-2017-004 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.0346 | 116.92 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 20SP | GEN-2017-032 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.03627 | 116.92 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06017 | 116.82 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06017 | 116.82 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06017 | 116.82 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 1 | 116.82 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06017 | 116.82 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 116.77 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 116.77 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 01NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.05345 | 116.76 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 06ALL | 2 | 24L | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.22039 | 116.74 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 00NR | 2 | 24WP | GEN-2016-103 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05215 | 116.66 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.16931 | 116.66 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05211 | 116.66 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 1 | 116.66 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 1 | 116.66 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05536 | 116.66 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03936 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03919 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05468 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.04982 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.07912 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03373 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.1697 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.04146 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.065 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.08082 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.07991 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.08464 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.04138 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05441 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.04138 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.33445 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05868 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03907 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03103 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03036 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03135 | 116.59 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04639 | 116.56 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05272 | 116.56 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0306 | 116.56 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.11888 | 116.56 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05516 | 116.56 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07711 | 116.56 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06017 | 116.56 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06017 | 116.56 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06017 | 116.56 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 1 | 116.56 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06017 | 116.56 | P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20
Thermal | 03NR | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03662 | 116.55 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06131 | 116.53 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06131 | 116.53 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06131 | 116.53 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 1 | 116.53 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.06131 | 116.53 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.08104 | 116.45 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.2477 | 116.45 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.14271 | 116.45 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z | 720 |  | 0.06129 | 116.43 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z | 720 |  | 0.16677 | 116.43 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04637 | 116.41 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05272 | 116.41 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03058 | 116.41 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.11888 | 116.41 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05516 | 116.41 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07711 | 116.41 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03936 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03919 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05468 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07912 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03373 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03153 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03006 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.065 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.08082 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07991 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.04138 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05441 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07887 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.04138 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.33445 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.06955 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03103 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03036 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03135 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.0481 | 116.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05469 | 116.36 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-011 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.09427 | 116.36 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-018 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05855 | 116.36 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-028 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03105 | 116.36 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-032 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05778 | 116.36 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.04863 | 116.36 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.04863 | 116.36 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-067 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03244 | 116.36 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.21221 | 116.36 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.07589 | 116.36 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.0323 | 116.3 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.08578 | 116.3 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.05272 | 116.3 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.0681 | 116.3 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.07364 | 116.3 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.03837 | 116.3 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.11888 | 116.3 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.05516 | 116.3 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.07711 | 116.3 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.03929 | 116.3 | P42:345:NPPD:BKR-HOS-3308
Thermal | 12ALL | 2 | 19WP | GEN-2017-082 | 'FROM -> TO' | ORO110 5 - FIR417 5 161 |  | 223 | 0.62001 | 116.27 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06131 | 116.26 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06131 | 116.26 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06131 | 116.26 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 1 | 116.26 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.06131 | 116.26 | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.08201 | 116.23 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24WP | GEN-2016-103 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05164 | 116.23 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.16387 | 116.23 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05211 | 116.23 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 1 | 116.23 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 1 | 116.23 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05536 | 116.23 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05944 | 116.21 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05944 | 116.21 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05944 | 116.21 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 1 | 116.21 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | NASHUA-5 - NASHUA11 161 11 |  | 715 | 0.05944 | 116.21 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.11534 | 116.19 | P42:345:OKGE:SB_CION7384
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.06582 | 116.19 | P42:345:OKGE:SB_CION7384
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.06582 | 116.19 | P42:345:OKGE:SB_CION7384
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.03352 | 116.15 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.03487 | 116.15 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.08364 | 116.1 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.08364 | 116.1 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.08364 | 116.1 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.08364 | 116.1 | System Intact
Thermal | 09ALL | 2 | 20SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.64818 | 116.08 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.57473 | 116.08 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.57473 | 116.08 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | LAMTON 3 - HALE_CNTY 3 115 1 |  | 79.7 | 0.3355 | 116.07 | P12:115:SPS:V09.1.HALECTR.PLANTX
Thermal | 09ALL | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - HOSKINS T2 230 |  | 336 | 0.21043 | 116.06 | P42:345:NPPD:BKR-HOS-3312
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.2156 | 116.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.20912 | 116.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.24959 | 116.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.22251 | 116.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.20912 | 116.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.24959 | 116.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.20947 | 116.04 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.18999 | 116.03 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.05218 | 116.03 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05046 | 116.01 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.16809 | 116.01 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2016-103 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.0525 | 115.97 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.11396 | 115.97 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05211 | 115.97 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 1 | 115.97 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 1 | 115.97 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05536 | 115.97 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2016-103 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.0525 | 115.97 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.11396 | 115.97 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05211 | 115.97 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 1 | 115.97 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 1 | 115.97 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05536 | 115.97 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05944 | 115.95 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05944 | 115.95 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05944 | 115.95 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 1 | 115.95 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | NASHUA 7 - NASHUA11 161 11 |  | 715 | 0.05944 | 115.95 | P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | ASB349 5 - CJ 366 5 161 |  | 223 | 0.31985 | 115.88 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | ASB349 5 - LITCH 5 161 |  | 223 | 0.31985 | 115.88 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.09408 | 115.85 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.07004 | 115.85 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-023 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05511 | 115.85 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05051 | 115.85 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.04694 | 115.85 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.10273 | 115.85 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.10273 | 115.85 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-074 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05829 | 115.85 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.07715 | 115.85 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-076 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05528 | 115.85 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-077 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05971 | 115.85 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.09408 | 115.85 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.07004 | 115.85 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-023 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05511 | 115.85 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05051 | 115.85 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.04694 | 115.85 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.10273 | 115.85 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.10273 | 115.85 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-074 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05829 | 115.85 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.07715 | 115.85 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-076 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05528 | 115.85 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-077 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05971 | 115.85 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.09152 | 115.84 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-078 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.05675 | 115.84 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.06606 | 115.84 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-012 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.03556 | 115.84 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-079 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.09421 | 115.84 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-081 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.03392 | 115.84 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-084 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.04336 | 115.84 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-091 | 'FROM -> TO' | HALE_CNTY 3 - TUCO_INT 3 115 1 | 79.7 |  | 0.14748 | 115.84 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 189 | 0.25007 | 115.82 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 115.77 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 115.77 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 08ALL | 2 | 20SP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.05782 | 115.73 | System Intact
Thermal | 08ALL | 2 | 20SP | GEN-2017-022 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.07782 | 115.73 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 |  | 559 | 0.22039 | 115.71 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03936 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03919 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05468 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.04982 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.07912 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03373 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.1697 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.04146 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.065 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.08082 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.07991 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.08464 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.04138 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05441 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.04138 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.33445 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05868 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03907 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03103 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03036 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03135 | 115.7 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.03936 | 115.69 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.07912 | 115.69 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.03373 | 115.69 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.06122 | 115.69 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.08082 | 115.69 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.07991 | 115.69 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.04138 | 115.69 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.05441 | 115.69 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.04138 | 115.69 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.33445 | 115.69 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.03907 | 115.69 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.03103 | 115.69 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.03036 | 115.69 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.03135 | 115.69 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.04865 | 115.69 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 |  | 956 | 0.73256 | 115.6 | P23:345:WERE:WOLF_345-120::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.0323 | 115.59 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05272 | 115.59 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.0681 | 115.59 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06919 | 115.59 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07364 | 115.59 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06919 | 115.59 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06919 | 115.59 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03837 | 115.59 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 1 | 115.59 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.11888 | 115.59 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05516 | 115.59 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06919 | 115.59 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07711 | 115.59 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03929 | 115.59 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 | 720 |  | 0.06129 | 115.58 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 | 720 |  | 0.16677 | 115.58 | System Intact
Thermal | 06ALL | 2 | 19WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.29227 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.29227 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.2191 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.22877 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.21169 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.20456 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.20511 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.20236 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.20149 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.22216 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.21878 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.32953 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.20149 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.21169 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.22216 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.2068 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.20126 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 699 | 0.22414 | 115.58 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 01ALL | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | DOVERSW4 - OKEENE 4 138 |  | 83 | 0.37135 | 115.56 | P12:138:WFEC:OKEENE_WATONGA:2024+
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.28974 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.28974 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.22276 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.21051 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20689 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20428 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20324 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.21693 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20557 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.33886 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20324 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.21305 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.21693 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20951 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20317 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.22472 | 115.55 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.27247 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.27247 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.189 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.19597 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.15286 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.17053 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.1418 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.16631 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.13619 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.1248 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.13669 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.14338 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.1465 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.32037 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.13669 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.17165 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.14338 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.15099 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.17148 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.13648 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.18174 | 115.42 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 615 |  | 0.12408 | 115.42 | System Intact
Thermal | 02ALL | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | COLE 3 - TC-AGGIE 3 115 | 79.7 | 79.7 | 1 | 115.33 | P12:115:SPS:W28.1.OCLTRE.COLE
Thermal | 00NR | 2 | 24WP | GEN-2016-103 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05164 | 115.25 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.16387 | 115.25 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05211 | 115.25 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 1 | 115.25 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 1 | 115.25 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05536 | 115.25 | P42:345:NPPD:BKR-SC-3306
Thermal | 01NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.05345 | 115.22 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 24SP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04663 | 115.2 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0723 | 115.2 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03054 | 115.2 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0723 | 115.2 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0723 | 115.2 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0723 | 115.2 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05389 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.07912 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.09371 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05708 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.08082 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.07991 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03055 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-032 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05883 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.04783 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05441 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-047 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03022 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.04783 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.33445 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03193 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.21027 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.07395 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-100 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.031 | 115.2 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2016-034 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 |  | 0.05116 | 115.2 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2016-093 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 |  | 0.04837 | 115.2 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-001 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 |  | 0.04521 | 115.2 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-008 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 |  | 0.03156 | 115.2 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-031 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 |  | 0.0497 | 115.2 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-037 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 |  | 0.04837 | 115.2 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03936 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03919 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.05468 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07912 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03373 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03006 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.065 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.08082 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07991 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.18985 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04138 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.05441 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07887 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04138 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.33445 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03907 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03103 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.05204 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03036 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03135 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.0481 | 115.19 | P12:345:OKGE:BKRBKR21
Thermal | 09ALL | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - HOSKINS T2 230 |  | 336 | 0.21063 | 115.18 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.03936 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.03919 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.05468 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.07912 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.03373 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.12658 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.04146 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.03006 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.065 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.08082 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.07991 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.08464 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.04138 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.05441 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.07887 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.04138 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.33445 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.05868 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.03907 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.03103 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.03036 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.03135 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | RAUN 3 - S3451 3 345 1 | 956 |  | 0.0481 | 115.17 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03936 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03919 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05468 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.04921 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.07912 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03373 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.16423 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.04146 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.065 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.08082 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.07991 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.08464 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.04138 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05441 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.04138 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.33445 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.05868 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03907 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03103 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03036 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z |  | 720 | 0.03135 | 115.15 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.0323 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2016-173 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.03737 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.05272 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.0681 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.74897 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.07364 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.74897 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.74897 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.03837 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 1 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.11888 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.03659 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.05516 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2017-086 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.03911 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.74897 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.07711 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.03929 | 115.13 | P23:161-345:GMO-KCPL:STJOE_R2-22::STJOE-NASHUA-STJOET33
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03936 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03919 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05468 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07912 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03373 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.04146 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03006 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.065 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.08082 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07991 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.08464 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06374 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.04138 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05441 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06374 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06374 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.49605 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07887 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.04138 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.33445 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05868 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03907 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03103 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03036 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03135 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06374 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.0481 | 115.09 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.11534 | 115.06 | P12:345:OKGE:BKRBKR24
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.06582 | 115.06 | P12:345:OKGE:BKRBKR24
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.06582 | 115.06 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.0911 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.03919 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05468 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.06706 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.03006 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.065 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05826 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05365 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.04671 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.09976 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.07887 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.09976 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.03907 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05533 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.07692 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05232 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05675 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.0481 | 115.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.0911 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.03919 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05468 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.06706 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.03006 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.065 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05826 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05365 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.04671 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.09976 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.07887 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.09976 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.03907 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05533 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.07692 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05232 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05675 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.0481 | 115.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.19006 | 115.03 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.05227 | 115.03 | P12:345:OKGE:BKRBKR21
Thermal | 03ALL | 2 | 24L | GEN-2016-049 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 | 350 | 0.07673 | 115.01 | System Intact
Thermal | 03ALL | 2 | 24L | GEN-2017-021 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 | 350 | 0.04899 | 115.01 | System Intact
Thermal | 03ALL | 2 | 24L | GEN-2017-032 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 | 350 | 0.03329 | 115.01 | System Intact
Thermal | 03ALL | 2 | 24L | GEN-2017-049 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 | 350 | 0.03242 | 115.01 | System Intact
Thermal | 03ALL | 2 | 24L | GEN-2017-052 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 | 350 | 0.03205 | 115.01 | System Intact
Thermal | 03ALL | 2 | 24L | GEN-2017-099 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 | 350 | 0.04899 | 115.01 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.04872 | 114.88 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 06ALL | 2 | 20SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.32904 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.32904 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.25216 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22516 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23805 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23391 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23091 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22972 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24543 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.2324 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.38535 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22972 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24094 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24543 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20478 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23693 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22964 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.25425 | 114.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 09ALL | 2 | 24SP | GEN-2016-109 | 'FROM -> TO' | BEATRCE7 - HARBINE7 115 |  | 99 | 0.57764 | 114.8 | P12:115:WERE:KNOB-NPPD_115::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03936 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03919 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05468 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.07912 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03373 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.08421 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.04146 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03006 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.065 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.08082 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.07991 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.08464 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.04138 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05441 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.07887 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.04138 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.33445 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05868 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03907 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03103 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03036 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03135 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.0481 | 114.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03936 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07912 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03373 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04512 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04146 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03006 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.08082 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07991 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.08464 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07216 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03073 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04138 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05441 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07216 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07216 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.49605 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07887 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04138 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.33445 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05868 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03907 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03103 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03036 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03135 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07216 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0481 | 114.76 | P12:345:WERE:87TH-CRAIG_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.03936 | 114.75 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.07912 | 114.75 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.03373 | 114.75 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.08075 | 114.75 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.08082 | 114.75 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.07991 | 114.75 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.04138 | 114.75 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.05441 | 114.75 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.04138 | 114.75 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.33445 | 114.75 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.03103 | 114.75 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.03036 | 114.75 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.03135 | 114.75 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0323 | 114.74 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.20826 | 114.74 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.17704 | 114.74 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.05272 | 114.74 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0681 | 114.74 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0622 | 114.74 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.21924 | 114.74 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.11888 | 114.74 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.21924 | 114.74 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.16236 | 114.74 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.10198 | 114.74 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.15873 | 114.74 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.16411 | 114.74 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.07711 | 114.74 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03936 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03919 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.05468 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.07912 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03373 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.0497 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.04146 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03006 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.065 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.08082 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.07991 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.08464 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.04138 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.05441 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.07887 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.04138 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.33445 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.05868 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03907 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03103 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03036 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03135 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.0481 | 114.68 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03936 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03919 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.05468 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07912 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03373 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03006 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.065 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.08082 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07991 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.15161 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04138 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.05441 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07887 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04138 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.33445 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03907 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03103 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04403 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03036 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03135 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.0481 | 114.67 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.07788 | 114.63 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.24372 | 114.63 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.1392 | 114.63 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.36049 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.36049 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.26647 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.35013 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.29162 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.35175 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.35417 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.25731 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.30236 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.29859 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.3041 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.31164 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.37663 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.29859 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.26665 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.3041 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.21116 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.25565 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.29913 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.28433 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20G | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.35531 | 114.63 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05747 | 114.61 | P42:345:NPPD:BKR-HOS-3322
Thermal | 09ALL | 2 | 20G | GEN-2016-109 | 'FROM -> TO' | FAIRBRY7 - HARBINE7115 | 99 |  | 0.62355 | 114.61 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-085 | 'FROM -> TO' | FAIRBRY7 - HARBINE7115 | 99 |  | 0.04988 | 114.61 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | BENTON 4 - BENT TX-2 138 1 |  | 440 | 0.03944 | 114.6 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 24SP | GEN-2017-076 | 'FROM -> TO' | GRDA1 7 - GRDAUTO1 161 1 |  | 560 | 0.04572 | 114.58 | P12:161:AECI:CHOTEAU-MAID
Thermal | 06NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.05976 | 114.55 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 06NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.05976 | 114.55 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 08ALL | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 | 151 |  | 0.24914 | 114.52 | System Intact
Thermal | 09ALL | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - HOSKINS T2 230 |  | 336 | 0.21004 | 114.49 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.03936 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.07483 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.07912 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.03373 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.0442 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.08082 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.07991 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.04138 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.05441 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.04138 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.33445 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.03907 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.03103 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.03036 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.03135 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.05712 | 114.47 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03936 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.039 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.07912 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03373 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03006 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.065 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.08082 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.07991 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.04138 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.05441 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.07887 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.04138 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.33445 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03907 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03103 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03036 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03135 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.0481 | 114.45 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 20SP | GEN-2017-011 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03216 | 114.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 20SP | GEN-2017-018 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03587 | 114.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.12721 | 114.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.04154 | 114.41 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.06014 | 114.35 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 1 | 114.35 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 1 | 114.35 | P42:345:NPPD:BKR-HOS-3322
Thermal | 16ALL | 2 | 20SP | GEN-2017-010 | 'FROM -> TO' | BROADLND-BE3 - BD KU2A 345/230 | 400 |  | 0.10219 | 114.33 | System Intact
Thermal | 16ALL | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | BROADLND-BE3 - BD KU2A 345/230 | 400 |  | 0.12965 | 114.33 | System Intact
Thermal | 12ALL | 2 | 24WP | GEN-2017-082 | 'FROM -> TO' | ORO110 5 - FIR417 5 161 |  | 223 | 0.62017 | 114.3 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03936 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03919 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05468 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.04921 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.07912 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03373 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.16423 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.04146 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.065 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.08082 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.07991 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.08464 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.04138 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05441 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.04138 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.33445 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.05868 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03907 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03103 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03036 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 |  | 720 | 0.03135 | 114.27 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.04465 | 114.15 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 1 | 114.15 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 1 | 114.15 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.0323 | 114.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-011 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03226 | 114.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.05272 | 114.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.0681 | 114.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.11888 | 114.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.11958 | 114.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-086 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.04342 | 114.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.07711 | 114.14 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.0323 | 114.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-011 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03226 | 114.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.05272 | 114.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.0681 | 114.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.11888 | 114.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.11958 | 114.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-086 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.04342 | 114.14 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.07711 | 114.14 | P23:345:WERE:BENT_345-110::
Thermal | 09ALL | 2 | 20SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.64818 | 114.14 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.57473 | 114.14 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.57473 | 114.14 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - HOSKINS T2 230 |  | 336 | 0.21386 | 114.13 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.16485 | 114.09 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24SP | GEN-2016-107 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.05165 | 114.09 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24SP | GEN-2017-023 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.08487 | 114.09 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.08407 | 114.09 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.03051 | 114.09 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.10244 | 114.09 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24SP | GEN-2017-036 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.0433 | 114.09 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.10244 | 114.09 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24SP | GEN-2017-066 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.26524 | 114.09 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24SP | GEN-2017-067 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.23756 | 114.09 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.03988 | 114.09 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.0323 | 114.08 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05272 | 114.08 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.0681 | 114.08 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.06187 | 114.08 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07364 | 114.08 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.06187 | 114.08 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.06187 | 114.08 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03837 | 114.08 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 1 | 114.08 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.11888 | 114.08 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05516 | 114.08 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.06187 | 114.08 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07711 | 114.08 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03929 | 114.08 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 09ALL | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T2 230 |  | 336 | 0.21043 | 114.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 20SP | GEN-2017-011 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03102 | 114.07 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05946 | 114.07 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-011 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03102 | 114.07 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05946 | 114.07 | P23:345:WERE:BENT_345-110::
Thermal | 09ALL | 2 | 24SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.65227 | 114.03 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.57832 | 114.03 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.57832 | 114.03 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | ASB349 5 - PUR421 5 161 |  | 223 | 0.29594 | 114.02 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03919 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05468 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07912 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.04146 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03006 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.065 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08082 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07991 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.08464 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05843 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05441 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05843 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05843 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.49605 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07887 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.33445 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05868 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.03907 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05843 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.0481 | 113.99 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 09ALL | 2 | 20SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.63345 | 113.99 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.56075 | 113.99 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.56075 | 113.99 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 19WP | GEN-2017-004 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.04484 | 113.94 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.05272 | 113.94 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.03644 | 113.94 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.11888 | 113.94 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.05516 | 113.94 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.07711 | 113.94 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04625 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04861 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06194 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0558 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06909 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03062 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06909 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06909 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 1 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.11509 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.26313 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 1 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05536 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07828 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06909 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07315 | 113.87 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 09ALL | 2 | 20SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.64818 | 113.86 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.57473 | 113.86 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.57473 | 113.86 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.04931 | 113.77 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 16NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | BRULE 7 - OGALALA_-TS7 115 1 |  | 120 | 0.03215 | 113.76 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 16NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | BRULE 7 - OGALALA_-TS7 115 1 |  | 120 | 0.07626 | 113.76 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 16NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | BRULE 7 - OGALALA_-TS7 115 1 |  | 120 | 0.04841 | 113.76 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | ASB349 5 - CJ 366 5 161 |  | 223 | 0.32006 | 113.75 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | ASB349 5 - LITCH 5 161 |  | 223 | 0.32006 | 113.75 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 07ALL | 2 | 24L | GEN-2017-053 | 'FROM -> TO' | GEROJCT2 - ESQNDLJ2 69 | 58 | 68 | 0.33052 | 113.73 | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04623 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04861 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06194 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0558 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06904 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0306 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06904 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06904 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 1 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.11509 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.26313 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 1 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05536 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07828 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06904 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07315 | 113.72 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05328 | 113.72 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-011 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.09378 | 113.72 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-018 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05851 | 113.72 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.06194 | 113.72 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.0558 | 113.72 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-028 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03056 | 113.72 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.05933 | 113.72 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.04722 | 113.72 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-047 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03071 | 113.72 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 1 | 113.72 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.04722 | 113.72 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-067 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03195 | 113.72 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.23032 | 113.72 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 1 | 113.72 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.09399 | 113.72 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-100 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 | 878 |  | 0.03149 | 113.72 | System Intact
Thermal | 01NR | 2 | 20G | GEN-2017-011 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.05372 | 113.72 | P42:345:OKGE:SB_CION7382
Thermal | 01NR | 2 | 20G | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.07932 | 113.72 | P42:345:OKGE:SB_CION7382
Thermal | 13NR | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 243 | 1 | 113.72 | P12:345:WERE:N345-AECI_345::
Thermal | 13NR | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 243 | 1 | 113.72 | P12:345:WERE:N345-AECI_345::
Thermal | 13NR | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 243 | 1 | 113.72 | P12:345:WERE:N345-AECI_345::
Thermal | 13NR | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 243 | 1 | 113.72 | P12:345:WERE:N345-AECI_345::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.0323 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2016-173 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.03777 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.05272 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.0681 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.74848 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.07364 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.74848 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.74848 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.03837 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 1 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.11888 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.03691 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.05516 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2017-086 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.03946 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.74848 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.07711 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | IATAN 7 - G17-030-TAP 345 1 |  | 1314 | 0.03929 | 113.71 | P23:161-345:KCPL-GMO:NASHUA_R2-22::NASHUA-STJOE-NASHT11
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.0323 | 113.67 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05272 | 113.67 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.0681 | 113.67 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06919 | 113.67 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07364 | 113.67 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06919 | 113.67 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06919 | 113.67 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03837 | 113.67 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 1 | 113.67 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.11888 | 113.67 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05516 | 113.67 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06919 | 113.67 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07711 | 113.67 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03929 | 113.67 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03936 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03919 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05468 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.07912 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03373 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-004 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03307 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.04146 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03006 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.08082 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.07991 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.08464 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06017 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.04138 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05441 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06017 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06017 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.49605 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.07887 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.04138 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.33445 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05868 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03907 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03103 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03036 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03135 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06017 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.0481 | 113.64 | P12:345:WERE:87TH-STRA_345::
Thermal | 06ALL | 2 | 20SP | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 |  | 559 | 0.27646 | 113.64 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 |  | 559 | 0.24071 | 113.64 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03936 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03919 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05468 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07912 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03373 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.04146 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03006 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.065 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08082 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07991 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08464 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06374 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.04138 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05441 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06374 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06374 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.49605 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07887 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.04138 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.33445 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05868 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03907 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03103 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03036 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03135 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06374 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.0481 | 113.6 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1434 | 0.11405 | 113.6 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1434 | 0.11405 | 113.6 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1434 | 0.11405 | 113.6 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1434 | 1 | 113.6 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 |  | 1434 | 0.11405 | 113.6 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | SIBLEY 5 - SIBLEYPL 161 1 |  | 446 | 0.03794 | 113.58 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | SIBLEY 5 - SIBLEYPL 161 1 |  | 446 | 0.03794 | 113.58 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | SIBLEY 5 - SIBLEYPL 161 1 |  | 446 | 0.03794 | 113.58 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | SIBLEY 5 - SIBLEYPL 161 1 |  | 446 | 0.03794 | 113.58 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 08ALL | 2 | 20G | GEN-2017-005 | 'FROM -> TO' | FRANKLIN5 161/69XFR |  | 110 | 0.27144 | 113.53 | P12:161:WERE:FRAN-LITC_161::
Thermal | 16ALL | 2 | 29SP | GEN-2017-010 | 'FROM -> TO' | BROADLND-BE3 - BD KU2A 345/230 | 400 |  | 0.10498 | 113.52 | System Intact
Thermal | 16ALL | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | BROADLND-BE3 - BD KU2A 345/230 | 400 |  | 0.13351 | 113.52 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-005 | 'FROM -> TO' | CAR395 5 - PUR421 5 161 |  | 279 | 0.29219 | 113.49 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 08ALL | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | VIOLA 345/138XFR |  | 440 | 0.23965 | 113.48 | P23:345:WERE:WICH_345-116::
Thermal | 06ALL | 2 | 20SP | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.27646 | 113.47 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 20SP | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.24071 | 113.47 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 00NR | 2 | 19WP | GEN-2017-004 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03443 | 113.46 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05272 | 113.46 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.11888 | 113.46 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.07711 | 113.46 | P12:345:WERE:87TH-STRA_345::
Thermal | 08NR | 2 | 20G | GEN-2017-011 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.05076 | 113.44 | P42:345:OKGE:SB_CION7382
Thermal | 08NR | 2 | 20G | GEN-2017-011 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.05076 | 113.44 | P42:345:OKGE:SB_CION7382
Thermal | 08NR | 2 | 20G | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.0811 | 113.44 | P42:345:OKGE:SB_CION7382
Thermal | 08NR | 2 | 20G | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.0811 | 113.44 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 19WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.27247 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.27247 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.189 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.19597 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.15286 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.17053 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.1418 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.16631 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.13619 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.1248 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.13669 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.14338 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.1465 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.32037 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.13669 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.17165 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.14338 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.15099 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.17148 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.13648 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.18174 | 113.43 | System Intact
Thermal | 06ALL | 2 | 19WP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 615 |  | 0.12408 | 113.43 | System Intact
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | BRULE 7 - OGALALA_-TS7 115 1 |  | 120 | 0.03215 | 113.4 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | BRULE 7 - OGALALA_-TS7 115 1 |  | 120 | 0.07626 | 113.4 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | BRULE 7 - OGALALA_-TS7 115 1 |  | 120 | 0.04841 | 113.4 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.0323 | 113.38 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.05008 | 113.38 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.05272 | 113.38 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.0681 | 113.38 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.07364 | 113.38 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03837 | 113.38 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.11888 | 113.38 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.05516 | 113.38 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.07711 | 113.38 | P13:115-345:NPPD:NUCOR-2
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03929 | 113.38 | P13:115-345:NPPD:NUCOR-2
Thermal | 14ALL | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.41395 | 113.37 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | BENTON 4 - BENT TX-2 138 1 |  | 440 | 0.03567 | 113.36 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.04951 | 113.36 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 1 | 113.36 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 1 | 113.36 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.15168 | 113.32 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.0441 | 113.32 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 24SP | GEN-2017-004 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03416 | 113.28 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06028 | 113.28 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06028 | 113.28 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06028 | 113.28 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06028 | 113.28 | P12:345:WERE:87TH-STRA_345::
Thermal | 02ALL | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | TEXAS_CNTY 3 - TC-MCMURRY 3 115 | 79.7 | 79.7 | 1 | 113.21 | P12:115:SPS:W28.1.OCLTRE.COLE
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.38496 | 113.17 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.51292 | 113.17 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.37198 | 113.17 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 09ALL | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T2 230 |  | 336 | 0.21063 | 113.16 | P42:345:NPPD:BKR-HOS-3312
Thermal | 16ALL | 2 | 24SP | GEN-2017-010 | 'FROM -> TO' | HEBRON 4 - MANDAN 4 230 |  | 264 | 0.23359 | 113.16 | P12:230:UMZ:# 5569 #: IN . PROPER N-1 (LINE) FOR 659351-652497-1
Thermal | 00NR | 2 | 24SP | GEN-2017-076 | 'FROM -> TO' | GRDA1 5 - GRDAUTO1 161 1 |  | 560 | 0.04572 | 113.15 | P12:161:AECI:CHOTEAU-MAID
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04129 | 113.1 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03783 | 113.1 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03783 | 113.1 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04129 | 113.1 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03783 | 113.1 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03783 | 113.1 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.3795 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.3795 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.28549 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.36915 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.31064 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.37077 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.37319 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.27633 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.32138 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.21023 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.31761 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.32312 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.33066 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.39565 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.31761 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.28567 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.32312 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.23018 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.27467 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.31815 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.30335 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.37433 | 113.07 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04145 | 113.06 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03801 | 113.06 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03801 | 113.06 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04145 | 113.06 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03801 | 113.06 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03801 | 113.06 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04145 | 113.06 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03801 | 113.06 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03801 | 113.06 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04145 | 113.06 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03801 | 113.06 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03801 | 113.06 | P42:345:GRDA:CLEVLND CB13280
Thermal | 03NR | 2 | 24L | GEN-2017-032 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.37597 | 113.04 | P42:345:OKGE:SB_BOER7384
Thermal | 03NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.27013 | 113.04 | P42:345:OKGE:SB_BOER7384
Thermal | 03NR | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.03009 | 113.04 | P42:345:OKGE:SB_BOER7384
Thermal | 03NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.28343 | 113.04 | P42:345:OKGE:SB_BOER7384
Thermal | 03NR | 2 | 24L | GEN-2017-032 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.37597 | 113.03 | P12:345:OKGE:BKRBKR429
Thermal | 03NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.27013 | 113.03 | P12:345:OKGE:BKRBKR429
Thermal | 03NR | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.03009 | 113.03 | P12:345:OKGE:BKRBKR429
Thermal | 03NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.28343 | 113.03 | P12:345:OKGE:BKRBKR429
Thermal | 03NR | 2 | 24L | GEN-2017-032 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.37597 | 113.03 | P42:345:OKGE:SB_BOER7383
Thermal | 03NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.27013 | 113.03 | P42:345:OKGE:SB_BOER7383
Thermal | 03NR | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.03009 | 113.03 | P42:345:OKGE:SB_BOER7383
Thermal | 03NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.28343 | 113.03 | P42:345:OKGE:SB_BOER7383
Thermal | 03NR | 2 | 24L | GEN-2017-032 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.37597 | 113.01 | P43:345:SPS:TUCO:NR20_19L
Thermal | 03NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.27013 | 113.01 | P43:345:SPS:TUCO:NR20_19L
Thermal | 03NR | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.03009 | 113.01 | P43:345:SPS:TUCO:NR20_19L
Thermal | 03NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.28343 | 113.01 | P43:345:SPS:TUCO:NR20_19L
Thermal | 00NR | 2 | 20SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03216 | 113 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 20SP | GEN-2017-018 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03587 | 113 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.12721 | 113 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.04154 | 113 | P23:345:WERE:WICH_345-50::
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18799 | 113 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 06NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.15133 | 113 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20189 | 113 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20189 | 113 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13235 | 113 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.12806 | 113 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13432 | 113 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18799 | 113 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.15133 | 113 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20189 | 113 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20189 | 113 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13235 | 113 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.12806 | 113 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13432 | 113 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-004 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.04484 | 112.98 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.05272 | 112.98 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.03644 | 112.98 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.11888 | 112.98 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.05516 | 112.98 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.07711 | 112.98 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.18307 | 112.96 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.13717 | 112.96 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.20236 | 112.96 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 08NR | 2 | 24L | GEN-2017-073 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.05559 | 112.96 | P22:345:SPS:EDDY_COUNTY_19L
Thermal | 09ALL | 2 | 20SP | GEN-2016-109 | 'FROM -> TO' | BEATRCE7 - HARBINE7 115 |  | 99 | 0.57081 | 112.96 | P12:115:WERE:KNOB-NPPD_115::
Thermal | 08NR | 2 | 24L | GEN-2017-073 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.05559 | 112.94 | P12:345:SPS:J14.1.EDDY.XRDS
Thermal | 09ALL | 2 | 20G | GEN-2016-034 | 'FROM -> TO' | S HAYS6 - GRTBEND6 230 | 297 |  | 0.05033 | 112.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2016-093 | 'FROM -> TO' | S HAYS6 - GRTBEND6 230 | 297 |  | 0.04816 | 112.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-001 | 'FROM -> TO' | S HAYS6 - GRTBEND6 230 | 297 |  | 0.04782 | 112.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-008 | 'FROM -> TO' | S HAYS6 - GRTBEND6 230 | 297 |  | 0.03786 | 112.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-031 | 'FROM -> TO' | S HAYS6 - GRTBEND6 230 | 297 |  | 0.04923 | 112.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-037 | 'FROM -> TO' | S HAYS6 - GRTBEND6 230 | 297 |  | 0.04816 | 112.93 | System Intact
Thermal | 07ALL | 2 | 20G | GEN-2017-036 | 'FROM -> TO' | ANADARK4 - CHERRYRD 4 138 | 145 | 169 | 0.56989 | 112.91 | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4
Thermal | 07ALL | 2 | 20G | GEN-2017-053 | 'FROM -> TO' | ANADARK4 - CHERRYRD 4 138 | 145 | 169 | 0.46247 | 112.91 | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.07912 | 112.89 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-004 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.03492 | 112.89 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.03006 | 112.89 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.08082 | 112.89 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.07991 | 112.89 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-032 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.03602 | 112.89 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.05441 | 112.89 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.07887 | 112.89 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.33445 | 112.89 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.03907 | 112.89 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.0481 | 112.89 | P11:RENO-G16-111-TAP
Thermal | 16ALL | 2 | 20SP | GEN-2017-010 | 'FROM -> TO' | HEBRON 4 - MANDAN 4 230 |  | 264 | 0.23303 | 112.89 | P12:230:UMZ:# 5569 #: IN . PROPER N-1 (LINE) FOR 659351-652497-1
Thermal | 08ALL | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | VIOLA 345/138XFR |  | 440 | 0.23969 | 112.88 | P12:345:WERE:VIOL-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.05211 | 112.87 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-011 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03049 | 112.87 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.04861 | 112.87 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 1 | 112.87 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.11509 | 112.87 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.08183 | 112.87 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 1 | 112.87 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.07315 | 112.87 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.05211 | 112.87 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-011 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03049 | 112.87 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.04861 | 112.87 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 1 | 112.87 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.11509 | 112.87 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.08183 | 112.87 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 1 | 112.87 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.07315 | 112.87 | P23:345:WERE:BENT_345-110::
Thermal | 06NR | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03369 | 112.74 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18797 | 112.72 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 06NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.15134 | 112.72 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20185 | 112.72 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20185 | 112.72 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 06NR | 2 | 24L | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13235 | 112.72 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 06NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.12806 | 112.72 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 06NR | 2 | 24L | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13433 | 112.72 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 08ALL | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | VIOLA 345/138XFR |  | 440 | 0.24004 | 112.71 | P23:345:WERE:WICH_345-116::
Thermal | 15NR | 2 | 20G | GEN-2017-048 | 'FROM -> TO' | BRKNGCO3 - WHITE 3 345 2 |  | 788.8 | 0.03812 | 112.7 | P23:345:UMZW:# 824 #: WH IN SD.
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0323 | 112.68 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.05272 | 112.68 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0681 | 112.68 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.11888 | 112.68 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.07711 | 112.68 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0323 | 112.68 | P13:345-500:OKGE:BKRBKR_3W068
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.05272 | 112.68 | P13:345-500:OKGE:BKRBKR_3W068
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0681 | 112.68 | P13:345-500:OKGE:BKRBKR_3W068
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.11888 | 112.68 | P13:345-500:OKGE:BKRBKR_3W068
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.07711 | 112.68 | P13:345-500:OKGE:BKRBKR_3W068
Thermal | 08ALL | 2 | 20G | GEN-2016-072 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.06217 | 112.67 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.03222 | 112.67 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2016-173 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.08413 | 112.67 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-068 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.07962 | 112.67 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-086 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.07326 | 112.67 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03583 | 112.66 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.05211 | 112.66 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.04861 | 112.66 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03198 | 112.66 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 112.66 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.11509 | 112.66 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 112.66 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.05536 | 112.66 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.07315 | 112.66 | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03583 | 112.66 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.05211 | 112.66 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.04861 | 112.66 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03198 | 112.66 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 112.66 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.11509 | 112.66 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 112.66 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.05536 | 112.66 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.07315 | 112.66 | P21:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Thermal | 06NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.06885 | 112.66 | P12:138:AEPW-WFEC:S.W.S.-4:WASHITA4
Thermal | 09ALL | 2 | 29SP | GEN-2016-109 | 'FROM -> TO' | BEATRCE7 - HARBINE7 115 |  | 99 | 0.57766 | 112.64 | P12:115:WERE:KNOB-NPPD_115::
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18753 | 112.55 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 06NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.15098 | 112.55 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20137 | 112.55 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20137 | 112.55 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13204 | 112.55 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.12776 | 112.55 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13401 | 112.55 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.18753 | 112.55 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.15098 | 112.55 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20137 | 112.55 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.20137 | 112.55 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13204 | 112.55 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.12776 | 112.55 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13401 | 112.55 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 | 152 |  | 0.24853 | 112.52 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | CAR395 5 - PUR421 5 161 |  | 279 | 0.29249 | 112.51 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 | 128.1 |  | 1 | 112.5 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 | 128.1 |  | 1 | 112.5 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 | 152 |  | 0.24914 | 112.45 | System Intact
Thermal | 09ALL | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - HOSKINS T2 230 |  | 336 | 0.21416 | 112.45 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.0323 | 112.39 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.06674 | 112.39 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.05272 | 112.39 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.0681 | 112.39 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.07364 | 112.39 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.03837 | 112.39 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.11888 | 112.39 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.05516 | 112.39 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.07711 | 112.39 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.03929 | 112.39 | P42:345:NPPD:BKR-SC-3306
Thermal | 12ALL | 2 | 19WP | GEN-2017-082 | 'FROM -> TO' | CARTHAG5 - CAR395 5 161 |  | 222 | 0.57115 | 112.38 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.30855 | 112.35 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.20232 | 112.35 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.19958 | 112.35 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.1991 | 112.35 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03459 | 112.35 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.20598 | 112.35 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03459 | 112.35 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.42046 | 112.35 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.30855 | 112.34 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.20232 | 112.34 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.19958 | 112.34 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.1991 | 112.34 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03459 | 112.34 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.20598 | 112.34 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.03459 | 112.34 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.42046 | 112.34 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 16ALL | 2 | 24SP | GEN-2017-010 | 'FROM -> TO' | BROADLND-BE3 - BD KU2A 345/230 | 400 |  | 0.1049 | 112.34 | System Intact
Thermal | 16ALL | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | BROADLND-BE3 - BD KU2A 345/230 | 400 |  | 0.13344 | 112.34 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-011 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03173 | 112.32 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.06934 | 112.32 | P23:345:WERE:WICH_345-50::
Thermal | 07ALL | 2 | 24L | GEN-2017-053 | 'FROM -> TO' | WALTRS-2 - ESQNDLJ2 69 | 58 | 68 | 0.33052 | 112.31 | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | LAWRENC7 - SIOUXFL7 115 1 |  | 262 | 0.05211 | 112.3 | P23:345:XEL:396 BKR SPK
Thermal | 00NR | 2 | 24WP | GEN-2017-048 | 'FROM -> TO' | LAWRENC7 - SIOUXFL7 115 1 |  | 262 | 0.03188 | 112.3 | P23:345:XEL:396 BKR SPK
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | LAWRENC7 - SIOUXFL7 115 1 |  | 262 | 1 | 112.3 | P23:345:XEL:396 BKR SPK
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | LAWRENC7 - SIOUXFL7 115 1 |  | 262 | 1 | 112.3 | P23:345:XEL:396 BKR SPK
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | LAWRENC7 - SIOUXFL7 115 1 |  | 262 | 0.05536 | 112.3 | P23:345:XEL:396 BKR SPK
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.0323 | 112.26 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05272 | 112.26 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.0681 | 112.26 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.06187 | 112.26 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07364 | 112.26 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.06187 | 112.26 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.06187 | 112.26 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03837 | 112.26 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 1 | 112.26 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.11888 | 112.26 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05516 | 112.26 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.06187 | 112.26 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07711 | 112.26 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.03929 | 112.26 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.0323 | 112.23 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03226 | 112.23 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.05272 | 112.23 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.0681 | 112.23 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.11888 | 112.23 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.11958 | 112.23 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-086 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.04342 | 112.23 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.07711 | 112.23 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.0323 | 112.23 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03226 | 112.23 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.05272 | 112.23 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.0681 | 112.23 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.11888 | 112.23 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.11958 | 112.23 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-086 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.04342 | 112.23 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.07711 | 112.23 | P23:345:WERE:BENT_345-110::
Thermal | 09ALL | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T2 230 |  | 336 | 0.21004 | 112.23 | P42:345:NPPD:BKR-HOS-3312
Thermal | 14ALL | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.41396 | 112.21 | P42:345:OKGE:SB_JOCO7303
Thermal | 17ALL | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 |  | 320 | 0.25053 | 112.2 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.03936 | 112.16 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.07912 | 112.16 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.03373 | 112.16 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.06122 | 112.16 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.08082 | 112.16 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.07991 | 112.16 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.04138 | 112.16 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.05441 | 112.16 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.04138 | 112.16 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.33445 | 112.16 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.03907 | 112.16 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.03103 | 112.16 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.03036 | 112.16 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.03135 | 112.16 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.04865 | 112.16 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.04377 | 112.16 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.05133 | 112.16 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.04635 | 112.16 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.05304 | 112.16 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.04423 | 112.16 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.05542 | 112.16 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.04377 | 112.16 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.05133 | 112.16 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.04635 | 112.16 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.05304 | 112.16 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.04423 | 112.16 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | STANTN.T-BE7 - PICKCITY-RR7 115 1 |  | 120 | 0.05542 | 112.16 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 08ALL | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | VIOLA 345/138XFR |  | 440 | 0.24007 | 112.13 | P12:345:WERE:VIOL-WICH_345::
Thermal | 09ALL | 2 | 24SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.65227 | 112.1 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.57832 | 112.1 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.57832 | 112.1 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.63345 | 112.08 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.56075 | 112.08 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.56075 | 112.08 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.03936 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.09712 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.07912 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.03373 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.08886 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.08082 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.07991 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.04138 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.05441 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.09364 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.08319 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.04138 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.33445 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.03907 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.03103 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.03036 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.03135 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.09836 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | UTICAJC7 - NAPA JCT7 115 1 |  | 120 | 0.08641 | 112.06 | P13:230:UMZW:# 235 #: FR IN SD. LOSS OF TRANSFORMER (E, F).
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.03936 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.07912 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.03373 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.07947 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.08082 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.07991 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.04138 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.05441 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.24613 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.04138 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.33445 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.03907 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.03103 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.03036 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.03135 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.14114 | 112.06 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.27149 | 112.06 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.27149 | 112.06 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20603 | 112.06 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.32644 | 112.06 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20481 | 112.06 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | ASB349 5 - PUR421 5 161 |  | 223 | 0.29608 | 112.06 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 16NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 1 |  | 478 | 0.09888 | 112.05 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 16NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 1 |  | 478 | 0.2407 | 112.05 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 16NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 1 |  | 478 | 0.15118 | 112.05 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03352 | 112.04 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03487 | 112.04 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03352 | 112.04 | P23:345:GRDA:CLEVLND CB13280
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03487 | 112.04 | P23:345:GRDA:CLEVLND CB13280
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03352 | 112.04 | P42:345:GRDA:CLEVLND CB13280
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03487 | 112.04 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.08333 | 112.01 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2016-107 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.07072 | 112.01 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-023 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.09226 | 112.01 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.09092 | 112.01 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.04402 | 112.01 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.04402 | 112.01 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-066 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.22387 | 112.01 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-067 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.08668 | 112.01 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0323 | 111.98 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19104 | 111.98 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.16692 | 111.98 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05272 | 111.98 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0681 | 111.98 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.04831 | 111.98 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19953 | 111.98 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.11888 | 111.98 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19953 | 111.98 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.15548 | 111.98 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07843 | 111.98 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.15258 | 111.98 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.15687 | 111.98 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07711 | 111.98 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.0323 | 111.97 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.04623 | 111.97 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.05272 | 111.97 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.0681 | 111.97 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.07364 | 111.97 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.03837 | 111.97 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.11888 | 111.97 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.05516 | 111.97 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.07711 | 111.97 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.03929 | 111.97 | P42:345:NPPD:BKR-CE-3306
Thermal | 09ALL | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T2 230 |  | 336 | 0.21386 | 111.97 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 20SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03187 | 111.92 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07685 | 111.92 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04573 | 111.88 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05272 | 111.88 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0302 | 111.88 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.11888 | 111.88 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05516 | 111.88 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07711 | 111.88 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0323 | 111.84 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.05272 | 111.84 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0681 | 111.84 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.11888 | 111.84 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.07711 | 111.84 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 17ALL | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 |  | 342 | 0.69751 | 111.83 | P42:345:NPPD:BKR-KEY-3310
Thermal | 17ALL | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 |  | 342 | 0.31304 | 111.83 | P42:345:NPPD:BKR-KEY-3310
Thermal | 17ALL | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 |  | 342 | 0.35674 | 111.83 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.63345 | 111.78 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.56075 | 111.78 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.56075 | 111.78 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 | 1056 |  | 0.0323 | 111.77 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 | 1056 |  | 0.17567 | 111.77 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 | 1056 |  | 0.154 | 111.77 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 | 1056 |  | 0.05272 | 111.77 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 | 1056 |  | 0.0681 | 111.77 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 | 1056 |  | 0.04351 | 111.77 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 | 1056 |  | 0.1833 | 111.77 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 | 1056 |  | 0.11888 | 111.77 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 | 1056 |  | 0.1833 | 111.77 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 | 1056 |  | 0.1437 | 111.77 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 | 1056 |  | 0.07046 | 111.77 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 | 1056 |  | 0.14108 | 111.77 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 | 1056 |  | 0.14496 | 111.77 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 | 1056 |  | 0.07711 | 111.77 | System Intact
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04946 | 111.77 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.285 | 111.77 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.26531 | 111.77 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 111.77 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 111.77 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04946 | 111.77 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.285 | 111.77 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.26531 | 111.77 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 111.77 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 111.77 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-004 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03426 | 111.76 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06265 | 111.76 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06265 | 111.76 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06265 | 111.76 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.06265 | 111.76 | P23:345:WERE:STRA_345-99::
Thermal | 08ALL | 2 | 24SP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.05768 | 111.76 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-022 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.07769 | 111.76 | System Intact
Thermal | 09ALL | 2 | 24SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.65227 | 111.76 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.57832 | 111.76 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.57832 | 111.76 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03936 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03919 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.05468 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07912 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03373 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03006 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.065 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.08082 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07991 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.15161 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04138 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.05441 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07887 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04138 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.33445 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03907 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03103 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04403 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03036 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03135 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.0481 | 111.73 | P42:345:OKGE:SB_JOCO7383
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.36409 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.36409 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.2736 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.32236 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.27725 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.30964 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.28785 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.26034 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.27151 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.26975 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.29118 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.29404 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.39389 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.26975 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.2687 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.29118 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.22159 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.2608 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.26965 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.28453 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.27068 | 111.72 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.0323 | 111.69 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.04757 | 111.69 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.05272 | 111.69 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.0681 | 111.69 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.07364 | 111.69 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03837 | 111.69 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.11888 | 111.69 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.05516 | 111.69 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.07711 | 111.69 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03929 | 111.69 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.05211 | 111.63 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.08401 | 111.63 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 1 | 111.63 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.20681 | 111.63 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 1 | 111.63 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.05536 | 111.63 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.12936 | 111.63 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.05211 | 111.63 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.08401 | 111.63 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 1 | 111.63 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.20681 | 111.63 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 1 | 111.63 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.05536 | 111.63 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.12936 | 111.63 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04539 | 111.63 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04097 | 111.63 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04097 | 111.63 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04539 | 111.63 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04097 | 111.63 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04097 | 111.63 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04539 | 111.63 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04097 | 111.63 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04097 | 111.63 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.18385 | 111.59 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.13766 | 111.59 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.20318 | 111.59 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.07788 | 111.58 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.24372 | 111.58 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.1392 | 111.58 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 06NR | 2 | 24L | GEN-2016-077 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.04089 | 111.53 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 06NR | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.06291 | 111.53 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.07912 | 111.51 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-004 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.03492 | 111.51 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.03006 | 111.51 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.08082 | 111.51 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.07991 | 111.51 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-032 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.03602 | 111.51 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.05441 | 111.51 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.07887 | 111.51 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.33445 | 111.51 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.03907 | 111.51 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.0481 | 111.51 | P11:RENO-G16-111-TAP
Thermal | 09ALL | 2 | 24SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.63727 | 111.5 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.56411 | 111.5 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.56411 | 111.5 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.15169 | 111.45 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04414 | 111.45 | P42:345:OKGE:SB_JOCO7303
Thermal | 08ALL | 2 | 20G | GEN-2017-005 | 'FROM -> TO' | FRANKLIN2 - FRAN TX-1 69 |  | 110 | 0.27144 | 111.42 | P12:161:WERE:FRAN-LITC_161::
Thermal | 14ALL | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.52864 | 111.41 | P12:138:OKGE:BKRBKR258_1
Thermal | 08ALL | 2 | 20G | GEN-2016-173 | 'FROM -> TO' | KILDARE4 - WHEAGLE4 138 1 |  | 222 | 0.29626 | 111.38 | P42:345:OKGE:SB_WONG7383
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | NELIGH 7 - PETERSBRG.N7 115 1 |  | 137 | 0.03391 | 111.37 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.20371 | 111.37 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04589 | 111.37 | P42:345:OKGE:SB_SUSD7383
Thermal | 09ALL | 2 | 19WP | GEN-2016-034 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.64845 | 111.36 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 19WP | GEN-2016-093 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.57499 | 111.36 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 19WP | GEN-2017-037 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.57499 | 111.36 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04611 | 111.35 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07125 | 111.35 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24SP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03024 | 111.35 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07125 | 111.35 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07125 | 111.35 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07125 | 111.35 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.04465 | 111.34 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 1 | 111.34 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 1 | 111.34 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0323 | 111.34 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.05272 | 111.34 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0681 | 111.34 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.11888 | 111.34 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.07711 | 111.34 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0323 | 111.34 | P13:345-500:OKGE:BKRBKR_3W068
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.05272 | 111.34 | P13:345-500:OKGE:BKRBKR_3W068
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0681 | 111.34 | P13:345-500:OKGE:BKRBKR_3W068
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.11888 | 111.34 | P13:345-500:OKGE:BKRBKR_3W068
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.07711 | 111.34 | P13:345-500:OKGE:BKRBKR_3W068
Thermal | 12ALL | 2 | 24WP | GEN-2017-082 | 'FROM -> TO' | CARTHAG5 - CAR395 5 161 |  | 222 | 0.57126 | 111.34 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 09ALL | 2 | 29SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.65238 | 111.3 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 29SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.57843 | 111.3 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 29SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.57843 | 111.3 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-004 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.04505 | 111.25 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24SP | GEN-2017-032 | 'FROM -> TO' | CIRCLE 3 - CIRC TX-1 115 1 |  | 308 | 0.03584 | 111.25 | P11:RENO-G16-111-TAP
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.25668 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.25668 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.18082 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.14655 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.13522 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.10424 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.0726 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.15579 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.11571 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.11721 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.11669 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.12481 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.11875 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.31875 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.11669 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.16049 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.12481 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.14488 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.16223 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.11638 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.16938 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.06088 | 111.24 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | PLSNT_HILL 3 - E_CLOVIS 3 115 1 |  | 123.1 | 0.36652 | 111.22 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | PLSNT_HILL 3 - E_CLOVIS 3 115 1 |  | 123.1 | 0.36652 | 111.22 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | PLSNT_HILL 3 - E_CLOVIS 3 115 1 |  | 123.1 | 0.27965 | 111.22 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.05211 | 111.2 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03049 | 111.2 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.04861 | 111.2 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 1 | 111.2 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.11509 | 111.2 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.08183 | 111.2 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 1 | 111.2 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.07315 | 111.2 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.05211 | 111.2 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03049 | 111.2 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.04861 | 111.2 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 1 | 111.2 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.11509 | 111.2 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.08183 | 111.2 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 1 | 111.2 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.07315 | 111.2 | P23:345:WERE:BENT_345-110::
Thermal | 14ALL | 2 | 19WP | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.30903 | 111.2 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 14ALL | 2 | 19WP | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.2893 | 111.2 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 03NR | 2 | 24L | GEN-2017-032 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.37597 | 111.19 | P42:345:OKGE:SB_BOER7384
Thermal | 03NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.27013 | 111.19 | P42:345:OKGE:SB_BOER7384
Thermal | 03NR | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.03009 | 111.19 | P42:345:OKGE:SB_BOER7384
Thermal | 03NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.28343 | 111.19 | P42:345:OKGE:SB_BOER7384
Thermal | 03NR | 2 | 24L | GEN-2017-032 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.37597 | 111.18 | P42:345:OKGE:SB_BOER7304
Thermal | 03NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.27013 | 111.18 | P42:345:OKGE:SB_BOER7304
Thermal | 03NR | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.03009 | 111.18 | P42:345:OKGE:SB_BOER7304
Thermal | 03NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.28343 | 111.18 | P42:345:OKGE:SB_BOER7304
Thermal | 03NR | 2 | 24L | GEN-2017-032 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.37597 | 111.17 | P12:345:OKGE:BKRBKR429
Thermal | 03NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.27013 | 111.17 | P12:345:OKGE:BKRBKR429
Thermal | 03NR | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.03009 | 111.17 | P12:345:OKGE:BKRBKR429
Thermal | 03NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.28343 | 111.17 | P12:345:OKGE:BKRBKR429
Thermal | 03NR | 2 | 24L | GEN-2017-032 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.37597 | 111.17 | P42:345:OKGE:SB_BOER7383
Thermal | 03NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.27013 | 111.17 | P42:345:OKGE:SB_BOER7383
Thermal | 03NR | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.03009 | 111.17 | P42:345:OKGE:SB_BOER7383
Thermal | 03NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | POTTER_CO 7 - WAUK 90343-A 230 1 |  | 559 | 0.28343 | 111.17 | P42:345:OKGE:SB_BOER7383
Thermal | 00NR | 2 | 20SP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04548 | 111.15 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 20SP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04548 | 111.15 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 01NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.2849 | 111.15 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 01NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.2652 | 111.15 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 01NR | 2 | 24L | GEN-2017-027 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05235 | 111.15 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 01NR | 2 | 24L | GEN-2017-075 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.13734 | 111.15 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 01NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.2849 | 111.15 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 01NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.2652 | 111.15 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 01NR | 2 | 24L | GEN-2017-027 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05235 | 111.15 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 01NR | 2 | 24L | GEN-2017-075 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.13734 | 111.15 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.04377 | 111.13 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.05133 | 111.13 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.04635 | 111.13 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.05304 | 111.13 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.04423 | 111.13 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.05542 | 111.13 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.04377 | 111.13 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.05133 | 111.13 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.04635 | 111.13 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.05304 | 111.13 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.04423 | 111.13 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | GARRISN7 - PICKCITY-RR7 115 1 |  | 120 | 0.05542 | 111.13 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04095 | 111.11 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07907 | 111.11 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 20SP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03124 | 111.11 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07907 | 111.11 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07907 | 111.11 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07907 | 111.11 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | COLMBUS7 - CRESTON7 115 1 |  | 120 | 0.08325 | 111.08 | P42:345:NPPD:BKR-HOS-3308
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 | 152 |  | 0.2483 | 111.05 | System Intact
Thermal | 14ALL | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.41406 | 111 | P42:345:OKGE:SB_JOCO7303
Thermal | 08ALL | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | VIOLA 4 - VIOLA TX-1 138 |  | 440 | 0.23965 | 110.99 | P23:345:WERE:WICH_345-116::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.03936 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.03919 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.05468 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.07912 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.03373 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.04387 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.04146 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.03006 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.065 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.08082 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.07991 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.08464 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.04138 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.05441 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.07887 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.04138 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.33445 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.05868 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.03907 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.03103 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.03036 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.03135 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.0481 | 110.96 | P42:345:NPPD:BKR-CE-3306
Thermal | 08ALL | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | VIOLA 345/138XFR |  | 440 | 0.23929 | 110.93 | P23:345:WERE:WICH_345-116::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03936 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07912 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03373 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04462 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04146 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03006 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.08082 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07991 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.08464 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07111 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03043 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04138 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05441 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07111 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07111 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.49605 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07887 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04138 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.33445 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05868 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03907 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03103 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03036 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03135 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07111 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0481 | 110.92 | P23:161-345:KCPL-WERE:CRAIG_R12-22::CRAIG-87TH-CRAIGT22
Thermal | 08ALL | 2 | 24L | GEN-2017-040 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 | 478 |  | 0.03194 | 110.9 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-092 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 | 478 |  | 0.03194 | 110.9 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2016-107 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.03092 | 110.88 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.05211 | 110.88 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.04861 | 110.88 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 1 | 110.88 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.11509 | 110.88 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.26313 | 110.88 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 1 | 110.88 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.05536 | 110.88 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.07828 | 110.88 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.07315 | 110.88 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-107 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.03092 | 110.88 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.05211 | 110.88 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.04861 | 110.88 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 1 | 110.88 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.11509 | 110.88 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.26313 | 110.88 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 1 | 110.88 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.05536 | 110.88 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.07828 | 110.88 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | ARBUCKL4 - MILL4 138 1 |  | 191 | 0.07315 | 110.88 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 03ALL | 2 | 29SP | GEN-2017-032 | 'FROM -> TO' | FINNEY 7 - G17-032-TAP 345 | 380 | 380 | 1 | 110.88 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-022 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.081 | 110.86 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 08ALL | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | VIOLA 4 - VIOLA TX-1 138 |  | 440 | 0.24004 | 110.86 | P23:345:WERE:WICH_345-116::
Thermal | 00NR | 2 | 20SP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04091 | 110.85 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07903 | 110.85 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 20SP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03122 | 110.85 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07903 | 110.85 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07903 | 110.85 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07903 | 110.85 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 | 128.1 |  | 1 | 110.85 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 | 128.1 |  | 1 | 110.85 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03936 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07912 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03373 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04459 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04146 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03006 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.08082 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07991 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.08464 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07107 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03041 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04138 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05441 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07107 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07107 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.49605 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07887 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04138 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.33445 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05868 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03907 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03103 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03036 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03135 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07107 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0481 | 110.75 | P23:161-345:KCPL-WERE:CRAIG_R11-12::CRAIG-87TH-CRAIGT11
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | LOGAN___-BE7 - KW1A 115 1 |  | 203 | 0.05913 | 110.74 | P12:115:UMZ:# 5503 #: IN . PROPER N-1 (LINE) FOR 603023-652440-1
Thermal | 08ALL | 2 | 24L | GEN-2017-040 | 'FROM -> TO' | TOLK 345/230XFR 1 | 478 |  | 0.03194 | 110.74 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-092 | 'FROM -> TO' | TOLK 345/230XFR 1 | 478 |  | 0.03194 | 110.74 | System Intact
Thermal | 06NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.1666 | 110.68 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06NR | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.10751 | 110.68 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.1787 | 110.68 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.1787 | 110.68 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06NR | 2 | 20G | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07356 | 110.68 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06NR | 2 | 20G | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.06544 | 110.68 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06NR | 2 | 20G | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07438 | 110.68 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 06NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.1666 | 110.68 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06NR | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.10751 | 110.68 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.1787 | 110.68 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.1787 | 110.68 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06NR | 2 | 20G | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07356 | 110.68 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06NR | 2 | 20G | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.06544 | 110.68 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 06NR | 2 | 20G | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07438 | 110.68 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0323 | 110.65 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.05272 | 110.65 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0681 | 110.65 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.11888 | 110.65 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.07711 | 110.65 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | ASB349 5 - CJ 366 5 161 |  | 223 | 0.32008 | 110.63 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | ASB349 5 - LITCH 5 161 |  | 223 | 0.32008 | 110.63 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.27149 | 110.62 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.27149 | 110.62 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20603 | 110.62 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.32644 | 110.62 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20481 | 110.62 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.18999 | 110.61 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.05218 | 110.61 | P12:345:OKGE:BKRBKR21
Thermal | 09ALL | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T2 230 |  | 336 | 0.21416 | 110.61 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03936 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03919 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.05468 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.07912 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03373 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03006 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.065 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.08082 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.07991 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.04138 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.05441 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.07887 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.04138 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.33445 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03907 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-071 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.16889 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-072 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.16889 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03103 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03036 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03135 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.0481 | 110.6 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03936 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03919 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.05468 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.07912 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03373 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03006 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.065 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.08082 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.07991 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.04138 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.05441 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.07887 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.04138 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.33445 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03907 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-071 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.16889 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-072 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.16889 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03103 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03036 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03135 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.0481 | 110.6 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | LOGAN___-BE7 - KW1A 115 1 |  | 203 | 0.05913 | 110.59 | P12:115:UMZ:# 5551 #: IN . PROPER N-1 (LINE) FOR 652440-655690-1
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | LOGAN___-BE7 - KW1A 115 1 |  | 203 | 0.05913 | 110.59 | P12:115:UMZW:# 156 #: NEL IN ND. FAULT ON ML-NEL-MX-GA 115 KV
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | SIBLEY 5 - SIBLEY11 161 11 |  | 440 | 0.03794 | 110.59 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | SIBLEY 5 - SIBLEY11 161 11 |  | 440 | 0.03794 | 110.59 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | SIBLEY 5 - SIBLEY11 161 11 |  | 440 | 0.03794 | 110.59 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | SIBLEY 5 - SIBLEY11 161 11 |  | 440 | 0.03794 | 110.59 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.03095 | 110.57 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.20232 | 110.57 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.19958 | 110.57 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.1991 | 110.57 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.20598 | 110.57 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.42046 | 110.57 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.03095 | 110.57 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.20232 | 110.57 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.19958 | 110.57 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.1991 | 110.57 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.20598 | 110.57 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.42046 | 110.57 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03936 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03919 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05468 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07912 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03373 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03153 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03006 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.065 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.08082 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07991 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.04138 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05441 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07887 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.04138 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.33445 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.06955 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03103 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03036 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03135 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.0481 | 110.55 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03936 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03919 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.05468 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07912 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03373 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03006 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.065 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.08082 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07991 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.20358 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04138 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.05441 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07887 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04138 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.33445 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03907 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03103 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04577 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03036 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03135 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.0481 | 110.55 | P42:345:OKGE:SB_SUSD7383
Thermal | 08ALL | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | VIOLA 345/138XFR |  | 440 | 0.23933 | 110.55 | P12:345:WERE:VIOL-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.0323 | 110.54 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03441 | 110.54 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.05272 | 110.54 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.0681 | 110.54 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.07364 | 110.54 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03837 | 110.54 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.11888 | 110.54 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.05516 | 110.54 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.07711 | 110.54 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03929 | 110.54 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 08ALL | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | VIOLA 4 - VIOLA TX-1 138 |  | 440 | 0.23969 | 110.54 | P12:345:WERE:VIOL-WICH_345::
Thermal | 08ALL | 2 | 20G | GEN-2016-173 | 'FROM -> TO' | KILDARE4 - WHEAGLE4 138 1 |  | 222 | 0.29736 | 110.52 | P12:345:OKGE:BKRBKR400
Thermal | 08ALL | 2 | 20G | GEN-2016-173 | 'FROM -> TO' | KILDARE4 - WHEAGLE4 138 1 |  | 222 | 0.29736 | 110.52 | P42:345:OKGE:SB_WONG7313
Thermal | 08ALL | 2 | 20G | GEN-2017-005 | 'FROM -> TO' | PUR421 5 - LITCH 5 161 |  | 251 | 0.36482 | 110.51 | P12:161:WERE:NSES-EMDE_161::
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.27509 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.27509 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.17006 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.22484 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.14011 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.21443 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.19923 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.14656 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.12572 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.09494 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.12557 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.1296 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.1427 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.31484 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.12557 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.15355 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.1296 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.12354 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.15104 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.12552 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.16679 | 110.46 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 | 956.1 |  | 0.1874 | 110.46 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 189 | 0.25508 | 110.46 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 |  | 189 | 0.25508 | 110.46 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 03NR | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.04461 | 110.45 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 24SP | GEN-2016-077 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03212 | 110.42 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 24SP | GEN-2016-090 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.04378 | 110.42 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04703 | 110.42 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04411 | 110.42 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04411 | 110.42 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04703 | 110.42 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04411 | 110.42 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04411 | 110.42 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04703 | 110.42 | P23:345:GRDA:CLEVLND CB13280
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04411 | 110.42 | P23:345:GRDA:CLEVLND CB13280
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04411 | 110.42 | P23:345:GRDA:CLEVLND CB13280
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04703 | 110.42 | P42:345:GRDA:CLEVLND CB13280
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04411 | 110.42 | P42:345:GRDA:CLEVLND CB13280
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04411 | 110.42 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08ALL | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | VIOLA 4 - VIOLA TX-1 138 |  | 440 | 0.24007 | 110.42 | P12:345:WERE:VIOL-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.0323 | 110.37 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05272 | 110.37 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.0681 | 110.37 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.08206 | 110.37 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07364 | 110.37 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.08206 | 110.37 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.08206 | 110.37 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03837 | 110.37 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 1 | 110.37 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.11888 | 110.37 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.05516 | 110.37 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.08206 | 110.37 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07711 | 110.37 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.03929 | 110.37 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.15168 | 110.36 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.0441 | 110.36 | P42:345:OKGE:SB_JOCO7383
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | ASB349 5 - PUR421 5 161 |  | 223 | 0.2961 | 110.28 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.25668 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.25668 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.18082 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.14655 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.13522 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.10424 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.0726 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.15579 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.11571 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.11721 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.11669 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.12481 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.11875 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.31875 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.11669 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.16049 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.12481 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.14488 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.16223 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.11638 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.16938 | 110.26 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.06088 | 110.26 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 110.22 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 110.22 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.20376 | 110.21 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04597 | 110.21 | P42:345:OKGE:SB_SUSD7383
Thermal | 01NR | 2 | 20G | GEN-2017-011 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.05372 | 110.21 | P42:345:OKGE:SB_CION7382
Thermal | 01NR | 2 | 20G | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.07932 | 110.21 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 110.21 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 110.21 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 00NR | 2 | 24SP | GEN-2017-004 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.04505 | 110.2 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 24SP | GEN-2017-032 | 'FROM -> TO' | CIRCLE 6 - CIRC TX-1 115 1 |  | 308 | 0.03584 | 110.2 | P11:RENO-G16-111-TAP
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.0323 | 110.19 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.04757 | 110.19 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.05272 | 110.19 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.0681 | 110.19 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.07364 | 110.19 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.03837 | 110.19 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.11888 | 110.19 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.05516 | 110.19 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.07711 | 110.19 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.03929 | 110.19 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24SP | GEN-2017-071 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.16834 | 110.19 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24SP | GEN-2017-072 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.16834 | 110.19 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24SP | GEN-2017-071 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.16834 | 110.19 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24SP | GEN-2017-072 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.16834 | 110.19 | P43:345:GRDA:CLEVLND CB10180
Thermal | 08NR | 2 | 20G | GEN-2017-011 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.05076 | 110.16 | P42:345:OKGE:SB_CION7382
Thermal | 08NR | 2 | 20G | GEN-2017-011 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.05076 | 110.16 | P42:345:OKGE:SB_CION7382
Thermal | 08NR | 2 | 20G | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.0811 | 110.16 | P42:345:OKGE:SB_CION7382
Thermal | 08NR | 2 | 20G | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.0811 | 110.16 | P42:345:OKGE:SB_CION7382
Thermal | 06ALL | 2 | 29SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.33791 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.33791 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.26109 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23386 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24798 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24288 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23996 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23883 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.25436 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24133 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.39429 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23883 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24996 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.25436 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.21369 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24588 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23873 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.26337 | 110.15 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 08ALL | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 189 | 0.25508 | 110.11 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 |  | 189 | 0.25508 | 110.11 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03936 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03919 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05468 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07912 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03373 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07055 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.04146 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03006 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.065 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.08082 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07991 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.08464 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.04138 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05441 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07887 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.04138 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.33445 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05868 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03907 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03103 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03036 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03135 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.0481 | 110.08 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.0323 | 110.08 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.05272 | 110.08 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.0681 | 110.08 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.11888 | 110.08 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 19WP | GEN-2017-071 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.08228 | 110.08 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 19WP | GEN-2017-072 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.08228 | 110.08 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.07711 | 110.08 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.0323 | 110.08 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.05272 | 110.08 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.0681 | 110.08 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.11888 | 110.08 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 19WP | GEN-2017-071 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.08228 | 110.08 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 19WP | GEN-2017-072 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.08228 | 110.08 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.07711 | 110.08 | P43:345:GRDA:CLEVLND CB10180
Thermal | 16NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 1 |  | 496 | 0.09888 | 110.08 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 16NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 1 |  | 496 | 0.2407 | 110.08 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 16NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 1 |  | 496 | 0.15118 | 110.08 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 17NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.77152 | 110.08 | P12:230:UMZ:# 5569 #: IN . PROPER N-1 (LINE) FOR 659351-652497-1
Thermal | 17NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.38448 | 110.08 | P12:230:UMZ:# 5569 #: IN . PROPER N-1 (LINE) FOR 659351-652497-1
Thermal | 17NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.45496 | 110.08 | P12:230:UMZ:# 5569 #: IN . PROPER N-1 (LINE) FOR 659351-652497-1
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.0323 | 110.07 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.06321 | 110.07 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.05272 | 110.07 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.0681 | 110.07 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.07364 | 110.07 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.03837 | 110.07 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.11888 | 110.07 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.05516 | 110.07 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.07711 | 110.07 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.03929 | 110.07 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.0323 | 110.07 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05272 | 110.07 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.0681 | 110.07 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08206 | 110.07 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07364 | 110.07 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08206 | 110.07 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08206 | 110.07 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03837 | 110.07 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 1 | 110.07 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.11888 | 110.07 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.05516 | 110.07 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.08206 | 110.07 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07711 | 110.07 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.03929 | 110.07 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03427 | 110.06 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05844 | 110.06 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05844 | 110.06 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05844 | 110.06 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 1 | 110.06 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 1 | 110.06 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05536 | 110.06 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05844 | 110.06 | P12:345:WERE:87TH-STRA_345::
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.15961 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2016-107 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.12333 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.10792 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05211 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.04861 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-028 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.03319 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16395 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-036 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.13088 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 1 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11509 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16395 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-066 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.13069 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-067 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.03603 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.26313 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 1 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07775 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.06977 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07865 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07828 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07315 | 110.03 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.15961 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2016-107 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.12333 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.10792 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05211 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.04861 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-028 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.03319 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16395 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-036 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.13088 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 1 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11509 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16395 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-066 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.13069 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-067 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.03603 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.26313 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 1 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07775 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.06977 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07865 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07828 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07315 | 110.03 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.03936 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.07391 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.07912 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.03373 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.04365 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.08082 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.07991 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.04138 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.05441 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.04138 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.33445 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.03907 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.03103 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.03036 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.03135 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | FTRANDL4 - LAKPLAT-ER4 230 1 |  | 320 | 0.05642 | 110.01 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.07531 | 110 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.0323 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.06405 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 19WP | GEN-2016-107 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.03449 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.05696 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.05272 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.0681 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.04419 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.06655 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.04286 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.11888 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.06655 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 19WP | GEN-2017-066 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.04108 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.05355 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.05266 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.05397 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.07711 | 109.98 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22504 | 109.95 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.18967 | 109.95 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07122 | 109.95 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06556 | 109.95 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06842 | 109.95 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.23775 | 109.95 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.23775 | 109.95 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1726 | 109.95 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.11418 | 109.95 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16839 | 109.95 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17462 | 109.95 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22504 | 109.95 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.18967 | 109.95 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07122 | 109.95 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06556 | 109.95 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06842 | 109.95 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.23775 | 109.95 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.23775 | 109.95 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1726 | 109.95 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.11418 | 109.95 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16839 | 109.95 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17462 | 109.95 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 14ALL | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.34771 | 109.94 | P12:138:OKGE:BKRBKR257
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.0969 | 109.86 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.07275 | 109.86 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-023 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.0545 | 109.86 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-024 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.04995 | 109.86 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.04666 | 109.86 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.10549 | 109.86 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.10549 | 109.86 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-074 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.06108 | 109.86 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.07658 | 109.86 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-076 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05807 | 109.86 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-077 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.06249 | 109.86 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.0969 | 109.86 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.07275 | 109.86 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-023 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.0545 | 109.86 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-024 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.04995 | 109.86 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.04666 | 109.86 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.10549 | 109.86 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.10549 | 109.86 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-074 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.06108 | 109.86 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.07658 | 109.86 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-076 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.05807 | 109.86 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-077 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 970 | 0.06249 | 109.86 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 109.84 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 109.84 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 06ALL | 2 | 24L | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.22039 | 109.83 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 109.78 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 109.78 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03936 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03919 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.05468 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.07912 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03373 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03006 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.065 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.08082 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.07991 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.18985 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.04138 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.05441 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.07887 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.04138 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.33445 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03907 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03103 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.05204 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03036 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03135 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.0481 | 109.77 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | LOGAN___-BE4 - KW1A 115 1 |  | 203 | 0.05913 | 109.76 | P12:115:UMZ:# 5503 #: IN . PROPER N-1 (LINE) FOR 603023-652440-1
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 109.75 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 109.75 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 109.75 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 109.75 | P12:115:SPS:W58.1.NORTON.LOPEZ
Thermal | 16ALL | 2 | 20SP | GEN-2017-010 | 'FROM -> TO' | BROADLND-BE3 - BD KU2A 345/230 | 400 |  | 0.10219 | 109.75 | System Intact
Thermal | 16ALL | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | BROADLND-BE3 - BD KU2A 345/230 | 400 |  | 0.12965 | 109.75 | System Intact
Thermal | 16NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 1 |  | 478 | 0.09634 | 109.68 | P42:345:NPPD:BKR-KEY-3310
Thermal | 16NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 1 |  | 478 | 0.23467 | 109.68 | P42:345:NPPD:BKR-KEY-3310
Thermal | 16NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 1 |  | 478 | 0.14736 | 109.68 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.19006 | 109.64 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.05227 | 109.64 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.0323 | 109.63 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.0463 | 109.63 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.05272 | 109.63 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.0681 | 109.63 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.07364 | 109.63 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03837 | 109.63 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.11888 | 109.63 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.05516 | 109.63 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.07711 | 109.63 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03929 | 109.63 | P42:345:NPPD:BKR-SC-3306
Thermal | 09ALL | 2 | 24WP | GEN-2016-034 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.65275 | 109.63 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24WP | GEN-2016-093 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.5788 | 109.63 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24WP | GEN-2017-037 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.5788 | 109.63 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04691 | 109.62 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04403 | 109.62 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04403 | 109.62 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04691 | 109.62 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04403 | 109.62 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04403 | 109.62 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | LOGAN___-BE4 - KW1A 115 1 |  | 203 | 0.05913 | 109.61 | P12:115:UMZ:# 5551 #: IN . PROPER N-1 (LINE) FOR 652440-655690-1
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | LOGAN___-BE4 - KW1A 115 1 |  | 203 | 0.05913 | 109.61 | P12:115:UMZW:# 156 #: NEL IN ND. FAULT ON ML-NEL-MX-GA 115 KV
Thermal | 09ALL | 2 | 20G | GEN-2016-034 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.64943 | 109.61 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20G | GEN-2016-093 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.57597 | 109.61 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20G | GEN-2017-037 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.57597 | 109.61 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.63727 | 109.61 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.56411 | 109.61 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.56411 | 109.61 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.05211 | 109.59 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.07984 | 109.59 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 1 | 109.59 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.24651 | 109.59 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 1 | 109.59 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.05536 | 109.59 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.14152 | 109.59 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 09ALL | 2 | 24L | GEN-2016-109 | 'FROM -> TO' | MARSHAL3 - SMITTYV3 115 | 86 |  | 0.08854 | 109.58 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07748 | 109.56 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07748 | 109.56 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07748 | 109.56 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 1 | 109.56 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07748 | 109.56 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 08ALL | 2 | 24L | GEN-2016-072 | 'FROM -> TO' | KILDARE4 - WHEAGLE4 138 1 | 194 |  | 0.03281 | 109.56 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2016-173 | 'FROM -> TO' | KILDARE4 - WHEAGLE4 138 1 | 194 |  | 0.25188 | 109.56 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-086 | 'FROM -> TO' | KILDARE4 - WHEAGLE4 138 1 | 194 |  | 0.03179 | 109.56 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | SIBLEY 7 - SIBLEY11 161 11 |  | 440 | 0.03794 | 109.54 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | SIBLEY 7 - SIBLEY11 161 11 |  | 440 | 0.03794 | 109.54 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | SIBLEY 7 - SIBLEY11 161 11 |  | 440 | 0.03794 | 109.54 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | SIBLEY 7 - SIBLEY11 161 11 |  | 440 | 0.03794 | 109.54 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 16NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 1 |  | 496 | 0.09888 | 109.52 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 16NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 1 |  | 496 | 0.2407 | 109.52 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 16NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 1 |  | 496 | 0.15118 | 109.52 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03765 | 109.48 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 08ALL | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 | 179 |  | 0.24769 | 109.48 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04558 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04861 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06194 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0558 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06776 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03023 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06776 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06776 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 1 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.11509 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.26313 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 1 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05536 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07828 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06776 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07315 | 109.47 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.03936 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.07912 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.03373 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.07947 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.08082 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.07991 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.04138 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.05441 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.24613 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.04138 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.33445 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.03907 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.03103 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.03036 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.03135 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.14114 | 109.46 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.08151 | 109.46 | P12:345:WERE:BENT-WICH_345::
Thermal | 08ALL | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | VIOLA 4 - VIOLA TX-1 138 |  | 440 | 0.23929 | 109.46 | P23:345:WERE:WICH_345-116::
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | LAMTON 3 - HALE_CNTY 3 115 1 |  | 79.7 | 0.34652 | 109.45 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 09ALL | 2 | 29SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.65238 | 109.42 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 29SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.57843 | 109.42 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 29SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.57843 | 109.42 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.22699 | 109.41 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.2205 | 109.41 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.26097 | 109.41 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.2339 | 109.41 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.2205 | 109.41 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.26097 | 109.41 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.22086 | 109.41 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 14ALL | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.3087 | 109.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 14ALL | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.28896 | 109.37 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05211 | 109.32 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.04861 | 109.32 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.06194 | 109.32 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.0558 | 109.32 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.04086 | 109.32 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 1 | 109.32 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.11509 | 109.32 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.26313 | 109.32 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 1 | 109.32 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05536 | 109.32 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.0616 | 109.32 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.07828 | 109.32 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.07315 | 109.32 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05211 | 109.32 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.04861 | 109.32 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.06194 | 109.32 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.0558 | 109.32 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.04086 | 109.32 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 1 | 109.32 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.11509 | 109.32 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.26313 | 109.32 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 1 | 109.32 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05536 | 109.32 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.0616 | 109.32 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.07828 | 109.32 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.07315 | 109.32 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05211 | 109.32 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.04861 | 109.32 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.06194 | 109.32 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.0558 | 109.32 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.04086 | 109.32 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 1 | 109.32 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.11509 | 109.32 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.26313 | 109.32 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 1 | 109.32 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05536 | 109.32 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.07828 | 109.32 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.07315 | 109.32 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.21929 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19152 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05211 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.04861 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.06643 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.06119 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05629 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.04086 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.22929 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 1 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.11509 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.22929 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.26313 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 1 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.17798 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.09131 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.17453 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.17962 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07828 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07315 | 109.29 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.21929 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19152 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05211 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.04861 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.06643 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.06119 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05629 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.04086 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.22929 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 1 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.11509 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.22929 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.26313 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 1 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.17798 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.09131 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.17453 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.17962 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07828 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07315 | 109.29 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.03104 | 109.29 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 20SP | GEN-2016-107 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.09616 | 109.29 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 20SP | GEN-2017-023 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.09521 | 109.29 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 20SP | GEN-2017-024 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.09408 | 109.29 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 20SP | GEN-2017-066 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.24726 | 109.29 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 00NR | 2 | 20SP | GEN-2017-067 | 'FROM -> TO' | S.W.S.-4 - ANADARK4 138 1 |  | 212 | 0.03511 | 109.29 | P12:138:OKGE-WFEC:BKRBKR368
Thermal | 03ALL | 2 | 19WP | GEN-2017-049 | 'FROM -> TO' | HANSTN 2 - KINSLY 2 69 | 48 | 48 | 1 | 109.29 | P12:69:MIDW:WALNUT CREEK-NEKOMA
Thermal | 09ALL | 2 | 24SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.63727 | 109.28 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.56411 | 109.28 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.56411 | 109.28 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.08464 | 109.26 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.20744 | 109.26 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.12999 | 109.26 | P12:230:UMZB:# 2934 #: SGQ IN NE. STEGALL TX
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.08464 | 109.26 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.20744 | 109.26 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | SCOTBLF7 - VICTRYH7 115 1 |  | 155 | 0.12999 | 109.26 | P13:230-345:NPPD:STEGALL3:KV3A
Thermal | 06NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04414 | 109.25 | P22:345:SPRM-AECI:17
Thermal | 06NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04414 | 109.25 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.0323 | 109.2 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.05272 | 109.2 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.0681 | 109.2 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.18786 | 109.2 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.03104 | 109.2 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.11888 | 109.2 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.03104 | 109.2 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.05009 | 109.2 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.07711 | 109.2 | P12:345:OKGE:BKRBKR21
Thermal | 08ALL | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | VIOLA 4 - VIOLA TX-1 138 |  | 440 | 0.23933 | 109.1 | P12:345:WERE:VIOL-WICH_345::
Thermal | 09ALL | 2 | 29SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.65238 | 109.1 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 29SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.57843 | 109.1 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 29SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.57843 | 109.1 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 06ALL | 2 | 24L | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 |  | 559 | 0.22039 | 109.09 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 09ALL | 2 | 24L | GEN-2016-109 | 'FROM -> TO' | BAILEYV3 - SMITTYV3 115 | 86 |  | 0.08854 | 109.09 | System Intact
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 1 |  | 478 | 0.09889 | 109.07 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 1 |  | 478 | 0.2407 | 109.07 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 1 |  | 478 | 0.15119 | 109.07 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 16ALL | 2 | 29SP | GEN-2017-010 | 'FROM -> TO' | BROADLND-BE3 - BD KU2A 345/230 | 400 |  | 0.10498 | 109.05 | System Intact
Thermal | 16ALL | 2 | 29SP | GEN-2017-048 | 'FROM -> TO' | BROADLND-BE3 - BD KU2A 345/230 | 400 |  | 0.13351 | 109.05 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.04951 | 109.04 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 1 | 109.04 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 1 | 109.04 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.0323 | 109.02 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.03441 | 109.02 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.05272 | 109.02 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.0681 | 109.02 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.07364 | 109.02 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.03837 | 109.02 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.11888 | 109.02 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.05516 | 109.02 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.07711 | 109.02 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.03929 | 109.02 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0323 | 109.01 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.19539 | 109.01 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.16559 | 109.01 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.05272 | 109.01 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0681 | 109.01 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.05934 | 109.01 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.20587 | 109.01 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.11888 | 109.01 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.20587 | 109.01 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.15158 | 109.01 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.09738 | 109.01 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.14813 | 109.01 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.15325 | 109.01 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.07711 | 109.01 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0323 | 109.01 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.19539 | 109.01 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.16559 | 109.01 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.05272 | 109.01 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0681 | 109.01 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.05934 | 109.01 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.20587 | 109.01 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.11888 | 109.01 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.20587 | 109.01 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.15158 | 109.01 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.09738 | 109.01 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.14813 | 109.01 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.15325 | 109.01 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.07711 | 109.01 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.03364 | 109 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 20SP | GEN-2017-036 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.0373 | 109 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.03364 | 109 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 20SP | GEN-2017-066 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.0539 | 109 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.03364 | 109 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 20SP | GEN-2017-036 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.0373 | 109 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.03364 | 109 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 20SP | GEN-2017-066 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.0539 | 109 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 14ALL | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.52868 | 108.96 | P12:138:OKGE:BKRBKR258_1
Thermal | 08ALL | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 | 179 |  | 0.24721 | 108.95 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03936 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03919 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.05468 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.07912 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03373 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03006 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.065 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.08082 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.07991 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.15161 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.04138 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.05441 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.07887 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.04138 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.33445 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03907 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03103 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.04403 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03036 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03135 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.0481 | 108.93 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.0323 | 108.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03259 | 108.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05272 | 108.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.0681 | 108.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.11888 | 108.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05852 | 108.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07711 | 108.92 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.0323 | 108.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03259 | 108.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05272 | 108.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.0681 | 108.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.11888 | 108.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05852 | 108.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07711 | 108.92 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.03936 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.03919 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.05468 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.07912 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.03373 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.04387 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.04146 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.03006 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.065 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.08082 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.07991 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.08464 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.04138 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.05441 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.07887 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.04138 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.33445 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.05868 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.03907 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.03103 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.03036 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.03135 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.0481 | 108.91 | P42:345:NPPD:BKR-CE-3306
Thermal | 09ALL | 2 | 19WP | GEN-2016-034 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.6336 | 108.88 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2016-093 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.5609 | 108.88 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2017-037 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.5609 | 108.88 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 | 1187 |  | 0.0323 | 108.83 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 | 1187 |  | 0.17623 | 108.83 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 | 1187 |  | 0.15125 | 108.83 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 | 1187 |  | 0.05272 | 108.83 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 | 1187 |  | 0.0681 | 108.83 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 | 1187 |  | 0.04987 | 108.83 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 | 1187 |  | 0.18502 | 108.83 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 | 1187 |  | 0.11888 | 108.83 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 | 1187 |  | 0.18502 | 108.83 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 | 1187 |  | 0.13947 | 108.83 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 | 1187 |  | 0.08149 | 108.83 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 | 1187 |  | 0.13653 | 108.83 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 | 1187 |  | 0.14088 | 108.83 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 | 1187 |  | 0.07711 | 108.83 | System Intact
Thermal | 01NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.05345 | 108.83 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 243 | 0.03352 | 108.81 | P23:345:WERE:N345_345-110::
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 243 | 0.03487 | 108.81 | P23:345:WERE:N345_345-110::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.07531 | 108.79 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.05211 | 108.78 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.04861 | 108.78 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.06194 | 108.78 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.0558 | 108.78 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.04086 | 108.78 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 1 | 108.78 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.11509 | 108.78 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 1 | 108.78 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.05536 | 108.78 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.07315 | 108.78 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.05211 | 108.78 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.04861 | 108.78 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.06194 | 108.78 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.0558 | 108.78 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.04086 | 108.78 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 1 | 108.78 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.11509 | 108.78 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 1 | 108.78 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.05536 | 108.78 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.07315 | 108.78 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.05211 | 108.78 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.04861 | 108.78 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.06194 | 108.78 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.0558 | 108.78 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.04086 | 108.78 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 1 | 108.78 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.11509 | 108.78 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 1 | 108.78 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.05536 | 108.78 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.07315 | 108.78 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - SHIDLER4 138 | 179 |  | 0.24715 | 108.78 | System Intact
Thermal | 09ALL | 2 | 29SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.63738 | 108.76 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 29SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.56422 | 108.76 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 29SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.56422 | 108.76 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2017-022 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.08096 | 108.73 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 08ALL | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 | 152 |  | 0.24853 | 108.69 | System Intact
Thermal | 07ALL | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | ANADARK4 - CHERRYRD 4 138 | 145 | 169 | 0.36345 | 108.67 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 07ALL | 2 | 24L | GEN-2017-053 | 'FROM -> TO' | ANADARK4 - CHERRYRD 4 138 | 145 | 169 | 0.35744 | 108.67 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.0323 | 108.65 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.04623 | 108.65 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.05272 | 108.65 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.0681 | 108.65 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.07364 | 108.65 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.03837 | 108.65 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.11888 | 108.65 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.05516 | 108.65 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.07711 | 108.65 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.03929 | 108.65 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03936 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03919 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05468 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.07912 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03373 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.06325 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.04146 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03006 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.065 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.08082 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.07991 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.08464 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.04138 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05441 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.07887 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.04138 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.33445 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05868 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03907 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03103 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03036 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03135 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.0481 | 108.59 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03936 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03919 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.05468 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.07912 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03373 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03006 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.065 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.08082 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.07991 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.04138 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.05441 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.07887 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.04138 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.33445 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03417 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03907 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03103 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03036 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03135 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.0481 | 108.56 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 09ALL | 2 | 19WP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 500 | 0.64845 | 108.56 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 19WP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 500 | 0.57499 | 108.56 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 19WP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 500 | 0.57499 | 108.56 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.15169 | 108.55 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04414 | 108.55 | P42:345:OKGE:SB_JOCO7383
Thermal | 08ALL | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 189 | 0.25508 | 108.55 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 189 | 0.25508 | 108.55 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 09ALL | 2 | 19WP | GEN-2016-109 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 | 112 |  | 0.04678 | 108.55 | System Intact
Thermal | 12NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05271 | 108.53 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 12NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.03265 | 108.53 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 12NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.06083 | 108.53 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 12NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.06083 | 108.53 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.06091 | 108.5 | P42:345:NPPD:BKR-SC-3306
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.03352 | 108.47 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.03487 | 108.47 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.03352 | 108.47 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.03487 | 108.47 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 09NR | 2 | 24L | GEN-2016-093 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03402 | 108.44 | P42:345:OKGE:SB_REOW7382
Thermal | 09NR | 2 | 24L | GEN-2017-001 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03037 | 108.44 | P42:345:OKGE:SB_REOW7382
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.0323 | 108.41 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.05272 | 108.41 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.0681 | 108.41 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.11888 | 108.41 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 19WP | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.05057 | 108.41 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.07711 | 108.41 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03936 | 108.4 | P23:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.07912 | 108.4 | P23:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03373 | 108.4 | P23:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.08082 | 108.4 | P23:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.07991 | 108.4 | P23:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.04138 | 108.4 | P23:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.05441 | 108.4 | P23:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.04138 | 108.4 | P23:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.33445 | 108.4 | P23:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03103 | 108.4 | P23:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03036 | 108.4 | P23:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03135 | 108.4 | P23:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03936 | 108.4 | P43:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.07912 | 108.4 | P43:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03373 | 108.4 | P43:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.08082 | 108.4 | P43:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.07991 | 108.4 | P43:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.04138 | 108.4 | P43:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.05441 | 108.4 | P43:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.04138 | 108.4 | P43:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.33445 | 108.4 | P43:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03103 | 108.4 | P43:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03036 | 108.4 | P43:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03135 | 108.4 | P43:345:GRDA:GRDA CB9580
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | LOGAN___-BE7 - KW1A 115 1 |  | 203 | 0.05913 | 108.38 | P12:115:XEL-WAPA:AUTO-SINGLE:MALLARD7:NELSON7:1
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.03352 | 108.38 | System Intact
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.03487 | 108.38 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07856 | 108.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07856 | 108.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07856 | 108.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 1 | 108.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07856 | 108.37 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.05421 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.05421 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.14369 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-077 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.05752 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-078 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.10779 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-090 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.05434 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-171 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.05003 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.15303 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.09156 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.23368 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.09628 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.08776 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.08239 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.04282 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.09628 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-079 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.14261 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.08776 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.19504 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-084 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.15588 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.09563 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.12289 | 108.37 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-104 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.04756 | 108.37 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0323 | 108.29 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.19167 | 108.29 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.16991 | 108.29 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.05272 | 108.29 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0681 | 108.29 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.04385 | 108.29 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.19935 | 108.29 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.11888 | 108.29 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.19935 | 108.29 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.15953 | 108.29 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.07059 | 108.29 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.15683 | 108.29 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.1608 | 108.29 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.07711 | 108.29 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.05421 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.05421 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.14369 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-077 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.05752 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-078 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.10779 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-090 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.05434 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-171 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.05003 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.15303 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.09156 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.23368 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.09628 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.08776 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.08239 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.04282 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.09628 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-079 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.14261 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.08776 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.19504 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-084 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.15588 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.09563 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.12289 | 108.28 | System Intact
Thermal | 06ALL | 2 | 20G | GEN-2017-104 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.04756 | 108.28 | System Intact
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.06118 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.06118 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.10369 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-077 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.08608 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-078 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.20185 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-090 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.07934 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-171 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.06007 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.13361 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.22714 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-012 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.10608 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.2224 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.27325 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.24334 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.03211 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.2224 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.1376 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.27325 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-081 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.08765 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.12185 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.22227 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.14516 | 108.27 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-104 | 'FROM -> TO' | TOLK 7 345/230XFR 1 | 478 |  | 0.0445 | 108.27 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2016-109 | 'FROM -> TO' | BAILEYV3 - SENECA 3 115 | 86 |  | 0.08854 | 108.27 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.21793 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19048 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05211 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.04861 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.066 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0608 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05567 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.04086 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.22781 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 1 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.11509 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.22781 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.26313 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 1 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.17709 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.09025 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.17366 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.17871 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07828 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07315 | 108.26 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.21793 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19048 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05211 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.04861 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.066 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.0608 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05567 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.04086 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.22781 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 1 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.11509 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.22781 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.26313 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 1 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.17709 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.09025 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.17366 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.17871 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07828 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07315 | 108.26 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | COLMBUS7 - CRESTON7 115 1 |  | 120 | 0.08461 | 108.24 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | COLMBUS7 - CRESTON7 115 1 |  | 120 | 1 | 108.24 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | COLMBUS7 - CRESTON7 115 1 |  | 120 | 1 | 108.24 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | WALL 7 - WICKSVL7 115 1 |  | 134 | 0.18307 | 108.2 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | WALL 7 - WICKSVL7 115 1 |  | 134 | 0.13717 | 108.2 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | WALL 7 - WICKSVL7 115 1 |  | 134 | 0.20236 | 108.2 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | HOLT.CO3 - GRPRAR1-LNX3 345 |  | 720 | 0.26491 | 108.19 | P23:345:MEC:RAUN 0270
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22429 | 108.18 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1886 | 108.18 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06874 | 108.18 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06341 | 108.18 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06882 | 108.18 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.23711 | 108.18 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.23711 | 108.18 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17139 | 108.18 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1151 | 108.18 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16715 | 108.18 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17342 | 108.18 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22429 | 108.18 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1886 | 108.18 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06874 | 108.18 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06341 | 108.18 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06882 | 108.18 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.23711 | 108.18 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.23711 | 108.18 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17139 | 108.18 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1151 | 108.18 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16715 | 108.18 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17342 | 108.18 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 03ALL | 2 | 24WP | GEN-2017-049 | 'FROM -> TO' | HANSTN 2 - KINSLY 2 69 | 48 | 48 | 1 | 108.18 | P12:69:MIDW:WALNUT CREEK-NEKOMA
Thermal | 14ALL | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.34774 | 108.18 | P12:138:OKGE:BKRBKR257
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.0323 | 108.16 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.0463 | 108.16 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.05272 | 108.16 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.0681 | 108.16 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.07364 | 108.16 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.03837 | 108.16 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.11888 | 108.16 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.05516 | 108.16 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.07711 | 108.16 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.03929 | 108.16 | P42:345:NPPD:BKR-SC-3306
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.06118 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.06118 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.10369 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-077 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.08608 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-078 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.20185 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-090 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.07934 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-171 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.06007 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.13361 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.22714 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-012 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.10608 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.2224 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.27325 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.24334 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.03211 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.2224 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.1376 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.27325 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-081 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.08765 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.12185 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.22227 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.14516 | 108.16 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-104 | 'FROM -> TO' | TOLK 6 - ABBXNL844501 230 1 | 478 |  | 0.0445 | 108.16 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07748 | 108.13 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07748 | 108.13 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07748 | 108.13 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 1 | 108.13 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07748 | 108.13 | P23:161-345:KCPL:HAWTHORN_R8-22::HAWTHORN-BVALY2-HAWT22
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.03375 | 108.12 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.0379 | 108.12 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.04807 | 108.12 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.0379 | 108.12 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2017-066 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.06447 | 108.12 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.03375 | 108.12 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.0379 | 108.12 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.04807 | 108.12 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.0379 | 108.12 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 19WP | GEN-2017-066 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.06447 | 108.12 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 09ALL | 2 | 19WP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 500 | 0.64845 | 108.11 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 19WP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 500 | 0.57499 | 108.11 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 19WP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 500 | 0.57499 | 108.11 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0323 | 108.08 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.19481 | 108.08 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.16519 | 108.08 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.05272 | 108.08 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0681 | 108.08 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.059 | 108.08 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.20523 | 108.08 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.11888 | 108.08 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.20523 | 108.08 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.15126 | 108.08 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0968 | 108.08 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.14782 | 108.08 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.15292 | 108.08 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.07711 | 108.08 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0323 | 108.08 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.19481 | 108.08 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.16519 | 108.08 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.05272 | 108.08 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0681 | 108.08 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.059 | 108.08 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.20523 | 108.08 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.11888 | 108.08 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.20523 | 108.08 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.15126 | 108.08 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0968 | 108.08 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.14782 | 108.08 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.15292 | 108.08 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.07711 | 108.08 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 16NR | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | BROADLND-BE3 345 - BD.LS-AV-BE3 345 Z |  | 478 | 0.10201 | 108.04 | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Thermal | 16NR | 2 | 20G | GEN-2017-048 | 'FROM -> TO' | BROADLND-BE3 345 - BD.LS-AV-BE3 345 Z |  | 478 | 0.09659 | 108.04 | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-011 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03203 | 108 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 24SP | GEN-2017-018 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03424 | 108 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.1405 | 108 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.05483 | 108 | P23:345:WERE:WICH_345-50::
Thermal | 07ALL | 2 | 24L | GEN-2017-053 | 'FROM -> TO' | GEROJCT2 - GRANFLD2 69 | 58 | 68 | 0.29882 | 108 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 01ALL | 2 | 20G | GEN-2017-011 | 'FROM -> TO' | NORTWST7 - MATHWSN7 345 1 |  | 1195 | 0.20696 | 107.99 | P42:345:OKGE:SB_CION7383
Thermal | 00NR | 2 | 20SP | GEN-2017-071 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.16838 | 107.94 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 20SP | GEN-2017-072 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.16838 | 107.94 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 20SP | GEN-2017-071 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.16838 | 107.94 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 20SP | GEN-2017-072 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.16838 | 107.94 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0323 | 107.93 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.19477 | 107.93 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.16516 | 107.93 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.05272 | 107.93 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0681 | 107.93 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.05898 | 107.93 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.20519 | 107.93 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.11888 | 107.93 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.20519 | 107.93 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.15124 | 107.93 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.09676 | 107.93 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.1478 | 107.93 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.1529 | 107.93 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.07711 | 107.93 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0323 | 107.93 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.19477 | 107.93 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.16516 | 107.93 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.05272 | 107.93 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.0681 | 107.93 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.05898 | 107.93 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.20519 | 107.93 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.11888 | 107.93 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.20519 | 107.93 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.15124 | 107.93 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.09676 | 107.93 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.1478 | 107.93 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.1529 | 107.93 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.07711 | 107.93 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 15ALL | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | GR PRAIRIE 3 - GRPRAR1-LNX3 345 |  | 720 | 0.26491 | 107.9 | P23:345:MEC:RAUN 0270
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03936 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03919 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.05468 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.07912 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03373 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03184 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03006 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03606 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.08082 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.07991 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.04138 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.05441 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.07887 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.04138 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.33445 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.14042 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03103 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03036 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03135 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.05475 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.0481 | 107.89 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 107.86 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 |  | 128.1 | 1 | 107.86 | P12:115:SPS:W59.1.LOPEZ.CMPBLL
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.08151 | 107.85 | P12:345:WERE:BENT-WICH_345::
Thermal | 14ALL | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.52874 | 107.84 | P12:138:OKGE:BKRBKR258_1
Thermal | 01NR | 2 | 24L | GEN-2017-071 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.10017 | 107.83 | P23:345:GRDA:CLEVLND CB10180
Thermal | 01NR | 2 | 24L | GEN-2017-072 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.10017 | 107.83 | P23:345:GRDA:CLEVLND CB10180
Thermal | 01NR | 2 | 24L | GEN-2017-071 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.10017 | 107.83 | P43:345:GRDA:CLEVLND CB10180
Thermal | 01NR | 2 | 24L | GEN-2017-072 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.10017 | 107.83 | P43:345:GRDA:CLEVLND CB10180
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 243 | 0.03352 | 107.83 | P12:161:WERE:LITC-EMDE_161::
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 243 | 0.03487 | 107.83 | P12:161:WERE:LITC-EMDE_161::
Thermal | 06NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04274 | 107.82 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03828 | 107.82 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03828 | 107.82 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 06NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04274 | 107.82 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03828 | 107.82 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03828 | 107.82 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 06NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04274 | 107.82 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03828 | 107.82 | P23:345:GRDA:CLEVLND CB13280
Thermal | 06NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03828 | 107.82 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 20SP | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03708 | 107.79 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | NORTWST7 - MATHWSN7 345 1 |  | 1195 | 0.03352 | 107.79 | P42:345:OKGE:SB_CION7383
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | NORTWST7 - MATHWSN7 345 1 |  | 1195 | 0.03487 | 107.79 | P42:345:OKGE:SB_CION7383
Thermal | 00NR | 2 | 20SP | GEN-2017-011 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03187 | 107.78 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07685 | 107.78 | P23:345:WERE:WICH_345-50::
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.28117 | 107.78 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.28117 | 107.78 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.21574 | 107.78 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20124 | 107.78 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.33619 | 107.78 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20382 | 107.78 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20124 | 107.78 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20162 | 107.78 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.21468 | 107.78 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 09ALL | 2 | 20G | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.64943 | 107.78 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20G | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.57597 | 107.78 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20G | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.57597 | 107.78 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 16NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 1 |  | 496 | 0.09634 | 107.76 | P42:345:NPPD:BKR-KEY-3310
Thermal | 16NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 1 |  | 496 | 0.23467 | 107.76 | P42:345:NPPD:BKR-KEY-3310
Thermal | 16NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 1 |  | 496 | 0.14736 | 107.76 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.06986 | 107.74 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22429 | 107.7 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.18862 | 107.7 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07159 | 107.7 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06591 | 107.7 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06898 | 107.7 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.2371 | 107.7 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.2371 | 107.7 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17141 | 107.7 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.11516 | 107.7 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16717 | 107.7 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 24SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17344 | 107.7 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03936 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03919 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.05468 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.07912 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03373 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03006 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.065 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.08082 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.07991 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.04138 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.05441 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.07887 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.04138 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.33445 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03907 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03103 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03036 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03135 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0481 | 107.69 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03936 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03919 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.05468 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.07912 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03373 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03006 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.065 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.08082 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.07991 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.04138 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.05441 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.07887 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.04138 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.33445 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03907 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03103 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03036 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03135 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0481 | 107.69 | P42:500:OKGE:SB_FTTH8585
Thermal | 08ALL | 2 | 29SP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.05789 | 107.69 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.0779 | 107.69 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 189 | 0.25508 | 107.62 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 08ALL | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 |  | 189 | 0.25508 | 107.62 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.21814 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.19065 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05211 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.04861 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.06608 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.06086 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.05575 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.04086 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.22804 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 1 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.11509 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.22804 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.26313 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 1 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.17724 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.09037 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.17381 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.17887 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07828 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1183 | 0.07315 | 107.61 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 14ALL | 2 | 19WP | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.30653 | 107.57 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 14ALL | 2 | 19WP | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.28685 | 107.57 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 14ALL | 2 | 19WP | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.30653 | 107.57 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 14ALL | 2 | 19WP | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.28685 | 107.57 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 | 317 |  | 0.04859 | 107.56 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.15168 | 107.56 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.0441 | 107.56 | P42:345:OKGE:SB_JOCO7303
Thermal | 08ALL | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 |  | 189 | 0.34259 | 107.56 | P12:138:GRDA:FAIRFAX-PAWNSW
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03936 | 107.54 | P23:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.07912 | 107.54 | P23:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03373 | 107.54 | P23:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.08082 | 107.54 | P23:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.07991 | 107.54 | P23:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.04138 | 107.54 | P23:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.05441 | 107.54 | P23:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.04138 | 107.54 | P23:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.33445 | 107.54 | P23:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03103 | 107.54 | P23:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03036 | 107.54 | P23:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03135 | 107.54 | P23:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03936 | 107.54 | P42:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.07912 | 107.54 | P42:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03373 | 107.54 | P42:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.08082 | 107.54 | P42:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.07991 | 107.54 | P42:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.04138 | 107.54 | P42:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.05441 | 107.54 | P42:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.04138 | 107.54 | P42:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.33445 | 107.54 | P42:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03103 | 107.54 | P42:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03036 | 107.54 | P42:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03135 | 107.54 | P42:345:GRDA:TONNECE CB9580
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07891 | 107.53 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07891 | 107.53 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07891 | 107.53 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 1 | 107.53 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.07891 | 107.53 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | LOGAN___-BE4 - KW1A 115 1 |  | 203 | 0.05913 | 107.52 | P12:115:XEL-WAPA:AUTO-SINGLE:MALLARD7:NELSON7:1
Thermal | 09ALL | 2 | 20G | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.64943 | 107.5 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20G | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.57597 | 107.5 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 20G | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.57597 | 107.5 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03203 | 107.46 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 24SP | GEN-2017-018 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03424 | 107.46 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.1405 | 107.46 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.05483 | 107.46 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.0323 | 107.45 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05008 | 107.45 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05272 | 107.45 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.0681 | 107.45 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07364 | 107.45 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03837 | 107.45 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.11888 | 107.45 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05516 | 107.45 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07711 | 107.45 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03929 | 107.45 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 03NR | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03323 | 107.43 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 16NR | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | ANTELOPE-BE3 - AV.LS-BD-BE3 345 Z |  | 478 | 0.10201 | 107.42 | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Thermal | 16NR | 2 | 20G | GEN-2017-048 | 'FROM -> TO' | ANTELOPE-BE3 - AV.LS-BD-BE3 345 Z |  | 478 | 0.09659 | 107.42 | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.06367 | 107.39 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.0511 | 107.39 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03936 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03919 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.05468 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.07912 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03373 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03006 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.065 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.08082 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.07991 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.04138 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.05441 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.07887 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.04138 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.33445 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03907 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03103 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03036 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03135 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0481 | 107.35 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03936 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03919 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.05468 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.07912 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03373 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03006 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.065 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.08082 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.07991 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.04138 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.05441 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.07887 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.04138 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.33445 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03907 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03103 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03036 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03135 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0481 | 107.35 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03936 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03919 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.05468 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.07912 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03373 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03184 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03006 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03606 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.08082 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.07991 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.04138 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.05441 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.07887 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.04138 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.33445 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.14042 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03103 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03036 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.03135 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.05475 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | EVANS N4 - WICH TX-12 138 1 |  | 430 | 0.0481 | 107.3 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 20SP | GEN-2017-004 | 'FROM -> TO' | SWISVAL7 - W.GRDNR7 345 1 |  | 956 | 0.0666 | 107.29 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | SWISVAL7 - W.GRDNR7 345 1 |  | 956 | 0.04894 | 107.29 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 20SP | GEN-2017-032 | 'FROM -> TO' | SWISVAL7 - W.GRDNR7 345 1 |  | 956 | 0.03164 | 107.29 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | SWISVAL7 - W.GRDNR7 345 1 |  | 956 | 0.04894 | 107.29 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | SWISVAL7 - W.GRDNR7 345 1 |  | 956 | 0.04894 | 107.29 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | SWISVAL7 - W.GRDNR7 345 1 |  | 956 | 0.04894 | 107.29 | P23:345:WERE:87TH_345_BKRS::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03936 | 107.28 | P23:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.07912 | 107.28 | P23:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03373 | 107.28 | P23:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.08082 | 107.28 | P23:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.07991 | 107.28 | P23:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.04138 | 107.28 | P23:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.05441 | 107.28 | P23:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.04138 | 107.28 | P23:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.33445 | 107.28 | P23:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03103 | 107.28 | P23:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03036 | 107.28 | P23:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03135 | 107.28 | P23:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03936 | 107.28 | P43:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.07912 | 107.28 | P43:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03373 | 107.28 | P43:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.08082 | 107.28 | P43:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.07991 | 107.28 | P43:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.04138 | 107.28 | P43:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.05441 | 107.28 | P43:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.04138 | 107.28 | P43:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.33445 | 107.28 | P43:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03103 | 107.28 | P43:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03036 | 107.28 | P43:345:GRDA:TONNECE CB90
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03135 | 107.28 | P43:345:GRDA:TONNECE CB90
Thermal | 08ALL | 2 | 20G | GEN-2016-072 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 | 956 |  | 0.05563 | 107.28 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2016-173 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 | 956 |  | 0.08156 | 107.28 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 | 956 |  | 0.72593 | 107.28 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-068 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 | 956 |  | 0.08559 | 107.28 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-086 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 | 956 |  | 0.0736 | 107.28 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05766 | 107.27 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05766 | 107.27 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05766 | 107.27 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 1 | 107.27 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 |  | 550 | 0.05766 | 107.27 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03936 | 107.26 | P43:345:GRDA:TONNECE CB12070
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.07912 | 107.26 | P43:345:GRDA:TONNECE CB12070
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03373 | 107.26 | P43:345:GRDA:TONNECE CB12070
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.08082 | 107.26 | P43:345:GRDA:TONNECE CB12070
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.07991 | 107.26 | P43:345:GRDA:TONNECE CB12070
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.04138 | 107.26 | P43:345:GRDA:TONNECE CB12070
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.05441 | 107.26 | P43:345:GRDA:TONNECE CB12070
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.04138 | 107.26 | P43:345:GRDA:TONNECE CB12070
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.33445 | 107.26 | P43:345:GRDA:TONNECE CB12070
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03103 | 107.26 | P43:345:GRDA:TONNECE CB12070
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03036 | 107.26 | P43:345:GRDA:TONNECE CB12070
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | NEO SPA5 - TIP292 5 161 1 |  | 222 | 0.03135 | 107.26 | P43:345:GRDA:TONNECE CB12070
Thermal | 16NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 1 |  | 496 | 0.09634 | 107.25 | P42:345:NPPD:BKR-KEY-3310
Thermal | 16NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 1 |  | 496 | 0.23467 | 107.25 | P42:345:NPPD:BKR-KEY-3310
Thermal | 16NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 1 |  | 496 | 0.14736 | 107.25 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24L | GEN-2016-109 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 | 112 |  | 0.04279 | 107.22 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07136 | 107.2 | P42:345:NPPD:BKR-HOS-3312
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 1 |  | 496 | 0.09889 | 107.19 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 1 |  | 496 | 0.2407 | 107.19 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 1 |  | 496 | 0.15119 | 107.19 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.22555 | 107.14 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.21906 | 107.14 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.25953 | 107.14 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.23245 | 107.14 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.21906 | 107.14 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.25953 | 107.14 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.21942 | 107.14 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 08ALL | 2 | 19WP | GEN-2016-072 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.06953 | 107.13 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.03956 | 107.13 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2016-173 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.09148 | 107.13 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.08697 | 107.13 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-071 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.033 | 107.13 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-072 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.033 | 107.13 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-086 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.08061 | 107.13 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - ELIZACK4 138 | 152 |  | 0.2483 | 107.11 | System Intact
Thermal | 09ALL | 2 | 24WP | GEN-2016-034 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.63761 | 107.1 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24WP | GEN-2016-093 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.56445 | 107.1 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24WP | GEN-2017-037 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.56445 | 107.1 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09NR | 2 | 24L | GEN-2016-093 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.0344 | 107.06 | P42:345:OKGE:SB_WONG7383
Thermal | 09NR | 2 | 24L | GEN-2017-001 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03064 | 107.06 | P42:345:OKGE:SB_WONG7383
Thermal | 08ALL | 2 | 19WP | GEN-2016-072 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 | 956 |  | 0.05871 | 107.05 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2016-173 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 | 956 |  | 0.08463 | 107.05 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 | 956 |  | 0.72895 | 107.05 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 | 956 |  | 0.08865 | 107.05 | System Intact
Thermal | 08ALL | 2 | 19WP | GEN-2017-086 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 | 956 |  | 0.07667 | 107.05 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 1 |  | 123 | 0.0323 | 107.04 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 00NR | 2 | 19WP | GEN-2016-109 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 1 |  | 123 | 0.03406 | 107.04 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 1 |  | 123 | 0.05272 | 107.04 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 1 |  | 123 | 0.0681 | 107.04 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 1 |  | 123 | 0.07364 | 107.04 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 1 |  | 123 | 0.03837 | 107.04 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 1 |  | 123 | 0.11888 | 107.04 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 1 |  | 123 | 0.05516 | 107.04 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 1 |  | 123 | 0.07711 | 107.04 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 1 |  | 123 | 0.03929 | 107.04 | P23:345:WERE:HOYT_345_BKRS::
Thermal | 00NR | 2 | 24SP | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03429 | 106.99 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 09NR | 2 | 24L | GEN-2016-093 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03434 | 106.99 | P12:345:OKGE:BKRBKR400
Thermal | 09NR | 2 | 24L | GEN-2017-001 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03059 | 106.99 | P12:345:OKGE:BKRBKR400
Thermal | 09NR | 2 | 24L | GEN-2016-093 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03434 | 106.99 | P42:345:OKGE:SB_WONG7313
Thermal | 09NR | 2 | 24L | GEN-2017-001 | 'FROM -> TO' | BENTON 7 - WICHITA7 345 1 |  | 956 | 0.03059 | 106.99 | P42:345:OKGE:SB_WONG7313
Thermal | 14ALL | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.41379 | 106.98 | P42:345:OKGE:SB_JOCO7303
Thermal | 08ALL | 2 | 20SP | GEN-2016-173 | 'FROM -> TO' | FARBER 4 - SC10BEL4 138 |  | 160 | 0.23846 | 106.97 | P23:345:WERE:WICH_345-116::
Thermal | 14ALL | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.41385 | 106.97 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07856 | 106.93 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07856 | 106.93 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07856 | 106.93 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 1 | 106.93 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07856 | 106.93 | P23:161-345:KCPL:HAWTHORN_R22-28::HAWTHORN-LEVEE-HAWT22
Thermal | 07ALL | 2 | 20G | GEN-2017-053 | 'FROM -> TO' | GEROJCT2 - GRANFLD2 69 | 58 | 68 | 0.33202 | 106.93 | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4
Thermal | 09ALL | 2 | 20G | GEN-2016-109 | 'FROM -> TO' | CRAIG7 - 87TH 7 345 | 1195 |  | 0.04937 | 106.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2016-159 | 'FROM -> TO' | CRAIG7 - 87TH 7 345 | 1195 |  | 0.04545 | 106.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-001 | 'FROM -> TO' | CRAIG7 - 87TH 7 345 | 1195 |  | 0.03324 | 106.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-006 | 'FROM -> TO' | CRAIG7 - 87TH 7 345 | 1195 |  | 0.05132 | 106.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-008 | 'FROM -> TO' | CRAIG7 - 87TH 7 345 | 1195 |  | 0.0437 | 106.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-055 | 'FROM -> TO' | CRAIG7 - 87TH 7 345 | 1195 |  | 0.05563 | 106.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-085 | 'FROM -> TO' | CRAIG7 - 87TH 7 345 | 1195 |  | 0.0506 | 106.93 | System Intact
Thermal | 09ALL | 2 | 29SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.63738 | 106.93 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 29SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.56422 | 106.93 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 29SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 496 | 0.56422 | 106.93 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20G | GEN-2016-109 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 | 1195 |  | 0.04937 | 106.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2016-159 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 | 1195 |  | 0.04545 | 106.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-001 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 | 1195 |  | 0.03324 | 106.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-006 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 | 1195 |  | 0.05132 | 106.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-008 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 | 1195 |  | 0.0437 | 106.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-055 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 | 1195 |  | 0.05563 | 106.93 | System Intact
Thermal | 09ALL | 2 | 20G | GEN-2017-085 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 | 1195 |  | 0.0506 | 106.93 | System Intact
Thermal | 09ALL | 2 | 24WP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 500 | 0.65275 | 106.92 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24WP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 500 | 0.5788 | 106.92 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24WP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 500 | 0.5788 | 106.92 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03936 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03919 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.05468 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.07912 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03373 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03006 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.065 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.08082 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.07991 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03247 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.04138 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.05441 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.07887 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.04138 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.33445 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03907 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03103 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03036 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03135 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.0481 | 106.91 | P12:138:OKGE:BKRBKR130
Thermal | 02NR | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.04052 | 106.9 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03936 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03919 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.05468 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.07912 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03373 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03006 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.065 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.08082 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.07991 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.04138 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.05441 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.07887 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.04138 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.33445 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03365 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03907 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03103 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03036 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03135 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.0481 | 106.87 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 01ALL | 2 | 20G | GEN-2016-107 | 'FROM -> TO' | EL RENO4 - SCOTTSW4 138 |  | 136 | 0.20795 | 106.84 | P12:138:OKGE:BKRBKR423
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.15961 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-107 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.12333 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.10792 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05211 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.04861 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-028 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.03319 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16395 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-036 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.13088 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 1 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11509 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16395 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-066 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.13069 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-067 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.03603 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.26313 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 1 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07775 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.06977 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07865 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07828 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07315 | 106.78 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.15961 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-107 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.12333 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.10792 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05211 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.04861 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-028 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.03319 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16395 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-036 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.13088 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 1 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11509 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16395 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-066 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.13069 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-067 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.03603 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.26313 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 1 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07775 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.06977 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07865 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07828 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07315 | 106.78 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | WALL 7 - WICKSVL7 115 1 |  | 134 | 0.18385 | 106.78 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | WALL 7 - WICKSVL7 115 1 |  | 134 | 0.13766 | 106.78 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | WALL 7 - WICKSVL7 115 1 |  | 134 | 0.20318 | 106.78 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.15961 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-107 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.12333 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.10792 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05211 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.04861 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-028 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.03319 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16395 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-036 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.13088 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 1 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11509 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16395 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-066 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.13069 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-067 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.03603 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.26313 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 1 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07775 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.06977 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07865 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07828 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07315 | 106.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.15961 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-107 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.12333 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.10792 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.05211 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.04861 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-028 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.03319 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16395 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-036 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.13088 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 1 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.11509 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.16395 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-066 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.13069 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-067 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.03603 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.26313 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 1 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07775 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.06977 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07865 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07828 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 |  | 956 | 0.07315 | 106.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | CARTHAG5 - CAR395 5 161 |  | 222 | 0.29594 | 106.77 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.05211 | 106.75 | P12:161:WERE:LITC-EMDE_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.04861 | 106.75 | P12:161:WERE:LITC-EMDE_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.07204 | 106.75 | P12:161:WERE:LITC-EMDE_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.06194 | 106.75 | P12:161:WERE:LITC-EMDE_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.0558 | 106.75 | P12:161:WERE:LITC-EMDE_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.04086 | 106.75 | P12:161:WERE:LITC-EMDE_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 1 | 106.75 | P12:161:WERE:LITC-EMDE_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.11509 | 106.75 | P12:161:WERE:LITC-EMDE_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 1 | 106.75 | P12:161:WERE:LITC-EMDE_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.05536 | 106.75 | P12:161:WERE:LITC-EMDE_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.07315 | 106.75 | P12:161:WERE:LITC-EMDE_161::
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 1 |  | 496 | 0.09889 | 106.75 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 1 |  | 496 | 0.2407 | 106.75 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 1 |  | 496 | 0.15119 | 106.75 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.0302 | 106.7 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.03226 | 106.7 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.04681 | 106.7 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.03523 | 106.7 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-094 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.03566 | 106.7 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.03452 | 106.7 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.0302 | 106.7 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.03226 | 106.7 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.04681 | 106.7 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.03523 | 106.7 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-094 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.03566 | 106.7 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.03452 | 106.7 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.0302 | 106.7 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.03226 | 106.7 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.04681 | 106.7 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.03523 | 106.7 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-094 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.03566 | 106.7 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | SIOUXCY3 - SC2 KU1B 230 1 |  | 250 | 0.03452 | 106.7 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.03936 | 106.62 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.07912 | 106.62 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.03373 | 106.62 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.08082 | 106.62 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.07991 | 106.62 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.04138 | 106.62 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.05441 | 106.62 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.04138 | 106.62 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.33445 | 106.62 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.03907 | 106.62 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.03103 | 106.62 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.03036 | 106.62 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.03135 | 106.62 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.03603 | 106.62 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 09ALL | 2 | 29SP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.63738 | 106.61 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 29SP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.56422 | 106.61 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 29SP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 496 | 0.56422 | 106.61 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03795 | 106.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.05211 | 106.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04861 | 106.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.06194 | 106.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.0558 | 106.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04086 | 106.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03448 | 106.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 1 | 106.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.11509 | 106.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03448 | 106.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.26313 | 106.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 1 | 106.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.05536 | 106.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.07828 | 106.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.07315 | 106.6 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03795 | 106.6 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.05211 | 106.6 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04861 | 106.6 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.06194 | 106.6 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.0558 | 106.6 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04086 | 106.6 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03448 | 106.6 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 1 | 106.6 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.11509 | 106.6 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03448 | 106.6 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.26313 | 106.6 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 1 | 106.6 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.05536 | 106.6 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.07828 | 106.6 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.07315 | 106.6 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03795 | 106.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.05211 | 106.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04861 | 106.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.06194 | 106.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.0558 | 106.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04086 | 106.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03448 | 106.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 1 | 106.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.11509 | 106.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03448 | 106.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.26313 | 106.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 1 | 106.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.05536 | 106.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.07828 | 106.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.07315 | 106.6 | P23:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03795 | 106.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.05211 | 106.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04861 | 106.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.06194 | 106.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.0558 | 106.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04086 | 106.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03448 | 106.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 1 | 106.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.11509 | 106.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03448 | 106.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.26313 | 106.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 1 | 106.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.05536 | 106.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.07828 | 106.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.07315 | 106.6 | P42:345:GRDA:CLEVLND CB13280
Thermal | 09ALL | 2 | 24WP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 500 | 0.65275 | 106.59 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24WP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 500 | 0.5788 | 106.59 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 09ALL | 2 | 24WP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 500 | 0.5788 | 106.59 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 14ALL | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.34784 | 106.59 | P12:138:OKGE:BKRBKR257
Thermal | 00NR | 2 | 20SP | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.04252 | 106.53 | P42:345:OKGE:SB_CION7381
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 1 |  | 478 | 0.09635 | 106.53 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 1 |  | 478 | 0.23467 | 106.53 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 1 |  | 478 | 0.14737 | 106.53 | P42:345:NPPD:BKR-KEY-3310
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.28117 | 106.52 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.28117 | 106.52 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.21574 | 106.52 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20124 | 106.52 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.33619 | 106.52 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20382 | 106.52 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20124 | 106.52 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20162 | 106.52 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.21468 | 106.52 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 09ALL | 2 | 24WP | GEN-2016-109 | 'FROM -> TO' | KELLY 5 - TECHILL5 161 | 112 |  | 0.04494 | 106.52 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 | 220 |  | 0.05211 | 106.49 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 | 220 |  | 0.04861 | 106.49 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 | 220 |  | 0.06194 | 106.49 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 | 220 |  | 0.0558 | 106.49 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 | 220 |  | 0.04086 | 106.49 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 | 220 |  | 1 | 106.49 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 | 220 |  | 0.11509 | 106.49 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 | 220 |  | 0.26313 | 106.49 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 | 220 |  | 1 | 106.49 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 | 220 |  | 0.05536 | 106.49 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 | 220 |  | 0.03796 | 106.49 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 | 220 |  | 0.07828 | 106.49 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 | 220 |  | 0.07315 | 106.49 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.0323 | 106.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.05272 | 106.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.0681 | 106.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.15544 | 106.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.07364 | 106.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.15544 | 106.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.15544 | 106.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.03837 | 106.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 19WP | GEN-2017-055 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 1 | 106.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.11888 | 106.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.05516 | 106.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.15544 | 106.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.07711 | 106.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.03929 | 106.45 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03787 | 106.42 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.05211 | 106.42 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04861 | 106.42 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.06194 | 106.42 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.0558 | 106.42 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04086 | 106.42 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03439 | 106.42 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 1 | 106.42 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.11509 | 106.42 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03439 | 106.42 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.26313 | 106.42 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 1 | 106.42 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.05536 | 106.42 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.07828 | 106.42 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.07315 | 106.42 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03787 | 106.42 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.05211 | 106.42 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04861 | 106.42 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.06194 | 106.42 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.0558 | 106.42 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.04086 | 106.42 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03439 | 106.42 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 1 | 106.42 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.11509 | 106.42 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.03439 | 106.42 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.26313 | 106.42 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 1 | 106.42 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.05536 | 106.42 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.07828 | 106.42 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 382 | 0.07315 | 106.42 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2016-077 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.04 | 106.42 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 24SP | GEN-2016-090 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.05678 | 106.42 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 19WP | GEN-2017-004 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03781 | 106.42 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05272 | 106.42 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.11888 | 106.42 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.07711 | 106.42 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.0323 | 106.4 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.05272 | 106.4 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.0681 | 106.4 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.20159 | 106.4 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.11888 | 106.4 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.04381 | 106.4 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 185 | 0.07711 | 106.4 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | PLSNT_HILL 3 - E_CLOVIS 3 115 1 |  | 123.1 | 0.3665 | 106.37 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | PLSNT_HILL 3 - E_CLOVIS 3 115 1 |  | 123.1 | 0.3665 | 106.37 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | PLSNT_HILL 3 - E_CLOVIS 3 115 1 |  | 123.1 | 0.27963 | 106.37 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03936 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03919 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05468 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.07912 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03373 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2016-173 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05543 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.04146 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03006 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.065 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05994 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.08082 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.07991 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.08464 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06352 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.04138 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05441 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06352 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06352 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.49605 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.07887 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.04138 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.33445 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05868 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.04796 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03103 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03036 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03135 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05269 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06352 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.0481 | 106.35 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.04172 | 106.33 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.0302 | 106.31 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03226 | 106.31 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.04681 | 106.31 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03523 | 106.31 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-094 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03566 | 106.31 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03452 | 106.31 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.0302 | 106.31 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03226 | 106.31 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.04681 | 106.31 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03523 | 106.31 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-094 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03566 | 106.31 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03452 | 106.31 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.0302 | 106.31 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03226 | 106.31 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.04681 | 106.31 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03523 | 106.31 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-094 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03566 | 106.31 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03452 | 106.31 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.0302 | 106.31 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03226 | 106.31 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.04681 | 106.31 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03523 | 106.31 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-094 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03566 | 106.31 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | SIOUXCY2 - SC2 KU1B 230 1 |  | 250 | 0.03452 | 106.31 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 01NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.05345 | 106.23 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.03936 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.04724 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.06459 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.07912 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.03373 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.03006 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.065 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.08082 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.07991 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.04138 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.05441 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.07887 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.04138 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.33445 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.03907 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.03103 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.03036 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.03135 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 | 119.5 |  | 0.0481 | 106.22 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.07912 | 106.16 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.03322 | 106.16 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.08082 | 106.16 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.07991 | 106.16 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.05441 | 106.16 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.33445 | 106.16 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.0465 | 106.16 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.04782 | 106.16 | P23:345:AEPW:FLINT CREEK CB 19140 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.07912 | 106.16 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.03322 | 106.16 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.08082 | 106.16 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.07991 | 106.16 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.05441 | 106.16 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.33445 | 106.16 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.0465 | 106.16 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.04782 | 106.16 | P42:345:AEPW:FLINT CREEK CB 19140 NBTB+FAULT
Thermal | 06ALL | 2 | 29SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.33791 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.33791 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.26109 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23386 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24798 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24288 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23996 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23883 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.25436 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24133 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.39429 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23883 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24996 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.25436 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.21369 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24588 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23873 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 29SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.26337 | 106.16 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03936 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03919 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.05468 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.07912 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03373 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.07055 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.04146 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03006 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.065 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.08082 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.07991 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.08464 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.04138 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.05441 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.07887 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.04138 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.33445 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.05868 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03907 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03103 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03036 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03135 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.0481 | 106.14 | P42:345:NPPD:BKR-HOS-3312
Thermal | 03ALL | 2 | 19WP | GEN-2017-049 | 'FROM -> TO' | SEWARD 2 - ZOOK 2 69 | 48 | 48 | 1 | 106.13 | P12:69:MIDW:WALNUT CREEK-NEKOMA
Thermal | 09ALL | 2 | 19WP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 500 | 0.6336 | 106.12 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 500 | 0.5609 | 106.12 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 500 | 0.5609 | 106.12 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.0323 | 106.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-011 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03259 | 106.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05272 | 106.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.0681 | 106.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.11888 | 106.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05852 | 106.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07711 | 106.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.0323 | 106.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-011 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03259 | 106.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05272 | 106.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.0681 | 106.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.11888 | 106.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05852 | 106.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07711 | 106.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07891 | 106.1 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07891 | 106.1 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07891 | 106.1 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 1 | 106.1 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.07891 | 106.1 | P55:161-345:KCPL:HAWTHORN_BUS_22::
Thermal | 14ALL | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.52836 | 106.05 | P12:138:OKGE:BKRBKR258_1
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | E_CLOVIS 3 - CURRY 3 115 1 |  | 123.1 | 0.36649 | 106.03 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | E_CLOVIS 3 - CURRY 3 115 1 |  | 123.1 | 0.36649 | 106.03 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | E_CLOVIS 3 - CURRY 3 115 1 |  | 123.1 | 0.27962 | 106.03 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.0323 | 106.01 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.05272 | 106.01 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.0681 | 106.01 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.18786 | 106.01 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.03104 | 106.01 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.11888 | 106.01 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.03104 | 106.01 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.05009 | 106.01 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.07711 | 106.01 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03936 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03919 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.05468 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.07912 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03373 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03006 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.065 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.08082 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.07991 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.15161 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.04138 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.05441 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.07887 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.04138 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.33445 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03907 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03103 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.04403 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03036 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03135 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.0481 | 106.01 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07912 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04397 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04146 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03006 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.08082 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07991 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.08464 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06976 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-032 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03004 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05441 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06976 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06976 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.49605 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07887 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.33445 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05868 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03907 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.06976 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0481 | 105.98 | P55:161-345:KCPL:CRAIG_BUS_22_345::
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.23068 | 105.97 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.19519 | 105.97 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07023 | 105.97 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06465 | 105.97 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06792 | 105.97 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.24329 | 105.97 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.24329 | 105.97 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17825 | 105.97 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.11322 | 105.97 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17406 | 105.97 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.18026 | 105.97 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.23068 | 105.97 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.19519 | 105.97 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07023 | 105.97 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06465 | 105.97 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06792 | 105.97 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.24329 | 105.97 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.24329 | 105.97 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17825 | 105.97 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.11322 | 105.97 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17406 | 105.97 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.18026 | 105.97 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.20371 | 105.94 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.04589 | 105.94 | P42:345:OKGE:SB_SUSD7383
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.07585 | 105.92 | P42:345:NPPD:BKR-CE-3306
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.18234 | 105.92 | P42:345:NPPD:BKR-CE-3306
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.11512 | 105.92 | P42:345:NPPD:BKR-CE-3306
Thermal | 01ALL | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | OKEENE 4 - G16-107-TAP 138 | 160 |  | 0.56673 | 105.91 | System Intact
Thermal | 14ALL | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.30619 | 105.91 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 14ALL | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.2865 | 105.91 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 14ALL | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.30619 | 105.91 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 14ALL | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.2865 | 105.91 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.05211 | 105.89 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.3814 | 105.89 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 1 | 105.89 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.50935 | 105.89 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 1 | 105.89 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.05536 | 105.89 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.36841 | 105.89 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 1 | 105.84 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 1 | 105.84 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 1 | 105.84 | P13:345-500:OKGE:BKRBKR_3W068
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 1 | 105.84 | P13:345-500:OKGE:BKRBKR_3W068
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03936 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03919 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05468 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.07912 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03373 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05974 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.04146 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03006 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.065 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.08082 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.07991 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.08464 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.04138 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05441 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.07887 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.04138 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.33445 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.05868 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03907 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03103 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03036 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.03135 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | MADISON7 - NORFOLK7 115 1 |  | 120 | 0.0481 | 105.81 | P42:345:NPPD:BKR-HOS-3322
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03174 | 105.8 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03174 | 105.8 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06283 | 105.79 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06283 | 105.79 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06283 | 105.79 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 1 | 105.79 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06283 | 105.79 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 14ALL | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.52844 | 105.79 | P12:138:OKGE:BKRBKR258_1
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.03936 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.03919 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.05468 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.07912 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.03373 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.08421 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.04146 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.03006 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.065 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.08082 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.07991 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.08464 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.04138 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.05441 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.07887 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.04138 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.33445 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.05868 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.03907 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.03103 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.03036 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.03135 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.0481 | 105.78 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03689 | 105.76 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 105.76 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 105.76 | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.15169 | 105.76 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.04414 | 105.76 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05766 | 105.71 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05766 | 105.71 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05766 | 105.71 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 1 | 105.71 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 |  | 550 | 0.05766 | 105.71 | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Thermal | 00NR | 2 | 19WP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03622 | 105.7 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05272 | 105.7 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.11888 | 105.7 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07711 | 105.7 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.07912 | 105.69 | P12:345:AEPW-GRDA:FLINTCR7:TONECE7
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.03322 | 105.69 | P12:345:AEPW-GRDA:FLINTCR7:TONECE7
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.08082 | 105.69 | P12:345:AEPW-GRDA:FLINTCR7:TONECE7
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.07991 | 105.69 | P12:345:AEPW-GRDA:FLINTCR7:TONECE7
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.05441 | 105.69 | P12:345:AEPW-GRDA:FLINTCR7:TONECE7
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.33445 | 105.69 | P12:345:AEPW-GRDA:FLINTCR7:TONECE7
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.04651 | 105.69 | P12:345:AEPW-GRDA:FLINTCR7:TONECE7
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.04782 | 105.69 | P12:345:AEPW-GRDA:FLINTCR7:TONECE7
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | CRESTON7 - MADISON7 115 1 |  | 120 | 0.05747 | 105.67 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03747 | 105.65 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 105.65 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 105.65 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03747 | 105.65 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 105.65 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 105.65 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03747 | 105.65 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 105.65 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 105.65 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03747 | 105.65 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 105.65 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 105.65 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03747 | 105.65 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 105.65 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 1 | 105.65 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.05211 | 105.62 | P12:345:WERE:N345-AECI_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.04861 | 105.62 | P12:345:WERE:N345-AECI_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.07915 | 105.62 | P12:345:WERE:N345-AECI_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.06194 | 105.62 | P12:345:WERE:N345-AECI_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.0558 | 105.62 | P12:345:WERE:N345-AECI_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.04086 | 105.62 | P12:345:WERE:N345-AECI_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 1 | 105.62 | P12:345:WERE:N345-AECI_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.11509 | 105.62 | P12:345:WERE:N345-AECI_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 1 | 105.62 | P12:345:WERE:N345-AECI_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.05536 | 105.62 | P12:345:WERE:N345-AECI_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 |  | 335 | 0.07315 | 105.62 | P12:345:WERE:N345-AECI_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.03508 | 105.62 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 09ALL | 2 | 19WP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 500 | 0.6336 | 105.6 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 500 | 0.5609 | 105.6 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 19WP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 500 | 0.5609 | 105.6 | P42:345:NPPD:BKR-KEY-3310
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.30855 | 105.57 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.20232 | 105.57 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.19958 | 105.57 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.1991 | 105.57 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03459 | 105.57 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.20598 | 105.57 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03459 | 105.57 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.42046 | 105.57 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.03936 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.03919 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.05468 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.07912 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.03373 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.04146 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.03006 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.065 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.08082 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.07991 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.08464 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.15849 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.04138 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.05441 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.15849 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.15849 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.49605 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.07887 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.04138 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.33445 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.05868 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.03907 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.03103 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.03036 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.03135 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.15849 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1136 | 0.0481 | 105.55 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03936 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03919 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.05468 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.07912 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03373 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03006 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.065 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.08082 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.07991 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.04138 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.05441 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.07887 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.04138 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.33445 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03898 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03907 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03103 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03036 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03135 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.0481 | 105.53 | P42:345:OKGE:SB_CION7381
Thermal | 01ALL | 2 | 24L | GEN-2017-067 | 'FROM -> TO' | NORTWST7 - MATHWSN7 345 1 |  | 1195 | 0.20114 | 105.52 | P12:345:OKGE:BKRBKR142
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | DOVERSW4 - OKEENE 4 138 |  | 83 | 0.37362 | 105.51 | P12:138:WFEC:OKEENE_WATONGA:2024+
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03936 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03919 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05468 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.07912 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03373 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-004 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.0364 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.04146 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03006 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.08082 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.07991 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.08464 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05502 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.04138 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05441 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05502 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05502 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.49605 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.07887 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.04138 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.33445 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05868 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03907 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03103 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03036 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03135 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05502 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.0481 | 105.48 | P23:345:WERE:STRA_345-99::
Thermal | 08NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 | 220 |  | 0.03444 | 105.48 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.0323 | 105.47 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.05272 | 105.47 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.0681 | 105.47 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.04258 | 105.47 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.11888 | 105.47 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.06849 | 105.47 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.07711 | 105.47 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.0323 | 105.47 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.05272 | 105.47 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.0681 | 105.47 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.04258 | 105.47 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.11888 | 105.47 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.06849 | 105.47 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.07711 | 105.47 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 08ALL | 2 | 24WP | GEN-2016-072 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 | 956 |  | 0.05781 | 105.43 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2016-173 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 | 956 |  | 0.07864 | 105.43 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 | 956 |  | 0.72777 | 105.43 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 | 956 |  | 0.08753 | 105.43 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 | 956 |  | 0.07619 | 105.43 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03936 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03919 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05468 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.07912 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03373 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2016-173 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05463 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.04146 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03006 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.065 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05905 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.08082 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.07991 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.08464 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06335 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.04138 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05441 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06335 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06335 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.49605 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.07887 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.04138 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.33445 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05868 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.04725 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03103 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03036 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03135 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05193 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06335 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.0481 | 105.42 | P23:345:WERE:STRA_345-96::
Thermal | 00NR | 2 | 24SP | GEN-2017-004 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03759 | 105.37 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05513 | 105.37 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05513 | 105.37 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05513 | 105.37 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05513 | 105.37 | P23:345:WERE:STRA_345-99::
Thermal | 10NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05271 | 105.34 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 10NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.03265 | 105.34 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 10NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.06083 | 105.34 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 10NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.06083 | 105.34 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 00NR | 2 | 24SP | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.03377 | 105.32 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.21183 | 105.32 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.18406 | 105.32 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.06288 | 105.32 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05765 | 105.32 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05416 | 105.32 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.22183 | 105.32 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.22183 | 105.32 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17053 | 105.32 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.08917 | 105.32 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.16707 | 105.32 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17216 | 105.32 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.21183 | 105.32 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.18406 | 105.32 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.06288 | 105.32 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05765 | 105.32 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05416 | 105.32 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.22183 | 105.32 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.22183 | 105.32 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17053 | 105.32 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.08917 | 105.32 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.16707 | 105.32 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17216 | 105.32 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.15813 | 105.31 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.15813 | 105.31 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.15813 | 105.31 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 1 | 105.31 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | ST JOE 3 - NASHUA 7 345 1 |  | 1195 | 0.15813 | 105.31 | P12:345:GMO:SIBLEY-KETCHEM-SIBREACTOR
Thermal | 00NR | 2 | 20SP | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03765 | 105.29 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.20416 | 105.27 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.24346 | 105.27 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.215 | 105.27 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.24346 | 105.27 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 03ALL | 2 | 20G | GEN-2017-049 | 'FROM -> TO' | HANSTN 2 - KINSLY 2 69 | 48 | 48 | 1 | 105.26 | P12:69:MIDW:WALNUT CREEK-NEKOMA
Thermal | 08NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04255 | 105.25 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04255 | 105.25 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03867 | 105.25 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03867 | 105.25 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03867 | 105.25 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03867 | 105.25 | P12:345:GRDA:T.NO.-CLEVLND
Thermal | 08NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04255 | 105.25 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04255 | 105.25 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03867 | 105.25 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03867 | 105.25 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03867 | 105.25 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03867 | 105.25 | P23:345:GRDA:CLEVLND CB13280
Thermal | 08NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04255 | 105.25 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.04255 | 105.25 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03867 | 105.25 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03867 | 105.25 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03867 | 105.25 | P42:345:GRDA:CLEVLND CB13280
Thermal | 08NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | 4CLEVLND - CLEVLND 4 138 Z1 |  | 371 | 0.03867 | 105.25 | P42:345:GRDA:CLEVLND CB13280
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.03375 | 105.17 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.0379 | 105.17 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.04807 | 105.17 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.0379 | 105.17 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-066 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.06447 | 105.17 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.03375 | 105.16 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.0379 | 105.16 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.04807 | 105.16 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.0379 | 105.16 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-066 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.06447 | 105.16 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.03375 | 105.16 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.0379 | 105.16 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.04807 | 105.16 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.0379 | 105.16 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-066 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.06447 | 105.16 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05211 | 105.15 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03078 | 105.15 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.04861 | 105.15 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 1 | 105.15 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.11509 | 105.15 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07037 | 105.15 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 1 | 105.15 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07315 | 105.15 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05211 | 105.15 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03078 | 105.15 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.04861 | 105.15 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 1 | 105.15 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.11509 | 105.15 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07037 | 105.15 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 1 | 105.15 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07315 | 105.15 | P23:345:WERE:BENT_345-110::
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 1 |  | 956 | 0.03352 | 105.14 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 1 |  | 956 | 0.03487 | 105.14 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03936 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03919 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.05468 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.07912 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03373 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03006 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.065 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.08082 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.07991 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.20358 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.04138 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.05441 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.07887 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.04138 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.33445 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03907 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03103 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.04577 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03036 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.03135 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.0481 | 105.11 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 1 | 105.04 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 1 | 105.04 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03936 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03919 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05468 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.07912 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03373 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2016-173 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.0543 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.04146 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03006 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.065 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05869 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.08082 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.07991 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.08464 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06328 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.04138 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05441 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06328 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06328 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.49605 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.07887 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.04138 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.33445 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05868 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.04695 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03103 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03036 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.03135 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05161 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06328 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.0481 | 105.04 | P23:345:WERE:STRA_345-97::
Thermal | 14NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 421 | 0.28621 | 104.96 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 14NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 421 | 0.26647 | 104.96 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 02NR | 2 | 24L | GEN-2016-077 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.05442 | 104.92 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 02NR | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | DENVER_N 3 - HIGGEAST 3 115 1 |  | 119.5 | 0.07574 | 104.92 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.03919 | 104.9 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.05468 | 104.9 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.03006 | 104.9 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.065 | 104.9 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.05159 | 104.9 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.04748 | 104.9 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.04069 | 104.9 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.07887 | 104.9 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.03907 | 104.9 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.06682 | 104.9 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.0481 | 104.9 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.03919 | 104.9 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.05468 | 104.9 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.03006 | 104.9 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.065 | 104.9 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.05159 | 104.9 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.04748 | 104.9 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.04069 | 104.9 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.07887 | 104.9 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.03907 | 104.9 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.06682 | 104.9 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | LONGWD 7 - WILKES 7 345 1 |  | 776 | 0.0481 | 104.9 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 09ALL | 2 | 29SP | GEN-2016-034 | 'FROM -> TO' | G16-110-TAP - STEGALL_-MB3 345 |  | 765 | 1 | 104.89 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.03936 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.03919 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.05468 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.07912 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.03373 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.04146 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.03006 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.065 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.08082 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.07991 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.08464 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.08932 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.04138 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.05441 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.08932 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.08932 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.49605 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.07887 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.04138 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.33445 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.05868 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.03907 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.03103 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.03036 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.03135 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.08932 | 104.87 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.0481 | 104.87 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.21077 | 104.81 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 1 | 104.81 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 1 | 104.81 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03652 | 104.8 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03652 | 104.8 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | CBLUFFS3 - S3456 3 345 1 |  | 956 | 0.03652 | 104.8 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.20376 | 104.8 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.04597 | 104.8 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.18999 | 104.79 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.05218 | 104.79 | P12:345:OKGE:BKRBKR21
Thermal | 03ALL | 2 | 24WP | GEN-2017-049 | 'FROM -> TO' | SEWARD 2 - ZOOK 2 69 | 48 | 48 | 1 | 104.77 | P12:69:MIDW:WALNUT CREEK-NEKOMA
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.05211 | 104.75 | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.04861 | 104.75 | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.06194 | 104.75 | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.0558 | 104.75 | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.04086 | 104.75 | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 1 | 104.75 | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.11509 | 104.75 | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.26313 | 104.75 | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 1 | 104.75 | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.05536 | 104.75 | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.04342 | 104.75 | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.07828 | 104.75 | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.07315 | 104.75 | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.05211 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.04861 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.06194 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.0558 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.04086 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 1 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.11509 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.26313 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 1 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.05536 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.04342 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.07828 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.07315 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5!:1
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.05211 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.04861 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5:1
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.06194 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5:1
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.0558 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5:1
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.04086 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 1 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.11509 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5:1
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.26313 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 1 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5:1
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.05536 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5:1
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.04342 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5:1
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.07828 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5:1
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.07315 | 104.75 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5:1
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03936 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03919 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.05468 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.07912 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03373 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03207 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.04146 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.12889 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.065 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.08082 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.07991 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.08464 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.04138 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.05441 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.3124 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.04138 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.33445 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.05868 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03907 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03103 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03036 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03135 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.19665 | 104.73 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.07912 | 104.71 | P23:345:AEPW:FLINT CREEK CB 12430 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.03343 | 104.71 | P23:345:AEPW:FLINT CREEK CB 12430 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.08082 | 104.71 | P23:345:AEPW:FLINT CREEK CB 12430 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.07991 | 104.71 | P23:345:AEPW:FLINT CREEK CB 12430 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.05441 | 104.71 | P23:345:AEPW:FLINT CREEK CB 12430 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.33445 | 104.71 | P23:345:AEPW:FLINT CREEK CB 12430 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.04589 | 104.71 | P23:345:AEPW:FLINT CREEK CB 12430 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.04731 | 104.71 | P23:345:AEPW:FLINT CREEK CB 12430 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.07912 | 104.71 | P43:345:AEPW:FLINT CREEK CB 12430 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.03343 | 104.71 | P43:345:AEPW:FLINT CREEK CB 12430 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.08082 | 104.71 | P43:345:AEPW:FLINT CREEK CB 12430 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.07991 | 104.71 | P43:345:AEPW:FLINT CREEK CB 12430 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.05441 | 104.71 | P43:345:AEPW:FLINT CREEK CB 12430 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.33445 | 104.71 | P43:345:AEPW:FLINT CREEK CB 12430 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.04589 | 104.71 | P43:345:AEPW:FLINT CREEK CB 12430 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SILOAM 5 - SILMCTY5 161 1 |  | 464 | 0.04731 | 104.71 | P43:345:AEPW:FLINT CREEK CB 12430 NBTB+FAULT
Thermal | 06ALL | 2 | 24WP | ASGI-2016-001 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.06634 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | ASGI-2017-007 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.06634 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.15595 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-077 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.06963 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-078 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.11992 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-090 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.06643 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-171 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.06216 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.16519 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.10369 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.24565 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.10841 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.09989 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.09452 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.05496 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.10841 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.03871 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-079 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.15477 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.09989 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.20746 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-084 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.16805 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.10776 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-091 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.13506 | 104.7 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-104 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 559 |  | 0.05969 | 104.7 | System Intact
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | CARTHAG5 - CAR395 5 161 |  | 222 | 0.29608 | 104.7 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 1 |  | 496 | 0.09635 | 104.7 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 1 |  | 496 | 0.23467 | 104.7 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 1 |  | 496 | 0.14737 | 104.7 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 1 | 104.68 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 1 | 104.68 | P12:EHV:EES::FTSMITH7%:FTSMITH8%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 1 | 104.68 | P13:345-500:OKGE:BKRBKR_3W068
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 1 | 104.68 | P13:345-500:OKGE:BKRBKR_3W068
Thermal | 09ALL | 2 | 24SP | GEN-2016-034 | 'FROM -> TO' | G16-110-TAP - STEGALL_-MB3 345 |  | 765 | 1 | 104.68 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.15168 | 104.62 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.0441 | 104.62 | P42:345:OKGE:SB_JOCO7383
Thermal | 14ALL | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.41396 | 104.61 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z | 720 |  | 0.0323 | 104.59 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z | 720 |  | 0.06406 | 104.59 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z | 720 |  | 0.16391 | 104.59 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z | 720 |  | 0.0681 | 104.59 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z | 720 |  | 0.07364 | 104.59 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z | 720 |  | 0.03837 | 104.59 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z | 720 |  | 0.05516 | 104.59 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | GR ISLD3 - GR ISLD-LNX3 345 Z | 720 |  | 0.03929 | 104.59 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.04342 | 104.57 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 1 | 104.57 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 1 | 104.57 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24SP | GEN-2017-028 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03251 | 104.56 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.03936 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.03919 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05468 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.07912 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.03373 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2016-173 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05441 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.04146 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.03006 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.065 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05885 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.08082 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.07991 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.08464 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06236 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.04138 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05441 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06236 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06236 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.49605 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.07887 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.04138 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.33445 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05868 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.04709 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.03103 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.03036 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.03135 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05172 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06236 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.0481 | 104.55 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 06ALL | 2 | 24WP | ASGI-2016-001 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.06634 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | ASGI-2017-007 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.06634 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.15595 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-077 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.06963 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-078 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.11992 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-090 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.06643 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-171 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.06216 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.16519 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.10369 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.24565 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.10841 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.09989 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.09452 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.05496 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.10841 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-078 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.03871 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-079 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.15477 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.09989 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.20746 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-084 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.16805 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.10776 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-091 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.13506 | 104.54 | System Intact
Thermal | 06ALL | 2 | 24WP | GEN-2017-104 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 559 |  | 0.05969 | 104.54 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | COLMBUS7 - CRESTON7 115 1 |  | 120 | 0.06416 | 104.53 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06283 | 104.52 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06283 | 104.52 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06283 | 104.52 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 1 | 104.52 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06283 | 104.52 | P23:161-345:KCPL:HAWTHORN_R10-20::HAWTHORN-SIBLEY-HAWT20
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.08104 | 104.52 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.2477 | 104.52 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | WAYSIDE4 - WAYSIDE T1 115 1 |  | 187 | 0.14271 | 104.52 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.20962 | 104.5 | P42:345:NPPD:BKR-HOS-3308
Thermal | 09ALL | 2 | 20SP | GEN-2016-034 | 'FROM -> TO' | G16-110-TAP - STEGALL_-MB3 345 |  | 765 | 1 | 104.49 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 14NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13783 | 104.48 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 14NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13032 | 104.48 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 14NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13783 | 104.48 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 14NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13032 | 104.48 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.04173 | 104.44 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.12531 | 104.44 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.3059 | 104.44 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.1919 | 104.44 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 09ALL | 2 | 24WP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 500 | 0.63761 | 104.43 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24WP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 500 | 0.56445 | 104.43 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24WP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB4 - SDQ 2A 230 |  | 500 | 0.56445 | 104.43 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.03936 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.07391 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.07912 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.03373 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.04365 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.08082 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.07991 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.04138 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.05441 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.04138 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.33445 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.03907 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.03103 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.03036 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.03135 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | FTTHOMP4 - LAKPLAT-ER4 230 1 |  | 352 | 0.05642 | 104.42 | P12:230:UMZW:# 693 #: FT IN SD. FT-FR LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.06986 | 104.42 | P42:345:NPPD:BKR-HOS-3312
Thermal | 08ALL | 2 | 20SP | GEN-2017-005 | 'FROM -> TO' | ORO110 5 - FIR417 5 161 |  | 223 | 0.31985 | 104.42 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 09ALL | 2 | 20G | GEN-2016-109 | 'FROM -> TO' | KELLY 3 - GOFF 3 115 1 | 86 |  | 0.0459 | 104.42 | System Intact
Thermal | 12NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.03699 | 104.42 | P12:345:OKGE:BKRBKR295
Thermal | 12NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.03699 | 104.42 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.04056 | 104.4 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0323 | 104.38 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.17711 | 104.38 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.15743 | 104.38 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.05272 | 104.38 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0681 | 104.38 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.03968 | 104.38 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.18405 | 104.38 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.11888 | 104.38 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.18405 | 104.38 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14803 | 104.38 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0638 | 104.38 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14559 | 104.38 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14919 | 104.38 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.07711 | 104.38 | P23:345:AEPW:NW TEXARKANA CB 11820 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0323 | 104.38 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.17711 | 104.38 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.15743 | 104.38 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.05272 | 104.38 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0681 | 104.38 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.03968 | 104.38 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.18405 | 104.38 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.11888 | 104.38 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.18405 | 104.38 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14803 | 104.38 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0638 | 104.38 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14559 | 104.38 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14919 | 104.38 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.07711 | 104.38 | P43:345:AEPW:NW TEXARKANA CB 11820 NBTB+FAULT
Thermal | 03ALL | 2 | 20G | GEN-2016-049 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 | 350 | 0.08797 | 104.36 | System Intact
Thermal | 03ALL | 2 | 20G | GEN-2017-021 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 | 350 | 0.0601 | 104.36 | System Intact
Thermal | 03ALL | 2 | 20G | GEN-2017-032 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 | 350 | 0.04465 | 104.36 | System Intact
Thermal | 03ALL | 2 | 20G | GEN-2017-049 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 | 350 | 0.04349 | 104.36 | System Intact
Thermal | 03ALL | 2 | 20G | GEN-2017-052 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 | 350 | 0.04343 | 104.36 | System Intact
Thermal | 03ALL | 2 | 20G | GEN-2017-099 | 'FROM -> TO' | SMOKYHL6 - SUMMIT 6 230 | 319 | 350 | 0.0601 | 104.36 | System Intact
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 7BLACKBERRY - NEOSHO 7 345 |  | 870 | 0.21821 | 104.35 | P23:345:GRDA:GRDA CB9080
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 7BLACKBERRY - NEOSHO 7 345 |  | 870 | 0.21821 | 104.35 | P43:345:GRDA:GRDA CB9080
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06959 | 104.34 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06959 | 104.34 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06959 | 104.34 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 1 | 104.34 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.06959 | 104.34 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 01NR | 2 | 20G | GEN-2017-071 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.08963 | 104.33 | P23:345:GRDA:CLEVLND CB10180
Thermal | 01NR | 2 | 20G | GEN-2017-072 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.08963 | 104.33 | P23:345:GRDA:CLEVLND CB10180
Thermal | 01NR | 2 | 20G | GEN-2017-071 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.08963 | 104.33 | P43:345:GRDA:CLEVLND CB10180
Thermal | 01NR | 2 | 20G | GEN-2017-072 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.08963 | 104.33 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.08952 | 104.31 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.08952 | 104.31 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.08952 | 104.31 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - NASHUA 7 345 1 | 1000 |  | 0.08952 | 104.31 | System Intact
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 1 |  | 496 | 0.09635 | 104.31 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 1 |  | 496 | 0.23467 | 104.31 | P42:345:NPPD:BKR-KEY-3310
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 1 |  | 496 | 0.14737 | 104.31 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2016-034 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 |  | 320 | 0.51919 | 104.29 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2016-093 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 |  | 320 | 0.48248 | 104.29 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2017-031 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 |  | 320 | 0.51465 | 104.29 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 20SP | GEN-2017-037 | 'FROM -> TO' | GENTLMN4 - OGALALA4 230 |  | 320 | 0.48248 | 104.29 | P42:345:NPPD:BKR-KEY-3310
Thermal | 14NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.14292 | 104.27 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 14NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13505 | 104.27 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22991 | 104.26 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1941 | 104.26 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06775 | 104.26 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06251 | 104.26 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06832 | 104.26 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.24263 | 104.26 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.24263 | 104.26 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17701 | 104.26 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.11414 | 104.26 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1728 | 104.26 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17904 | 104.26 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22991 | 104.26 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1941 | 104.26 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06775 | 104.26 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06251 | 104.26 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06832 | 104.26 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.24263 | 104.26 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.24263 | 104.26 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17701 | 104.26 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.11414 | 104.26 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1728 | 104.26 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17904 | 104.26 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.21049 | 104.21 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.18304 | 104.21 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.06248 | 104.21 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05727 | 104.21 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05356 | 104.21 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.22038 | 104.21 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.22038 | 104.21 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.16965 | 104.21 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.08813 | 104.21 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.16623 | 104.21 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17128 | 104.21 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-071 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.16838 | 104.18 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 20SP | GEN-2017-072 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.16838 | 104.18 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 20SP | GEN-2017-071 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.16838 | 104.18 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 20SP | GEN-2017-072 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.16838 | 104.18 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03936 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03919 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.05468 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.07912 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03373 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03006 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.065 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.08082 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.07991 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.04138 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.05441 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.07887 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.04138 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.33445 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03417 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03907 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03103 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03036 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03135 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.0481 | 104.17 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 06NR | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.04188 | 104.17 | P12:115:SPS:T89.1.DC_N.HIGG
Thermal | 09ALL | 2 | 19WP | GEN-2016-034 | 'FROM -> TO' | G16-110-TAP - STEGALL_-MB3 345 |  | 765 | 1 | 104.15 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.06367 | 104.14 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | MARTIN 7 - WANBLEE 7 115 1 |  | 120 | 0.0511 | 104.14 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.03936 | 104.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.07912 | 104.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.03373 | 104.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.08082 | 104.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.07991 | 104.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.04138 | 104.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.05441 | 104.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.04138 | 104.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.33445 | 104.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.09283 | 104.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.03103 | 104.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.03036 | 104.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.03135 | 104.1 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.03936 | 104.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.07912 | 104.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.03373 | 104.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.08082 | 104.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.07991 | 104.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.04138 | 104.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.05441 | 104.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.04138 | 104.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.33445 | 104.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.09283 | 104.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.03103 | 104.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.03036 | 104.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.03135 | 104.1 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.03936 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-103 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.07583 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.07912 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.03373 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.03713 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.08082 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.07991 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.04138 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.05441 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.04138 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.33445 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.03907 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.03103 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.03036 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.03135 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-094 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.05172 | 104.09 | P23:345:UMZW:# 2412 #: FT2 IN SD. FT2 3396 BKR FAULT
Thermal | 09ALL | 2 | 24WP | GEN-2016-034 | 'FROM -> TO' | G16-110-TAP - STEGALL_-MB3 345 |  | 765 | 1 | 104.08 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 14NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.14246 | 104.08 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 14NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13462 | 104.08 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 14NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.14246 | 104.08 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 14NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13462 | 104.08 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | DIANA 7 - DIANA 3 138 3 |  | 473 | 0.03314 | 104.07 | P23:345:AEPW:DIANA CB 11900 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | DIANA 7 - DIANA 3 138 3 |  | 473 | 0.03018 | 104.07 | P23:345:AEPW:DIANA CB 11900 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | DIANA 7 - DIANA 3 138 3 |  | 473 | 0.03419 | 104.07 | P23:345:AEPW:DIANA CB 11900 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | DIANA 7 - DIANA 3 138 3 |  | 473 | 0.03419 | 104.07 | P23:345:AEPW:DIANA CB 11900 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03936 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03919 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.05468 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.07912 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03373 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03006 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.065 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.08082 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.07991 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.18985 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.04138 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.05441 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.07887 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.04138 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.33445 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03907 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03103 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.05204 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03036 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03135 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.0481 | 104.05 | P12:345:OKGE:BKRBKR21
Thermal | 09ALL | 2 | 24WP | GEN-2016-034 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 500 | 0.63761 | 104.05 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24WP | GEN-2016-093 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 500 | 0.56445 | 104.05 | P42:345:NPPD:BKR-KEY-3310
Thermal | 09ALL | 2 | 24WP | GEN-2017-037 | 'FROM -> TO' | SIDNEY__-MB3 - SDQ 2A 230 |  | 500 | 0.56445 | 104.05 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.03936 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.05491 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.07673 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.07912 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.03373 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.03006 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.065 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.08082 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.07991 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.04138 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.05441 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.07887 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.04138 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.33445 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.03907 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.03103 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.03036 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.03135 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HIGGEAST 3 - HIGG 3 115 1 |  | 159.4 | 0.0481 | 104.04 | P12:115:SPS:W35.1.GAINES.JNSDRW
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.0323 | 104.03 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.05272 | 104.03 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.0681 | 104.03 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.11888 | 104.03 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 19WP | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.05057 | 104.03 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.07711 | 104.03 | P42:345:OKGE:SB_CION7382
Thermal | 08NR | 2 | 24L | GEN-2017-073 | 'FROM -> TO' | EDDY_CNTY 7 - ABB AEM30711 230 1 |  | 558 | 0.05559 | 104.02 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.0377 | 104.01 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05352 | 104.01 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05352 | 104.01 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05352 | 104.01 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 1 | 104.01 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 1 | 104.01 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05536 | 104.01 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05352 | 104.01 | P23:345:WERE:STRA_345-99::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 1 | 104 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 1 | 104 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 24SP | GEN-2017-067 | 'FROM -> TO' | CIMARON7 - CIMARON2 138 1 |  | 478 | 0.03908 | 103.99 | P42:345:OKGE:SB_CION7381
Thermal | 06ALL | 2 | 19WP | GEN-2016-078 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.21303 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-007 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.2632 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-016 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.25565 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-026 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.29156 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-039 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.27273 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-069 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.25565 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-080 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.29156 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 19WP | GEN-2017-087 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.25627 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.37646 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.37646 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.28239 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.36611 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.3076 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.36774 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.37013 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.27326 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.31833 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.20718 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.31456 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.32007 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.3276 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.3926 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.31456 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.28261 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.32007 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.22706 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.2716 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.3151 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.30032 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 24WP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 1142.5 | 0.37128 | 103.98 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 14NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.30721 | 103.93 | P12:138:AEPW-WFEC:S.W.S.-4:WASHITA4
Thermal | 14NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.31498 | 103.93 | P12:138:AEPW-WFEC:S.W.S.-4:WASHITA4
Thermal | 14NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.3138 | 103.93 | P12:138:AEPW-WFEC:S.W.S.-4:WASHITA4
Thermal | 14NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.22342 | 103.93 | P12:138:AEPW-WFEC:S.W.S.-4:WASHITA4
Thermal | 14NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.66442 | 103.93 | P12:138:AEPW-WFEC:S.W.S.-4:WASHITA4
Thermal | 14NR | 2 | 24L | GEN-2017-067 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.09396 | 103.93 | P12:138:AEPW-WFEC:S.W.S.-4:WASHITA4
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0323 | 103.9 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.17705 | 103.9 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.15739 | 103.9 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.05272 | 103.9 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0681 | 103.9 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.03965 | 103.9 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.18399 | 103.9 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.11888 | 103.9 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.18399 | 103.9 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.148 | 103.9 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.06374 | 103.9 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14556 | 103.9 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14916 | 103.9 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.07711 | 103.9 | P23:345:AEPW:NW TEXARKANA CB 11810 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0323 | 103.9 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.17705 | 103.9 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.15739 | 103.9 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.05272 | 103.9 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0681 | 103.9 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.03965 | 103.9 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.18399 | 103.9 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.11888 | 103.9 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.18399 | 103.9 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.148 | 103.9 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.06374 | 103.9 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14556 | 103.9 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14916 | 103.9 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.07711 | 103.9 | P43:345:AEPW:NW TEXARKANA CB 11810 NBTB+FAULT
Thermal | 16NR | 2 | 20G | GEN-2016-103 | 'FROM -> TO' | AV.LS-BD-BE3 - BD.LS-AV-BE3 345 1 |  | 478 | 0.10201 | 103.89 | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Thermal | 16NR | 2 | 20G | GEN-2017-048 | 'FROM -> TO' | AV.LS-BD-BE3 - BD.LS-AV-BE3 345 1 |  | 478 | 0.09659 | 103.89 | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.20715 | 103.86 | P42:345:NPPD:BKR-HOS-3308
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.11022 | 103.86 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-078 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.07419 | 103.86 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.11946 | 103.86 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.05796 | 103.86 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.19992 | 103.86 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.06268 | 103.86 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.05416 | 103.86 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.04879 | 103.86 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.06268 | 103.86 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-079 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.10905 | 103.86 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.05416 | 103.86 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.16173 | 103.86 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-084 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.12232 | 103.86 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.06204 | 103.86 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.08934 | 103.86 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | E_CLOVIS 3 - CURRY 3 115 1 |  | 123.1 | 0.36655 | 103.84 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | E_CLOVIS 3 - CURRY 3 115 1 |  | 123.1 | 0.36655 | 103.84 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | E_CLOVIS 3 - CURRY 3 115 1 |  | 123.1 | 0.27967 | 103.84 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.05211 | 103.83 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.04861 | 103.83 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.06194 | 103.83 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.0558 | 103.83 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.04086 | 103.83 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 1 | 103.83 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.11509 | 103.83 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 1 | 103.83 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.05536 | 103.83 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.07315 | 103.83 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.05211 | 103.83 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.04861 | 103.83 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.06194 | 103.83 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.0558 | 103.83 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.04086 | 103.83 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 1 | 103.83 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.11509 | 103.83 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 1 | 103.83 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.05536 | 103.83 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.07315 | 103.83 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.05211 | 103.83 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.04861 | 103.83 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.06194 | 103.83 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.0558 | 103.83 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.04086 | 103.83 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 1 | 103.83 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.11509 | 103.83 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 1 | 103.83 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.05536 | 103.83 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | SPRGFLD5 - LAR382 5 161 1 |  | 167 | 0.07315 | 103.83 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 1 | 103.82 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24WP | GEN-2017-071 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.08993 | 103.82 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24WP | GEN-2017-072 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.08993 | 103.82 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 1 | 103.82 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 1 | 103.82 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24WP | GEN-2017-071 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.08993 | 103.82 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24WP | GEN-2017-072 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.08993 | 103.82 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 1 | 103.82 | P43:345:GRDA:CLEVLND CB10180
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | NORTWST7 - MATHWSN7 345 1 |  | 1195 | 0.03352 | 103.82 | P12:345:OKGE:BKRBKR142
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | NORTWST7 - MATHWSN7 345 1 |  | 1195 | 0.03487 | 103.82 | P12:345:OKGE:BKRBKR142
Thermal | 08ALL | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | DOMES 4 - WESTERNWALL4 138 | 152 |  | 0.24914 | 103.82 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | FRANKLIN5 161/69XFR |  | 110 | 0.27238 | 103.81 | P12:161:WERE:FRAN-LITC_161::
Thermal | 00NR | 2 | 19WP | GEN-2017-022 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.07931 | 103.8 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22991 | 103.79 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.19412 | 103.79 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 20SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07061 | 103.79 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 20SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06501 | 103.79 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06849 | 103.79 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.24262 | 103.79 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.24262 | 103.79 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 20SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17704 | 103.79 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1142 | 103.79 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 20SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17281 | 103.79 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 20SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.17906 | 103.79 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 06ALL | 2 | 20SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.31943 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.31943 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.2443 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20006 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.21954 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22401 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20425 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20405 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22763 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.21228 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.38248 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20405 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23054 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22763 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22808 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20365 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.24291 | 103.79 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | WILKES 4 - WILKES 138 1 |  | 597 | 0.05172 | 103.78 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | WILKES 4 - WILKES 138 1 |  | 597 | 0.04858 | 103.78 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | WILKES 4 - WILKES 138 1 |  | 597 | 0.05284 | 103.78 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | WILKES 4 - WILKES 138 1 |  | 597 | 0.05284 | 103.78 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | WILKES 4 - WILKES 138 1 |  | 597 | 0.04713 | 103.78 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | WILKES 4 - WILKES 138 1 |  | 597 | 0.04677 | 103.78 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | WILKES 4 - WILKES 138 1 |  | 597 | 0.04731 | 103.78 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | WILKES 4 - WILKES 138 1 |  | 597 | 0.05172 | 103.78 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | WILKES 4 - WILKES 138 1 |  | 597 | 0.04858 | 103.78 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | WILKES 4 - WILKES 138 1 |  | 597 | 0.05284 | 103.78 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | WILKES 4 - WILKES 138 1 |  | 597 | 0.05284 | 103.78 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | WILKES 4 - WILKES 138 1 |  | 597 | 0.04713 | 103.78 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | WILKES 4 - WILKES 138 1 |  | 597 | 0.04677 | 103.78 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | WILKES 4 - WILKES 138 1 |  | 597 | 0.04731 | 103.78 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 7BLACKBERRY - NEOSHO 7 345 |  | 870 | 0.22167 | 103.77 | P12:345:GRDA:GRDA1 -GRECTAP
Thermal | 08ALL | 2 | 20G | GEN-2017-009 | 'FROM -> TO' | 7BLACKBERRY - NEOSHO 7 345 |  | 870 | 0.22167 | 103.77 | P24:345:GRDA:GRDA CB400T
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03936 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03919 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.05468 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07912 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03373 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03006 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.065 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.08082 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07991 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.13885 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04138 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.05441 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07887 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04138 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.33445 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03907 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03103 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03036 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03135 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.0481 | 103.76 | P12:138:OKGE:BKRBKR344
Thermal | 06ALL | 2 | 20SP | ASGI-2016-001 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.06952 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | ASGI-2017-007 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.06952 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.15898 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-077 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.07282 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-078 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.12309 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-090 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.06964 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-171 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.06533 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.16833 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.10686 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.24898 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.11158 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.10306 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.09769 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.05812 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.11158 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.04189 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-079 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.15791 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.10306 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.21034 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-084 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.17118 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.11093 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-091 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.13819 | 103.76 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-104 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.06285 | 103.76 | System Intact
Thermal | 12NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.04907 | 103.76 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 | 720 |  | 0.0323 | 103.75 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 | 720 |  | 0.06406 | 103.75 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 | 720 |  | 0.16391 | 103.75 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 | 720 |  | 0.0681 | 103.75 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 | 720 |  | 0.07364 | 103.75 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 | 720 |  | 0.03837 | 103.75 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 | 720 |  | 0.05516 | 103.75 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HOLT.CO3 - GR ISLD-LNX3 345 1 | 720 |  | 0.03929 | 103.75 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.19006 | 103.75 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.05227 | 103.75 | P12:345:OKGE:BKRBKR21
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.30855 | 103.74 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.20232 | 103.74 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.19958 | 103.74 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.1991 | 103.74 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03459 | 103.74 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.20598 | 103.74 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.03459 | 103.74 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.42046 | 103.74 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03936 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03919 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.05468 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.07912 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03373 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03065 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.04146 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.12684 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.065 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.08082 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.07991 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.08464 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.04138 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.05441 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.30735 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.04138 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.33445 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.05868 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03907 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03103 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03036 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03135 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.19349 | 103.73 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 14NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.14209 | 103.7 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 14NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13426 | 103.7 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 14NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.14209 | 103.7 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 14NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1324 | 0.13426 | 103.7 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 08ALL | 2 | 24L | GEN-2016-072 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.08919 | 103.68 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.05864 | 103.68 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2016-173 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.10653 | 103.68 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-022 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.04109 | 103.68 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-040 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.04097 | 103.68 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-068 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.10644 | 103.68 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-071 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.05237 | 103.68 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-072 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.05237 | 103.68 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-086 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.10069 | 103.68 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-092 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.04097 | 103.68 | System Intact
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | HUGO 7 - G16-063-TAP 345 1 |  | 1195 | 0.1474 | 103.67 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | HUGO 7 - G16-063-TAP 345 1 |  | 1195 | 0.10085 | 103.67 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | HUGO 7 - G16-063-TAP 345 1 |  | 1195 | 0.16956 | 103.67 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | HUGO 7 - G16-063-TAP 345 1 |  | 1195 | 0.16956 | 103.67 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-074 | 'FROM -> TO' | HUGO 7 - G16-063-TAP 345 1 |  | 1195 | 0.08295 | 103.67 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | HUGO 7 - G16-063-TAP 345 1 |  | 1195 | 0.07917 | 103.67 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-077 | 'FROM -> TO' | HUGO 7 - G16-063-TAP 345 1 |  | 1195 | 0.08412 | 103.67 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | HUGO 7 - G16-063-TAP 345 1 |  | 1195 | 0.1474 | 103.67 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | HUGO 7 - G16-063-TAP 345 1 |  | 1195 | 0.10085 | 103.67 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | HUGO 7 - G16-063-TAP 345 1 |  | 1195 | 0.16956 | 103.67 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | HUGO 7 - G16-063-TAP 345 1 |  | 1195 | 0.16956 | 103.67 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-074 | 'FROM -> TO' | HUGO 7 - G16-063-TAP 345 1 |  | 1195 | 0.08295 | 103.67 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | HUGO 7 - G16-063-TAP 345 1 |  | 1195 | 0.07917 | 103.67 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-077 | 'FROM -> TO' | HUGO 7 - G16-063-TAP 345 1 |  | 1195 | 0.08412 | 103.67 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.05211 | 103.65 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.04861 | 103.65 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 1 | 103.65 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.11509 | 103.65 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.03309 | 103.65 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 1 | 103.65 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.05536 | 103.65 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | BENTON 7 - BENT TX-2 138 1 |  | 440 | 0.07315 | 103.65 | P23:345:WERE:BENT_345-50::
Thermal | 00NR | 2 | 24SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.2107 | 103.65 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.18321 | 103.65 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.06255 | 103.65 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05733 | 103.65 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05363 | 103.65 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.2206 | 103.65 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.2206 | 103.65 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.1698 | 103.65 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.08826 | 103.65 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.16637 | 103.65 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17143 | 103.65 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.05211 | 103.63 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.17978 | 103.63 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 1 | 103.63 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.13358 | 103.63 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 1 | 103.63 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.05536 | 103.63 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.19911 | 103.63 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 20SP | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03708 | 103.61 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.03936 | 103.61 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.07912 | 103.61 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.03373 | 103.61 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.08082 | 103.61 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.07991 | 103.61 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.04138 | 103.61 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.05441 | 103.61 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.04138 | 103.61 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.33445 | 103.61 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.09447 | 103.61 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.03103 | 103.61 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.03036 | 103.61 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.03135 | 103.61 | P23:345:WERE:WICH_345-80::
Thermal | 06ALL | 2 | 24SP | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 |  | 559 | 0.28021 | 103.59 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 |  | 559 | 0.24479 | 103.59 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 08ALL | 2 | 24SP | GEN-2016-173 | 'FROM -> TO' | FARBER 4 - SC10BEL4 138 |  | 160 | 0.24172 | 103.59 | P23:345:WERE:WICH_345-116::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.0323 | 103.58 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.05008 | 103.58 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.05272 | 103.58 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.0681 | 103.58 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.07364 | 103.58 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03837 | 103.58 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.11888 | 103.58 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.05516 | 103.58 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.07711 | 103.58 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.03929 | 103.58 | P13:115-345:NPPD:HOSKINS3:T4
Thermal | 00NR | 2 | 24SP | GEN-2016-173 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05704 | 103.54 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 24SP | GEN-2017-022 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06153 | 103.54 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06366 | 103.54 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06366 | 103.54 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06366 | 103.54 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.04959 | 103.54 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05431 | 103.54 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06366 | 103.54 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.21761 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03919 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.05468 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.18225 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03006 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.065 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07514 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06948 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06807 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.23033 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07887 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.23033 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03907 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1652 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.11385 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16099 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16721 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.0481 | 103.45 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.21761 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03919 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.05468 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.18225 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03006 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.065 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07514 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06948 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06807 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.23033 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07887 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.23033 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03907 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1652 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.11385 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16099 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16721 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.0481 | 103.45 | P42:345:AEPW:NW TEXARKANA CB 15440 NBTB+FAULT
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.11022 | 103.44 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-078 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.07419 | 103.44 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.11946 | 103.44 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.05796 | 103.44 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.19992 | 103.44 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.06268 | 103.44 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.05416 | 103.44 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.04879 | 103.44 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.06268 | 103.44 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-079 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.10905 | 103.44 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.05416 | 103.44 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.16173 | 103.44 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-084 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.12232 | 103.44 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.06204 | 103.44 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | POTTER_CO 7 345/230XFR 1 | 516 |  | 0.08934 | 103.44 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-057 | 'FROM -> TO' | GILLIAM2 - SUPEROR2 69.0 1 |  | 39 | 0.45792 | 103.42 | P12:69:AEPW:HOSSTON2:VIVIAN2:SUPEROR2 \BREAKER TO BREAKER IS HOSSTON - SUPERIOR
Thermal | 06ALL | 2 | 19WP | GEN-2017-091 | 'FROM -> TO' | LAMTON 3 - HALE_CNTY 3 115 1 |  | 79.7 | 0.34723 | 103.35 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 01ALL | 2 | 24SP | GEN-2016-107 | 'FROM -> TO' | OKEENE 4 - G16-107-TAP 138 | 160 |  | 0.56718 | 103.34 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.03936 | 103.31 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.07912 | 103.31 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.03373 | 103.31 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.08082 | 103.31 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.07991 | 103.31 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.04138 | 103.31 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.05441 | 103.31 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.04138 | 103.31 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.33445 | 103.31 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.09283 | 103.31 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.03103 | 103.31 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.03036 | 103.31 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.03135 | 103.31 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.03936 | 103.31 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.07912 | 103.31 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.03373 | 103.31 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.08082 | 103.31 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.07991 | 103.31 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.04138 | 103.31 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.05441 | 103.31 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.04138 | 103.31 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.33445 | 103.31 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.09283 | 103.31 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.03103 | 103.31 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.03036 | 103.31 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.03135 | 103.31 | P23:345:WERE:BENT_345-110::
Thermal | 06ALL | 2 | 20SP | ASGI-2016-001 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.06952 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | ASGI-2017-007 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.06952 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.15898 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-077 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.07282 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-078 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.12309 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-090 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.06964 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-171 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.06533 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.16833 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.10686 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.24898 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.11158 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.10306 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.09769 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.05812 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.11158 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-078 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.04189 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-079 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.15791 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.10306 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.21034 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-084 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.17118 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.11093 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-091 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.13819 | 103.31 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-104 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.06285 | 103.31 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.04016 | 103.29 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.12333 | 103.29 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.30094 | 103.29 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.18881 | 103.29 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKINS T1 115 1 |  | 187 | 0.07136 | 103.28 | P42:345:NPPD:BKR-HOS-3312
Thermal | 09ALL | 2 | 29SP | GEN-2016-034 | 'FROM -> TO' | G16-110-TAP - STEGALL_-MB3 345 |  | 765 | 1 | 103.28 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.20715 | 103.26 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24SP | GEN-2017-071 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.16834 | 103.26 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24SP | GEN-2017-072 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.16834 | 103.26 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24SP | GEN-2017-071 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.16834 | 103.26 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24SP | GEN-2017-072 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.16834 | 103.26 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.03936 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.03919 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05468 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.07912 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.03373 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2016-173 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05331 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.04146 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.03006 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.065 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05761 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.08082 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.07991 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.08464 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06213 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.04138 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05441 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06213 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06213 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.49605 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.07887 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.04138 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.33445 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05868 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.04609 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.03103 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.03036 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.03135 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-086 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05067 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06213 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.0481 | 103.26 | P23:345:WERE:STRA_345-98::
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | LAMTON 3 - HALE_CNTY 3 115 1 |  | 79.7 | 0.34554 | 103.24 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07169 | 103.23 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07169 | 103.23 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07169 | 103.23 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 1 | 103.23 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07169 | 103.23 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.06094 | 103.22 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.06094 | 103.22 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.06094 | 103.22 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.06094 | 103.22 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.0323 | 103.19 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.05272 | 103.19 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.0681 | 103.19 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.20159 | 103.19 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.11888 | 103.19 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.04381 | 103.19 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 185 | 0.07711 | 103.19 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06959 | 103.19 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06959 | 103.19 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06959 | 103.19 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 1 | 103.19 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.06959 | 103.19 | P43:013-161-345:KCPL:HAWTHORN_R20-25::HAWTU5&HAWTHT20&HAWTH-RNDLPH
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.04172 | 103.18 | P42:345:NPPD:BKR-HOS-3322
Thermal | 08NR | 2 | 24L | GEN-2017-073 | 'FROM -> TO' | EDDY_NORTH 6 - ABB AEM30711 230 1 |  | 558 | 0.05559 | 103.18 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06NR | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | BV-COM-4 - MOUNDRD4 138 1 |  | 131 | 0.17552 | 103.12 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 06NR | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | BV-COM-4 - MOUNDRD4 138 1 |  | 131 | 0.17552 | 103.12 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04538 | 103.1 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 24SP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04538 | 103.1 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.04342 | 103.07 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 1 | 103.07 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 1 | 103.07 | P42:345:NPPD:BKR-HOS-3322
Thermal | 06NR | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | BV-COM-4 - MOUNDRD4 138 1 |  | 131 | 0.17552 | 103.07 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 06NR | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | BV-COM-4 - MOUNDRD4 138 1 |  | 131 | 0.17552 | 103.07 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | PHILIP 7 - WALL 7 115 1 |  | 132 | 0.18307 | 103.06 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | PHILIP 7 - WALL 7 115 1 |  | 132 | 0.13717 | 103.06 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | PHILIP 7 - WALL 7 115 1 |  | 132 | 0.20236 | 103.06 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24SP | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03429 | 103.01 | P13:138-345:OKGE:BKRBKR_3W020
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.09381 | 103.01 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-11 138 1 |  | 430 | 0.09381 | 103.01 | P23:345:WERE:BENT_345-110::
Thermal | 06NR | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.0312 | 103 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.05683 | 102.98 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.05683 | 102.98 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.05683 | 102.98 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.05683 | 102.98 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | DIANA 4 - DIANA 3 138 3 |  | 473 | 0.03314 | 102.97 | P23:345:AEPW:DIANA CB 11900 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | DIANA 4 - DIANA 3 138 3 |  | 473 | 0.03018 | 102.97 | P23:345:AEPW:DIANA CB 11900 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | DIANA 4 - DIANA 3 138 3 |  | 473 | 0.03419 | 102.97 | P23:345:AEPW:DIANA CB 11900 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | DIANA 4 - DIANA 3 138 3 |  | 473 | 0.03419 | 102.97 | P23:345:AEPW:DIANA CB 11900 NBTB
Thermal | 09ALL | 2 | 24L | GEN-2016-109 | 'FROM -> TO' | FAIRBRY7 - HARBINE7115 | 99 |  | 0.62716 | 102.96 | System Intact
Thermal | 09ALL | 2 | 24L | GEN-2017-085 | 'FROM -> TO' | FAIRBRY7 - HARBINE7115 | 99 |  | 0.05417 | 102.96 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.07625 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.05221 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.05211 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.04861 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.05823 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.05362 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.04878 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.04086 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.0849 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 1 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.11509 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.0849 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.26313 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 1 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.04047 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.07899 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.03745 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.04189 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.07828 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.07315 | 102.95 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.07625 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.05221 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.05211 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.04861 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.05823 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.05362 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.04878 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.04086 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.0849 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 1 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.11509 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.0849 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.26313 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 1 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.04047 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.07899 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.03745 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.04189 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.07828 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | WELSH 7 - WILKES 7 345 1 |  | 1220 | 0.07315 | 102.95 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 06ALL | 2 | 24SP | GEN-2017-012 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.28021 | 102.94 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 06ALL | 2 | 24SP | GEN-2017-081 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 |  | 559 | 0.24479 | 102.94 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.20962 | 102.92 | P42:345:NPPD:BKR-HOS-3308
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.21087 | 102.92 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.20497 | 102.92 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.25017 | 102.92 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.22171 | 102.92 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.20497 | 102.92 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.25017 | 102.92 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TOLK 6 - TUCO_INT 6 230 1 |  | 478 | 0.20514 | 102.92 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | COLMBUS4 - MEADOWGROVE4 230 1 |  | 387 | 0.0323 | 102.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | COLMBUS4 - MEADOWGROVE4 230 1 |  | 387 | 0.0334 | 102.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | COLMBUS4 - MEADOWGROVE4 230 1 |  | 387 | 0.05272 | 102.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | COLMBUS4 - MEADOWGROVE4 230 1 |  | 387 | 0.0681 | 102.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | COLMBUS4 - MEADOWGROVE4 230 1 |  | 387 | 0.07364 | 102.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | COLMBUS4 - MEADOWGROVE4 230 1 |  | 387 | 0.03837 | 102.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | COLMBUS4 - MEADOWGROVE4 230 1 |  | 387 | 0.11888 | 102.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | COLMBUS4 - MEADOWGROVE4 230 1 |  | 387 | 0.05516 | 102.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | COLMBUS4 - MEADOWGROVE4 230 1 |  | 387 | 0.07711 | 102.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | COLMBUS4 - MEADOWGROVE4 230 1 |  | 387 | 0.03929 | 102.91 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24SP | GEN-2016-103 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.0921 | 102.9 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.06147 | 102.9 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-048 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.03696 | 102.9 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.03093 | 102.9 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.0744 | 102.9 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | FTTHOMP4 - FTRANDL4 230 1 |  | 320 | 0.04595 | 102.9 | P12:230:UMZW:# 694 #: FT IN SD. FT-LP LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.08104 | 102.9 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.2477 | 102.9 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | WAYSIDE7 - WAYSIDE T1 115 1 |  | 187 | 0.14271 | 102.9 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.15169 | 102.88 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | DRPSPRG4 - STIRLNG4 138 1 |  | 153 | 0.04414 | 102.88 | P42:345:OKGE:SB_JOCO7383
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | WILKES 7 - WILKES 138 1 |  | 597 | 0.05172 | 102.87 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | WILKES 7 - WILKES 138 1 |  | 597 | 0.04858 | 102.87 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | WILKES 7 - WILKES 138 1 |  | 597 | 0.05284 | 102.87 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | WILKES 7 - WILKES 138 1 |  | 597 | 0.05284 | 102.87 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | WILKES 7 - WILKES 138 1 |  | 597 | 0.04713 | 102.87 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | WILKES 7 - WILKES 138 1 |  | 597 | 0.04677 | 102.87 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | WILKES 7 - WILKES 138 1 |  | 597 | 0.04731 | 102.87 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | WILKES 7 - WILKES 138 1 |  | 597 | 0.05172 | 102.87 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | WILKES 7 - WILKES 138 1 |  | 597 | 0.04858 | 102.87 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | WILKES 7 - WILKES 138 1 |  | 597 | 0.05284 | 102.87 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | WILKES 7 - WILKES 138 1 |  | 597 | 0.05284 | 102.87 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | WILKES 7 - WILKES 138 1 |  | 597 | 0.04713 | 102.87 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | WILKES 7 - WILKES 138 1 |  | 597 | 0.04677 | 102.87 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | WILKES 7 - WILKES 138 1 |  | 597 | 0.04731 | 102.87 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 0.21077 | 102.83 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 1 | 102.83 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS7 - HOSKN T4 115 1 |  | 336 | 1 | 102.83 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.03936 | 102.82 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.07912 | 102.82 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.03373 | 102.82 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.08082 | 102.82 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.07991 | 102.82 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.04138 | 102.82 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.05441 | 102.82 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.04138 | 102.82 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.33445 | 102.82 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.09447 | 102.82 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.03103 | 102.82 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.03036 | 102.82 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.03135 | 102.82 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03936 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03919 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.05468 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.07912 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03373 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03006 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.065 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.08082 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.07991 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.15161 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.04138 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.05441 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.07887 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.04138 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.33445 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03907 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03103 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.04403 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03036 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.03135 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.0481 | 102.82 | P42:345:OKGE:SB_JOCO7303
Thermal | 06ALL | 2 | 20SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.28675 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.28675 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.21975 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20746 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20384 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20123 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.2002 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.21389 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20252 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.33582 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.2002 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20997 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.21389 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20647 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.20012 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 |  | 643 | 0.22157 | 102.82 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03361 | 102.81 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.13036 | 102.81 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.31387 | 102.81 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.19812 | 102.81 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.07585 | 102.75 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.18234 | 102.75 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | CRAIG 5 - CRAIG11 161 11 |  | 605 | 0.11512 | 102.75 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 09ALL | 2 | 19WP | GEN-2016-034 | 'FROM -> TO' | G16-110-TAP - STEGALL_-MB3 345 |  | 765 | 1 | 102.74 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 07ALL | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | MINCO 7 - CIMARON7 345 | 1195 | 1195 | 0.51259 | 102.72 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 07ALL | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | MINCO 7 - CIMARON7 345 | 1195 | 1195 | 0.38408 | 102.72 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 07ALL | 2 | 19WP | GEN-2017-051 | 'FROM -> TO' | MINCO 7 - CIMARON7 345 | 1195 | 1195 | 0.33328 | 102.72 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 07ALL | 2 | 19WP | GEN-2017-053 | 'FROM -> TO' | MINCO 7 - CIMARON7 345 | 1195 | 1195 | 0.37242 | 102.72 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 07ALL | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | MINCO 7 - CIMARON7 345 | 1195 | 1195 | 0.51259 | 102.72 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 07ALL | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | MINCO 7 - CIMARON7 345 | 1195 | 1195 | 0.38408 | 102.72 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 07ALL | 2 | 19WP | GEN-2017-051 | 'FROM -> TO' | MINCO 7 - CIMARON7 345 | 1195 | 1195 | 0.33328 | 102.72 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 07ALL | 2 | 19WP | GEN-2017-053 | 'FROM -> TO' | MINCO 7 - CIMARON7 345 | 1195 | 1195 | 0.37242 | 102.72 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 08ALL | 2 | 24WP | GEN-2016-072 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.06302 | 102.71 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.03247 | 102.71 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2016-173 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.08036 | 102.71 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.08026 | 102.71 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | WAVERLY7 - LACYGNE7 345 | 1141 |  | 0.07451 | 102.71 | System Intact
Thermal | 08ALL | 2 | 29SP | GEN-2017-005 | 'FROM -> TO' | CARTHAG5 - CAR395 5 161 |  | 222 | 0.2961 | 102.69 | P12:161:EMDE:SCHD_ADD_BRKRSADD_2018__SCHD_REMOVE_BRKRSADD_2019::ASB349_FIR417
Thermal | 09ALL | 2 | 24WP | GEN-2017-006 | 'FROM -> TO' | MOORE 3 - MONOLITH 3 345 |  | 956 | 0.29526 | 102.69 | P12:345:OPPD:S3458-COOPER
Thermal | 09ALL | 2 | 24WP | GEN-2017-008 | 'FROM -> TO' | MOORE 3 - MONOLITH 3 345 |  | 956 | 0.23946 | 102.69 | P12:345:OPPD:S3458-COOPER
Thermal | 09ALL | 2 | 24WP | GEN-2017-006 | 'FROM -> TO' | MOORE 3 - MONOLITH 3 345 |  | 956 | 0.29526 | 102.69 | P22:345:OPPD:S3458-COOPER
Thermal | 09ALL | 2 | 24WP | GEN-2017-008 | 'FROM -> TO' | MOORE 3 - MONOLITH 3 345 |  | 956 | 0.23946 | 102.69 | P22:345:OPPD:S3458-COOPER
Thermal | 09ALL | 2 | 24WP | GEN-2016-034 | 'FROM -> TO' | G16-110-TAP - STEGALL_-MB3 345 |  | 765 | 1 | 102.68 | P12:345:UMZ:# 5864 #: IN . PROPER N-1 (LINE) FOR 659133-659426-Z
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.20232 | 102.67 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.19958 | 102.67 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.1991 | 102.67 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.20598 | 102.67 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.42046 | 102.67 | P12:345:AEPW:PITTSB-7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.05211 | 102.66 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.06334 | 102.66 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 1 | 102.66 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 1 | 102.66 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.05536 | 102.66 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | PHILIP 7 - WANBLEE 7 115 1 |  | 120 | 0.05077 | 102.66 | P13:115-230:NPPD:WAYSIDE4:T1
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.08319 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2016-107 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.10351 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.05211 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.04861 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.12505 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.1237 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.04086 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.04388 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-036 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.03477 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 1 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.11509 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.04388 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-066 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.25665 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-067 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.08933 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.26313 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 1 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.07828 | 102.65 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.07315 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.26621 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.26621 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.19038 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.15593 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.14482 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.11346 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.08221 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.1654 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.1253 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.12682 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.12629 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.1344 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.12834 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.32833 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.12629 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.17016 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.1344 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.15443 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.17182 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.12597 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.17917 | 102.65 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 2 | 559 |  | 0.07053 | 102.65 | System Intact
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.20232 | 102.6 | P12:345:OKGE:BKRBKR295
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.19958 | 102.6 | P12:345:OKGE:BKRBKR295
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.1991 | 102.6 | P12:345:OKGE:BKRBKR295
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.20598 | 102.6 | P12:345:OKGE:BKRBKR295
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.42046 | 102.6 | P12:345:OKGE:BKRBKR295
Thermal | 07NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.037 | 102.6 | P12:345:OKGE:BKRBKR295
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.20232 | 102.6 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.19958 | 102.6 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.1991 | 102.6 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.20598 | 102.6 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.42046 | 102.6 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.20232 | 102.6 | P41:345:OKGE:SB_MUGE7385
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.19958 | 102.6 | P41:345:OKGE:SB_MUGE7385
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.1991 | 102.6 | P41:345:OKGE:SB_MUGE7385
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.20598 | 102.6 | P41:345:OKGE:SB_MUGE7385
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.42046 | 102.6 | P41:345:OKGE:SB_MUGE7385
Thermal | 07NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.037 | 102.6 | P41:345:OKGE:SB_MUGE7385
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.20232 | 102.6 | P42:345:OKGE:SB_FTTH7385
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.19958 | 102.6 | P42:345:OKGE:SB_FTTH7385
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.1991 | 102.6 | P42:345:OKGE:SB_FTTH7385
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.20598 | 102.6 | P42:345:OKGE:SB_FTTH7385
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.42046 | 102.6 | P42:345:OKGE:SB_FTTH7385
Thermal | 07NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.03702 | 102.6 | P42:345:OKGE:SB_FTTH7385
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.04227 | 102.57 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 1 | 102.57 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 1 | 102.57 | P42:345:NPPD:BKR-SC-3306
Thermal | 08ALL | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 | 189 |  | 0.24769 | 102.57 | System Intact
Thermal | 06ALL | 2 | 20SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.31943 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.31943 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.2443 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20006 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.21954 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22401 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20425 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20405 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22763 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.21228 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.38248 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20405 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.23054 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22763 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.22808 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.20365 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 1 |  | 643 | 0.24291 | 102.53 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 00NR | 2 | 20SP | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.04252 | 102.52 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.1931 | 102.51 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.1472 | 102.51 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.21239 | 102.51 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 08ALL | 2 | 24L | GEN-2017-009 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.06139 | 102.51 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-022 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 0.08139 | 102.51 | System Intact
Thermal | 12NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.05972 | 102.51 | P22:345:SPRM-AECI:17
Thermal | 12NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.05972 | 102.51 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 12NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.05972 | 102.51 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03936 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03919 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.05468 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.07912 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03373 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03006 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.065 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.08082 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.07991 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.04138 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.05441 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.07887 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.04138 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.33445 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03365 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03907 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03103 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03036 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03135 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.0481 | 102.49 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 185 | 0.0323 | 102.43 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 185 | 0.05272 | 102.43 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 185 | 0.0681 | 102.43 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 185 | 0.18786 | 102.43 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 185 | 0.03104 | 102.43 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 185 | 0.11888 | 102.43 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 185 | 0.03104 | 102.43 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 185 | 0.05009 | 102.43 | P12:345:OKGE:BKRBKR21
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 185 | 0.07711 | 102.43 | P12:345:OKGE:BKRBKR21
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.20232 | 102.4 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.19958 | 102.4 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.1991 | 102.4 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.20598 | 102.4 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.42046 | 102.4 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.20232 | 102.4 | P42:345:OKGE:SB_FTTH7385
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.19958 | 102.4 | P42:345:OKGE:SB_FTTH7385
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.1991 | 102.4 | P42:345:OKGE:SB_FTTH7385
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.20598 | 102.4 | P42:345:OKGE:SB_FTTH7385
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.42046 | 102.4 | P42:345:OKGE:SB_FTTH7385
Thermal | 07NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.0491 | 102.4 | P42:345:OKGE:SB_FTTH7385
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 | 500 |  | 0.06094 | 102.37 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 | 500 |  | 0.06094 | 102.37 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 | 500 |  | 0.06094 | 102.37 | System Intact
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 | 500 |  | 0.06094 | 102.37 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03936 | 102.3 | P12:138:OKGE:BKRBKR204
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.07912 | 102.3 | P12:138:OKGE:BKRBKR204
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03373 | 102.3 | P12:138:OKGE:BKRBKR204
Thermal | 00NR | 2 | 29SP | GEN-2016-173 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03092 | 102.3 | P12:138:OKGE:BKRBKR204
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.08082 | 102.3 | P12:138:OKGE:BKRBKR204
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.07991 | 102.3 | P12:138:OKGE:BKRBKR204
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.04138 | 102.3 | P12:138:OKGE:BKRBKR204
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.05441 | 102.3 | P12:138:OKGE:BKRBKR204
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.04138 | 102.3 | P12:138:OKGE:BKRBKR204
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.33445 | 102.3 | P12:138:OKGE:BKRBKR204
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03103 | 102.3 | P12:138:OKGE:BKRBKR204
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03036 | 102.3 | P12:138:OKGE:BKRBKR204
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03135 | 102.3 | P12:138:OKGE:BKRBKR204
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.09381 | 102.29 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.09381 | 102.29 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | GRDA1 7 - GRDAUTO1 161 1 |  | 560 | 0.03838 | 102.28 | P12:161:AECI:CHOTEAU-MAID
Thermal | 08ALL | 2 | 20G | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 | 189 |  | 0.24715 | 102.28 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03936 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03919 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.05468 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.07912 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03373 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03006 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.065 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.08082 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.07991 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.04138 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.05441 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.07887 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.04138 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.33445 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03907 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-071 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.16889 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-072 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.16889 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03103 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03036 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03135 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.0481 | 102.27 | P23:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03936 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03919 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.05468 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.07912 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03373 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03006 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.065 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.08082 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.07991 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.04138 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.05441 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.07887 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.04138 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.33445 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03907 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-071 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.16889 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-072 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.16889 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03103 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03036 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.03135 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | KINZE 4 - UNVRSTY4 138 1 |  | 222 | 0.0481 | 102.27 | P43:345:GRDA:CLEVLND CB10180
Thermal | 07ALL | 2 | 24SP | GEN-2017-036 | 'FROM -> TO' | ANADARK4 - CHERRYRD 4 138 | 145 | 169 | 0.57261 | 102.25 | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4
Thermal | 07ALL | 2 | 24SP | GEN-2017-053 | 'FROM -> TO' | ANADARK4 - CHERRYRD 4 138 | 145 | 169 | 0.46495 | 102.25 | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05211 | 102.24 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-011 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03078 | 102.24 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.04861 | 102.24 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 1 | 102.24 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.11509 | 102.24 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07037 | 102.24 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 1 | 102.24 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07315 | 102.24 | P12:345:WERE:BENT-WICH_345::
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.05211 | 102.24 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-011 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.03078 | 102.24 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.04861 | 102.24 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 1 | 102.24 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.11509 | 102.24 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07037 | 102.24 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 1 | 102.24 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | CHISHLM4 - MAIZE 4 138 1 |  | 382 | 0.07315 | 102.24 | P23:345:WERE:BENT_345-110::
Thermal | 00NR | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.04377 | 102.24 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.05133 | 102.24 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.04635 | 102.24 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.05304 | 102.24 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.04423 | 102.24 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.05542 | 102.24 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2016-103 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.04377 | 102.24 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.05133 | 102.24 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-048 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.04635 | 102.24 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.05304 | 102.24 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-094 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.04423 | 102.24 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | STANTN.T-BE7 - BEULAH 7 115 1 |  | 132 | 0.05542 | 102.24 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 06NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03003 | 102.23 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.02738 | 102.23 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.02738 | 102.23 | P23:345:GRDA:CLEVLND CB10180
Thermal | 06NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03003 | 102.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.02738 | 102.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 06NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.02738 | 102.23 | P43:345:GRDA:CLEVLND CB10180
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 | 500 |  | 0.05683 | 102.22 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 | 500 |  | 0.05683 | 102.22 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 | 500 |  | 0.05683 | 102.22 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN20 161 20 | 500 |  | 0.05683 | 102.22 | System Intact
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | FRANKLIN2 - FRAN TX-1 69 |  | 110 | 0.27238 | 102.21 | P12:161:WERE:FRAN-LITC_161::
Thermal | 00NR | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | 4REMNGTON - SHIDLER4 138 1 |  | 174 | 0.48013 | 102.18 | P12:138:AEPW:MOUNDRD4:SHIDLER4
Thermal | 00NR | 2 | 20SP | GEN-2016-173 | 'FROM -> TO' | 4REMNGTON - SHIDLER4 138 1 |  | 174 | 0.03929 | 102.18 | P12:138:AEPW:MOUNDRD4:SHIDLER4
Thermal | 08ALL | 2 | 24SP | GEN-2017-005 | 'FROM -> TO' | ORO110 5 - FIR417 5 161 |  | 223 | 0.32006 | 102.18 | P12:161:EMDE:SCHD_REMOVE_2019::ASB349_CAR(SPA)
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 7BLACKBERRY - NEOSHO 7 345 |  | 956 | 0.21978 | 102.12 | P24:345:GRDA:GRDA CB400T
Thermal | 08ALL | 2 | 24WP | GEN-2017-009 | 'FROM -> TO' | 7BLACKBERRY - NEOSHO 7 345 |  | 956 | 0.21978 | 102.12 | P46:345:GRDA:GRDA CB400T
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 | 128.1 |  | 1 | 102.11 | System Intact
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 | 128.1 |  | 1 | 102.11 | System Intact
Thermal | 06ALL | 2 | 20SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.36008 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.36008 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.26961 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.31842 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.27321 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.30577 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.28381 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.25632 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.26748 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.26571 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.28715 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.29001 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.38985 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.26571 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.26466 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.28715 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.21762 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.25678 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.26562 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.28043 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20SP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.26662 | 102.1 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03919 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05468 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07912 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-004 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03495 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04146 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03006 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.08082 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07991 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.08464 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04395 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05441 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04395 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04395 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.49605 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.07887 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.33445 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.05868 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.03907 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.04395 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | 87TH 7 - CRAIG 7 345 2 |  | 1254 | 0.0481 | 102.09 | P55:161-345:KCPL-WERE:CRAIG_BUS_11_345::
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.11013 | 102.09 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.15573 | 102.09 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | CHADRON7 - WAYSIDE7 115 1 |  | 160 | 0.10431 | 102.09 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 20SP | GEN-2016-159 | 'FROM -> TO' | COLMBUS7 - CRESTON7 115 1 |  | 120 | 0.06066 | 102.07 | P42:345:NPPD:BKR-HOS-3322
Thermal | 08ALL | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | WPAWHSK4 - WESTERNWALL4 138 | 189 |  | 0.24721 | 102.07 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2016-173 | 'FROM -> TO' | MCELROY4 - UNVRSTY4 138 1 |  | 222 | 0.03094 | 102.06 | P12:138:OKGE:BKRBKR204
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07169 | 102.05 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07169 | 102.05 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07169 | 102.05 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 1 | 102.05 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07169 | 102.05 | P55:161-345:KCPL:HAWTHORN_BUS_20_161::
Thermal | 06ALL | 2 | 20G | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.34466 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.34466 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.2542 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.303 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.2578 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.29035 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.26839 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.24091 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.25207 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.2503 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.27174 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.27459 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.37444 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.2503 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.24924 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.27174 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.20221 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.24137 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.25021 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.26502 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 20G | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 7 - CRAWFISH_DR 345 2 |  | 997.3 | 0.2512 | 102 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.20232 | 102 | P22:345:SPRM-AECI:17
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.19958 | 102 | P22:345:SPRM-AECI:17
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.1991 | 102 | P22:345:SPRM-AECI:17
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.20598 | 102 | P22:345:SPRM-AECI:17
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.42046 | 102 | P22:345:SPRM-AECI:17
Thermal | 07NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.05972 | 102 | P22:345:SPRM-AECI:17
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.20232 | 102 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.19958 | 102 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.1991 | 102 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.20598 | 102 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.42046 | 102 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 07NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.05972 | 102 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.20232 | 102 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.19958 | 102 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.1991 | 102 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.20598 | 102 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.42046 | 102 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 07NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 247 | 0.05972 | 102 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 07NR | 2 | 24L | GEN-2016-107 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.20232 | 102 | P12:138:WFEC-AEPW:WAPANUCKA4:STONEWAL L4
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.19958 | 102 | P12:138:WFEC-AEPW:WAPANUCKA4:STONEWAL L4
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.1991 | 102 | P12:138:WFEC-AEPW:WAPANUCKA4:STONEWAL L4
Thermal | 07NR | 2 | 24L | GEN-2017-036 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.20598 | 102 | P12:138:WFEC-AEPW:WAPANUCKA4:STONEWAL L4
Thermal | 07NR | 2 | 24L | GEN-2017-066 | 'FROM -> TO' | TUPELO 4 - STNWLSW4 138 1 |  | 169 | 0.42046 | 102 | P12:138:WFEC-AEPW:WAPANUCKA4:STONEWAL L4
Thermal | 06ALL | 2 | 24SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.26621 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.26621 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.19038 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.15593 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.14482 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-090 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.11346 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-171 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.08221 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.1654 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.1253 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-012 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.12682 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.12629 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.1344 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.12834 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.32833 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.12629 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.17016 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.1344 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.15443 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.17182 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.12597 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.17917 | 101.99 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-104 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 | 559 |  | 0.07053 | 101.99 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03936 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03919 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.05468 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.07912 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03373 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.04274 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.04146 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03006 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.065 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.08082 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.07991 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.08464 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.04138 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.05441 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.07887 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.04138 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.33445 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.05868 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03907 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03103 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03036 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03135 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.0481 | 101.98 | P42:345:NPPD:BKR-HOS-3322
Thermal | 13NR | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 1 | 101.95 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 13NR | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 1 | 101.95 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 13NR | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 1 | 101.95 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 13NR | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 1 | 101.95 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.16391 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.03919 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.05468 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.08051 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.03006 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.065 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.11368 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.11288 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.03078 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.1015 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.07212 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.07887 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.1015 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.29405 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.23783 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.03907 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.04015 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.0481 | 101.94 | P42:345:OKGE:SB_CION7384
Thermal | 08NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.083 | 101.94 | P12:138:AEPW-WFEC:S.W.S.-4:WASHITA4
Thermal | 08NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.083 | 101.94 | P12:138:AEPW-WFEC:S.W.S.-4:WASHITA4
Thermal | 08NR | 2 | 20G | GEN-2017-067 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 234 | 0.07855 | 101.94 | P12:138:AEPW-WFEC:S.W.S.-4:WASHITA4
Thermal | 09NR | 2 | 24L | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07071 | 101.94 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 0.04435 | 101.93 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 1 | 101.93 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | S BROWN4 - BROWN 4 138 1 |  | 143 | 1 | 101.93 | P12:138:OKGE-SWPA-WFEC:BKRBKR250
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.07585 | 101.93 | P42:345:OKGE:SB_CION7382
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.18234 | 101.93 | P42:345:OKGE:SB_CION7382
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | CIMARON7 - CIMARON1 138 1 |  | 478 | 0.11512 | 101.93 | P42:345:OKGE:SB_CION7382
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.03936 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.03919 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.05468 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.07912 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.03373 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.03006 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.065 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.08082 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.07991 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.06107 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.04138 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.05441 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.07887 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.04138 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.33445 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.03907 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.03103 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.03036 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.03135 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | S BROWN4 - RUSSETT4 138 1 |  | 136 | 0.0481 | 101.92 | P12:138:OKGE:BKRBKR261
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.05211 | 101.9 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.04861 | 101.9 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 24WP | GEN-2017-022 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.0807 | 101.9 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 1 | 101.9 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.11509 | 101.9 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 1 | 101.9 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.05536 | 101.9 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.07315 | 101.9 | P13:069-138:WERE:MONT_TX-1_138-69::
Thermal | 00NR | 2 | 24SP | GEN-2016-127 | 'FROM -> TO' | 4REMNGTON - SHIDLER4 138 1 |  | 174 | 0.48017 | 101.89 | P12:138:AEPW:MOUNDRD4:SHIDLER4
Thermal | 00NR | 2 | 24SP | GEN-2016-173 | 'FROM -> TO' | 4REMNGTON - SHIDLER4 138 1 |  | 174 | 0.04012 | 101.89 | P12:138:AEPW:MOUNDRD4:SHIDLER4
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | GILLIAM2 - SUPEROR2 69.0 1 |  | 39 | 0.07912 | 101.87 | P12:69:AEPW:HOSSTON2:VIVIAN2:SUPEROR2 \BREAKER TO BREAKER IS HOSSTON - SUPERIOR
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | GILLIAM2 - SUPEROR2 69.0 1 |  | 39 | 0.08082 | 101.87 | P12:69:AEPW:HOSSTON2:VIVIAN2:SUPEROR2 \BREAKER TO BREAKER IS HOSSTON - SUPERIOR
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | GILLIAM2 - SUPEROR2 69.0 1 |  | 39 | 0.07991 | 101.87 | P12:69:AEPW:HOSSTON2:VIVIAN2:SUPEROR2 \BREAKER TO BREAKER IS HOSSTON - SUPERIOR
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | GILLIAM2 - SUPEROR2 69.0 1 |  | 39 | 0.05441 | 101.87 | P12:69:AEPW:HOSSTON2:VIVIAN2:SUPEROR2 \BREAKER TO BREAKER IS HOSSTON - SUPERIOR
Thermal | 00NR | 2 | 29SP | GEN-2017-057 | 'FROM -> TO' | GILLIAM2 - SUPEROR2 69.0 1 |  | 39 | 0.45784 | 101.87 | P12:69:AEPW:HOSSTON2:VIVIAN2:SUPEROR2 \BREAKER TO BREAKER IS HOSSTON - SUPERIOR
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | GILLIAM2 - SUPEROR2 69.0 1 |  | 39 | 0.33445 | 101.87 | P12:69:AEPW:HOSSTON2:VIVIAN2:SUPEROR2 \BREAKER TO BREAKER IS HOSSTON - SUPERIOR
Thermal | 09ALL | 2 | 24WP | GEN-2016-109 | 'FROM -> TO' | FAIRBRY7 - HARBINE7115 | 99 |  | 0.62734 | 101.86 | System Intact
Thermal | 09ALL | 2 | 24WP | GEN-2017-085 | 'FROM -> TO' | FAIRBRY7 - HARBINE7115 | 99 |  | 0.05435 | 101.86 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07136 | 101.85 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07136 | 101.85 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07136 | 101.85 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 1 | 101.85 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN22 161 22 |  | 605 | 0.07136 | 101.85 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.21712 | 101.85 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.18931 | 101.85 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.06198 | 101.85 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05682 | 101.85 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05367 | 101.85 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.22702 | 101.85 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.22702 | 101.85 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.1759 | 101.85 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.08824 | 101.85 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17246 | 101.85 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17753 | 101.85 | P23:345:AEPW:NW TEXARKANA CB 11830 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.21712 | 101.85 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.18931 | 101.85 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.06198 | 101.85 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05682 | 101.85 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05367 | 101.85 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.22702 | 101.85 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.22702 | 101.85 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.1759 | 101.85 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.08824 | 101.85 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17246 | 101.85 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17753 | 101.85 | P42:345:AEPW:NW TEXARKANA CB 11830 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | GRDA1 5 - GRDAUTO1 161 1 |  | 560 | 0.03838 | 101.83 | P12:161:AECI:CHOTEAU-MAID
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0323 | 101.81 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.17621 | 101.81 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.15681 | 101.81 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.05272 | 101.81 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0681 | 101.81 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.03916 | 101.81 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.18306 | 101.81 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.11888 | 101.81 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.18306 | 101.81 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14753 | 101.81 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.06289 | 101.81 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14511 | 101.81 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14868 | 101.81 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.07711 | 101.81 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0323 | 101.81 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.17621 | 101.81 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.15681 | 101.81 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.05272 | 101.81 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.0681 | 101.81 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.03916 | 101.81 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.18306 | 101.81 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.11888 | 101.81 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.18306 | 101.81 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14753 | 101.81 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.06289 | 101.81 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14511 | 101.81 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.14868 | 101.81 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | NWTXARK7 - WELSH 7 345 1 |  | 1186 | 0.07711 | 101.81 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2016-173 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.056 | 101.79 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 24SP | GEN-2017-022 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06041 | 101.79 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06249 | 101.79 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06249 | 101.79 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06249 | 101.79 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.04868 | 101.79 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05332 | 101.79 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06249 | 101.79 | P12:345:WERE:STRA-IATAN_345_1::
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.2169 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03919 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.05468 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.18122 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03006 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.065 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07247 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06714 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06847 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22973 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07887 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22973 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03907 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16402 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.11476 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.15979 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16605 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.0481 | 101.75 | P23:345:AEPW:VALLIANT CB 3405A NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.2169 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03919 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.05468 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.18122 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03006 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.065 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07247 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06714 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06847 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22973 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07887 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22973 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03907 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16402 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.11476 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.15979 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16605 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.0481 | 101.75 | P42:345:AEPW:VALLIANT CB 3405A NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.03936 | 101.71 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.07912 | 101.71 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.03373 | 101.71 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.08082 | 101.71 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.07991 | 101.71 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.04138 | 101.71 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.05441 | 101.71 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.04138 | 101.71 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.33445 | 101.71 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.03103 | 101.71 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.03036 | 101.71 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.03135 | 101.71 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.03936 | 101.71 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.07912 | 101.71 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.03373 | 101.71 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.08082 | 101.71 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.07991 | 101.71 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.04138 | 101.71 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.05441 | 101.71 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.04138 | 101.71 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.33445 | 101.71 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.03103 | 101.71 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.03036 | 101.71 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.03135 | 101.71 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.07912 | 101.71 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.08082 | 101.71 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.07991 | 101.71 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.05441 | 101.71 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CARTHAG5 - LAR382 5 161 1 |  | 222 | 0.33445 | 101.71 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 09ALL | 2 | 24L | GEN-2016-109 | 'FROM -> TO' | KELLY 3 - GOFF 3 115 1 | 86 |  | 0.04184 | 101.7 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 0.36192 | 101.64 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.64 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.64 | P23:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 0.36192 | 101.64 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.64 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.64 | P42:345:OPPD-MEC:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 0.36192 | 101.64 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.64 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.64 | P43:161-345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 0.36192 | 101.64 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.64 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.64 | P44:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 0.36192 | 101.64 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.64 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.64 | P45:345:OPPD:S3451-RAUN&T4
Thermal | 08ALL | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | BV-COM-4 - MOUNDRD4 138 1 | 131 |  | 0.18253 | 101.63 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 0.36181 | 101.61 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.61 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.61 | P12:345:OPPD-MEC:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 0.36181 | 101.61 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.61 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.61 | P14:345:OPPD-MEC:S3451 REAC-1
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 0.36181 | 101.61 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.61 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.61 | P21:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 0.36181 | 101.61 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.61 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.61 | P22:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 0.36181 | 101.61 | P23:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.61 | P23:345:OPPD:S3451-RAUN
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS3 - SHELCRK3 345 1 |  | 956 | 1 | 101.61 | P23:345:OPPD:S3451-RAUN
Thermal | 08NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.03973 | 101.59 | P12:161:EES-EAI-AEPW:5OSAGE#:EUREKA5
Thermal | 08NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5GRANDVIEW% - EUREKA 5 161 1 |  | 210 | 0.03973 | 101.59 | P12:HV:EES::5OSAGE CRK#!:EUREKA 5:1
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.07585 | 101.59 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.18234 | 101.59 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | CRAIG 7 - CRAIG11 161 11 |  | 605 | 0.11512 | 101.59 | P55:161-345:KCPL:CRAIG_BUS_33_345::
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.03211 | 101.58 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.12829 | 101.58 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.30879 | 101.58 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | SIDNEY__-MB3 - STEGALL_-MB3 345 1 |  | 765 | 0.19494 | 101.58 | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.16391 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.03919 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.05468 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.08051 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.03006 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.065 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.11368 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.11288 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.03078 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.1015 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.07212 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.07887 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.1015 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.29405 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.23783 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.03907 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.04015 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.0481 | 101.56 | P12:345:OKGE:BKRBKR24
Thermal | 09ALL | 2 | 20G | GEN-2016-109 | 'FROM -> TO' | CIRCLVL3 - GOFF 3 115 1 | 86 |  | 0.0459 | 101.56 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03936 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03919 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.05468 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07912 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03373 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03006 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.065 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.08082 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07991 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.15161 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04138 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.05441 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.07887 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04138 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.33445 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03907 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03103 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.04403 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03036 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.03135 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | SPRNDAL4 - DRPSPRG4 138 1 |  | 153 | 0.0481 | 101.55 | P42:345:OKGE:SB_JOCO7313
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0323 | 101.54 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.05272 | 101.54 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0681 | 101.54 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-028 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03022 | 101.54 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.11888 | 101.54 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-067 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03009 | 101.54 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-071 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0319 | 101.54 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-072 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0319 | 101.54 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.07711 | 101.54 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0323 | 101.54 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.05272 | 101.54 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0681 | 101.54 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-028 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03022 | 101.54 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.11888 | 101.54 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-067 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03009 | 101.54 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-071 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0319 | 101.54 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-072 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0319 | 101.54 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.07711 | 101.54 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0323 | 101.53 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.05272 | 101.53 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0681 | 101.53 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-028 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03022 | 101.53 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.11888 | 101.53 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-067 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03009 | 101.53 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-071 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0319 | 101.53 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-072 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0319 | 101.53 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.07711 | 101.53 | P42:500:OKGE:SB_FTTH8581
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0323 | 101.53 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.05272 | 101.53 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0681 | 101.53 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-028 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03022 | 101.53 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.11888 | 101.53 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-067 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.03009 | 101.53 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-071 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0319 | 101.53 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-072 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.0319 | 101.53 | P42:500:OKGE:SB_FTTH8585
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | FTSMITH7 - FTSMITH5 161 5 |  | 478 | 0.07711 | 101.53 | P42:500:OKGE:SB_FTTH8585
Thermal | 08ALL | 2 | 24WP | GEN-2017-005 | 'FROM -> TO' | PUR421 5 - LITCH 5 161 |  | 251 | 0.36775 | 101.52 | P12:161:WERE:NSES-EMDE_161::
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | PHILIP 7 - WALL 7 115 1 |  | 132 | 0.18385 | 101.5 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | PHILIP 7 - WALL 7 115 1 |  | 132 | 0.13766 | 101.5 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | PHILIP 7 - WALL 7 115 1 |  | 132 | 0.20318 | 101.5 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 09ALL | 2 | 24L | GEN-2016-159 | 'FROM -> TO' | DIXONCO - TWIN CH4 230 | 320 |  | 0.07681 | 101.46 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.0323 | 101.42 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2017-011 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03321 | 101.42 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.05272 | 101.42 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.0681 | 101.42 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.11888 | 101.42 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07524 | 101.42 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2017-086 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.03197 | 101.42 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | EVANS N4 - MAIZE 4 138 1 |  | 382 | 0.07711 | 101.42 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.0704 | 101.41 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 1 | 101.41 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 1 | 101.41 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03936 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03919 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05468 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.07912 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03373 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.04146 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03006 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.065 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.08082 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.07991 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.08464 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05757 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.04138 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05441 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05757 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05757 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.49605 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.07887 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.04138 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.33445 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05868 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03907 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03103 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03036 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.03135 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.05757 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | STRANGR7 - 87TH 7 345 2 |  | 1195 | 0.0481 | 101.41 | P23:345:WERE:STRA_345-100::
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05211 | 101.38 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.04861 | 101.38 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.06194 | 101.38 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.0558 | 101.38 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.04086 | 101.38 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 1 | 101.38 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.11509 | 101.38 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.26313 | 101.38 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 1 | 101.38 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05536 | 101.38 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05163 | 101.38 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.07828 | 101.38 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.07315 | 101.38 | P12:345:OKGE:BKRBKR295
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05211 | 101.38 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.04861 | 101.38 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.06194 | 101.38 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.0558 | 101.38 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.04086 | 101.38 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 1 | 101.38 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.11509 | 101.38 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.26313 | 101.38 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 1 | 101.38 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05536 | 101.38 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05163 | 101.38 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.07828 | 101.38 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.07315 | 101.38 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05211 | 101.38 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.04861 | 101.38 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.06194 | 101.38 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.0558 | 101.38 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.04086 | 101.38 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 1 | 101.38 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.11509 | 101.38 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.26313 | 101.38 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 1 | 101.38 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05536 | 101.38 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.05163 | 101.38 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.07828 | 101.38 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 |  | 317 | 0.07315 | 101.38 | P41:345:OKGE:SB_MUGE7385
Thermal | 00NR | 2 | 20SP | GEN-2016-173 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06758 | 101.38 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 20SP | GEN-2017-022 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.07321 | 101.38 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.07021 | 101.38 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.07021 | 101.38 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.07021 | 101.38 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 20SP | GEN-2017-068 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.05879 | 101.38 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 20SP | GEN-2017-086 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.06458 | 101.38 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 1 |  | 1195 | 0.07021 | 101.38 | P12:345:WERE:STRA-IATAN_345_2::FUTURE
Thermal | 00NR | 2 | 20SP | GEN-2017-057 | 'FROM -> TO' | GILLIAM2 - SUPEROR2 69.0 1 |  | 39 | 0.45793 | 101.37 | P12:69:AEPW:HOSSTON2:VIVIAN2:SUPEROR2 \BREAKER TO BREAKER IS HOSSTON - SUPERIOR
Thermal | 00NR | 2 | 24SP | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON1 138 1 |  | 478 | 0.03377 | 101.36 | P13:138-345:OKGE:BKRBKR_3W021
Thermal | 09NR | 2 | 20G | GEN-2016-159 | 'FROM -> TO' | E.COL. 4 - COL.EAST T3 115 1 |  | 187 | 0.03388 | 101.36 | P42:345:NPPD:BKR-CE-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03936 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03919 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.05468 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.07912 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03373 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03006 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.065 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.08082 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.07991 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.04138 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.05441 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.07887 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.04138 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.33445 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03898 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03907 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03103 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03036 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03135 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.0481 | 101.33 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.15168 | 101.32 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.0441 | 101.32 | P42:345:OKGE:SB_JOCO7303
Thermal | 09ALL | 2 | 24SP | GEN-2016-109 | 'FROM -> TO' | FAIRBRY7 - HEBRN N7115 |  | 99 | 1 | 101.32 | P12:115:NPPD:1175B:FAIRBRY7:HARBINE7:BTB
Thermal | 06ALL | 2 | 24SP | GEN-2017-016 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 | 128.1 |  | 1 | 101.31 | System Intact
Thermal | 06ALL | 2 | 24SP | GEN-2017-069 | 'FROM -> TO' | NORTON 3 - PLSNT_HILL 3 115 1 | 128.1 |  | 1 | 101.31 | System Intact
Thermal | 09ALL | 2 | 29SP | GEN-2016-109 | 'FROM -> TO' | FAIRBRY7 - HEBRN N7115 |  | 99 | 1 | 101.31 | P12:115:NPPD:1175B:FAIRBRY7:HARBINE7:BTB
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.2169 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03919 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.05468 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.18123 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03006 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.065 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07554 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06986 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06863 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22972 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07887 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22972 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03907 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16404 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.11482 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1598 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16607 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.0481 | 101.28 | P12:345:AEPW:VALIANT7:NWTXARK7
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07912 | 101.24 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.08082 | 101.24 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07991 | 101.24 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05441 | 101.24 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.33445 | 101.24 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04506 | 101.24 | P22:345:SPRM-AECI:17
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07912 | 101.24 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.08082 | 101.24 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07991 | 101.24 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05441 | 101.24 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.33445 | 101.24 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.04506 | 101.24 | P42:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07912 | 101.24 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.08082 | 101.24 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.07991 | 101.24 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.05441 | 101.24 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.33445 | 101.24 | P52:345:SPRM-AECI:STUCK BKR SIM17
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.04056 | 101.24 | P42:345:NPPD:BKR-SC-3306
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 | 956 | 956 |  | 101.22 | System Intact
Thermal | 06NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 | 956 |  | 0.0814 | 101.22 | System Intact
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 | 956 |  | 0.09499 | 101.22 | System Intact
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 | 956 |  | 0.09499 | 101.22 | System Intact
Thermal | 06NR | 2 | 24L | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 | 956 |  | 0.05252 | 101.22 | System Intact
Thermal | 06NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 | 956 |  | 0.04546 | 101.22 | System Intact
Thermal | 06NR | 2 | 24L | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - SEMINOL7 345 1 | 956 |  | 0.05324 | 101.22 | System Intact
Thermal | 12NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04946 | 101.22 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 12NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 101.22 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 12NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 101.22 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 12NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04946 | 101.22 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 12NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 101.22 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 12NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 101.22 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 00NR | 2 | 24SP | GEN-2016-090 | 'FROM -> TO' | GAINES 3 - OXY_WSEM_TP3 115 1 |  | 119.5 | 0.04272 | 101.2 | P12:115:SPS:W33.1.JNSDRW.HIGG
Thermal | 14ALL | 2 | 20G | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.41419 | 101.17 | P42:345:OKGE:SB_JOCO7303
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.1965 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2016-127 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.16557 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.05211 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.04861 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.06462 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.05979 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.06217 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.04086 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.20761 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 1 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.11509 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.20761 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.26313 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 1 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-074 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.15067 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.10231 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-076 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.14701 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-077 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.15243 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.07828 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | NWTXARK7 - VALIANT7 345 1 |  | 1416 | 0.07315 | 101.15 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 09ALL | 2 | 24L | GEN-2017-001 | 'FROM -> TO' | MOORE 3 - MONOLITH 3 345 |  | 956 | 0.21643 | 101.15 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001
Thermal | 09ALL | 2 | 24L | GEN-2017-006 | 'FROM -> TO' | MOORE 3 - MONOLITH 3 345 |  | 956 | 0.37753 | 101.15 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001
Thermal | 09ALL | 2 | 24L | GEN-2017-008 | 'FROM -> TO' | MOORE 3 - MONOLITH 3 345 |  | 956 | 0.30658 | 101.15 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.03936 | 101.11 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.03373 | 101.11 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.04138 | 101.11 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.04138 | 101.11 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.04236 | 101.11 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.03103 | 101.11 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.03036 | 101.11 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.03135 | 101.11 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.03936 | 101.11 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.03373 | 101.11 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.04138 | 101.11 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.04138 | 101.11 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.04236 | 101.11 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.03103 | 101.11 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.03036 | 101.11 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | NAPLSTP4 - PAYNESW4 138 1 |  | 169 | 0.03135 | 101.11 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 13NR | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 1 | 101.11 | System Intact
Thermal | 13NR | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 1 | 101.11 | System Intact
Thermal | 13NR | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 1 | 101.11 | System Intact
Thermal | 13NR | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | NEOSHO 5 - RIV4525 161 1 | 205 |  | 1 | 101.11 | System Intact
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.16345 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2016-107 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.08049 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.05211 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-011 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.0321 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.04861 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.11371 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.11291 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.0345 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.04086 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.10104 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-036 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.07214 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 1 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.11509 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.10104 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-066 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.29408 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-067 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.24155 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.26313 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 1 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.04387 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.07828 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.07315 | 101.1 | P42:345:OKGE:SB_CION7384
Thermal | 07ALL | 2 | 24L | GEN-2017-053 | 'FROM -> TO' | GEROJCT2 - ESQNDLJ2 69 | 58 | 68 | 0.29882 | 101.1 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 07ALL | 2 | 20SP | GEN-2017-053 | 'FROM -> TO' | GEROJCT2 - GRANFLD2 69 | 58 | 68 | 0.33206 | 101.1 | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4
Thermal | 09ALL | 2 | 19WP | GEN-2016-109 | 'FROM -> TO' | FAIRBRY7 - HEBRN N7115 |  | 99 | 1 | 101.09 | P12:115:NPPD:1175B:FAIRBRY7:HARBINE7:BTB
Thermal | 13NR | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 1 | 101.09 | P42:345:NPPD:BKR-KEY-3310
Thermal | 13NR | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 1 | 101.09 | P42:345:NPPD:BKR-KEY-3310
Thermal | 13NR | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 1 | 101.09 | P42:345:NPPD:BKR-KEY-3310
Thermal | 13NR | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 1 | 101.09 | P42:345:NPPD:BKR-KEY-3310
Thermal | 14NR | 2 | 20G | GEN-2017-023 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.03675 | 101.09 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 14NR | 2 | 20G | GEN-2017-024 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.03489 | 101.09 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 14NR | 2 | 20G | GEN-2017-027 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.06091 | 101.09 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 14NR | 2 | 20G | GEN-2017-075 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.04013 | 101.09 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 07ALL | 2 | 29SP | GEN-2017-053 | 'FROM -> TO' | GEROJCT2 - GRANFLD2 69 | 58 | 68 | 0.33085 | 101.08 | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4
Thermal | 09ALL | 2 | 24WP | GEN-2016-109 | 'FROM -> TO' | FAIRBRY7 - HEBRN N7115 |  | 99 | 1 | 101.08 | P12:115:NPPD:1175B:FAIRBRY7:HARBINE7:BTB
Thermal | 00NR | 2 | 24WP | GEN-2016-159 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 0.04227 | 101.07 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 1 | 101.07 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | ALBION 7 - PETRSBG7 115 1 |  | 137 | 1 | 101.07 | P42:345:NPPD:BKR-SC-3306
Thermal | 09ALL | 2 | 24L | GEN-2016-109 | 'FROM -> TO' | FAIRBRY7 - HEBRN N7115 |  | 99 | 1 | 101.05 | P12:115:NPPD:1175B:FAIRBRY7:HARBINE7:BTB
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03352 | 101.04 | P23:345:GRDA:CLEVLND CB10180
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03487 | 101.04 | P23:345:GRDA:CLEVLND CB10180
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03352 | 101.04 | P43:345:GRDA:CLEVLND CB10180
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.03487 | 101.04 | P43:345:GRDA:CLEVLND CB10180
Thermal | 09ALL | 2 | 20SP | GEN-2016-109 | 'FROM -> TO' | FAIRBRY7 - HEBRN N7115 |  | 99 | 1 | 101.03 | P12:115:NPPD:1175B:FAIRBRY7:HARBINE7:BTB
Thermal | 14ALL | 2 | 20G | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.52924 | 101.03 | P12:138:OKGE:BKRBKR258_1
Thermal | 03NR | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.035 | 100.96 | System Intact
Thermal | 03NR | 2 | 24L | GEN-2017-032 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.31219 | 100.96 | System Intact
Thermal | 03NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.21826 | 100.96 | System Intact
Thermal | 03NR | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.04566 | 100.96 | System Intact
Thermal | 03NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | POTTER_CO 6 - WAUK 90343-A 230 1 | 516 |  | 0.23075 | 100.96 | System Intact
Thermal | 14ALL | 2 | 19WP | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.30174 | 100.93 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 14ALL | 2 | 19WP | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.2822 | 100.93 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 14ALL | 2 | 19WP | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.30174 | 100.93 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 14ALL | 2 | 19WP | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 |  | 287 | 0.2822 | 100.93 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.03364 | 100.91 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 20SP | GEN-2017-036 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.0373 | 100.91 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.03364 | 100.91 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 20SP | GEN-2017-066 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.0539 | 100.91 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.03364 | 100.91 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 20SP | GEN-2017-036 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.0373 | 100.91 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.03364 | 100.91 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 20SP | GEN-2017-066 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 |  | 187 | 0.0539 | 100.91 | P12:345:OKGE-AEPW:BKRBKR25
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.21582 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03919 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.05468 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.18027 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03006 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.065 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07522 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06957 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06843 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22861 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07887 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22861 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03907 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16312 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.11449 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1589 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16515 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.0481 | 100.9 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.21582 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03919 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.05468 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.18027 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03006 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.065 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07522 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06957 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.06843 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22861 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.07887 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.22861 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.03907 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16312 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.11449 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.1589 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.16515 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | LYDIA 7 - VALIANT7 345 1 |  | 1176 | 0.0481 | 100.9 | P42:345:AEPW:NW TEXARKANA CB 16780 NBTB+FAULT
Thermal | 00NR | 2 | 24WP | GEN-2016-037 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.16345 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2016-107 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.08049 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-004 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.05211 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-011 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.0321 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-014 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.04861 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-023 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.11371 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-024 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.11291 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.0345 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-032 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.04086 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-033 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.10104 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-036 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.07214 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-055 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 1 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-064 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.11509 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-065 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.10104 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-066 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.29408 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-067 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.24155 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-068 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.26313 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 1 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-075 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.04387 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-086 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.07828 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 00NR | 2 | 24WP | GEN-2017-097 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 |  | 412 | 0.07315 | 100.84 | P12:345:OKGE:BKRBKR24
Thermal | 10NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.037 | 100.84 | P12:345:OKGE:BKRBKR295
Thermal | 10NR | 2 | 24L | GEN-2017-076 | 'FROM -> TO' | 5OSAGE CRK#! - EUREKA 5 161 1 |  | 220 | 0.037 | 100.84 | P41:345:OKGE:SB_MUGE7385
Thermal | 17ALL | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | SIDNEY___TS4 - SIDNEY__-MB4 230 |  | 478 | 0.28718 | 100.83 | P12:345:UMZ:# 5863 #: IN . PROPER N-1 (LINE) FOR 659133-659425-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | PECANCK7 - PECANCK1 161 1 |  | 370 | 0.03936 | 100.82 | P42:345:OKGE:SB_PECK7382
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | PECANCK7 - PECANCK1 161 1 |  | 370 | 0.03373 | 100.82 | P42:345:OKGE:SB_PECK7382
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | PECANCK7 - PECANCK1 161 1 |  | 370 | 0.04138 | 100.82 | P42:345:OKGE:SB_PECK7382
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | PECANCK7 - PECANCK1 161 1 |  | 370 | 0.04138 | 100.82 | P42:345:OKGE:SB_PECK7382
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | PECANCK7 - PECANCK1 161 1 |  | 370 | 0.03103 | 100.82 | P42:345:OKGE:SB_PECK7382
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | PECANCK7 - PECANCK1 161 1 |  | 370 | 0.03036 | 100.82 | P42:345:OKGE:SB_PECK7382
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | PECANCK7 - PECANCK1 161 1 |  | 370 | 0.03135 | 100.82 | P42:345:OKGE:SB_PECK7382
Thermal | 17NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.18843 | 100.81 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 17NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.14289 | 100.81 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 17NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | NUNDRWD7 - WICKSVL7 115 1 |  | 132 | 0.2077 | 100.81 | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | NORTWST7 - MATHWSN7 345 1 |  | 1195 | 0.15781 | 100.8 | P42:345:OKGE:SB_CION7383
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | NORTWST7 - MATHWSN7 345 1 |  | 1195 | 0.14104 | 100.8 | P42:345:OKGE:SB_CION7383
Thermal | 07NR | 2 | 24L | GEN-2017-057 | 'FROM -> TO' | NORTWST7 - MATHWSN7 345 1 |  | 1195 | 0.03104 | 100.8 | P42:345:OKGE:SB_CION7383
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | NORTWST7 - MATHWSN7 345 1 |  | 1195 | 0.14104 | 100.8 | P42:345:OKGE:SB_CION7383
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | COLMBUS7 - CRESTON7 115 1 |  | 120 | 0.08201 | 100.79 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.21586 | 100.76 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.18835 | 100.76 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.06161 | 100.76 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05648 | 100.76 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05311 | 100.76 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.22565 | 100.76 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.22565 | 100.76 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17507 | 100.76 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.08727 | 100.76 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17167 | 100.76 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 00NR | 2 | 20SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17669 | 100.76 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB
Thermal | 08ALL | 2 | 20G | GEN-2017-005 | 'FROM -> TO' | LITCH 5 - FRANKLIN5 161 |  | 251 | 0.3807 | 100.73 | P12:161:WERE:NSES-EMDE_161::
Thermal | 00NR | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07136 | 100.69 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07136 | 100.69 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07136 | 100.69 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24WP | GEN-2017-073 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 1 | 100.69 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 00NR | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | HAWTH 7 - HAWTHORN22 161 22 |  | 605 | 0.07136 | 100.69 | P55:161-345:KCPL:HAWTHORN_BUS_25::
Thermal | 14ALL | 2 | 19WP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.34753 | 100.69 | P12:138:OKGE:BKRBKR257
Thermal | 09NR | 2 | 20G | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.18643 | 100.68 | P42:345:NPPD:BKR-HOS-3322
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.0324 | 100.67 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 24SP | GEN-2017-001 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.05281 | 100.67 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 20SP | GEN-2017-028 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03517 | 100.65 | P12:138:OKGE:BKRBKR131
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | S.W.S.-4 - NORGE--4 138 1 |  | 136 | 0.03936 | 100.65 | P12:138:AEPW:CORNVIL4:S.W.S.-4
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | S.W.S.-4 - NORGE--4 138 1 |  | 136 | 0.03373 | 100.65 | P12:138:AEPW:CORNVIL4:S.W.S.-4
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | S.W.S.-4 - NORGE--4 138 1 |  | 136 | 0.04138 | 100.65 | P12:138:AEPW:CORNVIL4:S.W.S.-4
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | S.W.S.-4 - NORGE--4 138 1 |  | 136 | 0.04138 | 100.65 | P12:138:AEPW:CORNVIL4:S.W.S.-4
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | S.W.S.-4 - NORGE--4 138 1 |  | 136 | 0.06442 | 100.65 | P12:138:AEPW:CORNVIL4:S.W.S.-4
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | S.W.S.-4 - NORGE--4 138 1 |  | 136 | 0.03103 | 100.65 | P12:138:AEPW:CORNVIL4:S.W.S.-4
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | S.W.S.-4 - NORGE--4 138 1 |  | 136 | 0.03036 | 100.65 | P12:138:AEPW:CORNVIL4:S.W.S.-4
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | S.W.S.-4 - NORGE--4 138 1 |  | 136 | 0.03135 | 100.65 | P12:138:AEPW:CORNVIL4:S.W.S.-4
Thermal | 08ALL | 2 | 24L | GEN-2017-061 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 | 247 |  | 0.03363 | 100.63 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-073 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 | 247 |  | 0.03512 | 100.63 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-074 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 | 247 |  | 0.03972 | 100.63 | System Intact
Thermal | 08ALL | 2 | 24L | GEN-2017-077 | 'FROM -> TO' | BEAVER 5 - EUREKA 5 161 | 247 |  | 0.03722 | 100.63 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.03936 | 100.61 | P13:069-138:WERE:LIBE_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.07912 | 100.61 | P13:069-138:WERE:LIBE_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.03373 | 100.61 | P13:069-138:WERE:LIBE_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-022 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.03499 | 100.61 | P13:069-138:WERE:LIBE_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.08082 | 100.61 | P13:069-138:WERE:LIBE_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.07991 | 100.61 | P13:069-138:WERE:LIBE_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.04138 | 100.61 | P13:069-138:WERE:LIBE_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.05441 | 100.61 | P13:069-138:WERE:LIBE_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.04138 | 100.61 | P13:069-138:WERE:LIBE_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.33445 | 100.61 | P13:069-138:WERE:LIBE_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.03103 | 100.61 | P13:069-138:WERE:LIBE_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.03036 | 100.61 | P13:069-138:WERE:LIBE_TX-1_138-69::
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | ALTOO E2 - NEODJCT2 69.0 1 |  | 36 | 0.03135 | 100.61 | P13:069-138:WERE:LIBE_TX-1_138-69::
Thermal | 07ALL | 2 | 20SP | GEN-2017-036 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 | 145 | 169 | 0.04048 | 100.59 | System Intact
Thermal | 07ALL | 2 | 20SP | GEN-2017-051 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 | 145 | 169 | 0.03541 | 100.59 | System Intact
Thermal | 07ALL | 2 | 20SP | GEN-2017-053 | 'FROM -> TO' | NAPLSTP4 - CORN TP4 138 1 | 145 | 169 | 0.03644 | 100.59 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2016-159 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.03237 | 100.57 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 24SP | GEN-2017-001 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.05276 | 100.57 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 15NR | 2 | 20G | GEN-2017-014 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.07585 | 100.56 | P42:345:NPPD:BKR-CE-3306
Thermal | 15NR | 2 | 20G | GEN-2017-064 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.18234 | 100.56 | P42:345:NPPD:BKR-CE-3306
Thermal | 15NR | 2 | 20G | GEN-2017-097 | 'FROM -> TO' | COLMB.E7 - COL.EAST T3 115 1 |  | 187 | 0.11512 | 100.56 | P42:345:NPPD:BKR-CE-3306
Thermal | 09ALL | 2 | 19WP | GEN-2016-109 | 'FROM -> TO' | FAIRBRY7 - HARBINE7115 | 99 |  | 0.62293 | 100.55 | System Intact
Thermal | 09ALL | 2 | 19WP | GEN-2017-085 | 'FROM -> TO' | FAIRBRY7 - HARBINE7115 | 99 |  | 0.04926 | 100.55 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2016-173 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05486 | 100.53 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 24SP | GEN-2017-022 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05914 | 100.53 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06226 | 100.53 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06226 | 100.53 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06226 | 100.53 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.04766 | 100.53 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 24SP | GEN-2017-086 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.05223 | 100.53 | P23:345:WERE:STRA_345-98::
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - IATAN 7 345 2 |  | 1195 | 0.06226 | 100.53 | P23:345:WERE:STRA_345-98::
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | E_CLOVIS 3 - CURRY 3 115 1 |  | 123.1 | 0.36925 | 100.53 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | E_CLOVIS 3 - CURRY 3 115 1 |  | 123.1 | 0.36925 | 100.53 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | E_CLOVIS 3 - CURRY 3 115 1 |  | 123.1 | 0.28232 | 100.53 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04476 | 100.53 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.28231 | 100.53 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.26275 | 100.53 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05262 | 100.53 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05262 | 100.53 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04476 | 100.53 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-023 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.28231 | 100.53 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-024 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.26275 | 100.53 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05262 | 100.53 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05262 | 100.53 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 00NR | 2 | 20SP | GEN-2017-028 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03714 | 100.5 | P12:138:OKGE:BKRBKR130
Thermal | 00NR | 2 | 24SP | GEN-2017-094 | 'FROM -> TO' | WATERTN4 - APPLEDORN 4 230 1 |  | 352 | 0.03616 | 100.5 | P12:230:UMZW:# 137 #: GF IN MN. GF-FB LINE FAULT
Thermal | 00NR | 2 | 24SP | GEN-2017-071 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.09624 | 100.47 | P43:345:GRDA:CLEVLND CB13380
Thermal | 00NR | 2 | 24SP | GEN-2017-072 | 'FROM -> TO' | KINZEGR4 - KINZE 4 138 1 |  | 287 | 0.09624 | 100.47 | P43:345:GRDA:CLEVLND CB13380
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03936 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03016 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.07912 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03373 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03006 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.065 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.08082 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.07991 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.04138 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.05441 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.07887 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.04138 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.33445 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03907 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03103 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03036 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.03135 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | JOHNSON_DRW3 - HIGG 3 115 1 |  | 105.6 | 0.0481 | 100.46 | P12:115:SPS:W14.1.SMINLE.GAINES
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.03936 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.03919 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.05468 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.07912 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.03373 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.04146 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.03006 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.065 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.08082 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.07991 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.08464 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.05674 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.04138 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.05441 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.05674 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.05674 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-055 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.49605 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.07887 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.04138 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.33445 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.05868 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.03907 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.03103 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.03036 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.03135 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.05674 | 100.45 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HAWTHN5 - HAWTHORN20 161 20 | 500 |  | 0.0481 | 100.45 | System Intact
Thermal | 01ALL | 2 | 20SP | GEN-2016-107 | 'FROM -> TO' | OKEENE 4 - G16-107-TAP 138 | 160 |  | 0.56412 | 100.45 | System Intact
Thermal | 01NR | 2 | 24L | GEN-2017-027 | 'FROM -> TO' | MUSKOGE5 - THRERVR5 161 1 |  | 223 | 0.02244 | 100.45 | P12:161:OKGE:BKRBKR292
Thermal | 01NR | 2 | 24L | GEN-2017-067 | 'FROM -> TO' | MUSKOGE5 - THRERVR5 161 1 |  | 223 | 0.022 | 100.45 | P12:161:OKGE:BKRBKR292
Thermal | 01NR | 2 | 24L | GEN-2017-071 | 'FROM -> TO' | MUSKOGE5 - THRERVR5 161 1 |  | 223 | 0.04334 | 100.45 | P12:161:OKGE:BKRBKR292
Thermal | 01NR | 2 | 24L | GEN-2017-072 | 'FROM -> TO' | MUSKOGE5 - THRERVR5 161 1 |  | 223 | 0.04334 | 100.45 | P12:161:OKGE:BKRBKR292
Thermal | 01NR | 2 | 24L | GEN-2017-075 | 'FROM -> TO' | MUSKOGE5 - THRERVR5 161 1 |  | 223 | 0.02012 | 100.45 | P12:161:OKGE:BKRBKR292
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03936 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03919 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.05468 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.07912 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03373 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.21106 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.04146 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03006 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.065 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.08082 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.07991 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.08464 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.04138 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.05441 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.07887 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.04138 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.33445 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.05868 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03907 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03103 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03036 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.03135 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | HOSKINS3 - HOSKN T4 115 1 |  | 336 | 0.0481 | 100.42 | P42:345:NPPD:BKR-HOS-3308
Thermal | 06ALL | 2 | 29SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.32728 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.32728 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.25224 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20769 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22866 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23199 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.21231 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.21218 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23556 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.22021 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.39042 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.21218 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23858 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23556 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2017-081 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.20648 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.23603 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.21177 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 06ALL | 2 | 29SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 7 345/230XFR 1 |  | 643 | 0.25107 | 100.42 | P12:345:SPS:J15.1.XRDS.TOLK
Thermal | 09ALL | 2 | 24L | GEN-2016-109 | 'FROM -> TO' | CIRCLVL3 - GOFF 3 115 1 | 86 |  | 0.04184 | 100.39 | System Intact
Thermal | 07ALL | 2 | 20G | GEN-2017-053 | 'FROM -> TO' | GEROJCT2 - ESQNDLJ2 69 | 58 | 68 | 0.33202 | 100.38 | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4
Thermal | 06ALL | 2 | 20G | GEN-2017-016 | 'FROM -> TO' | E_CLOVIS 3 - CURRY 3 115 1 |  | 123.1 | 0.36653 | 100.37 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-069 | 'FROM -> TO' | E_CLOVIS 3 - CURRY 3 115 1 |  | 123.1 | 0.36653 | 100.37 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 06ALL | 2 | 20G | GEN-2017-087 | 'FROM -> TO' | E_CLOVIS 3 - CURRY 3 115 1 |  | 123.1 | 0.27965 | 100.37 | P12:115:SPS:W65.1.PLSTHL.CURRY
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03936 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03919 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.05468 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.07912 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03373 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03006 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.065 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.08082 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.07991 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03247 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.04138 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.05441 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.07887 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.04138 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.33445 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03907 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03103 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03036 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.03135 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | MUSTANG4 - SW 5TH 4 138 1 |  | 287 | 0.0481 | 100.36 | P12:138:OKGE:BKRBKR134
Thermal | 00NR | 2 | 20SP | GEN-2017-014 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.72608 | 100.34 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-064 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.36882 | 100.34 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 20SP | GEN-2017-097 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.39529 | 100.34 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 19WP | GEN-2017-011 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03342 | 100.33 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.05272 | 100.33 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.03504 | 100.33 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.11888 | 100.33 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2017-068 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.15106 | 100.33 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2017-086 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.06821 | 100.33 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | WICHITA7 - WICH TX-12 138 1 |  | 430 | 0.07711 | 100.33 | P23:345:WERE:WICH_345-50::
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.0323 | 100.32 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.06954 | 100.32 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-107 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.09841 | 100.32 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.05272 | 100.32 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.0681 | 100.32 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-023 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.09421 | 100.32 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-024 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.09269 | 100.32 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.03053 | 100.32 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.11888 | 100.32 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.03053 | 100.32 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-066 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.18829 | 100.32 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-067 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.07159 | 100.32 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | GRACMNT4 - ANADARK4 138 1 | 283 |  | 0.07711 | 100.32 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.14009 | 100.32 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-107 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.23982 | 100.32 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.1213 | 100.32 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.13864 | 100.32 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.24333 | 100.32 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.13864 | 100.32 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-066 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.24511 | 100.32 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.10749 | 100.32 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.10427 | 100.32 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.10865 | 100.32 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 00NR | 2 | 19WP | GEN-2016-037 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.14009 | 100.32 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-107 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.23982 | 100.32 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2016-127 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.1213 | 100.32 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-033 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.13864 | 100.32 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-036 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.24333 | 100.32 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-065 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.13864 | 100.32 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-066 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.24511 | 100.32 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-074 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.10749 | 100.32 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-076 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.10427 | 100.32 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 00NR | 2 | 19WP | GEN-2017-077 | 'FROM -> TO' | PITTSB-7 - VALIANT7 345 2 |  | 1143 | 0.10865 | 100.32 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 14ALL | 2 | 24WP | GEN-2017-027 | 'FROM -> TO' | CARTER 4 - CHIKSAW4 138 |  | 191 | 0.34761 | 100.29 | P12:138:OKGE:BKRBKR257
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.03919 | 100.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.05468 | 100.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.07912 | 100.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.04146 | 100.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.72256 | 100.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.065 | 100.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.08082 | 100.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.07991 | 100.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.08464 | 100.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.05441 | 100.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.36479 | 100.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.33445 | 100.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.05868 | 100.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.03907 | 100.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.39158 | 100.28 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 14NR | 2 | 20G | GEN-2017-023 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.03675 | 100.21 | P42:345:NPPD:BKR-KEY-3310
Thermal | 14NR | 2 | 20G | GEN-2017-024 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.03489 | 100.21 | P42:345:NPPD:BKR-KEY-3310
Thermal | 14NR | 2 | 20G | GEN-2017-027 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.06091 | 100.21 | P42:345:NPPD:BKR-KEY-3310
Thermal | 14NR | 2 | 20G | GEN-2017-075 | 'FROM -> TO' | OGALALA4 - SIDNEY___TS4 230 1 |  | 320 | 0.04013 | 100.21 | P42:345:NPPD:BKR-KEY-3310
Thermal | 00NR | 2 | 20SP | GEN-2016-037 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.21596 | 100.2 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 20SP | GEN-2016-127 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.18843 | 100.2 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 20SP | GEN-2017-023 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.06165 | 100.2 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 20SP | GEN-2017-024 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05651 | 100.2 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 20SP | GEN-2017-027 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.05315 | 100.2 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 20SP | GEN-2017-033 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.22576 | 100.2 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 20SP | GEN-2017-065 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.22576 | 100.2 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 20SP | GEN-2017-074 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17515 | 100.2 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 20SP | GEN-2017-075 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.08733 | 100.2 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 20SP | GEN-2017-076 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17174 | 100.2 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 20SP | GEN-2017-077 | 'FROM -> TO' | LYDIA 7 - WELSH 7 345 1 |  | 1059 | 0.17676 | 100.2 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 00NR | 2 | 24SP | GEN-2017-067 | 'FROM -> TO' | CIMARON4 - CIMARON2 138 1 |  | 478 | 0.03908 | 100.19 | P42:345:OKGE:SB_CION7381
Thermal | 00NR | 2 | 24SP | GEN-2017-030 | 'FROM -> TO' | SIBLEY 5 - SIBLEY11 161 11 |  | 440 | 0.032 | 100.16 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 00NR | 2 | 24SP | GEN-2017-038 | 'FROM -> TO' | SIBLEY 5 - SIBLEY11 161 11 |  | 440 | 0.032 | 100.16 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 00NR | 2 | 24SP | GEN-2017-041 | 'FROM -> TO' | SIBLEY 5 - SIBLEY11 161 11 |  | 440 | 0.032 | 100.16 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 00NR | 2 | 24SP | GEN-2017-095 | 'FROM -> TO' | SIBLEY 5 - SIBLEY11 161 11 |  | 440 | 0.032 | 100.16 | P23:161-345:KCPL:HAWTHORN_R20-22::HAWT20-HAWT22
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.03936 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.03919 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.05468 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.07912 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.03373 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.04168 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-001 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.06209 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.04146 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.03006 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.065 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.08082 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.07991 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.08464 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.04138 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.05441 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.07887 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.04138 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.33445 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.05868 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.03907 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.03103 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.03036 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.03135 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T2 115 1 |  | 316 | 0.0481 | 100.15 | P13:115-230:NPPD:GR ISLD4:T5
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.0323 | 100.13 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07183 | 100.13 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05272 | 100.13 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.0681 | 100.13 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07364 | 100.13 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03837 | 100.13 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.11888 | 100.13 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.05516 | 100.13 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.07711 | 100.13 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | HOSKINS4 - HOSKINS T1 115 1 |  | 187 | 0.03929 | 100.13 | P42:345:NPPD:BKR-HOS-3312
Thermal | 00NR | 2 | 19WP | GEN-2016-103 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.07768 | 100.1 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.07852 | 100.1 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-048 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.10856 | 100.1 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.07919 | 100.1 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-094 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.09189 | 100.1 | System Intact
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | SIOUXCY2 - SIOUXCY4 230 Z | 341 |  | 0.08082 | 100.1 | System Intact
Thermal | 00NR | 2 | 24SP | GEN-2017-027 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.20371 | 100.09 | P42:345:OKGE:SB_SUSD7383
Thermal | 00NR | 2 | 24SP | GEN-2017-075 | 'FROM -> TO' | RUSSET-4 - STIRLNG4 138 1 |  | 153 | 0.04589 | 100.09 | P42:345:OKGE:SB_SUSD7383
Thermal | 06ALL | 2 | 24L | ASGI-2016-001 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.0468 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | ASGI-2017-007 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.0468 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-039 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.03724 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-077 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.05723 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-078 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.09808 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-090 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.05708 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-171 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.05532 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2016-172 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.05511 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-007 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.09579 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-016 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.10237 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-026 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.08701 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-039 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.08238 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-059 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.0378 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-069 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.10237 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-078 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.04036 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-079 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.05953 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-080 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.08701 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-084 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.03409 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-087 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.10154 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-091 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.0679 | 100.07 | System Intact
Thermal | 06ALL | 2 | 24L | GEN-2017-104 | 'FROM -> TO' | POTTER_CO 6 - BUSHLAND 6 230 1 | 318.7 |  | 0.0539 | 100.07 | System Intact
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03936 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03919 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.05468 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.07912 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03373 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.04159 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.04146 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03006 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.065 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.08082 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.07991 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.08464 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.04138 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.05441 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.07887 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.04138 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.33445 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.05868 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03907 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03103 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03036 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.03135 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | PETRSBG7 - PETERSBRG.N7 115 Z1 |  | 137 | 0.0481 | 100.06 | P42:345:NPPD:BKR-SC-3306
Thermal | 06ALL | 2 | 20SP | ASGI-2016-001 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.28675 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | ASGI-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.28675 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.21975 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-078 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20746 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2016-172 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20384 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-007 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20123 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-016 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.2002 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-026 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.21389 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-039 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20252 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-059 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.33582 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-069 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.2002 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-079 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20997 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-080 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.21389 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-084 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20647 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-087 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.20012 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 06ALL | 2 | 20SP | GEN-2017-091 | 'FROM -> TO' | TUCO_INT 6 - SIEM 8743066 230 2 |  | 643 | 0.22157 | 100.06 | P42:345:SPS:CROSSROADS_6R30_19L
Thermal | 00NR | 2 | 19WP | GEN-2016-005 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.0323 | 100.05 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 19WP | GEN-2016-159 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.03789 | 100.05 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 19WP | GEN-2017-014 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.15509 | 100.05 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 19WP | GEN-2017-018 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.0681 | 100.05 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 19WP | GEN-2017-032 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.07364 | 100.05 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 19WP | GEN-2017-047 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.03837 | 100.05 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 19WP | GEN-2017-064 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.41286 | 100.05 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 19WP | GEN-2017-075 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.05516 | 100.05 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 19WP | GEN-2017-097 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.25033 | 100.05 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 19WP | GEN-2017-100 | 'FROM -> TO' | G17-064-TAP - 640404 WAYSIDE4 230 1 |  | 341 | 0.03929 | 100.05 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.03936 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.03919 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.05468 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.07912 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.03373 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2016-159 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.04164 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-001 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.06203 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-011 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.04146 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.03006 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.065 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.08082 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.07991 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-028 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.08464 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.04138 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.05441 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.07887 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.04138 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.33445 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-067 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.05868 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.03907 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.03103 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.03036 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.03135 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | GR ISLD4 - GRAND.ISD T5 115 2 |  | 316 | 0.0481 | 100.05 | P13:115-230:NPPD:GR ISLD4:T2
Thermal | 07ALL | 2 | 20SP | GEN-2017-036 | 'FROM -> TO' | ANADARK4 - CHERRYRD 4 138 | 145 | 169 | 0.56998 | 100.05 | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4
Thermal | 07ALL | 2 | 20SP | GEN-2017-053 | 'FROM -> TO' | ANADARK4 - CHERRYRD 4 138 | 145 | 169 | 0.46256 | 100.05 | P12:138:WFEC-AEPW:SNYDER4:SNYDER-4
Thermal | 00NR | 2 | 24SP | GEN-2017-068 | 'FROM -> TO' | EVANS N4 - WICH TX-11 138 1 |  | 430 | 0.09552 | 100.03 | P23:345:WERE:WICH_345-80::
Thermal | 00NR | 2 | 24SP | GEN-2017-014 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.7235 | 100.02 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-064 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.36573 | 100.02 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 24SP | GEN-2017-097 | 'FROM -> TO' | G17-014-TAP - PHILIP_T-BE4 230 1 |  | 342 | 0.39252 | 100.02 | P12:230:UMZ:# 5866 #: IN . PROPER N-1 (LINE) FOR 652573-652873-Z
Thermal | 00NR | 2 | 29SP | GEN-2016-037 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03936 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2016-077 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03919 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2016-090 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.05468 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2016-107 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.07912 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2016-127 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03373 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2017-014 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03006 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2017-018 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.065 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2017-023 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.08082 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2017-024 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.07991 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2017-033 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.04138 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2017-036 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.05441 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2017-064 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.07887 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2017-065 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.04138 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2017-066 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.33445 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2017-068 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03907 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2017-074 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03103 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2017-076 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03036 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2017-077 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.03135 | 100 | P43:345-500:OKGE:SB_FTTH8584
Thermal | 00NR | 2 | 29SP | GEN-2017-097 | 'FROM -> TO' | FTSMTHW5 - FTSMITH5 161 5 |  | 478 | 0.0481 | 100 | P43:345-500:OKGE:SB_FTTH8584
Non-Converge | 00NR | 0 | 19WP | GEN-2017-076 | '' | Non-Converge |  |  | 0.04921 |  | P12:161:SWPA-AEPW:BEAVER5:EUREKA5
Non-Converge | 00NR | 0 | 19WP | GEN-2017-076 | '' | Non-Converge |  |  | 0.04921 |  | P12:161:SWPA-AEPW:BEAVER5:EUREKA5
Non-Converge | 00NR | 0 | 19WP | GEN-2016-037 | '' | Non-Converge |  |  | 0.13131 |  | P12:345:AEPW:PITTSB-7:VALIANT7
Non-Converge | 00NR | 0 | 19WP | GEN-2016-127 | '' | Non-Converge |  |  | 0.12877 |  | P12:345:AEPW:PITTSB-7:VALIANT7
Non-Converge | 00NR | 0 | 19WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.12541 |  | P12:345:AEPW:PITTSB-7:VALIANT7
Non-Converge | 00NR | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.12541 |  | P12:345:AEPW:PITTSB-7:VALIANT7
Non-Converge | 00NR | 0 | 19WP | GEN-2017-074 | '' | Non-Converge |  |  | 0.121 |  | P12:345:AEPW:PITTSB-7:VALIANT7
Non-Converge | 00NR | 0 | 19WP | GEN-2017-076 | '' | Non-Converge |  |  | 0.11975 |  | P12:345:AEPW:PITTSB-7:VALIANT7
Non-Converge | 00NR | 0 | 19WP | GEN-2017-077 | '' | Non-Converge |  |  | 0.12235 |  | P12:345:AEPW:PITTSB-7:VALIANT7
Non-Converge | 00NR | 0 | 19WP | GEN-2016-037 | '' | Non-Converge |  |  | 0.04368 |  | P12:345:CLEC-AEPW:DOLHILL7:SWSHV7
Non-Converge | 00NR | 0 | 19WP | GEN-2016-127 | '' | Non-Converge |  |  | 0.05397 |  | P12:345:CLEC-AEPW:DOLHILL7:SWSHV7
Non-Converge | 00NR | 0 | 19WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.03986 |  | P12:345:CLEC-AEPW:DOLHILL7:SWSHV7
Non-Converge | 00NR | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.03986 |  | P12:345:CLEC-AEPW:DOLHILL7:SWSHV7
Non-Converge | 00NR | 0 | 19WP | GEN-2017-074 | '' | Non-Converge |  |  | 0.05873 |  | P12:345:CLEC-AEPW:DOLHILL7:SWSHV7
Non-Converge | 00NR | 0 | 19WP | GEN-2017-076 | '' | Non-Converge |  |  | 0.06 |  | P12:345:CLEC-AEPW:DOLHILL7:SWSHV7
Non-Converge | 00NR | 0 | 19WP | GEN-2017-077 | '' | Non-Converge |  |  | 0.05814 |  | P12:345:CLEC-AEPW:DOLHILL7:SWSHV7
Non-Converge | 00NR | 0 | 19WP | GEN-2016-037 | '' | Non-Converge |  |  | 0.06742 |  | P12:345:EES-AEPW:7SAREPT:LONGWD7
Non-Converge | 00NR | 0 | 19WP | GEN-2016-127 | '' | Non-Converge |  |  | 0.08276 |  | P12:345:EES-AEPW:7SAREPT:LONGWD7
Non-Converge | 00NR | 0 | 19WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.06189 |  | P12:345:EES-AEPW:7SAREPT:LONGWD7
Non-Converge | 00NR | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.06189 |  | P12:345:EES-AEPW:7SAREPT:LONGWD7
Non-Converge | 00NR | 0 | 19WP | GEN-2017-074 | '' | Non-Converge |  |  | 0.09013 |  | P12:345:EES-AEPW:7SAREPT:LONGWD7
Non-Converge | 00NR | 0 | 19WP | GEN-2017-076 | '' | Non-Converge |  |  | 0.09206 |  | P12:345:EES-AEPW:7SAREPT:LONGWD7
Non-Converge | 00NR | 0 | 19WP | GEN-2017-077 | '' | Non-Converge |  |  | 0.08929 |  | P12:345:EES-AEPW:7SAREPT:LONGWD7
Non-Converge | 00NR | 0 | 20SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.0395 |  | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Non-Converge | 00NR | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.03757 |  | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Non-Converge | 00NR | 0 | 20SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.07123 |  | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Non-Converge | 00NR | 0 | 29SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06495 |  | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Non-Converge | 00NR | 0 | 20SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.032 |  | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Non-Converge | 00NR | 0 | 20SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.03881 |  | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Non-Converge | 00NR | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.03687 |  | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Non-Converge | 00NR | 0 | 20SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.0395 |  | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Non-Converge | 00NR | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.03757 |  | P12:345:MEC-NPPD:AUTO-SINGLE:ATCHSN3:COOPER3:1
Non-Converge | 00NR | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.03293 |  | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Non-Converge | 00NR | 0 | 29SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.12597 |  | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Non-Converge | 00NR | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.03156 |  | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Non-Converge | 00NR | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.03293 |  | P12:345:MEC-OPPD:AUTO-SINGLE:RAUN3:S34513:1
Non-Converge | 00NR | 0 | 20SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.03742 |  | P13:230-345:NPPD:STEGALL3:KV3A
Non-Converge | 00NR | 0 | 20SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.03742 |  | P13:230-345:NPPD:STEGALL3:KV3A
Non-Converge | 00NR | 0 | 20SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.10892 |  | P13:230-345:NPPD:STEGALL3:KV3A
Non-Converge | 00NR | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.10963 |  | P13:230-345:NPPD:STEGALL3:KV3A
Non-Converge | 00NR | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.10963 |  | P13:230-345:NPPD:STEGALL3:KV3A
Non-Converge | 00NR | 0 | 20SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.10892 |  | P13:230-345:NPPD:STEGALL3:KV3A
Non-Converge | 00NR | 0 | 19WP | GEN-2016-037 | '' | Non-Converge |  |  | 0.16877 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2016-037 | '' | Non-Converge |  |  | 0.16791 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2016-127 | '' | Non-Converge |  |  | 0.14724 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2016-127 | '' | Non-Converge |  |  | 0.14311 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.17671 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.17707 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.17671 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.17707 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-074 | '' | Non-Converge |  |  | 0.13723 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-074 | '' | Non-Converge |  |  | 0.13168 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-076 | '' | Non-Converge |  |  | 0.13463 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-076 | '' | Non-Converge |  |  | 0.12877 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-077 | '' | Non-Converge |  |  | 0.13842 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-077 | '' | Non-Converge |  |  | 0.13301 |  | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2016-037 | '' | Non-Converge |  |  | 0.06742 |  | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2016-127 | '' | Non-Converge |  |  | 0.08276 |  | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.06189 |  | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.06189 |  | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-074 | '' | Non-Converge |  |  | 0.09013 |  | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-076 | '' | Non-Converge |  |  | 0.09206 |  | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-077 | '' | Non-Converge |  |  | 0.08929 |  | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2016-037 | '' | Non-Converge |  |  | 0.06742 |  | P42:345:AEPW:LONGWOOD CB 1N20 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2016-127 | '' | Non-Converge |  |  | 0.08276 |  | P42:345:AEPW:LONGWOOD CB 1N20 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.06189 |  | P42:345:AEPW:LONGWOOD CB 1N20 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.06189 |  | P42:345:AEPW:LONGWOOD CB 1N20 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-074 | '' | Non-Converge |  |  | 0.09013 |  | P42:345:AEPW:LONGWOOD CB 1N20 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-076 | '' | Non-Converge |  |  | 0.09206 |  | P42:345:AEPW:LONGWOOD CB 1N20 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-077 | '' | Non-Converge |  |  | 0.08929 |  | P42:345:AEPW:LONGWOOD CB 1N20 NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2016-037 | '' | Non-Converge |  |  | 0.03867 |  | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.05764 |  | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-057 | '' | Non-Converge |  |  | 0.07406 |  | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.05764 |  | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2016-037 | '' | Non-Converge |  |  | 0.06606 |  | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.10375 |  | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Non-Converge | 00NR | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.10375 |  | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT
Non-Converge | 00NR | 0 | 20SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.0395 |  | P42:345:NPPD:BKR-CPR-3304
Non-Converge | 00NR | 0 | 20SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.07123 |  | P42:345:NPPD:BKR-CPR-3304
Non-Converge | 00NR | 0 | 20SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.032 |  | P42:345:NPPD:BKR-CPR-3304
Non-Converge | 00NR | 0 | 20SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.03881 |  | P42:345:NPPD:BKR-CPR-3304
Non-Converge | 00NR | 0 | 20SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.0395 |  | P42:345:NPPD:BKR-CPR-3304
Non-Converge | 00NR | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.03168 |  | P42:345:NPPD:BKR-HOS-3308
Non-Converge | 00NR | 0 | 20SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.34368 |  | P42:345:NPPD:BKR-HOS-3308
Non-Converge | 00NR | 0 | 29SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.33546 |  | P42:345:NPPD:BKR-HOS-3308
Non-Converge | 00NR | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.03235 |  | P42:345:NPPD:BKR-HOS-3308
Non-Converge | 00NR | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.03168 |  | P42:345:NPPD:BKR-HOS-3308
Non-Converge | 00NR | 0 | 19WP | GEN-2017-040 | '' | Non-Converge |  |  | 0.05808 |  | P43:345-500:OKGE:SB_FTTH7306
Non-Converge | 00NR | 0 | 19WP | GEN-2017-040 | '' | Non-Converge |  |  | 0.03063 |  | P43:345-500:OKGE:SB_FTTH7306
Non-Converge | 00NR | 0 | 19WP | GEN-2017-092 | '' | Non-Converge |  |  | 0.05808 |  | P43:345-500:OKGE:SB_FTTH7306
Non-Converge | 00NR | 0 | 19WP | GEN-2017-092 | '' | Non-Converge |  |  | 0.03063 |  | P43:345-500:OKGE:SB_FTTH7306
Non-Converge | 00NR | 0 | 19WP | GEN-2017-030 | '' | Non-Converge |  |  | 0.06262 |  | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Non-Converge | 00NR | 0 | 19WP | GEN-2017-030 | '' | Non-Converge |  |  | 0.0649 |  | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Non-Converge | 00NR | 0 | 19WP | GEN-2017-038 | '' | Non-Converge |  |  | 0.06262 |  | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Non-Converge | 00NR | 0 | 19WP | GEN-2017-038 | '' | Non-Converge |  |  | 0.0649 |  | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Non-Converge | 00NR | 0 | 19WP | GEN-2017-041 | '' | Non-Converge |  |  | 0.06262 |  | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Non-Converge | 00NR | 0 | 19WP | GEN-2017-041 | '' | Non-Converge |  |  | 0.0649 |  | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Non-Converge | 00NR | 0 | 19WP | GEN-2017-095 | '' | Non-Converge |  |  | 0.06262 |  | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Non-Converge | 00NR | 0 | 19WP | GEN-2017-095 | '' | Non-Converge |  |  | 0.0649 |  | P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.16101 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.07552 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.10835 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.05738 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.16281 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.07615 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.16101 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.08329 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.25073 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.10835 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.04596 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.16075 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.16281 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.08455 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.25378 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.16101 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.06991 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-047 | '' | Non-Converge |  |  | 0.26345 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.24192 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.10835 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.05178 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-058 | '' | Non-Converge |  |  | 0.19467 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.17112 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.16281 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.07054 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-100 | '' | Non-Converge |  |  | 0.26584 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.24434 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23743 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-047 | '' | Non-Converge |  |  | 0.23595 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23795 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.22297 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.2404 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23889 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.2435 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23767 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-047 | '' | Non-Converge |  |  | 0.23619 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23819 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-047 | '' | Non-Converge |  |  | 0.22319 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.24064 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-047 | '' | Non-Converge |  |  | 0.23913 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.24374 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-047 | '' | Non-Converge |  |  | 0.47554 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-047 | '' | Non-Converge |  |  | 0.47554 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-047 | '' | Non-Converge |  |  | 0.47258 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-047 | '' | Non-Converge |  |  | 0.47258 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.47618 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.47618 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.48047 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.48047 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.48605 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-047 | '' | Non-Converge |  |  | 0.48605 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-058 | '' | Non-Converge |  |  | 0.12974 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-058 | '' | Non-Converge |  |  | 0.12581 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.1278 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.11275 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.13018 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-058 | '' | Non-Converge |  |  | 0.12867 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.13324 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-058 | '' | Non-Converge |  |  | 0.12987 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-058 | '' | Non-Converge |  |  | 0.12593 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.12793 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-058 | '' | Non-Converge |  |  | 0.11286 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.13031 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-058 | '' | Non-Converge |  |  | 0.1288 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.13337 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-058 | '' | Non-Converge |  |  | 0.26005 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-058 | '' | Non-Converge |  |  | 0.26005 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-058 | '' | Non-Converge |  |  | 0.25217 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-058 | '' | Non-Converge |  |  | 0.25217 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.25578 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.25578 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.25992 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.25992 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.26542 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-058 | '' | Non-Converge |  |  | 0.26542 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-100 | '' | Non-Converge |  |  | 0.241 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-100 | '' | Non-Converge |  |  | 0.23956 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24156 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.22657 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.244 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24249 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24711 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24125 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-100 | '' | Non-Converge |  |  | 0.2398 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.2418 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24L | GEN-2017-100 | '' | Non-Converge |  |  | 0.2268 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24425 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24WP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24274 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.24735 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-100 | '' | Non-Converge |  |  | 0.4827 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 19WP | GEN-2017-100 | '' | Non-Converge |  |  | 0.4827 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-100 | '' | Non-Converge |  |  | 0.47979 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20G | GEN-2017-100 | '' | Non-Converge |  |  | 0.47979 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.4834 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 20SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.4834 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.48769 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 24SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.48769 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.49327 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 02ALL | 0 | 29SP | GEN-2017-100 | '' | Non-Converge |  |  | 0.49327 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 03ALL | 0 | 29SP | GEN-2016-005 | '' | Non-Converge |  |  | 0.05491 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 03ALL | 0 | 29SP | GEN-2016-049 | '' | Non-Converge |  |  | 0.12032 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 03ALL | 0 | 29SP | GEN-2016-049 | '' | Non-Converge |  |  | 0.08594 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-018 | '' | Non-Converge |  |  | 0.11603 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-021 | '' | Non-Converge |  |  | 0.09273 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-032 | '' | Non-Converge |  |  | 0.75867 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-049 | '' | Non-Converge |  |  | 0.0803 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-052 | '' | Non-Converge |  |  | 0.06296 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-099 | '' | Non-Converge |  |  | 0.09273 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2016-005 | '' | Non-Converge |  |  | 0.05327 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2016-049 | '' | Non-Converge |  |  | 0.0466 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-018 | '' | Non-Converge |  |  | 0.04518 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-018 | '' | Non-Converge |  |  | 0.03684 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-021 | '' | Non-Converge |  |  | 0.04621 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-032 | '' | Non-Converge |  |  | 0.19673 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-049 | '' | Non-Converge |  |  | 0.0875 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.15709 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.20735 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-099 | '' | Non-Converge |  |  | 0.03721 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-099 | '' | Non-Converge |  |  | 0.04621 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2016-049 | '' | Non-Converge |  |  | 0.03212 |  | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-032 | '' | Non-Converge |  |  | 0.51078 |  | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-049 | '' | Non-Converge |  |  | 0.15131 |  | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.31162 |  | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.04046 |  | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.03164 |  | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.38599 |  | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-099 | '' | Non-Converge |  |  | 0.05271 |  | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2017-099 | '' | Non-Converge |  |  | 0.06248 |  | P12:345:SUNC:SPEARVILLE-BUCKNER::531469-531501(1)
Non-Converge | 03ALL | 0 | 24L | GEN-2016-005 | '' | Non-Converge |  |  | 0.05137 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 29SP | GEN-2016-049 | '' | Non-Converge |  |  | 0.12032 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-018 | '' | Non-Converge |  |  | 0.11603 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-018 | '' | Non-Converge |  |  | 0.03374 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-021 | '' | Non-Converge |  |  | 0.06872 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-021 | '' | Non-Converge |  |  | 0.04376 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-032 | '' | Non-Converge |  |  | 0.2148 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.16364 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-099 | '' | Non-Converge |  |  | 0.1793 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-099 | '' | Non-Converge |  |  | 0.04376 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 03ALL | 0 | 29SP | GEN-2016-049 | '' | Non-Converge |  |  | 0.12032 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-018 | '' | Non-Converge |  |  | 0.11603 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-018 | '' | Non-Converge |  |  | 0.04371 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-021 | '' | Non-Converge |  |  | 0.06872 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-032 | '' | Non-Converge |  |  | 1.0023 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 03ALL | 0 | 29SP | GEN-2017-099 | '' | Non-Converge |  |  | 0.1793 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 03ALL | 0 | 24L | GEN-2016-005 | '' | Non-Converge |  |  | 0.05422 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2016-049 | '' | Non-Converge |  |  | 0.0466 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2016-049 | '' | Non-Converge |  |  | 0.045 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-018 | '' | Non-Converge |  |  | 0.04518 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-018 | '' | Non-Converge |  |  | 0.04367 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-018 | '' | Non-Converge |  |  | 0.03839 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-021 | '' | Non-Converge |  |  | 0.04744 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-032 | '' | Non-Converge |  |  | 0.1877 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-049 | '' | Non-Converge |  |  | 0.08002 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-049 | '' | Non-Converge |  |  | 0.12899 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.15709 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.19987 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.22921 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-099 | '' | Non-Converge |  |  | 0.03721 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-099 | '' | Non-Converge |  |  | 0.03873 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2017-099 | '' | Non-Converge |  |  | 0.04744 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 03ALL | 0 | 24L | GEN-2016-005 | '' | Non-Converge |  |  | 0.05572 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 03ALL | 0 | 24L | GEN-2016-049 | '' | Non-Converge |  |  | 0.0466 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 03ALL | 0 | 24L | GEN-2017-018 | '' | Non-Converge |  |  | 0.04518 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 03ALL | 0 | 24L | GEN-2017-018 | '' | Non-Converge |  |  | 0.0367 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 03ALL | 0 | 24L | GEN-2017-021 | '' | Non-Converge |  |  | 0.0493 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 03ALL | 0 | 24L | GEN-2017-032 | '' | Non-Converge |  |  | 0.23214 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.15709 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 03ALL | 0 | 24L | GEN-2017-099 | '' | Non-Converge |  |  | 0.03721 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 03ALL | 0 | 24L | GEN-2017-099 | '' | Non-Converge |  |  | 0.0493 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 03ALL | 0 | 24L | GEN-2016-005 | '' | Non-Converge |  |  | 0.05422 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 03ALL | 0 | 24L | GEN-2016-049 | '' | Non-Converge |  |  | 0.0466 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 03ALL | 0 | 24L | GEN-2017-018 | '' | Non-Converge |  |  | 0.04518 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 03ALL | 0 | 24L | GEN-2017-018 | '' | Non-Converge |  |  | 0.03839 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 03ALL | 0 | 24L | GEN-2017-021 | '' | Non-Converge |  |  | 0.04744 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 03ALL | 0 | 24L | GEN-2017-032 | '' | Non-Converge |  |  | 0.1877 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 03ALL | 0 | 24L | GEN-2017-049 | '' | Non-Converge |  |  | 0.08508 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 03ALL | 0 | 24L | GEN-2017-049 | '' | Non-Converge |  |  | 0.12899 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.15709 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.159 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.22921 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 03ALL | 0 | 24L | GEN-2017-099 | '' | Non-Converge |  |  | 0.03721 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 03ALL | 0 | 24L | GEN-2017-099 | '' | Non-Converge |  |  | 0.04744 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 03ALL | 0 | 24L | GEN-2016-005 | '' | Non-Converge |  |  | 0.08897 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 03ALL | 0 | 24L | GEN-2016-049 | '' | Non-Converge |  |  | 0.045 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 03ALL | 0 | 24L | GEN-2016-049 | '' | Non-Converge |  |  | 0.04628 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 03ALL | 0 | 24L | GEN-2017-018 | '' | Non-Converge |  |  | 0.04367 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 03ALL | 0 | 24L | GEN-2017-018 | '' | Non-Converge |  |  | 0.06091 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 03ALL | 0 | 24L | GEN-2017-021 | '' | Non-Converge |  |  | 0.09155 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 03ALL | 0 | 24L | GEN-2017-032 | '' | Non-Converge |  |  | 0.26718 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 03ALL | 0 | 24L | GEN-2017-049 | '' | Non-Converge |  |  | 0.08002 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 03ALL | 0 | 24L | GEN-2017-049 | '' | Non-Converge |  |  | 0.06103 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 03ALL | 0 | 24L | GEN-2017-049 | '' | Non-Converge |  |  | 0.13502 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.19987 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.09433 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 03ALL | 0 | 24L | GEN-2017-052 | '' | Non-Converge |  |  | 0.27916 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 03ALL | 0 | 24L | GEN-2017-099 | '' | Non-Converge |  |  | 0.03873 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 03ALL | 0 | 24L | GEN-2017-099 | '' | Non-Converge |  |  | 0.05809 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 03ALL | 0 | 24L | GEN-2017-099 | '' | Non-Converge |  |  | 0.09155 |  | P42:345:NPPD:BKR-RW-3302
Non-Converge | 04ALL | 0 | 24L | GEN-2017-004 | '' | Non-Converge |  |  | 0.08083 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 04ALL | 0 | 24L | GEN-2017-004 | '' | Non-Converge |  |  | 0.08083 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 04ALL | 0 | 24L | GEN-2017-013 | '' | Non-Converge |  |  | 0.05833 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 04ALL | 0 | 24L | GEN-2017-013 | '' | Non-Converge |  |  | 0.08083 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 04ALL | 0 | 24L | GEN-2017-013 | '' | Non-Converge |  |  | 0.08083 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 04ALL | 0 | 24L | GEN-2017-083 | '' | Non-Converge |  |  | 0.42381 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 04ALL | 0 | 24L | GEN-2017-083 | '' | Non-Converge |  |  | 0.08083 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 04ALL | 0 | 24L | GEN-2017-083 | '' | Non-Converge |  |  | 0.08083 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.07981 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.0881 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.05234 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08878 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08626 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.07981 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.0881 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.05234 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08878 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08626 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.08299 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09128 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.05552 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09196 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.08943 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.0986 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10689 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.07111 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10755 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10503 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.08261 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.0909 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.05514 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.09158 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.08906 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.09267 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.10096 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.0652 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.10164 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.09911 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.07519 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.08348 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.04773 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.08417 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.08164 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.09666 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.10496 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.06919 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.10563 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.1031 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.09154 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09983 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.06407 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.10051 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09798 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.10597 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11425 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07847 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11491 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11239 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.09454 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.10283 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.06706 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.1035 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.10097 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.1272 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13549 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.09959 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13603 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.1335 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.10928 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11757 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.08179 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11823 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.1157 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.09652 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.10481 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.06905 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.10549 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.10296 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.10109 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10938 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.0736 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11004 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10751 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.08269 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09098 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.05522 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09166 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.08914 |  | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.0881 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08878 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.04694 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.07642 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.0881 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08878 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.04694 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.07642 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09128 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09196 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.0508 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.08028 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10689 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10755 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.0686 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.09807 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.0909 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.09158 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.05047 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.07995 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.04074 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.07022 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.10096 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.10164 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.06203 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.09151 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.08348 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.08417 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.04166 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.07114 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.10496 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.10563 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.06657 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.09605 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09983 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.10051 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.06074 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09022 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11425 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11491 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07658 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.10605 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.10283 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.1035 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.06418 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.09365 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13549 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13603 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.09276 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12223 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11757 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11823 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.08009 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10956 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.10481 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.10549 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.06641 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.09589 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10938 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11004 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.07085 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10033 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09098 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09166 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.05057 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.08005 |  | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.2537 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12719 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08437 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.2537 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12719 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08437 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.14696 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.10221 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.24679 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12564 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.08284 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.21432 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.1185 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.07576 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.24744 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.12578 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.08297 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.04876 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.22641 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.12114 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.07837 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.26332 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12931 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.08647 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.69443 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23982 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.19549 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.21812 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11932 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.07657 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.22876 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.12166 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.07889 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.19955 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11529 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07257 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.22251 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.12028 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.07752 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.16568 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10862 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.06592 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.19301 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11387 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07117 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.21841 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11938 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.07663 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.20988 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11758 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.07484 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.24726 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.12574 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.08293 |  | P12:345:AEPW:L.E.S7:TERRYRD7
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.25789 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.2537 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26705 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.20833 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26626 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.25789 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.2537 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26705 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.20833 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26626 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.23988 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.24679 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.26014 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.20142 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25935 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.21442 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.21432 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22768 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.16893 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22686 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.23168 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.24744 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2608 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.20207 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.26 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.22337 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.22641 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23976 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.18102 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23894 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27251 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.26332 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27668 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.21796 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27589 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70482 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.69443 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70779 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.64968 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70761 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70529 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70529 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.21653 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.21812 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23147 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.17272 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23065 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.22361 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.22876 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.24212 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.18337 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.2413 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20295 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.19955 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.2129 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.15413 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.21206 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.22157 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.22251 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23586 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.17711 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23504 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.1711 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.16568 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17904 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.12024 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17817 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.19722 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.19301 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20637 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.14759 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20552 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.21676 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.21841 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23176 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.17301 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23094 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.21292 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.20988 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22324 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.16449 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22242 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.23032 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.24726 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.26062 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.20189 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.25982 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12307 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12719 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08437 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12496 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12691 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12307 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12719 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08437 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12496 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12691 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.14284 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.14696 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.10221 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.1428 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-039 | '' | Non-Converge |  |  | 0.14475 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.12153 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12564 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.08284 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12343 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12538 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.11438 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.1185 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.07576 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.11635 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.1183 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.12166 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.12578 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.08297 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.12357 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.12551 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-012 | '' | Non-Converge |  |  | 0.04466 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.04876 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.04804 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-012 | '' | Non-Converge |  |  | 0.04998 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.11702 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.12114 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.07837 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.11897 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.12091 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.12519 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12931 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.08647 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12706 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12901 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.23569 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23982 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.19549 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23609 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23803 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.1152 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11932 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.07657 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11716 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11911 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.11754 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.12166 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.07889 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.11948 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.12143 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.11117 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11529 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07257 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11317 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11511 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.11616 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.12028 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.07752 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.11812 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.12006 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.10451 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10862 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.06592 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10652 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10846 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.10976 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11387 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07117 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11176 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11371 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.11527 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11938 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.07663 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11723 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11917 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.11346 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11758 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.07484 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11544 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11738 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.12162 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.12574 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.08293 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.12353 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.12547 |  | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.25789 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.2537 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26705 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.20833 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26626 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.25789 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.2537 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26705 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.20833 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26626 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.23988 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.24679 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.26014 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.20142 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25935 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.21442 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.21432 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22768 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.16893 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22686 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.23168 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.24744 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2608 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.20207 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.26 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.22337 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.22641 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23976 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.18102 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23894 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27251 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.26332 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27668 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.21796 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27589 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.21653 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.21812 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23147 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.17272 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23065 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.22361 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.22876 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.24212 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.18337 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.2413 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20295 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.19955 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.2129 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.15413 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.21206 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.22157 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.22251 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23586 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.17711 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23504 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.1711 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.16568 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17904 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.12024 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17817 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.19722 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.19301 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20637 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.14759 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20552 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.21676 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.21841 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23176 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.17301 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23094 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.21292 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.20988 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22324 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.16449 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22242 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.23032 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.24726 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.26062 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.20189 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.25982 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P12:345:AEPW-SPS:O.K.U.-7:TUCO_INT7
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.13563 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.14177 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.11113 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.13696 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.13563 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.14177 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.11113 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.13696 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.43446 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.4406 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.40371 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.42954 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.1342 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.14034 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.10976 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.13559 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.12788 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.13402 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.10368 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.12951 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.1343 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.14044 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.10985 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.13568 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2017-026 | '' | Non-Converge |  |  | 0.04897 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-026 | '' | Non-Converge |  |  | 0.0551 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-026 | '' | Non-Converge |  |  | 0.05268 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.13017 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.13631 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.10588 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.13171 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.13751 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.14365 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.11293 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.13877 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.28593 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.29207 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.25616 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.28199 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.12856 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.1347 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.10433 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.13016 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.13063 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.13677 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.10632 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.13215 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.12514 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.13128 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.10104 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.12687 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.1294 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.13554 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.10514 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.13097 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.12124 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12738 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.09723 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12306 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.12396 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.1301 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.0999 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.12573 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.12862 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.13476 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.10438 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.13022 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.12721 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.13335 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.10303 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.12886 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.13426 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.1404 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.10981 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.13564 |  | P12:345:OKGE:BKRBKR24
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.25789 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.20728 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21954 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.17372 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21816 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21586 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21586 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.25789 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.20728 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21954 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.17372 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21816 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21586 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21586 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.23988 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.20071 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.21297 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.16716 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2116 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2093 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2093 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.21442 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.16994 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.18221 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.13642 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.18086 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.17856 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.17856 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.23168 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.20132 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.21358 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.16776 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2122 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2099 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2099 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.22337 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.18137 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.19364 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.14783 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.19227 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.18998 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.18998 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27251 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.2164 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22867 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.18284 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22728 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22498 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22498 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70482 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.07282 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08508 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.03888 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08332 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08102 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08102 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.21653 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.17352 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18579 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.13999 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18443 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18213 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18213 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.22361 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.18361 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19587 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.15006 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19451 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19221 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19221 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20295 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.15598 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.16825 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.12246 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1669 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1646 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1646 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.22157 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.17767 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18994 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.14414 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18858 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18628 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18628 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.1711 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.12474 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.137 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.09121 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13565 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13335 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13335 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.19722 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.14982 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.16208 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.11629 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.16073 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15843 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15843 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.21676 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.1738 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18606 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.14026 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18471 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18241 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18241 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.21292 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.1658 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17806 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.13228 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17672 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17442 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17442 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.23032 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.20115 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.21341 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.16759 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.21203 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.20973 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.20973 |  | P12:345:OKGE:BKRBKR429
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12307 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12719 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08437 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12496 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12691 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12307 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12719 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08437 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12496 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12691 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.14284 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.14696 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.10221 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.1428 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-039 | '' | Non-Converge |  |  | 0.14475 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.12153 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12564 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.08284 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12343 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12538 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.11438 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.1185 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.07576 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.11635 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.1183 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.12166 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.12578 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.08297 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.12357 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.12551 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2017-012 | '' | Non-Converge |  |  | 0.04466 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.04876 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.04804 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-012 | '' | Non-Converge |  |  | 0.04998 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.11702 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.12114 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.07837 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.11897 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.12091 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.12519 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12931 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.08647 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12706 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12901 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.23569 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23982 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.19549 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23609 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23803 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.1152 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11932 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.07657 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11716 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11911 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.11754 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.12166 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.07889 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.11948 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.12143 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.11117 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11529 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07257 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11317 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11511 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.11616 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.12028 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.07752 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.11812 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.12006 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.10451 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10862 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.06592 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10652 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10846 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.10976 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11387 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07117 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11176 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11371 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.11527 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11938 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.07663 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11723 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11917 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.11346 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11758 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.07484 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11544 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11738 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.12162 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.12574 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.08293 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.12353 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.12547 |  | P12:345:OKGE-AEPW:BKRBKR25
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21067 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.20728 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21954 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.17372 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21816 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21586 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21586 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21067 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.20728 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21954 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.17372 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21816 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21586 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21586 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.19359 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.20071 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.21297 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.16716 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2116 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2093 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2093 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.16945 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.16994 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.18221 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.13642 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.18086 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.17856 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.17856 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.18581 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.20132 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.21358 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.16776 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2122 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2099 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2099 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.17792 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.18137 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.19364 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.14783 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.19227 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.18998 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.18998 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22454 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.2164 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22867 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.18284 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22728 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22498 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22498 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08217 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.07282 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08508 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.03888 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08332 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08102 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08102 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.17144 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.17352 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18579 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.13999 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18443 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18213 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18213 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.17815 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.18361 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19587 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.15006 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19451 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19221 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19221 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.15863 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.15598 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.16825 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.12246 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1669 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1646 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1646 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.1762 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.17767 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18994 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.14414 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18858 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18628 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18628 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12929 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.12474 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.137 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.09121 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13565 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13335 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13335 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15322 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.14982 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.16208 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.11629 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.16073 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15843 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15843 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.17166 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.1738 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18606 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.14026 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18471 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18241 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18241 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.16809 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.1658 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17806 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.13228 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17672 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17442 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17442 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.18451 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.20115 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.21341 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.16759 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.21203 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.20973 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.20973 |  | P12:345:OKGE-SPS:BKRBKR430
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.07935 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.09489 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.05668 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.09456 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.09111 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.09111 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.07935 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.09489 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.05668 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.09456 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.09111 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.09111 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.03886 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.03817 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-039 | '' | Non-Converge |  |  | 0.03472 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.03472 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.08107 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09661 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.0584 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09628 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09283 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09283 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.08896 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.1045 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.06632 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10421 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10076 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10076 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.08092 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.09646 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.05826 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.09614 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.09269 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.09269 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2017-012 | '' | Non-Converge |  |  | 0.08066 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.0962 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2017-012 | '' | Non-Converge |  |  | 0.05819 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.09607 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-012 | '' | Non-Converge |  |  | 0.09262 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.09262 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2017-033 | '' | Non-Converge |  |  | 0.72454 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.7401 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.7032 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.74108 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.73764 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.73764 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.08605 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.1016 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.06341 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.10129 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.09784 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.09784 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.077 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.09254 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.05433 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.09221 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.08876 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.08876 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.03199 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.04752 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.04687 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.04342 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.04342 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.08807 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.10361 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.06542 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.10331 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.09986 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.09986 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.08548 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.10102 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.06283 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.10071 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09726 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09726 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.09249 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.10803 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.06987 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.10775 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1043 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1043 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.08701 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.10255 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.06436 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.10224 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.09879 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.09879 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.09946 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.115 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.07689 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.11477 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.11132 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.11132 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.09404 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10958 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07142 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10931 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10586 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10586 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.088 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.10354 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.06535 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.10324 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.09979 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.09979 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.08995 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10549 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.06731 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.1052 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10175 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10175 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.08097 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09651 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.0583 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09619 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09274 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09274 |  | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1)
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.04168 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.0425 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.03672 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.05428 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.03967 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.03967 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.3093 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.30351 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.32109 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.30648 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.30648 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.03878 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.06255 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.05677 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.07432 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.05971 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.05971 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.03125 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.03688 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.03873 |  | P12:345:SPS:J14.1.EDDY.XRDS
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.07059 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.04157 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.04735 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.04849 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.04458 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.04458 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.17749 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.10967 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.11546 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.09788 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.1164 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.11249 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.11249 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.7314 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.6907 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.69649 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.67891 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.69743 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.69352 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.69352 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.23545 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.14335 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.14914 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.13152 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.15004 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.14613 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.14613 |  | P12:345:SPS:J15.1.XRDS.TOLK
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.04168 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.0425 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.03672 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.05428 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.03967 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.03967 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.3093 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.30351 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.32109 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.30648 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.30648 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.03878 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.06255 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.05677 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.07432 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.05971 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.05971 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.03125 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.03688 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.03873 |  | P22:345:SPS:EDDY_COUNTY_19L
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12307 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12719 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08437 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12496 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12307 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12719 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08437 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12496 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.14284 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.14696 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.10221 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.1428 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.12153 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12564 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.08284 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12343 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.11438 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.1185 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.07576 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.11635 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.12166 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.12578 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.08297 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.12357 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-012 | '' | Non-Converge |  |  | 0.04466 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.04876 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.04804 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.11702 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.12114 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.07837 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.11897 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.12519 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12931 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.08647 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12706 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.23569 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23982 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.19549 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23609 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.1152 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11932 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.07657 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11716 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.11754 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.12166 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.07889 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.11948 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.11117 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11529 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07257 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11317 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.11616 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.12028 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.07752 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.11812 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.10451 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10862 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.06592 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10652 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.10976 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11387 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07117 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11176 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.11527 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11938 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.07663 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11723 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.11346 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11758 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.07484 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11544 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.12162 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.12574 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.08293 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.12353 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.25789 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.25789 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.2537 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26705 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.20833 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26626 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.25789 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.25789 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.2537 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26705 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.20833 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26626 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.23988 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.23988 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.24679 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.26014 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.20142 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25935 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.21442 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.21442 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.21432 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22768 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.16893 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22686 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.23168 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.23168 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.24744 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2608 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.20207 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.26 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.22337 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.22337 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.22641 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23976 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.18102 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23894 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27251 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27251 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.26332 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27668 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.21796 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27589 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70482 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70482 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.69443 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70779 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.64968 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70761 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70529 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70529 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.21653 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.21653 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.21812 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23147 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.17272 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23065 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.22361 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.22361 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.22876 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.24212 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.18337 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.2413 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20295 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20295 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.19955 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.2129 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.15413 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.21206 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.22157 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.22157 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.22251 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23586 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.17711 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23504 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.1711 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.1711 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.16568 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17904 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.12024 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17817 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.19722 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.19722 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.19301 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20637 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.14759 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20552 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.21676 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.21676 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.21841 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23176 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.17301 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23094 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.21292 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.21292 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.20988 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22324 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.16449 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22242 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.23032 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.23032 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.24726 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.26062 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.20189 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.25982 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.25789 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26705 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26626 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12546 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12307 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08437 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.25789 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26705 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26626 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12546 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12307 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08437 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-039 | '' | Non-Converge |  |  | 0.14602 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.14284 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.10221 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.23988 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.26014 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25935 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12148 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.12153 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.08284 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.21442 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22768 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22686 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.11589 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.11438 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.07576 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.23168 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2608 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.26 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.11967 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.12166 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.08297 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-012 | '' | Non-Converge |  |  | 0.0481 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-012 | '' | Non-Converge |  |  | 0.04466 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.22337 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23976 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23894 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.11783 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.11702 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.07837 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27251 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27668 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27589 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12867 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.12519 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.08647 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70482 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70779 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70761 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70529 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70529 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23924 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.23569 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.19549 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.21653 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23147 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23065 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11633 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.1152 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.07657 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.22361 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.24212 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.2413 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.11789 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.11754 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.07889 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20295 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.2129 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.21206 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1134 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.11117 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07257 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.22157 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23586 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23504 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.11743 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.11616 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.07752 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.1711 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17904 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17817 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10719 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.10451 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.06592 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.19722 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20637 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20552 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11217 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.10976 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07117 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.21676 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23176 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23094 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11638 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.11527 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.07663 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.21292 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22324 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22242 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11561 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.11346 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.07484 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.23032 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.26062 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.25982 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.11937 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.12162 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.08293 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.25789 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.2537 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26705 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.20833 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26626 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.25789 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.2537 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26705 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.20833 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26626 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.23988 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.24679 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.26014 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.20142 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25935 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.21442 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.21432 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22768 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.16893 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22686 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.23168 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.24744 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2608 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.20207 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.26 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.22337 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.22641 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23976 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.18102 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23894 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27251 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.26332 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27668 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.21796 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27589 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.21653 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.21812 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23147 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.17272 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23065 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.22361 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.22876 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.24212 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.18337 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.2413 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20295 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.19955 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.2129 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.15413 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.21206 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.22157 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.22251 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23586 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.17711 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23504 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.1711 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.16568 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17904 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.12024 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17817 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.19722 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.19301 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20637 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.14759 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20552 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.21676 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.21841 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23176 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.17301 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23094 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.21292 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.20988 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22324 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.16449 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22242 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.23032 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.24726 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.26062 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.20189 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.25982 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.25789 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.2537 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26705 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.20833 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26626 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.25789 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.2537 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.25789 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.2537 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26705 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.20833 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26626 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.25789 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.2537 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.23988 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.24679 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.26014 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.20142 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25935 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.23988 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.24679 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.21442 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.21432 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22768 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.16893 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22686 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.21442 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.21432 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.23168 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.24744 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2608 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.20207 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.26 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.23168 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.24744 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.22337 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.22641 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23976 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.18102 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23894 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.22337 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.22641 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27251 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.26332 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27668 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.21796 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27589 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27251 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.26332 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70482 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.69443 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70779 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.64968 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70761 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70529 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70529 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.21653 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.21812 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23147 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.17272 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23065 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.21653 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.21812 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.22361 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.22876 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.24212 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.18337 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.2413 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.22361 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.22876 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20295 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.19955 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.2129 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.15413 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.21206 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20295 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.19955 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.22157 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.22251 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23586 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.17711 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23504 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.22157 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.22251 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.1711 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.16568 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17904 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.12024 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17817 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.1711 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.16568 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.19722 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.19301 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20637 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.14759 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20552 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.19722 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.19301 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.21676 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.21841 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23176 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.17301 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23094 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.21676 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.21841 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.21292 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.20988 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22324 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.16449 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22242 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.21292 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.20988 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.23032 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.24726 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.26062 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.20189 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.25982 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.23032 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.24726 |  | P23:345:AEPW:OKLAUNION CB 3409A NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12307 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12719 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08437 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12307 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12719 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08437 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.14284 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.14696 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.10221 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.12153 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12564 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.08284 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.11438 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.1185 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.07576 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.12166 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.12578 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.08297 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-012 | '' | Non-Converge |  |  | 0.04466 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.04876 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.11702 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.12114 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.07837 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.12519 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12931 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.08647 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.23569 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23982 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.19549 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.1152 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11932 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.07657 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.11754 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.12166 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.07889 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.11117 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11529 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07257 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.11616 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.12028 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.07752 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.10451 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10862 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.06592 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.10976 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11387 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07117 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.11527 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11938 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.07663 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.11346 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11758 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.07484 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.12162 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.12574 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.08293 |  | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12307 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12719 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08437 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12307 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12719 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08437 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.14284 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.14696 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.10221 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.12153 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12564 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.08284 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.11438 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.1185 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.07576 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.12166 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.12578 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.08297 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-012 | '' | Non-Converge |  |  | 0.04466 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.04876 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.11702 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.12114 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.07837 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.12519 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12931 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.08647 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.23569 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23982 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.19549 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.1152 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11932 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.07657 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.11754 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.12166 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.07889 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.11117 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11529 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07257 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.11616 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.12028 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.07752 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.10451 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10862 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.06592 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.10976 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11387 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07117 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.11527 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11938 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.07663 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.11346 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11758 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.07484 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.12162 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.12574 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.08293 |  | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12307 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08437 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12307 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08437 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.14284 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.10221 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.12153 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.08284 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.11438 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.07576 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.12166 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.08297 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-012 | '' | Non-Converge |  |  | 0.04466 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.11702 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.07837 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.12519 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.08647 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.23569 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.19549 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.1152 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.07657 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.11754 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.07889 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.11117 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07257 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.11616 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.07752 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.10451 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.06592 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.10976 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07117 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.11527 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.07663 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.11346 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.07484 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.12162 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.08293 |  | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.07935 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.09489 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.05668 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.09456 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.09111 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.09111 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.07935 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.09489 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.05668 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.09456 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.09111 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.09111 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.03886 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.03817 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-039 | '' | Non-Converge |  |  | 0.03472 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.03472 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.08107 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09661 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.0584 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09628 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09283 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09283 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.08896 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.1045 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.06632 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10421 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10076 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10076 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.08092 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.09646 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.05826 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.09614 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.09269 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.09269 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2017-012 | '' | Non-Converge |  |  | 0.08066 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.0962 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2017-012 | '' | Non-Converge |  |  | 0.05819 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.09607 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-012 | '' | Non-Converge |  |  | 0.09262 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.09262 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2017-033 | '' | Non-Converge |  |  | 0.72454 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.7401 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.7032 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.74108 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.73764 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.73764 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.08605 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.1016 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.06341 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.10129 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.09784 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.09784 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.077 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.09254 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.05433 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.09221 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.08876 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.08876 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.03199 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.04752 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.04687 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.04342 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.04342 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.08807 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.10361 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.06542 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.10331 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.09986 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.09986 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.08548 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.10102 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.06283 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.10071 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09726 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09726 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.09249 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.10803 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.06987 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.10775 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1043 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1043 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.08701 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.10255 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.06436 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.10224 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.09879 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.09879 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.09946 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.115 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.07689 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.11477 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.11132 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.11132 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.09404 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10958 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07142 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10931 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10586 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10586 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.088 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.10354 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.06535 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.10324 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.09979 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.09979 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.08995 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10549 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.06731 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.1052 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10175 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10175 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.08097 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09651 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.0583 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09619 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09274 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09274 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.07935 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.09489 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.05668 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.09456 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.09111 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.09111 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.07935 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.09489 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.05668 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.09456 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.09111 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.09111 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.03886 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.03817 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-039 | '' | Non-Converge |  |  | 0.03472 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.03472 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.08107 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09661 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.0584 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09628 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09283 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.09283 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.08896 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.1045 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.06632 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10421 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10076 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10076 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.08092 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.09646 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.05826 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.09614 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.09269 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.09269 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2017-012 | '' | Non-Converge |  |  | 0.08066 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.0962 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2017-012 | '' | Non-Converge |  |  | 0.05819 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.09607 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-012 | '' | Non-Converge |  |  | 0.09262 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.09262 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2017-033 | '' | Non-Converge |  |  | 0.72454 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.7401 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.7032 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.74108 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.73764 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.73764 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.08605 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.1016 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.06341 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.10129 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.09784 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.09784 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.077 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.09254 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.05433 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.09221 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.08876 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.08876 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.03199 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.04752 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.04687 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.04342 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.04342 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.08807 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.10361 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.06542 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.10331 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.09986 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.09986 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.08548 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.10102 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.06283 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.10071 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09726 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09726 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.09249 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.10803 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.06987 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.10775 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1043 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1043 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.08701 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.10255 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.06436 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.10224 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.09879 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.09879 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.09946 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.115 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.07689 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.11477 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.11132 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.11132 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.09404 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10958 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07142 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10931 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10586 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10586 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.088 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.10354 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.06535 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.10324 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.09979 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.09979 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.08995 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10549 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.06731 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.1052 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10175 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10175 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.08097 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09651 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.0583 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09619 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09274 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09274 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12307 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12719 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08437 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12496 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12307 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12719 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08437 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12496 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.14284 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.14696 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.10221 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.1428 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.12153 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12564 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.08284 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12343 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.11438 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.1185 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.07576 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.11635 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.12166 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.12578 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.08297 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.12357 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-012 | '' | Non-Converge |  |  | 0.04466 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.04876 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.04804 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.11702 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.12114 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.07837 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.11897 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.12519 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12931 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.08647 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12706 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.23569 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23982 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.19549 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23609 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.1152 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11932 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.07657 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11716 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.11754 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.12166 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.07889 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.11948 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.11117 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11529 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07257 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11317 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.11616 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.12028 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.07752 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.11812 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.10451 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10862 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.06592 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10652 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.10976 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11387 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07117 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11176 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.11527 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11938 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.07663 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11723 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.11346 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11758 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.07484 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11544 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.12162 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.12574 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.08293 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.12353 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.25789 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26705 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26626 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12546 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12307 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08437 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.25789 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26705 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26626 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12546 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12307 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08437 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-039 | '' | Non-Converge |  |  | 0.14602 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.14284 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.10221 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.23988 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.26014 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25935 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12148 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.12153 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.08284 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.21442 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22768 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22686 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.11589 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.11438 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.07576 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.23168 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2608 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.26 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.11967 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.12166 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.08297 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-012 | '' | Non-Converge |  |  | 0.0481 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-012 | '' | Non-Converge |  |  | 0.04466 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.22337 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23976 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23894 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.11783 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.11702 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.07837 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27251 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27668 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27589 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12867 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.12519 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.08647 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70482 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70779 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70761 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70529 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70529 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23924 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.23569 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.19549 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.21653 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23147 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23065 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11633 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.1152 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.07657 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.22361 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.24212 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.2413 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.11789 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.11754 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.07889 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20295 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.2129 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.21206 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1134 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.11117 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07257 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.22157 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23586 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23504 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.11743 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.11616 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.07752 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.1711 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17904 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17817 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10719 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.10451 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.06592 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.19722 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20637 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20552 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11217 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.10976 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07117 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.21676 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23176 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23094 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11638 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.11527 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.07663 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.21292 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22324 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22242 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11561 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.11346 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.07484 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.23032 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.26062 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.25982 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.11937 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.12162 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.08293 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.25789 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.2537 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26705 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.20833 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26626 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.25789 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.2537 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26705 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.20833 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26626 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.23988 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.24679 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.26014 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.20142 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25935 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.21442 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.21432 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22768 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.16893 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22686 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.23168 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.24744 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2608 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.20207 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.26 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.22337 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.22641 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23976 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.18102 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23894 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27251 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.26332 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27668 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.21796 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27589 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.21653 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.21812 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23147 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.17272 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23065 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.22361 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.22876 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.24212 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.18337 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.2413 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20295 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.19955 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.2129 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.15413 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.21206 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.22157 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.22251 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23586 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.17711 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23504 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.1711 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.16568 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17904 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.12024 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17817 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.19722 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.19301 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20637 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.14759 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20552 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.21676 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.21841 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23176 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.17301 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23094 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.21292 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.20988 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22324 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.16449 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22242 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.23032 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.24726 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.26062 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.20189 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.25982 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P42:345:AEPW:OKLAUNION CB 3401A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.25789 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.2537 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26705 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.20833 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26626 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.25789 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.2537 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.25789 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.2537 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26705 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.20833 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26626 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.25789 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.2537 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.23988 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.24679 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.26014 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.20142 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25935 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.23988 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.24679 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.21442 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.21432 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22768 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.16893 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22686 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.21442 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.21432 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.23168 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.24744 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2608 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.20207 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.26 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.23168 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.24744 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.22337 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.22641 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23976 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.18102 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23894 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.22337 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.22641 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27251 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.26332 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27668 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.21796 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27589 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27251 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.26332 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70482 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.69443 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70779 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.64968 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70761 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70529 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70529 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.21653 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.21812 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23147 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.17272 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23065 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.21653 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.21812 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.22361 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.22876 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.24212 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.18337 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.2413 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.22361 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.22876 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20295 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.19955 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.2129 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.15413 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.21206 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20295 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.19955 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.22157 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.22251 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23586 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.17711 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23504 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.22157 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.22251 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.1711 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.16568 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17904 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.12024 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17817 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.1711 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.16568 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.19722 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.19301 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20637 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.14759 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20552 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.19722 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.19301 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.21676 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.21841 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23176 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.17301 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23094 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.21676 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.21841 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.21292 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.20988 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22324 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.16449 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22242 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.21292 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.20988 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.23032 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.24726 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.26062 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.20189 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.25982 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.23032 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.24726 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26705 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12307 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08437 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26705 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12307 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08437 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.14284 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.10221 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.26014 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.12153 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.08284 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22768 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.11438 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.07576 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2608 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.12166 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.08297 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-012 | '' | Non-Converge |  |  | 0.04466 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23976 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.11702 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.07837 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27668 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.12519 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.08647 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70779 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.23569 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.19549 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23147 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.1152 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.07657 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.24212 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.11754 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.07889 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.2129 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.11117 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07257 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23586 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.11616 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.07752 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17904 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.10451 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.06592 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20637 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.10976 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07117 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23176 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.11527 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.07663 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22324 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.11346 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.07484 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.26062 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.12162 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.08293 |  | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12307 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12719 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08437 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12307 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12719 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08437 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.14284 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.14696 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.10221 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.12153 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.12564 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.08284 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.11438 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.1185 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.07576 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.12166 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.12578 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.08297 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-012 | '' | Non-Converge |  |  | 0.04466 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-012 | '' | Non-Converge |  |  | 0.04876 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.11702 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.12114 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.07837 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.12519 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.12931 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.08647 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.23569 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.23982 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.19549 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.1152 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.11932 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.07657 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.11754 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.12166 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.07889 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.11117 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.11529 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07257 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.11616 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.12028 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.07752 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.10451 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.10862 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.06592 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.10976 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11387 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07117 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.11527 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.11938 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.07663 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.11346 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.11758 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.07484 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.12162 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.12574 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.08293 |  | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.12307 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.08437 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.12307 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.08437 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.14284 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.10221 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.12153 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.08284 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.11438 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.07576 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.12166 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.08297 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-012 | '' | Non-Converge |  |  | 0.04466 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.11702 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.07837 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.12519 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.08647 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.23569 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.19549 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.1152 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.07657 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.11754 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.07889 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.11117 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07257 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.11616 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.07752 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.10451 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.06592 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.10976 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.07117 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.11527 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.07663 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.11346 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.07484 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.12162 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.08293 |  | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.07477 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.07236 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.07836 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.04694 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.07849 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.07642 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.07642 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.07484 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.07243 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.07844 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.07477 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.07236 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.07836 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.04694 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.07849 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.07642 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.07642 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.07484 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.07243 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.07844 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.08471 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.07622 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.08222 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.0508 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.08235 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.08028 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.08028 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.08479 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.0763 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.0823 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.09867 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.09402 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10002 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.0686 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10015 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.09807 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.09807 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.09877 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.09412 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.10012 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.08923 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.07589 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.08189 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.05047 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.08202 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.07995 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.07995 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.08932 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.07597 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.08197 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.06665 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-033 | '' | Non-Converge |  |  | 0.06643 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.07242 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | GEN-2017-033 | '' | Non-Converge |  |  | 0.04074 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.0723 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.07022 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.07022 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-033 | '' | Non-Converge |  |  | 0.06672 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-033 | '' | Non-Converge |  |  | 0.06649 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-033 | '' | Non-Converge |  |  | 0.0725 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.09382 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.08745 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.09345 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.06203 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.09358 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.09151 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.09151 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.09392 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.08754 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.09354 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.06674 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.06708 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.07307 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.04166 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.07321 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.07114 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.07114 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.06681 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.06714 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.07315 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.09757 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.09199 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.09799 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.06657 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.09812 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.09605 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.09605 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.09766 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.09208 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.09809 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09369 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.08616 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09216 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.06074 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09229 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09022 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09022 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09378 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.08625 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.09225 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.10484 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.102 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.10799 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.07658 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.10813 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.10605 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.10605 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.10494 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.1021 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1081 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.09482 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.0896 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.0956 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.06418 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.09573 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.09365 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.09365 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.09491 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.08969 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.09569 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.11985 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.11812 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12411 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.09276 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12431 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12223 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12223 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.11997 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.11824 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12424 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.1079 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.1055 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.1115 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.08009 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11164 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10956 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10956 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.10801 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.10561 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.11161 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.09744 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.09183 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.09783 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.06641 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.09796 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.09589 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.09589 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.09754 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.09193 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.09793 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.09932 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.09628 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10227 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.07085 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.1024 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10033 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10033 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.09942 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.09637 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.10238 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.08998 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.07599 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.08199 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.05057 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.08212 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.08005 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.08005 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.09007 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.07607 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.08207 |  | P42:345:OKGE:SB_BAER7314
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21067 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.20728 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21954 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.17372 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21816 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21586 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21067 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.20728 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21954 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.17372 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21816 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21586 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.19359 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.20071 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.21297 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.16716 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2116 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2093 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.16945 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.16994 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.18221 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.13642 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.18086 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.17856 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.18581 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.20132 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.21358 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.16776 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2122 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2099 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.17792 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.18137 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.19364 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.14783 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.19227 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.18998 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22454 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.2164 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22867 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.18284 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22728 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22498 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08217 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.07282 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08508 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.03888 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08332 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08102 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.17144 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.17352 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18579 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.13999 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18443 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18213 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.17815 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.18361 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19587 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.15006 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19451 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19221 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.15863 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.15598 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.16825 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.12246 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1669 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1646 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.1762 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.17767 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18994 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.14414 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18858 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18628 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12929 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.12474 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.137 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.09121 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13565 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13335 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15322 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.14982 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.16208 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.11629 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.16073 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15843 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.17166 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.1738 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18606 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.14026 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18471 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18241 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.16809 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.1658 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17806 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.13228 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17672 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17442 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.18451 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.20115 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.21341 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.16759 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.21203 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.20973 |  | P42:345:OKGE:SB_BOER7304
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21067 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.20728 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21954 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.17372 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21816 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21586 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21586 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21067 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.20728 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21954 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.17372 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21816 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21586 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21586 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.19359 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.20071 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.21297 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.16716 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2116 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2093 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2093 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.16945 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.16994 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.18221 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.13642 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.18086 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.17856 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.17856 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.18581 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.20132 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.21358 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.16776 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2122 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2099 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2099 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.17792 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.18137 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.19364 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.14783 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.19227 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.18998 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.18998 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22454 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.2164 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22867 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.18284 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22728 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22498 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22498 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08217 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.07282 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08508 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.03888 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08332 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08102 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08102 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.17144 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.17352 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18579 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.13999 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18443 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18213 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18213 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.17815 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.18361 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19587 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.15006 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19451 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19221 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19221 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.15863 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.15598 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.16825 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.12246 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1669 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1646 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1646 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.1762 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.17767 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18994 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.14414 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18858 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18628 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18628 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12929 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.12474 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.137 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.09121 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13565 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13335 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13335 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15322 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.14982 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.16208 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.11629 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.16073 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15843 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15843 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.17166 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.1738 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18606 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.14026 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18471 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18241 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18241 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.16809 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.1658 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17806 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.13228 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17672 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17442 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17442 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.18451 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.20115 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.21341 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.16759 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.21203 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.20973 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.20973 |  | P42:345:OKGE:SB_BOER7383
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21067 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.20728 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21954 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.17372 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21816 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21586 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21586 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21067 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21067 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.20728 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21954 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.17372 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21816 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21586 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21586 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21067 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.19359 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.20071 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.21297 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.16716 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2116 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2093 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2093 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.19359 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.16945 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.16994 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.18221 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.13642 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.18086 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.17856 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.17856 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.16945 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.18581 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.20132 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.21358 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.16776 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2122 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2099 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2099 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.18581 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.17792 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.18137 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.19364 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.14783 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.19227 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.18998 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.18998 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.17792 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22454 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.2164 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22867 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.18284 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22728 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22498 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22498 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22454 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08217 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.07282 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08508 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.03888 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08332 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08102 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08102 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08217 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.17144 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.17352 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18579 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.13999 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18443 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18213 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18213 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.17144 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.17815 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.18361 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19587 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.15006 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19451 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19221 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19221 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.17815 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.15863 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.15598 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.16825 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.12246 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1669 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1646 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1646 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.15863 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.1762 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.17767 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18994 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.14414 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18858 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18628 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18628 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.1762 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12929 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.12474 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.137 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.09121 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13565 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13335 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13335 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12929 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15322 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.14982 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.16208 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.11629 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.16073 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15843 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15843 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15322 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.17166 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.1738 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18606 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.14026 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18471 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18241 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18241 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.17166 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.16809 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.1658 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17806 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.13228 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17672 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17442 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17442 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.16809 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.18451 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.20115 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.21341 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.16759 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.21203 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.20973 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.20973 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.18451 |  | P42:345:OKGE:SB_BOER7384
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.13563 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.14177 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.11113 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.13696 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.1327 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.13563 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.14177 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.11113 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.13696 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.1327 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.43446 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.4406 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.40371 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.42954 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-039 | '' | Non-Converge |  |  | 0.42529 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.1342 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.14034 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.10976 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.13559 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.13133 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.12788 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.13402 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.10368 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.12951 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.12525 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.1343 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.14044 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.10985 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.13568 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.13142 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-026 | '' | Non-Converge |  |  | 0.04897 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-026 | '' | Non-Converge |  |  | 0.0551 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-026 | '' | Non-Converge |  |  | 0.05268 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-026 | '' | Non-Converge |  |  | 0.04842 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.13017 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.13631 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.10588 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.13171 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.12745 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.13751 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.14365 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.11293 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.13877 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.13451 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.28593 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.29207 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.25616 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.28199 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.27773 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.12856 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.1347 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.10433 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.13016 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.12591 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.13063 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.13677 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.10632 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.13215 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.1279 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.12514 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.13128 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.10104 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.12687 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.12261 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.1294 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.13554 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.10514 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.13097 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.12672 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.12124 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12738 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.09723 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12306 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.11881 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.12396 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.1301 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.0999 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.12573 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.12147 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.12862 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.13476 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.10438 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.13022 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.12596 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.12721 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.13335 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.10303 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.12886 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.12461 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.13426 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.1404 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.10981 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.13564 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.13139 |  | P42:345:OKGE:SB_CION7384
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.13563 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.14177 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.11113 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.13696 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.1327 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.13563 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.14177 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.11113 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.13696 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.1327 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.43446 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.4406 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.40371 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.42954 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-039 | '' | Non-Converge |  |  | 0.42529 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.1342 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.14034 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.10976 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.13559 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.13133 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.12788 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.13402 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.10368 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.12951 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.12525 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.1343 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.14044 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.10985 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.13568 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.13142 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2017-026 | '' | Non-Converge |  |  | 0.04897 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-026 | '' | Non-Converge |  |  | 0.0551 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-026 | '' | Non-Converge |  |  | 0.05268 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-026 | '' | Non-Converge |  |  | 0.04842 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.13017 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.13631 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.10588 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.13171 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.12745 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.13751 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.14365 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.11293 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.13877 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.13451 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.28593 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.29207 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.25616 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.28199 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.27773 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.12856 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.1347 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.10433 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.13016 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.12591 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.13063 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.13677 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.10632 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.13215 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.1279 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.12514 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.13128 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.10104 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.12687 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.12261 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.1294 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.13554 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.10514 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.13097 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.12672 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.12124 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12738 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.09723 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12306 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.11881 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.12396 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.1301 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.0999 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.12573 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.12147 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.12862 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.13476 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.10438 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.13022 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.12596 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.12721 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.13335 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.10303 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.12886 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.12461 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.13426 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.1404 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.10981 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.13564 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.13139 |  | P42:345:OKGE:SB_MICO7301
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.13563 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.14177 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.11113 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.13696 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.13563 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.14177 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.11113 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.13696 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2016-039 | '' | Non-Converge |  |  | 0.43446 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.4406 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2016-039 | '' | Non-Converge |  |  | 0.40371 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-039 | '' | Non-Converge |  |  | 0.42954 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.1342 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.14034 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.10976 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.13559 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.12788 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.13402 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.10368 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.12951 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.1343 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.14044 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.10985 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.13568 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2017-026 | '' | Non-Converge |  |  | 0.04897 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-026 | '' | Non-Converge |  |  | 0.0551 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-026 | '' | Non-Converge |  |  | 0.05268 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.13017 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.13631 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.10588 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.13171 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.13751 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.14365 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.11293 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.13877 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.28593 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.29207 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.25616 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.28199 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.12856 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.1347 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.10433 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.13016 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.13063 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.13677 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.10632 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.13215 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.12514 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.13128 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.10104 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.12687 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.1294 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.13554 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.10514 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.13097 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.12124 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12738 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.09723 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.12306 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.12396 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.1301 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.0999 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.12573 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.12862 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.13476 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.10438 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.13022 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.12721 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.13335 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.10303 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.12886 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.13426 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.1404 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.10981 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.13564 |  | P42:345:OKGE:SB_MICO7312
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.25789 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.2537 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26705 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.20833 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26626 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.26394 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.25789 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.2537 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26705 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.20833 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26626 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.26394 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.23988 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.24679 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.26014 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.20142 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25935 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.25703 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.21442 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.21432 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22768 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.16893 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22686 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.22454 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.23168 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.24744 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2608 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.20207 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.26 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.25768 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.22337 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.22641 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23976 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.18102 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23894 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.23663 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27251 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.26332 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27668 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.21796 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27589 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.27357 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70482 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.69443 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70779 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.64968 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70761 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70529 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.70529 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.21653 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.21812 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23147 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.17272 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.23065 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.22833 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.22361 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.22876 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.24212 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.18337 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.2413 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.23898 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20295 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.19955 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.2129 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.15413 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.21206 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.20974 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.22157 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.22251 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23586 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.17711 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23504 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.23272 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.1711 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.16568 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17904 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.12024 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17817 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.17586 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.19722 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.19301 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20637 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.14759 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.20552 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.2032 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.21676 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.21841 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23176 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.17301 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.23094 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.22862 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.21292 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.20988 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22324 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.16449 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.22242 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.2201 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.23032 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.24726 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.26062 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.20189 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.25982 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.2575 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 06ALL | 0 | 20G | ASGI-2016-001 | '' | Non-Converge |  |  | 0.20728 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21954 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | ASGI-2016-001 | '' | Non-Converge |  |  | 0.17372 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21816 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21586 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.21586 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | ASGI-2016-001 | '' | Non-Converge |  |  | 0.25037 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | ASGI-2017-007 | '' | Non-Converge |  |  | 0.20728 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21954 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | ASGI-2017-007 | '' | Non-Converge |  |  | 0.17372 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21816 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21586 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.21586 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | ASGI-2017-007 | '' | Non-Converge |  |  | 0.25037 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2016-078 | '' | Non-Converge |  |  | 0.20071 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.21297 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2016-078 | '' | Non-Converge |  |  | 0.16716 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2116 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2093 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-078 | '' | Non-Converge |  |  | 0.2093 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-078 | '' | Non-Converge |  |  | 0.23162 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2016-090 | '' | Non-Converge |  |  | 0.16994 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.18221 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2016-090 | '' | Non-Converge |  |  | 0.13642 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.18086 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.17856 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-090 | '' | Non-Converge |  |  | 0.17856 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-090 | '' | Non-Converge |  |  | 0.20512 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2016-172 | '' | Non-Converge |  |  | 0.20132 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.21358 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2016-172 | '' | Non-Converge |  |  | 0.16776 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2122 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2099 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2016-172 | '' | Non-Converge |  |  | 0.2099 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | GEN-2016-172 | '' | Non-Converge |  |  | 0.22308 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2017-039 | '' | Non-Converge |  |  | 0.18137 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.19364 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-039 | '' | Non-Converge |  |  | 0.14783 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.19227 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.18998 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-039 | '' | Non-Converge |  |  | 0.18998 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-039 | '' | Non-Converge |  |  | 0.21442 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2017-059 | '' | Non-Converge |  |  | 0.2164 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22867 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-059 | '' | Non-Converge |  |  | 0.18284 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22728 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22498 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-059 | '' | Non-Converge |  |  | 0.22498 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-059 | '' | Non-Converge |  |  | 0.26559 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2017-065 | '' | Non-Converge |  |  | 0.07282 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08508 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-065 | '' | Non-Converge |  |  | 0.03888 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08332 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08102 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-065 | '' | Non-Converge |  |  | 0.08102 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2017-069 | '' | Non-Converge |  |  | 0.17352 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18579 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-069 | '' | Non-Converge |  |  | 0.13999 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18443 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18213 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-069 | '' | Non-Converge |  |  | 0.18213 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-069 | '' | Non-Converge |  |  | 0.20731 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2017-078 | '' | Non-Converge |  |  | 0.18361 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19587 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-078 | '' | Non-Converge |  |  | 0.15006 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19451 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19221 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-078 | '' | Non-Converge |  |  | 0.19221 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-078 | '' | Non-Converge |  |  | 0.21468 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2017-079 | '' | Non-Converge |  |  | 0.15598 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.16825 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-079 | '' | Non-Converge |  |  | 0.12246 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1669 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1646 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-079 | '' | Non-Converge |  |  | 0.1646 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-079 | '' | Non-Converge |  |  | 0.19321 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2017-080 | '' | Non-Converge |  |  | 0.17767 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18994 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-080 | '' | Non-Converge |  |  | 0.14414 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18858 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18628 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-080 | '' | Non-Converge |  |  | 0.18628 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-080 | '' | Non-Converge |  |  | 0.21254 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2017-081 | '' | Non-Converge |  |  | 0.12474 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.137 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-081 | '' | Non-Converge |  |  | 0.09121 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13565 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13335 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-081 | '' | Non-Converge |  |  | 0.13335 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-081 | '' | Non-Converge |  |  | 0.16051 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2017-084 | '' | Non-Converge |  |  | 0.14982 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.16208 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-084 | '' | Non-Converge |  |  | 0.11629 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.16073 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15843 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-084 | '' | Non-Converge |  |  | 0.15843 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-084 | '' | Non-Converge |  |  | 0.18725 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2017-087 | '' | Non-Converge |  |  | 0.1738 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18606 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-087 | '' | Non-Converge |  |  | 0.14026 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18471 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18241 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-087 | '' | Non-Converge |  |  | 0.18241 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-087 | '' | Non-Converge |  |  | 0.20755 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2017-091 | '' | Non-Converge |  |  | 0.1658 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17806 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-091 | '' | Non-Converge |  |  | 0.13228 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17672 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17442 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-091 | '' | Non-Converge |  |  | 0.17442 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-091 | '' | Non-Converge |  |  | 0.20359 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20G | GEN-2017-104 | '' | Non-Converge |  |  | 0.20115 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 20SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.21341 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24L | GEN-2017-104 | '' | Non-Converge |  |  | 0.16759 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.21203 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 24WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.20973 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 29SP | GEN-2017-104 | '' | Non-Converge |  |  | 0.20973 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 06ALL | 0 | 19WP | GEN-2017-104 | '' | Non-Converge |  |  | 0.22166 |  | P43:345:SPS:TUCO:NR20_19L
Non-Converge | 08ALL | 0 | 24L | GEN-2016-072 | '' | Non-Converge |  |  | 0.03043 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 08ALL | 0 | 24L | GEN-2016-072 | '' | Non-Converge |  |  | 0.03043 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.04111 |  | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.04081 |  | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.06201 |  | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06678 |  | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2017-001 | '' | Non-Converge |  |  | 0.05026 |  | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.06893 |  | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06112 |  | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.04128 |  | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.04081 |  | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.0775 |  | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.06815 |  | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.03231 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.04111 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.0329 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.04081 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.04185 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.06201 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.05706 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06678 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2017-001 | '' | Non-Converge |  |  | 0.037 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2017-001 | '' | Non-Converge |  |  | 0.05026 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.04676 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.06893 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.0425 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06112 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.03276 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.04128 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.0329 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.04081 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.05322 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.0775 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.0471 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.06815 |  | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.17168 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.16812 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.15554 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.15906 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.15409 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.1637 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.16014 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.14878 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.15229 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.14732 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.06299 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05941 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05842 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.06193 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05695 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06567 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.0621 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06531 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06881 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06381 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.12095 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.11738 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10991 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.11342 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10844 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.07075 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06717 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06563 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06914 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06415 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.08204 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07847 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.0754 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07891 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07393 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.16706 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.1635 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15162 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15513 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15016 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.1637 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.16014 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.14878 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.15229 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.14732 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.06114 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05756 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.0574 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.06091 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05592 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.07114 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06757 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06704 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.07055 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06556 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.1562 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.14462 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.1489 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.13843 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05755 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05651 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.05941 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06222 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.11001 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10309 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06417 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06265 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07453 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07162 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15198 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.14103 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.1489 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.13843 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05537 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05509 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06459 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06397 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1)
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.04111 |  | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.04081 |  | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.06201 |  | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06678 |  | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2017-001 | '' | Non-Converge |  |  | 0.05026 |  | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.06893 |  | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06112 |  | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.04128 |  | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.04081 |  | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.0775 |  | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.06815 |  | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.07291 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.07463 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.10665 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.11366 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2017-001 | '' | Non-Converge |  |  | 0.0885 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.13152 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.11304 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.07412 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.07463 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.13758 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.1253 |  | P23:345:GMO-KCPL-NPPD:STJOE_R2-5::STJOE-NASHUA-COOPER
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.04111 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.04081 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.03171 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.06201 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.0303 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.04259 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06678 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2017-001 | '' | Non-Converge |  |  | 0.05026 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.0357 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.06893 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.03324 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.03254 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06112 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.04128 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.04081 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.03962 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.0775 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.03788 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.03581 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.06815 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.03234 |  | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.03231 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.04111 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.0329 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.04081 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.04185 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.06201 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.05706 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06678 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2017-001 | '' | Non-Converge |  |  | 0.037 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2017-001 | '' | Non-Converge |  |  | 0.05026 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.04676 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.06893 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.0425 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06112 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.03276 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.04128 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.0329 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.04081 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.05322 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.0775 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.0471 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.06815 |  | P23:345:MEC:BONDURANT 906
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.04111 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.04081 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.03171 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.06201 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.04259 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06678 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2017-001 | '' | Non-Converge |  |  | 0.05026 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.0357 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.06893 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.03254 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06112 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.04128 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.04081 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.03962 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.0775 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.03581 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.06815 |  | P23:345:MEC:MONTEZUMA 903
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.03231 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.04111 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.0329 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.04081 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.04185 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.06201 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.05706 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06678 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2017-001 | '' | Non-Converge |  |  | 0.037 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2017-001 | '' | Non-Converge |  |  | 0.05026 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.04676 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.06893 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.0425 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06112 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.03276 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.04128 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.0329 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.04081 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.05322 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.0775 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.0471 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.06815 |  | P23:345:MEC:SYCAMORE 901
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.03231 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.04111 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.0329 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.04081 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.04185 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.06201 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.05706 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.06678 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2017-001 | '' | Non-Converge |  |  | 0.037 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2017-001 | '' | Non-Converge |  |  | 0.05026 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.04676 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.06893 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.0425 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.06112 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.03276 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.04128 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.0329 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.04081 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.05322 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.0775 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.0471 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.06815 |  | P23:345:MEC:SYCAMORE 902
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.09052 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.08314 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.04532 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.04159 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.08701 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.08014 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.04147 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.03835 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.04767 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.04516 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.0454 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.04465 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.07613 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.07089 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.05156 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.0488 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.06026 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.05687 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.0886 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.08151 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.04297 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.03959 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.08701 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.08014 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.04147 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.03835 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.04441 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.04224 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.05053 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.04823 |  | P23:345:SUNC:HLC_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.08314 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.14462 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.08014 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.13843 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.04516 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05651 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.04465 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06222 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.07089 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10309 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.0488 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06265 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.05687 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07162 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.08151 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.14103 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.08014 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.13843 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.04224 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05509 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.04823 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06397 |  | P23:345:SUNC:HLC_BRK282
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.1562 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.14462 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.14045 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.1489 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.13843 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.13427 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05755 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05651 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05234 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.05941 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06222 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.05803 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.11001 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10309 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.09892 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06417 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06265 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.05847 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07453 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07162 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.06745 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15198 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.14103 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.13686 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.1489 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.13843 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.13427 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05537 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05509 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05091 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06459 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06397 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.05979 |  | P23:345:SUNC:HLC_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.17168 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.16812 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.15906 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.15409 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.1637 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.16014 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.15229 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.14732 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.06299 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05941 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.06193 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05695 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06567 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.0621 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06881 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06381 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.12095 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.11738 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.11342 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10844 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.07075 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06717 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06914 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06415 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.08204 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07847 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07891 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07393 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.16706 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.1635 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15513 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15016 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.1637 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.16014 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.15229 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.14732 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.06114 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05756 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.06091 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05592 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.07114 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06757 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.07055 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06556 |  | P23:345:SUNC:MO_BRK182
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.20369 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.18867 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.19393 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.18041 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.06683 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.06609 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.07362 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.07796 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.13984 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.13108 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.07882 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.07731 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.09187 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.0885 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.19802 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.18384 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.19393 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.18041 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.06763 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.06786 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.07916 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.079 |  | P23:345:SUNC:MO_BRK188
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.17168 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.16812 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.15906 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.15409 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.1637 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.16014 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.15229 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.14732 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.06299 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05941 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.06193 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05695 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06567 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.0621 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06881 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06381 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.12095 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.11738 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.11342 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10844 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.07075 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06717 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06914 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06415 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.08204 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07847 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07891 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07393 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.16706 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.1635 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15513 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15016 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.1637 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.16014 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.15229 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.14732 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.06114 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05756 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.06091 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05592 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.07114 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06757 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.07055 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06556 |  | P23:345:SUNC:MO_BRK382
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.20369 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.18867 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.18358 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.19393 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.18041 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.17532 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.06683 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.06609 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.06099 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.07362 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.07796 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.07284 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.13984 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.13108 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.12598 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.07882 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.07731 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.0722 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.09187 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.0885 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.0834 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.19802 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.18384 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.17876 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.19393 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.18041 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.17532 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.06763 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.06786 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.06275 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.07916 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.079 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.07389 |  | P23:345:SUNC:MO_BRK388
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.1562 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.15356 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.14197 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.14462 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.14045 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.17168 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.16812 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.15554 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.15906 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.15409 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.1489 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.14627 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.13579 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.13843 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.13427 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.1637 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.16014 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.14878 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.15229 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.14732 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05755 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.0549 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05387 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05651 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05234 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.06299 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05941 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05842 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.06193 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05695 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.05941 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.05677 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.05958 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06222 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.05803 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06567 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.0621 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06531 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06881 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06381 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.11001 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10738 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10044 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10309 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.09892 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.12095 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.11738 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10991 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.11342 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10844 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06417 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06153 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06265 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.05847 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.07075 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06717 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06563 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06914 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06415 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07453 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07189 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.06898 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07162 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.06745 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.08204 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07847 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.0754 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07891 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07393 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15198 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.14935 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.13838 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.14103 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.13686 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.16706 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.1635 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15162 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15513 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15016 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.1489 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.14627 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.13579 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.13843 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.13427 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.1637 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.16014 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.14878 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.15229 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.14732 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05537 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05272 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05245 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05509 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05091 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.06114 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05756 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.0574 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.06091 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05592 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06459 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06194 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06133 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06397 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.05979 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.07114 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06757 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06704 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.07055 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06556 |  | P23:345:SUNC:SB_BRK482
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.16812 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.15554 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.15906 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.15409 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.16014 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.14878 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.15229 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.14732 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05941 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05842 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.06193 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05695 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.0621 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06531 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06881 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06381 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.11738 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10991 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.11342 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10844 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06717 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06563 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06914 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06415 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07847 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.0754 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07891 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07393 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.1635 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15162 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15513 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15016 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.16014 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.14878 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.15229 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.14732 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05756 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.0574 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.06091 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05592 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06757 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06704 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.07055 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06556 |  | P23:345:SUNC:SB_BRK488
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.1562 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.15356 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.14197 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.14462 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.14045 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.1489 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.14627 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.13579 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.13843 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.13427 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05755 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.0549 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05387 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05651 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-109 | '' | Non-Converge |  |  | 0.05234 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.05941 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.05677 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.05958 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-159 | '' | Non-Converge |  |  | 0.06222 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-159 | '' | Non-Converge |  |  | 0.05803 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.11001 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10738 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10044 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-001 | '' | Non-Converge |  |  | 0.10309 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-001 | '' | Non-Converge |  |  | 0.09892 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06417 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06153 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-006 | '' | Non-Converge |  |  | 0.06265 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-006 | '' | Non-Converge |  |  | 0.05847 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07453 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07189 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.06898 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-008 | '' | Non-Converge |  |  | 0.07162 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-008 | '' | Non-Converge |  |  | 0.06745 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.15198 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.14935 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.13838 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.14103 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.13686 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.1489 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.14627 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.13579 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.13843 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.13427 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05537 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05272 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05245 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05509 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-055 | '' | Non-Converge |  |  | 0.05091 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06459 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06194 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06133 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-085 | '' | Non-Converge |  |  | 0.06397 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-085 | '' | Non-Converge |  |  | 0.05979 |  | P23:345:SUNC:SB_BRK582
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.75815 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.75858 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.75804 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.76029 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.76049 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.76033 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.75815 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.75858 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.75804 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.76029 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.76049 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.76033 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.2157 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.21568 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.21578 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.21739 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.21733 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.21743 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.21743 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.21739 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.21733 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-034 | '' | Non-Converge |  |  | 0.2157 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-034 | '' | Non-Converge |  |  | 0.21578 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.21568 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.20956 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.20999 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.20945 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.21144 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.21164 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.21148 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.20956 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.20999 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.20945 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.21144 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.21164 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.21148 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.18447 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.18446 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.18455 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.18605 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.18599 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.18609 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 29SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.18609 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.18605 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.18599 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 19WP | GEN-2016-093 | '' | Non-Converge |  |  | 0.18447 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20SP | GEN-2016-093 | '' | Non-Converge |  |  | 0.18455 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.18446 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.05888 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.05931 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.05877 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.06085 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.06105 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.06089 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.05888 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.05931 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.05877 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.06085 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-031 | '' | Non-Converge |  |  | 0.06105 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-031 | '' | Non-Converge |  |  | 0.06089 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.20956 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.20999 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.20945 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.21144 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.21164 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.21148 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.20956 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.20999 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.20945 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.21144 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.21164 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.21148 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.18447 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.18446 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.18455 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.18605 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.18599 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.18609 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 29SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.18609 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.18605 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 24WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.18599 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 19WP | GEN-2017-037 | '' | Non-Converge |  |  | 0.18447 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20SP | GEN-2017-037 | '' | Non-Converge |  |  | 0.18455 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.18446 |  | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
Non-Converge | 09ALL | 0 | 20G | GEN-2016-034 | '' | Non-Converge |  |  | 0.04824 |  | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Non-Converge | 09ALL | 0 | 20G | GEN-2016-093 | '' | Non-Converge |  |  | 0.04934 |  | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Non-Converge | 09ALL | 0 | 20G | GEN-2016-109 | '' | Non-Converge |  |  | 0.06825 |  | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Non-Converge | 09ALL | 0 | 20G | GEN-2016-159 | '' | Non-Converge |  |  | 0.07675 |  | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Non-Converge | 09ALL | 0 | 20G | GEN-2017-001 | '' | Non-Converge |  |  | 0.0581 |  | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Non-Converge | 09ALL | 0 | 20G | GEN-2017-006 | '' | Non-Converge |  |  | 0.0842 |  | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Non-Converge | 09ALL | 0 | 20G | GEN-2017-008 | '' | Non-Converge |  |  | 0.07298 |  | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Non-Converge | 09ALL | 0 | 20G | GEN-2017-031 | '' | Non-Converge |  |  | 0.04902 |  | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Non-Converge | 09ALL | 0 | 20G | GEN-2017-037 | '' | Non-Converge |  |  | 0.04934 |  | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Non-Converge | 09ALL | 0 | 20G | GEN-2017-055 | '' | Non-Converge |  |  | 0.09479 |  | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Non-Converge | 09ALL | 0 | 20G | GEN-2017-085 | '' | Non-Converge |  |  | 0.08143 |  | P55:161-345:GMO-KCPL:SIBLEY_BUS_11::
Non-Converge | 13ALL | 0 | 19WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05562 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20G | GEN-2017-090 | '' | Non-Converge |  |  | 0.05585 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05518 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24L | GEN-2017-090 | '' | Non-Converge |  |  | 0.05579 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05543 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.0564 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 29SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05516 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 19WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06325 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 19WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06325 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20G | GEN-2017-090 | '' | Non-Converge |  |  | 0.06348 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06082 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24L | GEN-2017-090 | '' | Non-Converge |  |  | 0.06318 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 29SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06136 |  | P12:345:GMO-OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 19WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05562 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 20G | GEN-2017-090 | '' | Non-Converge |  |  | 0.05585 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 20SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05518 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 24L | GEN-2017-090 | '' | Non-Converge |  |  | 0.05579 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 24SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05543 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 24WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.0564 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 29SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05516 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 20G | GEN-2017-090 | '' | Non-Converge |  |  | 0.06348 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 24WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.0646 |  | P14:345:GMO-OPPD:S3458 REACTOR
Non-Converge | 13ALL | 0 | 19WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05562 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20G | GEN-2017-090 | '' | Non-Converge |  |  | 0.05585 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 20SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05518 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24L | GEN-2017-090 | '' | Non-Converge |  |  | 0.05579 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05543 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.0564 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 29SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05516 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.0612 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 24WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.0646 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 29SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.06136 |  | P23:345:OPPD:S3458-HOLT
Non-Converge | 13ALL | 0 | 19WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05562 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 20G | GEN-2017-090 | '' | Non-Converge |  |  | 0.05585 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 20SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05518 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 24L | GEN-2017-090 | '' | Non-Converge |  |  | 0.05579 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 24SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05543 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 24WP | GEN-2017-090 | '' | Non-Converge |  |  | 0.0564 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 29SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.05516 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 20G | GEN-2017-090 | '' | Non-Converge |  |  | 0.06348 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 24L | GEN-2017-090 | '' | Non-Converge |  |  | 0.06318 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 13ALL | 0 | 24SP | GEN-2017-090 | '' | Non-Converge |  |  | 0.0612 |  | P44:345:OPPD:S3458-HOL&R1
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.80701 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80825 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.80315 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81098 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 24WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81009 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81101 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.19314 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.19685 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80686 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.80701 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80825 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.80315 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81098 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 24WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81009 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81101 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.19314 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.19685 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 24L | GEN-2017-094 | '' | Non-Converge |  |  | 0.03412 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 24L | GEN-2017-094 | '' | Non-Converge |  |  | 0.03412 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80686 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.80701 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80825 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.80315 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81098 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81009 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81101 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.19314 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.19685 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80686 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.80701 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80825 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.80315 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81098 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81009 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81101 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.19314 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.19685 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24L | GEN-2017-094 | '' | Non-Converge |  |  | 0.03412 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 24L | GEN-2017-094 | '' | Non-Converge |  |  | 0.03412 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80686 |  | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.80701 |  | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80825 |  | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.80315 |  | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81098 |  | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Non-Converge | 15ALL | 0 | 24WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81009 |  | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81101 |  | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80686 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.80701 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80825 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.80315 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81098 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81009 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81101 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.19314 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.19685 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80686 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.80701 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80825 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.80315 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81098 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81009 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81101 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.19314 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.19685 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24L | GEN-2017-094 | '' | Non-Converge |  |  | 0.03412 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 24L | GEN-2017-094 | '' | Non-Converge |  |  | 0.03412 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80686 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.80701 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80825 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.80315 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81098 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81101 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.19314 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.19685 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80686 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.80701 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80825 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.80315 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81098 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81101 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.19314 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.19685 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 24L | GEN-2017-094 | '' | Non-Converge |  |  | 0.03412 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 24L | GEN-2017-094 | '' | Non-Converge |  |  | 0.03412 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80686 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.80701 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80825 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.80315 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81098 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 24WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81009 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81101 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.19314 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.19685 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80686 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 20G | GEN-2016-103 | '' | Non-Converge |  |  | 0.80701 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 20SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.80825 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.80315 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 24SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81098 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 24WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81009 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 29SP | GEN-2016-103 | '' | Non-Converge |  |  | 0.81101 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 19WP | GEN-2016-103 | '' | Non-Converge |  |  | 0.19314 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 24L | GEN-2016-103 | '' | Non-Converge |  |  | 0.19685 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 24L | GEN-2017-094 | '' | Non-Converge |  |  | 0.03412 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 15ALL | 0 | 24L | GEN-2017-094 | '' | Non-Converge |  |  | 0.03412 |  | P42:345:UMZB:# 2493 #: LO IN ND. STUCK BREAKER (2596)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.03189 |  | P12:230:GRE:AUTO-SINGLE:GRE-RAMSEY4:GRE-BALTA4:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04897 |  | P12:230:GRE:AUTO-SINGLE:GRE-RAMSEY4:GRE-BALTA4:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08943 |  | P12:230:MDU::MERRICOURT:WISHEK:1::::
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09148 |  | P12:230:MDU::MERRICOURT:WISHEK:1::::
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.25202 |  | P12:230:UMZ:# 5569 #: IN . PROPER N-1 (LINE) FOR 659351-652497-1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.25202 |  | P12:230:UMZ:# 5569 #: IN . PROPER N-1 (LINE) FOR 659351-652497-1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.0854 |  | P12:230:UMZ:# 5569 #: IN . PROPER N-1 (LINE) FOR 659351-652497-1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.0854 |  | P12:230:UMZ:# 5569 #: IN . PROPER N-1 (LINE) FOR 659351-652497-1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04577 |  | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04606 |  | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04577 |  | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04606 |  | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04594 |  | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04623 |  | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04594 |  | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04623 |  | P12:345:MPC:CENTER-PRAIRIE:CENTER 3:PRAIRIE3
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08069 |  | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08572 |  | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08626 |  | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08349 |  | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08931 |  | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.08757 |  | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09468 |  | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09522 |  | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09045 |  | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09843 |  | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08349 |  | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08911 |  | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08876 |  | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08931 |  | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09045 |  | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09823 |  | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09788 |  | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09843 |  | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04577 |  | P12:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04606 |  | P12:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.0624 |  | P12:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04594 |  | P12:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04623 |  | P12:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.0518 |  | P12:345:OTP:AUTO-SINGLE:CENTER3:CNTSHNT3:Z1
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04595 |  | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.06199 |  | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.0625 |  | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04612 |  | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.05139 |  | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.05191 |  | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08933 |  | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09865 |  | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04577 |  | P12:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04606 |  | P12:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04594 |  | P12:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04623 |  | P12:345:OTP:AUTO-SINGLE:PRAIRIE3:CNTSHNT3:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P12:345:UMZ:# 5852 #: IN . PROPER N-1 (LINE) FOR 659101-659420-Z
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P12:345:UMZ:# 5852 #: IN . PROPER N-1 (LINE) FOR 659101-659420-Z
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P12:345:UMZ:# 5852 #: IN . PROPER N-1 (LINE) FOR 659101-659420-Z
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P12:345:UMZ:# 5852 #: IN . PROPER N-1 (LINE) FOR 659101-659420-Z
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P12:345:UMZ:# 5852 #: IN . PROPER N-1 (LINE) FOR 659101-659420-Z
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P12:345:UMZ:# 5852 #: IN . PROPER N-1 (LINE) FOR 659101-659420-Z
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10908 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10908 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.14983 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.14983 |  | P12:345:UMZ:# 5854 #: IN . PROPER N-1 (LINE) FOR 652506-652806-Z
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09796 |  | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09796 |  | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09796 |  | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.12376 |  | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.12376 |  | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.12376 |  | P12:345:UMZ:# 5859 #: IN . PROPER N-1 (LINE) FOR 659160-659423-Z
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10908 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10908 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10908 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10908 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.14983 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.14983 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.14983 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.14983 |  | P12:345:UMZB:# 103 #: LOS FT IN ND. LELAND OLDS-FORT THOMPSON
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09849 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09796 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09849 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09796 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09849 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09796 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1243 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.12376 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1243 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.12376 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1243 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.12376 |  | P12:345:UMZB:# 104 #: LOS GRT IN ND. LELAND OLDS-GROTON
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P12:345:UMZB:# 98 #: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P12:345:UMZB:# 98 #: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P12:345:UMZB:# 98 #: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P12:345:UMZB:# 98 #: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P12:345:UMZB:# 98 #: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P12:345:UMZB:# 98 #: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P12:345:UMZB:# 99 #: BD IN SD. BROADLAND-ANTELOPE VALLEY
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P12:345:UMZB:# 99 #: BD IN SD. BROADLAND-ANTELOPE VALLEY
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P12:345:UMZB:# 99 #: BD IN SD. BROADLAND-ANTELOPE VALLEY
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P12:345:UMZB:# 99 #: BD IN SD. BROADLAND-ANTELOPE VALLEY
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P12:345:UMZB:# 99 #: BD IN SD. BROADLAND-ANTELOPE VALLEY
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P12:345:UMZB:# 99 #: BD IN SD. BROADLAND-ANTELOPE VALLEY
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P12:345:UMZB:# 99 #: BD IN SD. BROADLAND-ANTELOPE VALLEY
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P12:345:UMZB:# 99 #: BD IN SD. BROADLAND-ANTELOPE VALLEY
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.07656 |  | P12:345:XEL:AUTO-SINGLE:QUARRY3:GRE-RIVRVRD3:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.08616 |  | P12:345:XEL:AUTO-SINGLE:QUARRY3:GRE-RIVRVRD3:1
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08606 |  | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08572 |  | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08626 |  | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09502 |  | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09468 |  | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09522 |  | P12:345:XEL-OTP:AUTO-SINGLE:BISON3:BUFFALO3:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.07778 |  | P12:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.08769 |  | P12:345:XEL-OTP:AUTO-SINGLE:GRE-RIVRVRD3:ALEXMRES3:1
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.07743 |  | P12:500:MH:M602F
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09713 |  | P12:500:MH:M602F
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.07743 |  | P12:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09713 |  | P12:500:XEL:AUTO-SINGLE:FORBES2:ROSEAUS2:1
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.07743 |  | P12:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09713 |  | P12:500:XEL:AUTO-SINGLE:ROSEAUN2:ROSEAUM2:1
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.07743 |  | P12:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09713 |  | P12:500:XEL:AUTO-SINGLE:ROSEAUS2:ROSEAUM2:1
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.07743 |  | P12:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09713 |  | P12:500:XEL-MH:AUTO-SINGLE:ROSEAUN2:RIEL2:1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.03189 |  | P13:115-230:GRE:RMS TR1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.03062 |  | P13:115-230:GRE:RMS TR1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04897 |  | P13:115-230:GRE:RMS TR1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04884 |  | P13:115-230:GRE:RMS TR1
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P13:345:UMZB:# 233 #: BD IN SD. BROADLAND TX
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10908 |  | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11014 |  | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.14983 |  | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15089 |  | P21:345:UMZW:# 323 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08572 |  | P23:345:MPC:BISON 3:6720
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08626 |  | P23:345:MPC:BISON 3:6720
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09468 |  | P23:345:MPC:BISON 3:6720
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09522 |  | P23:345:MPC:BISON 3:6720
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.03681 |  | P23:345:MPC:CENTER 3:8810
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04577 |  | P23:345:MPC:CENTER 3:8810
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04606 |  | P23:345:MPC:CENTER 3:8810
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04577 |  | P23:345:MPC:CENTER 3:8810
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04606 |  | P23:345:MPC:CENTER 3:8810
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04692 |  | P23:345:MPC:CENTER 3:8810
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04594 |  | P23:345:MPC:CENTER 3:8810
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04623 |  | P23:345:MPC:CENTER 3:8810
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04594 |  | P23:345:MPC:CENTER 3:8810
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04623 |  | P23:345:MPC:CENTER 3:8810
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.03647 |  | P23:345:MPC:CENTER 3:8820
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.03631 |  | P23:345:MPC:CENTER 3:8820
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04577 |  | P23:345:MPC:CENTER 3:8820
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04577 |  | P23:345:MPC:CENTER 3:8820
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04644 |  | P23:345:MPC:CENTER 3:8820
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04628 |  | P23:345:MPC:CENTER 3:8820
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04594 |  | P23:345:MPC:CENTER 3:8820
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04594 |  | P23:345:MPC:CENTER 3:8820
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04577 |  | P23:345:MPC:PRAIRIE3:4440
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04606 |  | P23:345:MPC:PRAIRIE3:4440
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04577 |  | P23:345:MPC:PRAIRIE3:4440
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04606 |  | P23:345:MPC:PRAIRIE3:4440
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04594 |  | P23:345:MPC:PRAIRIE3:4440
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04623 |  | P23:345:MPC:PRAIRIE3:4440
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04594 |  | P23:345:MPC:PRAIRIE3:4440
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04623 |  | P23:345:MPC:PRAIRIE3:4440
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04577 |  | P23:345:MPC:PRAIRIE3:4450
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04606 |  | P23:345:MPC:PRAIRIE3:4450
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04577 |  | P23:345:MPC:PRAIRIE3:4450
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04606 |  | P23:345:MPC:PRAIRIE3:4450
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04594 |  | P23:345:MPC:PRAIRIE3:4450
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04623 |  | P23:345:MPC:PRAIRIE3:4450
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04594 |  | P23:345:MPC:PRAIRIE3:4450
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04623 |  | P23:345:MPC:PRAIRIE3:4450
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04577 |  | P23:345:MPC:PRAIRIE3:4470
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.04606 |  | P23:345:MPC:PRAIRIE3:4470
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.03062 |  | P23:345:MPC:PRAIRIE3:4470
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.03043 |  | P23:345:MPC:PRAIRIE3:4470
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04594 |  | P23:345:MPC:PRAIRIE3:4470
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04623 |  | P23:345:MPC:PRAIRIE3:4470
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.03073 |  | P23:345:MPC:PRAIRIE3:4470
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.03054 |  | P23:345:MPC:PRAIRIE3:4470
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.07778 |  | P23:345:MRES:ALEXMRES3:3385:FUTURE
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.08769 |  | P23:345:MRES:ALEXMRES3:3385:FUTURE
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08606 |  | P23:345:OTP:BUFFALO3:3615:V2016
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08572 |  | P23:345:OTP:BUFFALO3:3615:V2016
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08626 |  | P23:345:OTP:BUFFALO3:3615:V2016
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09502 |  | P23:345:OTP:BUFFALO3:3615:V2016
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09468 |  | P23:345:OTP:BUFFALO3:3615:V2016
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09522 |  | P23:345:OTP:BUFFALO3:3615:V2016
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08349 |  | P23:345:OTP:BUFFALO3:3655:V2016
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08876 |  | P23:345:OTP:BUFFALO3:3655:V2016
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08931 |  | P23:345:OTP:BUFFALO3:3655:V2016
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09045 |  | P23:345:OTP:BUFFALO3:3655:V2016
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09788 |  | P23:345:OTP:BUFFALO3:3655:V2016
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09843 |  | P23:345:OTP:BUFFALO3:3655:V2016
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08933 |  | P23:345:OTP:CENTER 3:3245
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.03631 |  | P23:345:OTP:CENTER 3:3245
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09865 |  | P23:345:OTP:CENTER 3:3245
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.04628 |  | P23:345:OTP:CENTER 3:3245
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08933 |  | P23:345:OTP:JAMESTN3:3115:V2020
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09865 |  | P23:345:OTP:JAMESTN3:3115:V2020
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08933 |  | P23:345:OTP:JAMESTN3:3125:V2020
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09865 |  | P23:345:OTP:JAMESTN3:3125:V2020
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08349 |  | P23:345:OTP:JAMESTN3:3135:V2020
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08911 |  | P23:345:OTP:JAMESTN3:3135:V2020
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08876 |  | P23:345:OTP:JAMESTN3:3135:V2020
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08931 |  | P23:345:OTP:JAMESTN3:3135:V2020
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09045 |  | P23:345:OTP:JAMESTN3:3135:V2020
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09823 |  | P23:345:OTP:JAMESTN3:3135:V2020
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09788 |  | P23:345:OTP:JAMESTN3:3135:V2020
Non-Converge | 16ALL | 0 | 29SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09843 |  | P23:345:OTP:JAMESTN3:3135:V2020
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08349 |  | P23:345:OTP:JAMESTN3:3145:V2020
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08911 |  | P23:345:OTP:JAMESTN3:3145:V2020
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.08876 |  | P23:345:OTP:JAMESTN3:3145:V2020
Non-Converge | 16ALL | 0 | 20SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09045 |  | P23:345:OTP:JAMESTN3:3145:V2020
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09823 |  | P23:345:OTP:JAMESTN3:3145:V2020
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.09788 |  | P23:345:OTP:JAMESTN3:3145:V2020
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09396 |  | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09351 |  | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09849 |  | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09796 |  | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.11416 |  | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1137 |  | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1243 |  | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.12376 |  | P23:345:UMZB:# 102 #: GRT IN SD. BREAKER FAULT (8392)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10908 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10908 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10908 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10908 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.14983 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.14983 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.14983 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.14983 |  | P23:345:UMZW:# 702 #: FT2 IN SD. BREAKER FAULT (2992)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10908 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10908 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10908 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.11016 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10908 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.14983 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.14983 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.14983 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.15091 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.14983 |  | P23:345:UMZW:# 703 #: FT2 IN SD. BREAKER FAULT (2996)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10454 |  | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10454 |  | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.11808 |  | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.11808 |  | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10454 |  | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09351 |  | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.11808 |  | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1137 |  | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.07656 |  | P23:345:XEL:8N46 QRY
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.08616 |  | P23:345:XEL:8N46 QRY
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09849 |  | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09796 |  | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09849 |  | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09796 |  | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09849 |  | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.09796 |  | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1243 |  | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.12376 |  | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1243 |  | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.12376 |  | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Non-Converge | 16ALL | 0 | 24SP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1243 |  | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.12376 |  | P42:345:UMZB:# 2495 #: LO IN ND. STUCK BREAKER (2396)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P42:345:UMZB:# 2503 #: AVS IN ND. STUCK BREAKER (4596)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P42:345:UMZB:# 2503 #: AVS IN ND. STUCK BREAKER (4596)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P42:345:UMZB:# 2503 #: AVS IN ND. STUCK BREAKER (4596)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P42:345:UMZB:# 2503 #: AVS IN ND. STUCK BREAKER (4596)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-010 | '' | Non-Converge |  |  | 0.10416 |  | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Non-Converge | 16ALL | 0 | 24WP | GEN-2017-048 | '' | Non-Converge |  |  | 0.1327 |  | P42:345:UMZB:# 2514 #: BD IN SD. BREAKER FAULT (192)
Non-Converge | 17ALL | 0 | 19WP | GEN-2017-014 | '' | Non-Converge |  |  | 0.68161 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20G | GEN-2017-014 | '' | Non-Converge |  |  | 0.68165 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 19WP | GEN-2017-014 | '' | Non-Converge |  |  | 0.16676 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20G | GEN-2017-014 | '' | Non-Converge |  |  | 0.16681 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 19WP | GEN-2017-014 | '' | Non-Converge |  |  | 0.51485 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20G | GEN-2017-014 | '' | Non-Converge |  |  | 0.51484 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 19WP | GEN-2017-064 | '' | Non-Converge |  |  | 0.28228 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20G | GEN-2017-064 | '' | Non-Converge |  |  | 0.28231 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 19WP | GEN-2017-064 | '' | Non-Converge |  |  | 0.28215 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20G | GEN-2017-064 | '' | Non-Converge |  |  | 0.28214 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 19WP | GEN-2017-097 | '' | Non-Converge |  |  | 0.33536 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20G | GEN-2017-097 | '' | Non-Converge |  |  | 0.3354 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 19WP | GEN-2017-097 | '' | Non-Converge |  |  | 0.34489 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Non-Converge | 17ALL | 0 | 20G | GEN-2017-097 | '' | Non-Converge |  |  | 0.34488 |  | P12:230:UMZW:# 161 #: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP)
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.23733 | 140.1 | '104178'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.23733 | 140.1 | '104178'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.23733 | 140.1 | '104178'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.23733 | 140.1 | '104178'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2484 | 131.3 | '104178'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2484 | 131.3 | '104178'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2484 | 131.3 | '104178'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2484 | 131.3 | '104178'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21059 | 120.1 | '84337'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21059 | 120.1 | '84337'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21059 | 120.1 | '84337'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21059 | 120.1 | '84337'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.22362 | 118.8 | 'P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.22362 | 118.8 | 'P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.22362 | 118.8 | 'P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.22362 | 118.8 | 'P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20529 | 117.8 | '104084'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20529 | 117.8 | '104084'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20529 | 117.8 | '104084'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20529 | 117.8 | '104084'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.205 | 117.7 | '104082'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20528 | 117.7 | '92254'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.205 | 117.7 | '104082'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20528 | 117.7 | '92254'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.205 | 117.7 | '104082'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20528 | 117.7 | '92254'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.205 | 117.7 | '104082'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20528 | 117.7 | '92254'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20443 | 117.6 | '104109'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20443 | 117.6 | '92255'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20486 | 117.6 | '92258'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20443 | 117.6 | '104109'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20443 | 117.6 | '92255'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20486 | 117.6 | '92258'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20443 | 117.6 | '104109'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20443 | 117.6 | '92255'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20486 | 117.6 | '92258'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20443 | 117.6 | '104109'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20443 | 117.6 | '92255'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20486 | 117.6 | '92258'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20407 | 117.5 | '104083'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20598 | 117.5 | '104105'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20448 | 117.5 | '84354'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20448 | 117.5 | '84825'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20408 | 117.5 | '92251'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.206 | 117.5 | '92252'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20448 | 117.5 | 'P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20407 | 117.5 | '104083'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20598 | 117.5 | '104105'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20448 | 117.5 | '84354'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20448 | 117.5 | '84825'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20408 | 117.5 | '92251'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.206 | 117.5 | '92252'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20448 | 117.5 | 'P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20407 | 117.5 | '104083'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20598 | 117.5 | '104105'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20448 | 117.5 | '84354'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20448 | 117.5 | '84825'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20408 | 117.5 | '92251'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.206 | 117.5 | '92252'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20448 | 117.5 | 'P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20407 | 117.5 | '104083'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20598 | 117.5 | '104105'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20448 | 117.5 | '84354'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20448 | 117.5 | '84825'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20408 | 117.5 | '92251'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.206 | 117.5 | '92252'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20448 | 117.5 | 'P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20498 | 117.4 | '104107'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20497 | 117.4 | '104144'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20531 | 117.4 | '84372'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20494 | 117.4 | 'P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20498 | 117.4 | '104107'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20497 | 117.4 | '104144'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20531 | 117.4 | '84372'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20494 | 117.4 | 'P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20498 | 117.4 | '104107'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20497 | 117.4 | '104144'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20531 | 117.4 | '84372'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20494 | 117.4 | 'P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20498 | 117.4 | '104107'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20497 | 117.4 | '104144'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20531 | 117.4 | '84372'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20494 | 117.4 | 'P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20608 | 117.3 | '104080'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20605 | 117.3 | '104087'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20507 | 117.3 | '84336'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20597 | 117.3 | '92256'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20498 | 117.3 | 'P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20608 | 117.3 | '104080'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20605 | 117.3 | '104087'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20507 | 117.3 | '84336'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20597 | 117.3 | '92256'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20498 | 117.3 | 'P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20608 | 117.3 | '104080'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20605 | 117.3 | '104087'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20507 | 117.3 | '84336'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20597 | 117.3 | '92256'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20498 | 117.3 | 'P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20608 | 117.3 | '104080'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20605 | 117.3 | '104087'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20507 | 117.3 | '84336'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20597 | 117.3 | '92256'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20498 | 117.3 | 'P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20496 | 117.2 | '104102'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20504 | 117.2 | '104147'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20504 | 117.2 | '84371'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20504 | 117.2 | '84486'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20496 | 117.2 | '104102'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20504 | 117.2 | '104147'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20504 | 117.2 | '84371'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20504 | 117.2 | '84486'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20496 | 117.2 | '104102'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20504 | 117.2 | '104147'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20504 | 117.2 | '84371'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20504 | 117.2 | '84486'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20496 | 117.2 | '104102'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20504 | 117.2 | '104147'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20504 | 117.2 | '84371'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.20504 | 117.2 | '84486'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | 87TH7 - CRAIG7 345 |  | 1254 | 0.20285 | 112.91 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | 87TH7 - CRAIG7 345 |  | 1254 | 0.20285 | 112.91 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | 87TH7 - CRAIG7 345 |  | 1254 | 0.20285 | 112.91 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | 87TH7 - CRAIG7 345 |  | 1254 | 0.20285 | 112.91 | P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21854 | 112.4 | '84337'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21854 | 112.4 | '84337'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21854 | 112.4 | '84337'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21854 | 112.4 | '84337'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.22024 | 112 | '84337'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.22024 | 112 | '84337'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.22024 | 112 | '84337'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.22024 | 112 | '84337'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2133 | 110.3 | '104084'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21329 | 110.3 | '92254'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21237 | 110.3 | '92255'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2133 | 110.3 | '104084'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21329 | 110.3 | '92254'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21237 | 110.3 | '92255'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2133 | 110.3 | '104084'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21329 | 110.3 | '92254'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21237 | 110.3 | '92255'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2133 | 110.3 | '104084'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21329 | 110.3 | '92254'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21237 | 110.3 | '92255'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21237 | 110.2 | '104109'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21238 | 110.2 | '84354'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21238 | 110.2 | '84825'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21238 | 110.2 | 'P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21237 | 110.2 | '104109'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21238 | 110.2 | '84354'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21238 | 110.2 | '84825'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21238 | 110.2 | 'P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21237 | 110.2 | '104109'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21238 | 110.2 | '84354'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21238 | 110.2 | '84825'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21238 | 110.2 | 'P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21237 | 110.2 | '104109'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21238 | 110.2 | '84354'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21238 | 110.2 | '84825'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21238 | 110.2 | 'P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21299 | 110.1 | '104082'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21284 | 110.1 | '104085'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21407 | 110.1 | '104105'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21302 | 110.1 | '104107'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 110.1 | '104144'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21329 | 110.1 | '84372'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21409 | 110.1 | '92252'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21284 | 110.1 | '92258'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21289 | 110.1 | 'P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21294 | 110.1 | 'P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21299 | 110.1 | '104082'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21284 | 110.1 | '104085'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21407 | 110.1 | '104105'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21302 | 110.1 | '104107'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 110.1 | '104144'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21329 | 110.1 | '84372'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21409 | 110.1 | '92252'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21284 | 110.1 | '92258'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21289 | 110.1 | 'P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21294 | 110.1 | 'P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21299 | 110.1 | '104082'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21284 | 110.1 | '104085'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21407 | 110.1 | '104105'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21302 | 110.1 | '104107'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 110.1 | '104144'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21329 | 110.1 | '84372'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21409 | 110.1 | '92252'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21284 | 110.1 | '92258'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21289 | 110.1 | 'P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21294 | 110.1 | 'P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21299 | 110.1 | '104082'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21284 | 110.1 | '104085'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21407 | 110.1 | '104105'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21302 | 110.1 | '104107'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 110.1 | '104144'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21329 | 110.1 | '84372'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21409 | 110.1 | '92252'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21284 | 110.1 | '92258'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21289 | 110.1 | 'P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21294 | 110.1 | 'P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21201 | 110 | '104083'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.212 | 110 | '104115'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21304 | 110 | '84336'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21201 | 110 | '92251'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21201 | 110 | '104083'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.212 | 110 | '104115'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21304 | 110 | '84336'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21201 | 110 | '92251'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21201 | 110 | '104083'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.212 | 110 | '104115'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21304 | 110 | '84336'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21201 | 110 | '92251'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21201 | 110 | '104083'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.212 | 110 | '104115'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21304 | 110 | '84336'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21201 | 110 | '92251'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21479 | 109.9 | '104084'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21383 | 109.9 | '104109'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21389 | 109.9 | '104119'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21389 | 109.9 | '84354'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21478 | 109.9 | '92254'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21383 | 109.9 | '92255'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.214 | 109.9 | '92256'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21389 | 109.9 | 'P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21479 | 109.9 | '104084'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21383 | 109.9 | '104109'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21389 | 109.9 | '104119'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21389 | 109.9 | '84354'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21478 | 109.9 | '92254'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21383 | 109.9 | '92255'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.214 | 109.9 | '92256'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21389 | 109.9 | 'P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21479 | 109.9 | '104084'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21383 | 109.9 | '104109'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21389 | 109.9 | '104119'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21389 | 109.9 | '84354'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21478 | 109.9 | '92254'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21383 | 109.9 | '92255'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.214 | 109.9 | '92256'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21389 | 109.9 | 'P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21479 | 109.9 | '104084'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21383 | 109.9 | '104109'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21389 | 109.9 | '104119'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21389 | 109.9 | '84354'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21478 | 109.9 | '92254'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21383 | 109.9 | '92255'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.214 | 109.9 | '92256'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21389 | 109.9 | 'P55:161-345:KCPL-GMO:HAWTHORN_BUS_20_345::'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21415 | 109.8 | '104080'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21412 | 109.8 | '104087'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21299 | 109.8 | '104102'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 109.8 | '104147'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 109.8 | '84371'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 109.8 | '84486'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21415 | 109.8 | '104080'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21412 | 109.8 | '104087'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21299 | 109.8 | '104102'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 109.8 | '104147'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 109.8 | '84371'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 109.8 | '84486'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21415 | 109.8 | '104080'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21412 | 109.8 | '104087'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21299 | 109.8 | '104102'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 109.8 | '104147'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 109.8 | '84371'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 109.8 | '84486'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21415 | 109.8 | '104080'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21412 | 109.8 | '104087'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21299 | 109.8 | '104102'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 109.8 | '104147'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 109.8 | '84371'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21301 | 109.8 | '84486'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21454 | 109.7 | '104082'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21351 | 109.7 | '104083'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21438 | 109.7 | '104085'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21437 | 109.7 | '104107'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21436 | 109.7 | '104144'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21472 | 109.7 | '84372'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21454 | 109.7 | '92242'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21351 | 109.7 | '92251'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21438 | 109.7 | '92258'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21434 | 109.7 | 'P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21454 | 109.7 | '104082'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21351 | 109.7 | '104083'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21438 | 109.7 | '104085'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21437 | 109.7 | '104107'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21436 | 109.7 | '104144'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21472 | 109.7 | '84372'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21454 | 109.7 | '92242'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21351 | 109.7 | '92251'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21438 | 109.7 | '92258'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21434 | 109.7 | 'P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21454 | 109.7 | '104082'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21351 | 109.7 | '104083'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21438 | 109.7 | '104085'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21437 | 109.7 | '104107'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21436 | 109.7 | '104144'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21472 | 109.7 | '84372'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21454 | 109.7 | '92242'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21351 | 109.7 | '92251'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21438 | 109.7 | '92258'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21434 | 109.7 | 'P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21454 | 109.7 | '104082'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21351 | 109.7 | '104083'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21438 | 109.7 | '104085'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21437 | 109.7 | '104107'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21436 | 109.7 | '104144'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21472 | 109.7 | '84372'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21454 | 109.7 | '92242'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21351 | 109.7 | '92251'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21438 | 109.7 | '92258'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21434 | 109.7 | 'P23:161-345:KCPL:HAWTHORN_R11-20::HAWTHORN-NASHUA-HAWT20'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21545 | 109.6 | '104105'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21448 | 109.6 | '84336'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21547 | 109.6 | '92252'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21439 | 109.6 | 'P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21545 | 109.6 | '104105'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21448 | 109.6 | '84336'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21547 | 109.6 | '92252'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21439 | 109.6 | 'P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21545 | 109.6 | '104105'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21448 | 109.6 | '84336'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21547 | 109.6 | '92252'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21439 | 109.6 | 'P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21545 | 109.6 | '104105'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21448 | 109.6 | '84336'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21547 | 109.6 | '92252'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21439 | 109.6 | 'P23:161-345:KCPL:HAWTHORN_R11-22::HAWTHORN-NASHUA-HAWT22'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2144 | 109.4 | '104089'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21438 | 109.4 | '104102'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21447 | 109.4 | '104147'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21447 | 109.4 | '84371'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21447 | 109.4 | '84486'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2144 | 109.4 | '104089'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21438 | 109.4 | '104102'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21447 | 109.4 | '104147'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21447 | 109.4 | '84371'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21447 | 109.4 | '84486'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2144 | 109.4 | '104089'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21438 | 109.4 | '104102'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21447 | 109.4 | '104147'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21447 | 109.4 | '84371'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21447 | 109.4 | '84486'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2144 | 109.4 | '104089'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21438 | 109.4 | '104102'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21447 | 109.4 | '104147'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21447 | 109.4 | '84371'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21447 | 109.4 | '84486'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2156 | 109.3 | '104080'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21556 | 109.3 | '104087'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21547 | 109.3 | '92256'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2156 | 109.3 | '104080'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21556 | 109.3 | '104087'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21547 | 109.3 | '92256'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2156 | 109.3 | '104080'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21556 | 109.3 | '104087'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21547 | 109.3 | '92256'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2156 | 109.3 | '104080'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21556 | 109.3 | '104087'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.21547 | 109.3 | '92256'
Thermal | 13ALL | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22841 | 108.4 | 'P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN'
Thermal | 13ALL | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22841 | 108.4 | 'P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN'
Thermal | 13ALL | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22841 | 108.4 | 'P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN'
Thermal | 13ALL | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22841 | 108.4 | 'P23:345:KCPL:NASHUA_R9-11::NASHUA-HAWTHORN-IATAN'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25965 | 107.4 | '1045320'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25965 | 107.4 | '1045320'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25965 | 107.4 | '1045320'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25965 | 107.4 | '1045320'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25965 | 107.3 | '1045300'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25965 | 107.3 | '921960'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25965 | 107.3 | '1045300'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25965 | 107.3 | '921960'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25965 | 107.3 | '1045300'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25965 | 107.3 | '921960'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25965 | 107.3 | '1045300'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25965 | 107.3 | '921960'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.20637 | 106 | 'P23:161-345:KCPL:NASHUA_R9-22::NASHUA-IATAN-NASHT11'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.20637 | 106 | 'P23:161-345:KCPL:NASHUA_R9-22::NASHUA-IATAN-NASHT11'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.20637 | 106 | 'P23:161-345:KCPL:NASHUA_R9-22::NASHUA-IATAN-NASHT11'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.20637 | 106 | 'P23:161-345:KCPL:NASHUA_R9-22::NASHUA-IATAN-NASHT11'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.26693 | 104.2 | '1045300'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.26693 | 104.2 | '1045320'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.26693 | 104.2 | '921960'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.26693 | 104.2 | '1045300'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.26693 | 104.2 | '1045320'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.26693 | 104.2 | '921960'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.26693 | 104.2 | '1045300'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.26693 | 104.2 | '1045320'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.26693 | 104.2 | '921960'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.26693 | 104.2 | '1045300'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.26693 | 104.2 | '1045320'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.26693 | 104.2 | '921960'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.23156 | 104 | '84807'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.23156 | 104 | '84807'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.23156 | 104 | '84807'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.23156 | 104 | '84807'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2683 | 103.6 | '1045300'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2683 | 103.6 | '1045320'
Thermal | 13ALL | 2 | 19WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2683 | 103.6 | '921960'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2683 | 103.6 | '1045300'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2683 | 103.6 | '1045320'
Thermal | 13ALL | 2 | 19WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2683 | 103.6 | '921960'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2683 | 103.6 | '1045300'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2683 | 103.6 | '1045320'
Thermal | 13ALL | 2 | 19WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2683 | 103.6 | '921960'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2683 | 103.6 | '1045300'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2683 | 103.6 | '1045320'
Thermal | 13ALL | 2 | 19WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.2683 | 103.6 | '921960'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22546 | 102.8 | '84337'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22546 | 102.8 | '84337'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22546 | 102.8 | '84337'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22546 | 102.8 | '84337'
Thermal | 13ALL | 2 | 29SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.2246 | 101.2 | '84337'
Thermal | 13ALL | 2 | 29SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.2246 | 101.2 | '84337'
Thermal | 13ALL | 2 | 29SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.2246 | 101.2 | '84337'
Thermal | 13ALL | 2 | 29SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.2246 | 101.2 | '84337'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21906 | 101.1 | '84825'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21996 | 101.1 | '92244'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21906 | 101.1 | '84825'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21996 | 101.1 | '92244'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21906 | 101.1 | '84825'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21996 | 101.1 | '92244'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21906 | 101.1 | '84825'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21996 | 101.1 | '92244'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.2187 | 101 | '104083'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21986 | 101 | '104118'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.2187 | 101 | '92243'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.2187 | 101 | '104083'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21986 | 101 | '104118'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.2187 | 101 | '92243'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.2187 | 101 | '104083'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21986 | 101 | '104118'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.2187 | 101 | '92243'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.2187 | 101 | '104083'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21986 | 101 | '104118'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.2187 | 101 | '92243'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21973 | 100.9 | '104082'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25929 | 100.9 | '84315'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21973 | 100.9 | '92242'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21958 | 100.9 | '92245'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21973 | 100.9 | '104082'
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25929 | 100.9 | '84315'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21973 | 100.9 | '92242'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21958 | 100.9 | '92245'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21973 | 100.9 | '104082'
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25929 | 100.9 | '84315'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21973 | 100.9 | '92242'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21958 | 100.9 | '92245'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21973 | 100.9 | '104082'
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.25929 | 100.9 | '84315'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21973 | 100.9 | '92242'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21958 | 100.9 | '92245'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21965 | 100.7 | '84336'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21965 | 100.7 | '84336'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21965 | 100.7 | '84336'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21965 | 100.7 | '84336'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22058 | 100.6 | '104116'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22058 | 100.6 | '104116'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22058 | 100.6 | '104116'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22058 | 100.6 | '104116'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21959 | 100.5 | '92249'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21959 | 100.5 | '92249'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21959 | 100.5 | '92249'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.21959 | 100.5 | '92249'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22077 | 100.4 | '104080'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22074 | 100.4 | '104087'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22077 | 100.4 | '92240'
Thermal | 13ALL | 2 | 20SP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22074 | 100.4 | '92247'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22077 | 100.4 | '104080'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22074 | 100.4 | '104087'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22077 | 100.4 | '92240'
Thermal | 13ALL | 2 | 20SP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22074 | 100.4 | '92247'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22077 | 100.4 | '104080'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22074 | 100.4 | '104087'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22077 | 100.4 | '92240'
Thermal | 13ALL | 2 | 20SP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22074 | 100.4 | '92247'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22077 | 100.4 | '104080'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22074 | 100.4 | '104087'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22077 | 100.4 | '92240'
Thermal | 13ALL | 2 | 20SP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1099 | 1195 | 0.22074 | 100.4 | '92247'
Thermal | 13ALL | 2 | 24WP | GEN-2017-030 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.23845 | 100.1 | '84807'
Thermal | 13ALL | 2 | 24WP | GEN-2017-038 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.23845 | 100.1 | '84807'
Thermal | 13ALL | 2 | 24WP | GEN-2017-041 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.23845 | 100.1 | '84807'
Thermal | 13ALL | 2 | 24WP | GEN-2017-095 | 'FROM -> TO' | STRANGR7 - 87TH7 345kV | 1195 | 1195 | 0.23845 | 100.1 | '84807'
Thermal | 13ALL | 2 | 20G | GEN-2017-030 | 'FROM -> TO' | HAWTH7 - NASHUA7 345 |  | 1325 | 0.27176 | 100.69 | P23:345:WERE:STRA_345-100::
Thermal | 13ALL | 2 | 20G | GEN-2017-038 | 'FROM -> TO' | HAWTH7 - NASHUA7 345 |  | 1325 | 0.27176 | 100.69 | P23:345:WERE:STRA_345-100::
Thermal | 13ALL | 2 | 20G | GEN-2017-041 | 'FROM -> TO' | HAWTH7 - NASHUA7 345 |  | 1325 | 0.27176 | 100.69 | P23:345:WERE:STRA_345-100::
Thermal | 13ALL | 2 | 20G | GEN-2017-095 | 'FROM -> TO' | HAWTH7 - NASHUA7 345 |  | 1325 | 0.27176 | 100.69 | P23:345:WERE:STRA_345-100::
Thermal | 06NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | TUPELO - STNWLSW4 138 1 |  | 169 | 0.03335 | 121.14 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 20G | GEN-2016-037 | 'FROM -> TO' | TUPELO - STNWLSW4 138 1 |  | 169 | 0.03335 | 121.14 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | TUPELO - STNWLSW4 138 1 |  | 169 | 0.03278 | 121.14 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 20G | GEN-2017-033 | 'FROM -> TO' | TUPELO - STNWLSW4 138 1 |  | 169 | 0.03278 | 121.14 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | TUPELO - STNWLSW4 138 1 |  | 169 | 0.03278 | 121.14 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 20G | GEN-2017-065 | 'FROM -> TO' | TUPELO - STNWLSW4 138 1 |  | 169 | 0.03278 | 121.14 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | TUPELO - STNWLSW4 138 1 |  | 169 | 0.03166 | 142.75 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | TUPELO - STNWLSW4 138 1 |  | 169 | 0.03166 | 142.75 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | TUPELO - STNWLSW4 138 1 |  | 169 | 0.03095 | 110.57 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | TUPELO - STNWLSW4 138 1 |  | 169 | 0.03095 | 110.57 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | TUPELO - STNWLSW4 138 1 |  | 169 | 0.03105 | 142.75 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | TUPELO - STNWLSW4 138 1 |  | 169 | 0.03105 | 142.75 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | TUPELO - STNWLSW4 138 1 |  | 169 | 0.03105 | 142.75 | P23:345:AEPW:PITTSBURG CB 3425A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | TUPELO - STNWLSW4 138 1 |  | 169 | 0.03105 | 142.75 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT
Thermal | 02NR | 2 | 24L | GEN-2017-047 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 1 |  | 956 | 0.03352 | 105.14 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 02NR | 2 | 24L | GEN-2017-100 | 'FROM -> TO' | NEOSHO 7 - G17-009-TAP 345 1 |  | 956 | 0.03487 | 105.14 | P23:345:KCPL-WERE:LACYGNE_R9-10::LACYGNE-WAVERLY-WGARD
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04848 | 138.5 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04523 | 130.05 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04523 | 130.05 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05272 | 119.69 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 06NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04054 | 117.5 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04946 | 111.77 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04946 | 111.77 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 12NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05271 | 108.53 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 10NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05271 | 105.34 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 12NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04946 | 101.22 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 12NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04946 | 101.22 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04476 | 100.53 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 07NR | 2 | 24L | GEN-2016-037 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.04476 | 100.53 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.03249 | 138.5 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 07NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.03265 | 119.69 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 12NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.03265 | 108.53 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 10NR | 2 | 24L | GEN-2016-127 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.03265 | 105.34 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05634 | 138.5 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05289 | 130.05 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05289 | 130.05 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.06083 | 119.69 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 06NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.0479 | 117.5 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 111.77 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 111.77 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 12NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.06083 | 108.53 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 10NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.06083 | 105.34 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 12NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 101.22 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 12NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 101.22 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05262 | 100.53 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-033 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05262 | 100.53 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05634 | 138.5 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05289 | 130.05 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05289 | 130.05 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.06083 | 119.69 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 06NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.0479 | 117.5 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 111.77 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 111.77 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 12NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.06083 | 108.53 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 10NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.06083 | 105.34 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 12NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 101.22 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 12NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05748 | 101.22 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05262 | 100.53 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 07NR | 2 | 24L | GEN-2017-065 | 'FROM -> TO' | VALIANT4 - HUGO PP4 138 1 |  | 287 | 0.05262 | 100.53 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT

## All Voltage
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
NRIS | 00NR | 3 | 19WP | N/A | ROLETTE_-CP7 | 0.8353 | 0.859 | 0.0237 | 115 | 0.9 | 1.05 | N/A | P12:115:WAPA-OTP:AUTO-SINGLE:RUGBY7:RUGBYTAP-CP7:Z
NRIS | 00NR | 3 | 19WP | N/A | RUGBY TP-CP7 | 0.8358 | 0.86 | 0.0242 | 115 | 0.9 | 1.05 | N/A | P12:115:WAPA-OTP:AUTO-SINGLE:RUGBY7:RUGBYTAP-CP7:Z
NRIS | 00NR | 3 | 19WP | N/A | THORNE -CP7 | 0.8394 | 0.8627 | 0.0233 | 115 | 0.9 | 1.05 | N/A | P12:115:WAPA-OTP:AUTO-SINGLE:RUGBY7:RUGBYTAP-CP7:Z
NRIS | 00NR | 3 | 19WP | N/A | PLTSMTH8 | 0.9151 | 0.8793 | -0.0358 | 69 | 0.9 | 1.05 | N/A | P12:69:OPPD:S985-PLTSMTH
NRIS | 00NR | 3 | 19WP | N/A | S961 8 | 0.9189 | 0.8832 | -0.0357 | 69 | 0.9 | 1.05 | N/A | P12:69:OPPD:S985-PLTSMTH
NRIS | 00NR | 3 | 19WP | N/A | SEDEAST5 | 0.8898 | 0.8548 | -0.035 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 19WP | N/A | SEDALIA5 | 0.9018 | 0.867 | -0.0348 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 19WP | N/A | MIAMI_ 5 | 0.9034 | 0.8623 | -0.0411 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 19WP | N/A | WEST---5 | 0.9036 | 0.8625 | -0.0411 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 19WP | N/A | S EAST 5 | 0.9038 | 0.8626 | -0.0412 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 19WP | N/A | MRSHLJT5 | 0.9041 | 0.863 | -0.0411 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 19WP | N/A | NORTON-5 | 0.9045 | 0.8634 | -0.0411 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 19WP | N/A | MALTABN5 | 0.9062 | 0.8659 | -0.0403 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 19WP | N/A | SWAVRLY5 | 0.9072 | 0.8674 | -0.0398 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 19WP | N/A | SWAVCAP5 | 0.9072 | 0.8674 | -0.0398 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 19WP | N/A | WAFBE5 | 0.915 | 0.8805 | -0.0345 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 19WP | N/A | WAFBE_SW5 | 0.9154 | 0.8809 | -0.0345 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 19WP | N/A | WAFBW5 | 0.9157 | 0.8813 | -0.0344 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 19WP | N/A | WAFBW_SW5 | 0.916 | 0.8815 | -0.0345 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 19WP | N/A | WINDSR 5 | 0.9195 | 0.8884 | -0.0311 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 20SP | N/A | PLTSMTH8 | 0.9093 | 0.8765 | -0.0328 | 69 | 0.9 | 1.05 | N/A | P12:69:OPPD:S985-PLTSMTH
NRIS | 00NR | 3 | 20SP | N/A | S961 8 | 0.914 | 0.8813 | -0.0327 | 69 | 0.9 | 1.05 | N/A | P12:69:OPPD:S985-PLTSMTH
NRIS | 00NR | 3 | 20SP | N/A | SEDALIA5 | 0.909 | 0.8869 | -0.0221 | 161 | 0.9 | 1.05 | N/A | P22:345:AMMO::OVERTON:1
NRIS | 00NR | 3 | 20SP | N/A | MIAMI_ 5 | 0.9121 | 0.8764 | -0.0357 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 20SP | N/A | WEST---5 | 0.9124 | 0.8767 | -0.0357 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 20SP | N/A | S EAST 5 | 0.9126 | 0.8769 | -0.0357 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 20SP | N/A | SEDALIA5 | 0.9129 | 0.8794 | -0.0335 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 20SP | N/A | MRSHLJT5 | 0.9131 | 0.8774 | -0.0357 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 20SP | N/A | NORTON-5 | 0.9136 | 0.878 | -0.0356 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 20SP | N/A | MALTABN5 | 0.9143 | 0.8791 | -0.0352 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 20SP | N/A | SWAVRLY5 | 0.9152 | 0.8804 | -0.0348 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 20SP | N/A | SWAVCAP5 | 0.9152 | 0.8804 | -0.0348 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
NRIS | 00NR | 3 | 24SP | N/A | MIAMI_ 5 | 0.9191 | 0.8988 | -0.0203 | 161 | 0.9 | 1.05 | N/A | P12:HV:EES::5NEWMAD!:1
NRIS | 00NR | 3 | 24SP | N/A | WEST---5 | 0.9194 | 0.899 | -0.0204 | 161 | 0.9 | 1.05 | N/A | P12:HV:EES::5NEWMAD!:1
NRIS | 00NR | 3 | 24SP | N/A | S EAST 5 | 0.9196 | 0.8992 | -0.0204 | 161 | 0.9 | 1.05 | N/A | P12:HV:EES::5NEWMAD!:1
NRIS | 00NR | 3 | 24SP | N/A | MIAMI_ 5 | 0.9182 | 0.897 | -0.0212 | 161 | 0.9 | 1.05 | N/A | P12:LV-EHV:EES::1NM G2:7NEWMAD%:1
NRIS | 00NR | 3 | 24SP | N/A | WEST---5 | 0.9184 | 0.8972 | -0.0212 | 161 | 0.9 | 1.05 | N/A | P12:LV-EHV:EES::1NM G2:7NEWMAD%:1
NRIS | 00NR | 3 | 24SP | N/A | S EAST 5 | 0.9186 | 0.8974 | -0.0212 | 161 | 0.9 | 1.05 | N/A | P12:LV-EHV:EES::1NM G2:7NEWMAD%:1
NRIS | 00NR | 3 | 24SP | N/A | MRSHLJT5 | 0.9191 | 0.8979 | -0.0212 | 161 | 0.9 | 1.05 | N/A | P12:LV-EHV:EES::1NM G2:7NEWMAD%:1
NRIS | 00NR | 3 | 24SP | N/A | NORTON-5 | 0.9196 | 0.8984 | -0.0212 | 161 | 0.9 | 1.05 | N/A | P12:LV-EHV:EES::1NM G2:7NEWMAD%:1
NRIS | 00NR | 3 | 24WP | N/A | GRNDFKS4 | 0.8632 | 0.8089 | -0.0543 | 230 | 0.9 | 1.05 | N/A | P13:69-115:MPC:PRAIRIE7:1
NRIS | 00NR | 3 | 24WP | N/A | GRNDFKS7 | 0.8638 | 0.807 | -0.0568 | 115 | 0.9 | 1.05 | N/A | P13:69-115:MPC:PRAIRIE7:1
NRIS | 00NR | 3 | 24WP | N/A | EGF IND7 | 0.8668 | 0.8094 | -0.0574 | 115 | 0.9 | 1.05 | N/A | P13:69-115:MPC:PRAIRIE7:1
NRIS | 00NR | 3 | 24WP | N/A | GRNDFKS8 | 0.8755 | 0.815 | -0.0605 | 69 | 0.9 | 1.05 | N/A | P13:69-115:MPC:PRAIRIE7:1
NRIS | 00NR | 3 | 24WP | N/A | PICKERT4 | 0.8773 | 0.8264 | -0.0509 | 230 | 0.9 | 1.05 | N/A | P13:69-115:MPC:PRAIRIE7:1
NRIS | 00NR | 3 | 24WP | N/A | CALEDON7 | 0.8939 | 0.8335 | -0.0604 | 115 | 0.9 | 1.05 | N/A | P13:69-115:MPC:PRAIRIE7:1
NRIS | 00NR | 3 | 24WP | N/A | GRNDFKS4 | 0.861 | 0.8062 | -0.0548 | 230 | 0.9 | 1.05 | N/A | P13:69-115:MPC:PRAIRIE7:2-
NRIS | 00NR | 3 | 24WP | N/A | GRNDFKS7 | 0.8612 | 0.8038 | -0.0574 | 115 | 0.9 | 1.05 | N/A | P13:69-115:MPC:PRAIRIE7:2-
NRIS | 00NR | 3 | 24WP | N/A | EGF IND7 | 0.8642 | 0.8062 | -0.058 | 115 | 0.9 | 1.05 | N/A | P13:69-115:MPC:PRAIRIE7:2-
NRIS | 00NR | 3 | 24WP | N/A | GRNDFKS8 | 0.8718 | 0.8105 | -0.0613 | 69 | 0.9 | 1.05 | N/A | P13:69-115:MPC:PRAIRIE7:2-
NRIS | 00NR | 3 | 24WP | N/A | PICKERT4 | 0.8755 | 0.8241 | -0.0514 | 230 | 0.9 | 1.05 | N/A | P13:69-115:MPC:PRAIRIE7:2-
NRIS | 00NR | 3 | 24WP | N/A | CALEDON7 | 0.8911 | 0.8302 | -0.0609 | 115 | 0.9 | 1.05 | N/A | P13:69-115:MPC:PRAIRIE7:2-
NRIS | 00NR | 3 | 29SP | N/A | BOL 73 5 | 0.9128 | 0.8925 | -0.0203 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | OZK457 5 | 0.8743 | 0.8514 | -0.0229 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | NIXA 5 | 0.8717 | 0.8485 | -0.0232 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | SPRGFLD5 | 0.8682 | 0.8447 | -0.0235 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | BIL221 2 | 0.9116 | 0.8881 | -0.0235 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | MC CARTNEY 5 | 0.8623 | 0.8387 | -0.0236 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | BATTLEFIELD5 | 0.8679 | 0.8443 | -0.0236 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | CLAY 5 | 0.8635 | 0.8399 | -0.0236 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | SW DISP PLT5 | 0.8717 | 0.8481 | -0.0236 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | JTEC 5 | 0.8729 | 0.8492 | -0.0237 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | BROOKLINE 5 | 0.8691 | 0.8453 | -0.0238 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | MENTOR 5 | 0.8619 | 0.8381 | -0.0238 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | MILL 5 | 0.859 | 0.8351 | -0.0239 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | PIC WEST 5 | 0.8634 | 0.8393 | -0.0241 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | JUNCTION 5 | 0.8644 | 0.8403 | -0.0241 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | JAMES RIVER5 | 0.8593 | 0.8351 | -0.0242 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | SUMMIT 5 | 0.8609 | 0.8367 | -0.0242 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | MAIN STREET5 | 0.8618 | 0.8376 | -0.0242 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | WEST BELT 5 | 0.8623 | 0.8381 | -0.0242 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | NICHOLS 5 | 0.8629 | 0.8387 | -0.0242 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | NORTON 5 | 0.8591 | 0.8347 | -0.0244 | 161 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | MILL 2 | 0.8656 | 0.8399 | -0.0257 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | REP359 2 | 0.8916 | 0.8656 | -0.026 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | MAIN STREET2 | 0.8727 | 0.8467 | -0.026 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | REP451 2 | 0.8912 | 0.8652 | -0.026 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | WIL445 2 | 0.9149 | 0.8889 | -0.026 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | PACKER 2 | 0.8602 | 0.8341 | -0.0261 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | CHAD 2 | 0.8635 | 0.8374 | -0.0261 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | HARGISS 2 | 0.8655 | 0.8394 | -0.0261 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | JAMES RIVER2 | 0.8665 | 0.8404 | -0.0261 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | WIL369 2 | 0.9135 | 0.8874 | -0.0261 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | BLACKMAN 2 | 0.8583 | 0.8321 | -0.0262 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | INGRAM 2 | 0.8593 | 0.8331 | -0.0262 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | REP345 2 | 0.8913 | 0.8651 | -0.0262 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | HIGHWAY M 2 | 0.8601 | 0.8338 | -0.0263 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | WASHINGTON 2 | 0.8722 | 0.8459 | -0.0263 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | NX ESPY2 | 0.9138 | 0.8874 | -0.0264 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | NIX_SLR_U1_2 | 0.9141 | 0.8877 | -0.0264 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | GRAND 2 | 0.8656 | 0.8392 | -0.0264 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | NORTON 2 | 0.8736 | 0.8472 | -0.0264 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | LECOMPTE 2 | 0.856 | 0.8295 | -0.0265 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | GALLOWAY 2 | 0.8583 | 0.8318 | -0.0265 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | MONROE 2 | 0.8642 | 0.8377 | -0.0265 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | JRPS 69B-2 2 | 0.8741 | 0.8476 | -0.0265 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | NIXA DT2 | 0.9051 | 0.8786 | -0.0265 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | S HWY 65 2 | 0.861 | 0.8344 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | DAYTON 2 | 0.8729 | 0.8463 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | GOLDEN 2 | 0.8743 | 0.8477 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | BATTLEFIELD2 | 0.8749 | 0.8483 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | N HWY13 2 | 0.8764 | 0.8498 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | NIXA NE2 | 0.8852 | 0.8586 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | NIC170 2 | 0.8912 | 0.8646 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | NEERGARD 2 | 0.8627 | 0.8361 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | PLAINVIEW 2 | 0.8715 | 0.8449 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | FRISCO 2 | 0.8858 | 0.8592 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | NICHOLS 2 | 0.891 | 0.8644 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | NXA TRK2 | 0.8947 | 0.8681 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | LAUREL 2 | 0.8804 | 0.8537 | -0.0267 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | COX 2 | 0.8682 | 0.8414 | -0.0268 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | SUNSET 2 | 0.8637 | 0.8369 | -0.0268 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | FORT 2 | 0.8659 | 0.8391 | -0.0268 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | KICKAPOO 2 | 0.8616 | 0.8347 | -0.0269 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | SEMINOLE 2 | 0.8626 | 0.8357 | -0.0269 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | TWIN OAKS 2 | 0.863 | 0.8361 | -0.0269 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | SED 80 2 | 0.8966 | 0.8691 | -0.0275 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | FRG397 2 | 0.9102 | 0.882 | -0.0282 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | STR370 2 | 0.9158 | 0.8876 | -0.0282 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | BUF243J2 | 0.9195 | 0.8907 | -0.0288 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | BUF243 2 | 0.9194 | 0.8906 | -0.0288 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
NRIS | 00NR | 3 | 29SP | N/A | BOL 73 5 | 0.9128 | 0.8925 | -0.0203 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | OZK457 5 | 0.8743 | 0.8514 | -0.0229 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | NIXA 5 | 0.8717 | 0.8485 | -0.0232 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | SPRGFLD5 | 0.8682 | 0.8447 | -0.0235 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | BIL221 2 | 0.9116 | 0.8881 | -0.0235 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | MC CARTNEY 5 | 0.8623 | 0.8387 | -0.0236 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | BATTLEFIELD5 | 0.8679 | 0.8443 | -0.0236 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | CLAY 5 | 0.8635 | 0.8399 | -0.0236 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | SW DISP PLT5 | 0.8717 | 0.8481 | -0.0236 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | JTEC 5 | 0.8729 | 0.8492 | -0.0237 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | BROOKLINE 5 | 0.8691 | 0.8453 | -0.0238 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | MENTOR 5 | 0.8619 | 0.8381 | -0.0238 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | MILL 5 | 0.859 | 0.8351 | -0.0239 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | PIC WEST 5 | 0.8634 | 0.8393 | -0.0241 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | JUNCTION 5 | 0.8644 | 0.8403 | -0.0241 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | JAMES RIVER5 | 0.8593 | 0.8351 | -0.0242 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | SUMMIT 5 | 0.8609 | 0.8367 | -0.0242 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | MAIN STREET5 | 0.8618 | 0.8376 | -0.0242 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | WEST BELT 5 | 0.8623 | 0.8381 | -0.0242 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | NICHOLS 5 | 0.8629 | 0.8387 | -0.0242 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | NORTON 5 | 0.8591 | 0.8347 | -0.0244 | 161 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | MILL 2 | 0.8656 | 0.8399 | -0.0257 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | REP359 2 | 0.8916 | 0.8656 | -0.026 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | MAIN STREET2 | 0.8727 | 0.8467 | -0.026 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | REP451 2 | 0.8912 | 0.8652 | -0.026 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | WIL445 2 | 0.9149 | 0.8889 | -0.026 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | PACKER 2 | 0.8602 | 0.8341 | -0.0261 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | CHAD 2 | 0.8635 | 0.8374 | -0.0261 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | HARGISS 2 | 0.8655 | 0.8394 | -0.0261 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | JAMES RIVER2 | 0.8665 | 0.8404 | -0.0261 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | WIL369 2 | 0.9135 | 0.8874 | -0.0261 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | BLACKMAN 2 | 0.8583 | 0.8321 | -0.0262 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | INGRAM 2 | 0.8593 | 0.8331 | -0.0262 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | REP345 2 | 0.8913 | 0.8651 | -0.0262 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | HIGHWAY M 2 | 0.8601 | 0.8338 | -0.0263 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | WASHINGTON 2 | 0.8722 | 0.8459 | -0.0263 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | NX ESPY2 | 0.9138 | 0.8874 | -0.0264 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | NIX_SLR_U1_2 | 0.9141 | 0.8877 | -0.0264 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | GRAND 2 | 0.8656 | 0.8392 | -0.0264 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | NORTON 2 | 0.8736 | 0.8472 | -0.0264 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | LECOMPTE 2 | 0.856 | 0.8295 | -0.0265 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | GALLOWAY 2 | 0.8583 | 0.8318 | -0.0265 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | MONROE 2 | 0.8642 | 0.8377 | -0.0265 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | JRPS 69B-2 2 | 0.8741 | 0.8476 | -0.0265 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | NIXA DT2 | 0.9051 | 0.8786 | -0.0265 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | S HWY 65 2 | 0.861 | 0.8344 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | DAYTON 2 | 0.8729 | 0.8463 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | GOLDEN 2 | 0.8743 | 0.8477 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | BATTLEFIELD2 | 0.8749 | 0.8483 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | N HWY13 2 | 0.8764 | 0.8498 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | NIXA NE2 | 0.8852 | 0.8586 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | NIC170 2 | 0.8912 | 0.8646 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | NEERGARD 2 | 0.8627 | 0.8361 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | PLAINVIEW 2 | 0.8715 | 0.8449 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | FRISCO 2 | 0.8858 | 0.8592 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | NICHOLS 2 | 0.891 | 0.8644 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | NXA TRK2 | 0.8947 | 0.8681 | -0.0266 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | LAUREL 2 | 0.8804 | 0.8537 | -0.0267 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | COX 2 | 0.8682 | 0.8414 | -0.0268 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | SUNSET 2 | 0.8637 | 0.8369 | -0.0268 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | FORT 2 | 0.8659 | 0.8391 | -0.0268 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | KICKAPOO 2 | 0.8616 | 0.8347 | -0.0269 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | SEMINOLE 2 | 0.8626 | 0.8357 | -0.0269 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | TWIN OAKS 2 | 0.863 | 0.8361 | -0.0269 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | SED 80 2 | 0.8966 | 0.8691 | -0.0275 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | FRG397 2 | 0.9102 | 0.882 | -0.0282 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | STR370 2 | 0.9158 | 0.8876 | -0.0282 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | BUF243J2 | 0.9195 | 0.8907 | -0.0288 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 29SP | N/A | BUF243 2 | 0.9194 | 0.8906 | -0.0288 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
NRIS | 00NR | 3 | 19WP | N/A | CRAWFISH765 | 1.0979 | 1.054 | -0.0439 | 765 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 19WP | N/A | FWL-WND-SWYD | 1.462 | 1.4355 | -0.0265 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 19WP | N/A | GEN-2017-040 | 1.4622 | 1.4354 | -0.0268 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 20SP | N/A | FWL-WND-SWYD | 1.4574 | 1.4258 | -0.0316 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 20SP | N/A | GEN-2017-040 | 1.4575 | 1.4257 | -0.0318 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 24SP | N/A | COLBY 2 | 1.0384 | 1.0668 | 0.0284 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 24SP | N/A | CRAWFISH765 | 1.0912 | 1.0542 | -0.037 | 765 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 24SP | N/A | FWL-WND-SWYD | 1.4518 | 1.4214 | -0.0304 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 24SP | N/A | GEN-2017-040 | 1.452 | 1.4213 | -0.0307 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 24WP | N/A | CDSEMMID | 1.0828 | 1.0594 | -0.0234 | 765 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 24WP | N/A | RSVLT_CC_W 7 | 1.0844 | 1.0558 | -0.0286 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 24WP | N/A | RSVLT_CC_E 7 | 1.0848 | 1.056 | -0.0288 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 24WP | N/A | GEN-2016-123 | 1.0852 | 1.0561 | -0.0291 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 24WP | N/A | CROSSROADS 7 | 1.0852 | 1.0561 | -0.0291 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 24WP | N/A | GEN-2017-078 | 1.0852 | 1.056 | -0.0292 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 24WP | N/A | CROSSRDS765 | 1.0937 | 1.0646 | -0.0291 | 765 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 24WP | N/A | CRAWFISH765 | 1.1004 | 1.073 | -0.0274 | 765 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 24WP | N/A | FWL-WND-SWYD | 1.4582 | 1.4351 | -0.0231 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 24WP | N/A | GEN-2017-040 | 1.4584 | 1.435 | -0.0234 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 29SP | N/A | CRAWFISH765 | 1.0844 | 1.06 | -0.0244 | 765 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 29SP | N/A | FWL-WND-SWYD | 1.4502 | 1.423 | -0.0272 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 00NR | 3 | 29SP | N/A | GEN-2017-040 | 1.4503 | 1.4229 | -0.0274 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 9 | 3 | 24L | N/A | BUSHLAND 3 | 1.0323 | 1.0532 | 0.0209 | 115 | 0.9 | 1.05 | N/A | P12:115:SPS:V52.1.COLTR.BSHLND
NRIS | 08NR | 3 | 24L | N/A | CROSROD2 | 1.0301 | 1.0532 | 0.0231 | 69 | 0.9 | 1.05 | N/A | P12:138:AEPW:MARSHL-4:JEFFRSN4
NRIS | 09NR | 3 | 24L | N/A | GEN-2016-087 | 1.032 | 1.0537 | 0.0217 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 09NR | 3 | 24L | N/A | GEN-2016-087 | 1.032 | 1.0537 | 0.0217 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 09NR | 3 | 24L | N/A | CAMPBELL 4 | 1.032 | 1.0537 | 0.0217 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 09NR | 3 | 24L | N/A | CAMPBELL 4 | 1.032 | 1.0537 | 0.0217 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 16NR | 3 | 24L | N/A | GLENHAM4 | 1.0328 | 1.054 | 0.0212 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 16NR | 3 | 24L | N/A | GLENHAM4 | 1.0328 | 1.054 | 0.0212 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 09NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0307 | 1.0544 | 0.0237 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 09NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0307 | 1.0544 | 0.0237 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 02NR | 3 | 24L | N/A | TIPTCTY2 | 1.035 | 1.0556 | 0.0206 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:SNYDER-2:HOBART-2
NRIS | 02NR | 3 | 24L | N/A | TIPTON 2 | 1.0351 | 1.0556 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:SNYDER-2:HOBART-2
NRIS | 02NR | 3 | 24L | N/A | TIPTE T2 | 1.0351 | 1.0557 | 0.0206 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:SNYDER-2:HOBART-2
NRIS | 02NR | 3 | 24L | N/A | FREDJC-2 | 1.036 | 1.056 | 0.02 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW-WFEC:VRNMTAP2:VERNON2
NRIS | 06NR | 3 | 24L | N/A | JERIC2WT | 1.0342 | 1.0583 | 0.0241 | 69 | 0.9 | 1.05 | N/A | P14:12.47:AEPW:W CHILDR REAC:-15.0:WC2TERT
NRIS | 06NR | 3 | 24L | N/A | MCLEAN 3 | 1.033 | 1.0585 | 0.0255 | 115 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:SHAM 2WT
NRIS | 07NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0358 | 1.0586 | 0.0228 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 07NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0358 | 1.0586 | 0.0228 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 07NR | 3 | 24L | N/A | GEN-2016-087 | 1.0372 | 1.0586 | 0.0214 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 07NR | 3 | 24L | N/A | GEN-2016-087 | 1.0372 | 1.0586 | 0.0214 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 07NR | 3 | 24L | N/A | CAMPBELL 4 | 1.0372 | 1.0586 | 0.0214 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 07NR | 3 | 24L | N/A | CAMPBELL 4 | 1.0372 | 1.0586 | 0.0214 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 06NR | 3 | 24L | N/A | HWRDWCK2 | 1.036 | 1.0586 | 0.0226 | 69 | 0.9 | 1.05 | N/A | P14:12.47:AEPW:W CHILDR REAC:-15.0:WC2TERT
NRIS | 04NR | 3 | 24L | N/A | LARAMIE_-MB3 | 1.0327 | 1.059 | 0.0263 | 345 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 2959 #: LRS IN WY. LARAMIE RIVER STATION SHUNT
NRIS | 06NR | 3 | 24L | N/A | CLARDON2 | 1.0378 | 1.0592 | 0.0214 | 69 | 0.9 | 1.05 | N/A | P14:12.47:AEPW:W CHILDR REAC:-15.0:WC2TERT
NRIS | 06NR | 3 | 24L | N/A | CLARREC2 | 1.0382 | 1.0593 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P14:12.47:AEPW:W CHILDR REAC:-15.0:WC2TERT
NRIS | 04NR | 3 | 24L | N/A | GEN-2016-087 | 1.037 | 1.0609 | 0.0239 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 04NR | 3 | 24L | N/A | GEN-2016-087 | 1.037 | 1.0609 | 0.0239 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 04NR | 3 | 24L | N/A | CAMPBELL 4 | 1.037 | 1.0609 | 0.0239 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 04NR | 3 | 24L | N/A | CAMPBELL 4 | 1.037 | 1.0609 | 0.0239 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 04NR | 3 | 24L | N/A | GLENHAM4 | 1.0404 | 1.061 | 0.0206 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 04NR | 3 | 24L | N/A | GLENHAM4 | 1.0404 | 1.061 | 0.0206 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 04NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0356 | 1.0611 | 0.0255 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 04NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0356 | 1.0611 | 0.0255 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 08NR | 3 | 24L | N/A | DAVDSON2 | 1.0389 | 1.0613 | 0.0224 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW-WFEC:VRNMTAP2:VERNON2
NRIS | 08NR | 3 | 24L | N/A | DAV TAP2 | 1.0389 | 1.0613 | 0.0224 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW-WFEC:VRNMTAP2:VERNON2
NRIS | 06NR | 3 | 24L | N/A | GLENHAM4 | 1.0373 | 1.0616 | 0.0243 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 06NR | 3 | 24L | N/A | GLENHAM4 | 1.0373 | 1.0616 | 0.0243 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 08NR | 3 | 24L | N/A | VRNMTAP2 | 1.0391 | 1.0628 | 0.0237 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW-WFEC:VRNMTAP2:VERNON2
NRIS | 06NR | 3 | 24L | N/A | GEN-2016-087 | 1.0343 | 1.0632 | 0.0289 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 06NR | 3 | 24L | N/A | GEN-2016-087 | 1.0343 | 1.0632 | 0.0289 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 06NR | 3 | 24L | N/A | CAMPBELL 4 | 1.0343 | 1.0632 | 0.0289 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 06NR | 3 | 24L | N/A | CAMPBELL 4 | 1.0343 | 1.0632 | 0.0289 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 14NR | 3 | 24L | N/A | GLENHAM4 | 1.04 | 1.0638 | 0.0238 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 14NR | 3 | 24L | N/A | GLENHAM4 | 1.04 | 1.0638 | 0.0238 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 06NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0328 | 1.0639 | 0.0311 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 06NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0328 | 1.0639 | 0.0311 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 07NR | 3 | 24L | N/A | LARAMIE_-MB3 | 1.0328 | 1.0644 | 0.0316 | 345 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 2959 #: LRS IN WY. LARAMIE RIVER STATION SHUNT
NRIS | 14NR | 3 | 24L | N/A | GEN-2016-087 | 1.0367 | 1.0646 | 0.0279 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 14NR | 3 | 24L | N/A | GEN-2016-087 | 1.0367 | 1.0646 | 0.0279 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 14NR | 3 | 24L | N/A | CAMPBELL 4 | 1.0367 | 1.0646 | 0.0279 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 14NR | 3 | 24L | N/A | CAMPBELL 4 | 1.0367 | 1.0646 | 0.0279 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 03NR | 3 | 24L | N/A | GLENHAM4 | 1.0384 | 1.0649 | 0.0265 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 03NR | 3 | 24L | N/A | GLENHAM4 | 1.0384 | 1.0649 | 0.0265 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 14NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0353 | 1.065 | 0.0297 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 14NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0353 | 1.065 | 0.0297 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 16NR | 3 | 24L | N/A | LARAMIE_-MB3 | 1.0348 | 1.0653 | 0.0305 | 345 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 2959 #: LRS IN WY. LARAMIE RIVER STATION SHUNT
NRIS | 02NR | 3 | 24L | N/A | GLENHAM4 | 1.0399 | 1.0661 | 0.0262 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 02NR | 3 | 24L | N/A | GLENHAM4 | 1.0399 | 1.0661 | 0.0262 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 03NR | 3 | 24L | N/A | GEN-2016-087 | 1.035 | 1.0662 | 0.0312 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 03NR | 3 | 24L | N/A | GEN-2016-087 | 1.035 | 1.0662 | 0.0312 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 03NR | 3 | 24L | N/A | CAMPBELL 4 | 1.0351 | 1.0662 | 0.0311 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 03NR | 3 | 24L | N/A | CAMPBELL 4 | 1.0351 | 1.0662 | 0.0311 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 12NR | 3 | 24L | N/A | GEN-2016-110 | 1.0386 | 1.0667 | 0.0281 | 345 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 2959 #: LRS IN WY. LARAMIE RIVER STATION SHUNT
NRIS | 12NR | 3 | 24L | N/A | G16-110-TAP | 1.0386 | 1.0667 | 0.0281 | 345 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 2959 #: LRS IN WY. LARAMIE RIVER STATION SHUNT
NRIS | 03NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0335 | 1.0668 | 0.0333 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 03NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0335 | 1.0668 | 0.0333 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 02NR | 3 | 24L | N/A | GEN-2016-087 | 1.0366 | 1.067 | 0.0304 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 02NR | 3 | 24L | N/A | GEN-2016-087 | 1.0366 | 1.067 | 0.0304 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 02NR | 3 | 24L | N/A | CAMPBELL 4 | 1.0366 | 1.067 | 0.0304 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 02NR | 3 | 24L | N/A | CAMPBELL 4 | 1.0366 | 1.067 | 0.0304 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 12NR | 3 | 24L | N/A | LARAMIE_-MB3 | 1.0367 | 1.0672 | 0.0305 | 345 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 2959 #: LRS IN WY. LARAMIE RIVER STATION SHUNT
NRIS | 08NR | 3 | 24L | N/A | FOREMAN2 | 1.0326 | 1.0672 | 0.0346 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:PATTERS2:NEKOOSA2
NRIS | 08NR | 3 | 24L | N/A | FOREMAG2 | 1.0326 | 1.0672 | 0.0346 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:PATTERS2:NEKOOSA2
NRIS | 01NR | 3 | 24L | N/A | GLENHAM4 | 1.0408 | 1.0672 | 0.0264 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 01NR | 3 | 24L | N/A | GLENHAM4 | 1.0408 | 1.0672 | 0.0264 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 08NR | 3 | 24L | N/A | FORMANR2 | 1.0327 | 1.0673 | 0.0346 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:PATTERS2:NEKOOSA2
NRIS | 08NR | 3 | 24L | N/A | SD.LS-LR-M32 | 1.0465 | 1.0673 | 0.0208 | 345 | 0.9 | 1.05 | N/A | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
NRIS | 08NR | 3 | 24L | N/A | SIDNEY__-MB3 | 1.0465 | 1.0673 | 0.0208 | 345 | 0.9 | 1.05 | N/A | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
NRIS | 08NR | 3 | 24L | N/A | SD.LS-KS-MB3 | 1.0465 | 1.0673 | 0.0208 | 345 | 0.9 | 1.05 | N/A | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
NRIS | 08NR | 3 | 24L | N/A | PATTERS2 | 1.0333 | 1.0675 | 0.0342 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:PATTERS2:NEKOOSA2
NRIS | 02NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0352 | 1.0675 | 0.0323 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 02NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0352 | 1.0675 | 0.0323 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 01NR | 3 | 24L | N/A | GEN-2016-087 | 1.0375 | 1.0683 | 0.0308 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 01NR | 3 | 24L | N/A | GEN-2016-087 | 1.0375 | 1.0683 | 0.0308 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 01NR | 3 | 24L | N/A | CAMPBELL 4 | 1.0375 | 1.0683 | 0.0308 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 01NR | 3 | 24L | N/A | CAMPBELL 4 | 1.0375 | 1.0683 | 0.0308 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 01NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0361 | 1.069 | 0.0329 | 230 | 0.9 | 1.05 | N/A | P14:230:UMZB:# 275 #: GH IN SD. GLENHAM LINE REACTORS
NRIS | 01NR | 3 | 24L | N/A | CAMPBL._-PP4 | 1.0361 | 1.069 | 0.0329 | 230 | 0.9 | 1.05 | N/A | P14:230:MDU::GLENHAM::SWREACT::::
NRIS | 08NR | 3 | 24L | N/A | SD.LS-LR-MB3 | 1.0463 | 1.0691 | 0.0228 | 345 | 0.9 | 1.05 | N/A | P13:230-345:NPPD:SIDNEY 3:KV2A
NRIS | 08NR | 3 | 24L | N/A | SD.LS-LR-M32 | 1.0463 | 1.0691 | 0.0228 | 345 | 0.9 | 1.05 | N/A | P13:230-345:NPPD:SIDNEY 3:KV2A
NRIS | 08NR | 3 | 24L | N/A | SIDNEY__-MB3 | 1.0463 | 1.0691 | 0.0228 | 345 | 0.9 | 1.05 | N/A | P13:230-345:NPPD:SIDNEY 3:KV2A
NRIS | 08NR | 3 | 24L | N/A | SD.LS-KS-MB3 | 1.0463 | 1.0691 | 0.0228 | 345 | 0.9 | 1.05 | N/A | P13:230-345:NPPD:SIDNEY 3:KV2A
NRIS | 08NR | 3 | 24L | N/A | ASHDOWN2 | 1.0344 | 1.0695 | 0.0351 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:PATTERS2:NEKOOSA2
NRIS | 08NR | 3 | 24L | N/A | HOLOX 2 | 1.0348 | 1.0709 | 0.0361 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:PATTERS2:NEKOOSA2
NRIS | 08NR | 3 | 24L | N/A | NEKOSAT2 | 1.0349 | 1.0709 | 0.036 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:PATTERS2:NEKOOSA2
NRIS | 08NR | 3 | 24L | N/A | G16-034-TAP | 1.0481 | 1.0721 | 0.024 | 345 | 0.9 | 1.05 | N/A | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
NRIS | 08NR | 3 | 24L | N/A | GEN-2016-034 | 1.0481 | 1.0721 | 0.024 | 345 | 0.9 | 1.05 | N/A | P42:345:UMZB:# 2496 #: SDQ IN NE. STUCK BREAKER (2796)
NRIS | 12NR | 3 | 24L | N/A | PRY-JCT3 | 1.042 | 1.0722 | 0.0302 | 115 | 0.9 | 1.05 | N/A | P12:115:GRDA-AEPW:KERRGR3:PRY-JCT3
NRIS | 08NR | 3 | 24L | N/A | SAWMILL2 | 1.0505 | 1.0724 | 0.0219 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:BECKVIL2:POYNTER2
NRIS | 08NR | 3 | 24L | N/A | NLANVIL2 | 1.052 | 1.0739 | 0.0219 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:BECKVIL2:POYNTER2
NRIS | 08NR | 3 | 24L | N/A | PALINE PL 2 | 1.0521 | 1.074 | 0.0219 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:BECKVIL2:POYNTER2
NRIS | 08NR | 3 | 24L | N/A | G16-034-TAP | 1.0493 | 1.0741 | 0.0248 | 345 | 0.9 | 1.05 | N/A | P13:230-345:NPPD:SIDNEY 3:KV2A
NRIS | 08NR | 3 | 24L | N/A | GEN-2016-034 | 1.0493 | 1.0741 | 0.0248 | 345 | 0.9 | 1.05 | N/A | P13:230-345:NPPD:SIDNEY 3:KV2A
NRIS | 08NR | 3 | 24L | N/A | FEARSCO2 | 1.0522 | 1.0741 | 0.0219 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:BECKVIL2:POYNTER2
NRIS | 08NR | 3 | 24L | N/A | LOCKESB2 | 1.0366 | 1.0753 | 0.0387 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::ASHDWN_W 4:PATTERS4!:1
NRIS | 10NR | 3 | 24L | N/A | BASELIN4 | 1.0485 | 1.0759 | 0.0274 | 138 | 0.9 | 1.05 | N/A | P12:138:WFEC:BASELN_LOCO_PAOLI
NRIS | 12NR | 3 | 24L | N/A | BASELIN4 | 1.0472 | 1.0765 | 0.0293 | 138 | 0.9 | 1.05 | N/A | P12:138:WFEC:BASELN_LOCO_PAOLI
NRIS | 08NR | 3 | 24L | N/A | EVENSID2 | 1.0565 | 1.0783 | 0.0218 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:BECKVIL2:POYNTER2
NRIS | 08NR | 3 | 24L | N/A | POYNTER2 | 1.0571 | 1.0789 | 0.0218 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:BECKVIL2:POYNTER2
NRIS | 08NR | 3 | 24L | N/A | NWHENDR2 | 1.0574 | 1.0792 | 0.0218 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:BECKVIL2:POYNTER2
NRIS | 06NR | 3 | 24L | N/A | RSS T2 4 | 1.0593 | 1.0793 | 0.02 | 138 | 0.9 | 1.05 | N/A | P12:138:AEPW:R.S.S.-4:RSST24
NRIS | 06NR | 3 | 24L | N/A | RSS T1 4 | 1.0593 | 1.0793 | 0.02 | 138 | 0.9 | 1.05 | N/A | P12:138:AEPW:RSST14:R.S.S.-4
NRIS | 08NR | 3 | 24L | N/A | NWHENDR2 | 1.0582 | 1.0802 | 0.022 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:NROGERS2:ECNTRTN2
NRIS | 08NR | 3 | 24L | N/A | COVEREC2 | 1.0402 | 1.0804 | 0.0402 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::ASHDWN_W 4:PATTERS4!:1
NRIS | 04NR | 3 | 24L | N/A | RSS T2 4 | 1.0567 | 1.0815 | 0.0248 | 138 | 0.9 | 1.05 | N/A | P12:138:AEPW:R.S.S.-4:RSST24
NRIS | 04NR | 3 | 24L | N/A | RSS T1 4 | 1.0568 | 1.0815 | 0.0247 | 138 | 0.9 | 1.05 | N/A | P12:138:AEPW:RSST14:R.S.S.-4
NRIS | 08NR | 3 | 24L | N/A | WICKES 2 | 1.0453 | 1.0856 | 0.0403 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::ASHDWN_W 4:PATTERS4!:1
NRIS | 08NR | 3 | 24L | N/A | GRANNIS 2 | 1.0468 | 1.0871 | 0.0403 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::ASHDWN_W 4:PATTERS4!:1
NRIS | 08NR | 3 | 24L | N/A | DEQUEEN 2 | 1.0463 | 1.0877 | 0.0414 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::ASHDWN_W 4:PATTERS4!:1
NRIS | 08NR | 3 | 24L | N/A | ASHDOWN2 | 1.0352 | 1.0879 | 0.0527 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:ASHDOWN2:PATTERS2
NRIS | 08NR | 3 | 24L | N/A | HOLOX 2 | 1.0354 | 1.0881 | 0.0527 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:ASHDOWN2:PATTERS2
NRIS | 08NR | 3 | 24L | N/A | NEKOSAT2 | 1.0355 | 1.0882 | 0.0527 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:ASHDOWN2:PATTERS2
NRIS | 08NR | 3 | 24L | N/A | SEMINOL7 | 1.0475 | 1.0904 | 0.0429 | 345 | 0.9 | 1.05 | N/A | P42:345:SPS:CROSSROADS_6R30_19L
NRIS | 08NR | 3 | 24L | N/A | PLEASHL2 | 1.0461 | 1.091 | 0.0449 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:TEXARK2:TEX12ST2
NRIS | 08NR | 3 | 24L | N/A | S_TEXARK 2 | 1.0462 | 1.091 | 0.0448 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:TEXARK2:TEX12ST2
NRIS | 08NR | 3 | 24L | N/A | TEXARK 2 | 1.0442 | 1.0941 | 0.0499 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:TEXARK2:TEX12ST2
NRIS | 08NR | 3 | 24L | N/A | SUGHLET2 | 1.0413 | 1.0943 | 0.053 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:ASHDOWN2:TEX12ST2
NRIS | 08NR | 3 | 24L | N/A | SETEXAR2 | 1.0444 | 1.0945 | 0.0501 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:TEXARK2:TEX12ST2
NRIS | 08NR | 3 | 24L | N/A | DEQUEEN2 | 1.0548 | 1.095 | 0.0402 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::ASHDWN_W 4:PATTERS4!:1
NRIS | 08NR | 3 | 24L | N/A | SETEXAR2 | 1.0443 | 1.098 | 0.0537 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:SETEXAR2:TEXARK 2
NRIS | 08NR | 3 | 24L | N/A | GEN-2016-123 | 1.0903 | 1.1127 | 0.0224 | 345 | 0.9 | 1.05 | N/A | P12:345:SPS:J15.1.XRDS.TOLK
NRIS | 08NR | 3 | 24L | N/A | GEN-2017-078 | 1.0903 | 1.1127 | 0.0224 | 345 | 0.9 | 1.05 | N/A | P12:345:SPS:J15.1.XRDS.TOLK
NRIS | 08NR | 3 | 24L | N/A | RSVLT_CC_W 7 | 1.0852 | 1.1128 | 0.0276 | 345 | 0.9 | 1.05 | N/A | P12:345:SPS:J15.1.XRDS.TOLK
NRIS | 08NR | 3 | 24L | N/A | CROSSROADS 7 | 1.0903 | 1.1128 | 0.0225 | 345 | 0.9 | 1.05 | N/A | P12:345:SPS:J15.1.XRDS.TOLK
NRIS | 08NR | 3 | 24L | N/A | RSVLT_CC_E 7 | 1.0877 | 1.1129 | 0.0252 | 345 | 0.9 | 1.05 | N/A | P12:345:SPS:J15.1.XRDS.TOLK
NRIS | 08NR | 3 | 24L | N/A | SEMINOLE765 | 1.0752 | 1.1192 | 0.044 | 765 | 0.9 | 1.05 | N/A | P42:345:SPS:CROSSROADS_6R30_19L
NRIS | 08NR | 3 | 24L | N/A | CROSSRDS765 | 1.0974 | 1.1192 | 0.0218 | 765 | 0.9 | 1.05 | N/A | P12:345:SPS:J15.1.XRDS.TOLK
NRIS | 08NR | 3 | 24L | N/A | CDSEMMID | 1.1151 | 1.1607 | 0.0456 | 765 | 0.9 | 1.05 | N/A | P42:345:SPS:CROSSROADS_6R30_19L
NRIS | 08NR | 3 | 24L | N/A | BORDER 7 | 1.0305 | 1.1612 | 0.1307 | 345 | 0.9 | 1.05 | N/A | P43:345:SPS:TUCO:NR20_19L
NRIS | 08NR | 3 | 24L | N/A | CRAWFISH765 | 1.1588 | 1.2062 | 0.0474 | 765 | 0.9 | 1.05 | N/A | P42:345:SPS:CROSSROADS_6R30_19L
NRIS | 08NR | 3 | 24L | N/A | CROSSRDS765 | 1.181 | 1.2293 | 0.0483 | 765 | 0.9 | 1.05 | N/A | P42:345:SPS:CROSSROADS_6R30_19L
NRIS | 15NR | 3 | 24L | N/A | OGMARTN2 | 1.0798 | 1.0543 | -0.0255 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 15NR | 3 | 24L | N/A | DX----E2 | 1.0798 | 1.0544 | -0.0254 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 15NR | 3 | 24L | N/A | WILLPIP2 | 1.0798 | 1.0544 | -0.0254 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 15NR | 3 | 24L | N/A | T.P.S.-2 | 1.0822 | 1.0568 | -0.0254 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 15NR | 3 | 24L | N/A | MUSKOGE7 | 1.0836 | 1.0619 | -0.0217 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 15NR | 3 | 24L | N/A | T.S.E.-2 | 1.0858 | 1.0628 | -0.023 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 15NR | 3 | 24L | N/A | FIREWHL-TAP | 1.1218 | 1.1006 | -0.0212 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 15NR | 3 | 24L | N/A | G17-092-SWYD | 1.1235 | 1.1023 | -0.0212 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 15NR | 3 | 24L | N/A | GEN-2017-092 | 1.1236 | 1.1021 | -0.0215 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 15NR | 3 | 24L | N/A | FWL-WND-SWYD | 1.4821 | 1.4467 | -0.0354 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 15NR | 3 | 24L | N/A | GEN-2017-040 | 1.4823 | 1.4466 | -0.0357 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | BLCOKRT2 | 1.03 | 1.0503 | 0.0203 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | ZONE-4 SUB | 1.0303 | 1.0516 | 0.0213 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | ZONE-2 SUB | 1.0305 | 1.0522 | 0.0217 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | ZONE-1 SUB | 1.0305 | 1.0522 | 0.0217 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | ZONE-6 SUB | 1.0307 | 1.0522 | 0.0215 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | GILL 2 | 1.0309 | 1.0512 | 0.0203 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | GILLT 2 | 1.0313 | 1.0516 | 0.0203 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | LOCKESB2 | 1.0313 | 1.067 | 0.0357 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | USMOTOR2 | 1.0318 | 1.0595 | 0.0277 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | BLOCKER2 | 1.032 | 1.0522 | 0.0202 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | DALLAS 2 | 1.032 | 1.0595 | 0.0275 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | BLOCKRT2 | 1.0326 | 1.0528 | 0.0202 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | AVINGER2 | 1.0328 | 1.0628 | 0.03 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | USMOTAP2 | 1.0329 | 1.0606 | 0.0277 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | WASHST 2 | 1.0334 | 1.0813 | 0.0479 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | MENA 2 | 1.0338 | 1.0616 | 0.0278 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | MENA 2 | 1.0338 | 1.0616 | 0.0278 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | TEX12ST2 | 1.034 | 1.0819 | 0.0479 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | DEQUEEN 2 | 1.0342 | 1.0727 | 0.0385 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | BLOOMBG2 | 1.0346 | 1.0715 | 0.0369 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | COVEREC2 | 1.0348 | 1.065 | 0.0302 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | NMARSHL2 | 1.0349 | 1.0561 | 0.0212 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | RODESSA2 | 1.035 | 1.0641 | 0.0291 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | GODFREYRDTP2 | 1.035 | 1.064 | 0.029 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | STEEL 2 | 1.0352 | 1.0651 | 0.0299 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | ORECITY2 | 1.0352 | 1.0652 | 0.03 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | ATLANTA2 | 1.0353 | 1.0705 | 0.0352 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | MARAUTO2 | 1.0354 | 1.0564 | 0.021 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | MARSHAL2 | 1.0354 | 1.0564 | 0.021 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | WOODLWN2 | 1.0355 | 1.056 | 0.0205 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | SUGHLET2 | 1.0357 | 1.0836 | 0.0479 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | EASTMNT2 | 1.0358 | 1.0657 | 0.0299 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | WICKES 2 | 1.0361 | 1.0691 | 0.033 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | WATLANT2 | 1.0363 | 1.0698 | 0.0335 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | REDRVR-2 | 1.0363 | 1.0821 | 0.0458 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | GRANNIS 2 | 1.0365 | 1.0704 | 0.0339 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | COOKVIL2 | 1.0366 | 1.0606 | 0.024 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | COOKVTP2 | 1.0366 | 1.0606 | 0.024 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | GLENWOD2 | 1.0366 | 1.0665 | 0.0299 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | SUGARHL2 | 1.0367 | 1.0848 | 0.0481 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | JEFFRSN2 | 1.037 | 1.0573 | 0.0203 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | TEXARK 2 | 1.0374 | 1.085 | 0.0476 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | LINDEN 2 | 1.0374 | 1.0686 | 0.0312 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | IPC 2 | 1.0374 | 1.0788 | 0.0414 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | IPC TAP2 | 1.0376 | 1.0789 | 0.0413 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | SUGHLWT2 | 1.0376 | 1.0854 | 0.0478 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | BETHLHM2 | 1.0377 | 1.0675 | 0.0298 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | NW_TEXAR 2 | 1.0378 | 1.0863 | 0.0485 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | SETEXAR2 | 1.0378 | 1.0857 | 0.0479 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | RICHMND2 | 1.0379 | 1.0867 | 0.0488 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | TAYLOR 2 | 1.0379 | 1.0854 | 0.0475 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | TEXOPER2 | 1.0382 | 1.0865 | 0.0483 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | NEWBOST2 | 1.0383 | 1.0828 | 0.0445 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | REDLICK2 | 1.0384 | 1.088 | 0.0496 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | KINGHWY2 | 1.0384 | 1.0873 | 0.0489 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | NNBOSTN2 | 1.0384 | 1.0832 | 0.0448 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | LSORD 2 | 1.0385 | 1.086 | 0.0475 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | TEX39ST2 | 1.0386 | 1.0854 | 0.0468 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | BANN 2 | 1.0387 | 1.0887 | 0.05 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | DEQUEEN2 | 1.0387 | 1.0768 | 0.0381 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | LSORDTP2 | 1.039 | 1.0865 | 0.0475 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | BUFORDR2 | 1.0391 | 1.0664 | 0.0273 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | DAINGER2 | 1.0391 | 1.0614 | 0.0223 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | NAPLES 2 | 1.0392 | 1.0664 | 0.0272 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | JENKNST2 | 1.0392 | 1.0618 | 0.0226 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | HOOKS 2 | 1.0392 | 1.0858 | 0.0466 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | DIAN 2 | 1.0393 | 1.0691 | 0.0298 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | HOSSTON2 | 1.0401 | 1.063 | 0.0229 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | GEN-2017-057 | 1.0401 | 1.063 | 0.0229 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | HNDRSNR2 | 1.0402 | 1.0607 | 0.0205 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | PLEASHL2 | 1.0403 | 1.083 | 0.0427 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | S_TEXARK 2 | 1.0403 | 1.0831 | 0.0428 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | JENKINS2 | 1.0405 | 1.0627 | 0.0222 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | VIVIAN 2 | 1.0409 | 1.0623 | 0.0214 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | GILLIAM2 | 1.041 | 1.0626 | 0.0216 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | BELCHER2 | 1.041 | 1.0626 | 0.0216 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | HUGHES 2 | 1.0418 | 1.0651 | 0.0233 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | AIRPRD-2 | 1.0422 | 1.0641 | 0.0219 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | AIRPRDT2 | 1.0422 | 1.0641 | 0.0219 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | LETRNST2 | 1.0423 | 1.0654 | 0.0231 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | HALLSVL2 | 1.0425 | 1.0645 | 0.022 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | LSREC 2 | 1.0427 | 1.0649 | 0.0222 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | LSTARTP2 | 1.043 | 1.0647 | 0.0217 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | LONSTAR2 | 1.0433 | 1.065 | 0.0217 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | LETOURN2 | 1.0434 | 1.0666 | 0.0232 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | SAWMILL2 | 1.0437 | 1.0653 | 0.0216 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | MVLONG 2 | 1.0437 | 1.0649 | 0.0212 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | LSSOUTH2 | 1.0441 | 1.0656 | 0.0215 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | BIG 3 2 | 1.0447 | 1.0678 | 0.0231 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | NLANVIL2 | 1.0451 | 1.0668 | 0.0217 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | PALINE PL 2 | 1.0453 | 1.0669 | 0.0216 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | FEARSCO2 | 1.0453 | 1.067 | 0.0217 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | NETTLTN2 | 1.0456 | 1.0667 | 0.0211 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | BIG3TAP2 | 1.0458 | 1.0688 | 0.023 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | AIRLINE2 | 1.0464 | 1.0694 | 0.023 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | NETTLTP2 | 1.0464 | 1.0676 | 0.0212 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | GREGGTN2 | 1.0465 | 1.0683 | 0.0218 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | LONGVHT2 | 1.0466 | 1.0693 | 0.0227 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | LLAMOND2 | 1.0467 | 1.0699 | 0.0232 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | GATES 2 | 1.0472 | 1.0703 | 0.0231 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | LONGVUE2 | 1.0478 | 1.0708 | 0.023 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | LETOURT2 | 1.048 | 1.071 | 0.023 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | SABINE 2 | 1.0482 | 1.0684 | 0.0202 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | SELONGV2 | 1.0482 | 1.071 | 0.0228 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | WHITNEY2 | 1.0486 | 1.0715 | 0.0229 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | MONROCR2 | 1.0494 | 1.0711 | 0.0217 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | POYNTER2 | 1.0496 | 1.0711 | 0.0215 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | EVENSID2 | 1.0497 | 1.0712 | 0.0215 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | KILGORE2 | 1.0498 | 1.0704 | 0.0206 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | DEKALB 2 | 1.051 | 1.0846 | 0.0336 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | NWHENDR2 | 1.0518 | 1.0733 | 0.0215 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | KNOXLEE2 | 1.0518 | 1.0742 | 0.0224 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | TURNERT2 | 1.0553 | 1.0756 | 0.0203 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | OVERTON2 | 1.0555 | 1.0758 | 0.0203 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | T.S.E.-2 | 1.0742 | 1.0516 | -0.0226 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | FWL-WND-SWYD | 1.4634 | 1.4111 | -0.0523 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 08NR | 3 | 24L | N/A | GEN-2017-040 | 1.4636 | 1.41 | -0.0536 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | SAPLPRD4 | 1.0377 | 1.0579 | 0.0202 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | JENKS--4 | 1.0419 | 1.0627 | 0.0208 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | KIMCLRK4 | 1.0425 | 1.063 | 0.0205 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | 52DEL-W4 | 1.0426 | 1.0632 | 0.0206 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | S HILLW4 | 1.0427 | 1.0633 | 0.0206 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | 136YALE4 | 1.0428 | 1.0633 | 0.0205 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | 52DELWT4 | 1.0428 | 1.0634 | 0.0206 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | WAREN-W4 | 1.0435 | 1.0641 | 0.0206 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | 81YALES4 | 1.0436 | 1.0641 | 0.0205 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | 96YALE-4 | 1.0436 | 1.0641 | 0.0205 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | S.HIL E4 | 1.0437 | 1.064 | 0.0203 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | SHILETP4 | 1.0438 | 1.064 | 0.0202 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | WARNTAP4 | 1.0438 | 1.0644 | 0.0206 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | ORU W4 | 1.0439 | 1.0644 | 0.0205 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | ORU-WTP4 | 1.044 | 1.0645 | 0.0205 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | ORU E4 | 1.0442 | 1.065 | 0.0208 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | ORU ETP4 | 1.0443 | 1.0651 | 0.0208 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | 116JENK4 | 1.0445 | 1.0656 | 0.0211 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | R.S.S.-4 | 1.0453 | 1.0665 | 0.0212 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | RSS T2 4 | 1.0465 | 1.0683 | 0.0218 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | RSS T1 4 | 1.0466 | 1.0685 | 0.0219 | 138 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | OGMARTN2 | 1.0609 | 1.0809 | 0.02 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | DX----E2 | 1.0609 | 1.0809 | 0.02 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | WILLPIP2 | 1.0609 | 1.0809 | 0.02 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 07NR | 3 | 24L | N/A | T.P.S.-2 | 1.0633 | 1.0833 | 0.02 | 69 | 0.9 | 1.05 | N/A | Base Case
NRIS | 06NR | 3 | 24L | N/A | G16133_765R2 | 1.031 | 1.0572 | 0.0262 | 765 | 0.9 | 1.05 | N/A | Base Case
NRIS | 06NR | 3 | 24L | N/A | FWL-WND-SWYD | 1.483 | 1.4586 | -0.0244 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 06NR | 3 | 24L | N/A | GEN-2017-040 | 1.4831 | 1.4585 | -0.0246 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 17NR | 3 | 20G | N/A | FLANDRU7 | 1.0439 | 1.0723 | 0.0284 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | HOLLAND -LO7 | 1.0474 | 1.0756 | 0.0282 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | WARD-ER8 | 1.0512 | 1.0804 | 0.0292 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | EGAN-ER8 | 1.0538 | 1.0833 | 0.0295 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | FLANDRU8 | 1.0544 | 1.0834 | 0.029 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | SW234-ER8 | 1.0544 | 1.0834 | 0.029 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | WENTWRTH-ER8 | 1.0554 | 1.0856 | 0.0302 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | AURORAIP-ER7 | 1.0554 | 1.0756 | 0.0202 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | SW209-ER8 | 1.0555 | 1.0849 | 0.0294 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | COLEMAN-ER8 | 1.0561 | 1.0859 | 0.0298 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | MOS-LKV2-ER8 | 1.0562 | 1.0869 | 0.0307 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | AURORA 7 | 1.0564 | 1.0766 | 0.0202 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | MOS-CLMN-ER8 | 1.0572 | 1.0869 | 0.0297 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | RUTLAND-ER8 | 1.0577 | 1.0877 | 0.03 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | MADISON-ER8 | 1.0582 | 1.0888 | 0.0306 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | MOS-FLDT-ER8 | 1.0582 | 1.0888 | 0.0306 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | MOS-WTWR-ER8 | 1.0583 | 1.0884 | 0.0301 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | SW211-ER8 | 1.059 | 1.089 | 0.03 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 17NR | 3 | 20G | N/A | MOS-LKV1-ER8 | 1.0592 | 1.0898 | 0.0306 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 127 #: BR IN SD. BR-WHT LINE FAULT
NRIS | 15NR | 3 | 20G | N/A | EDWRDVL5 | 1.0379 | 1.0634 | 0.0255 | 161 | 0.9 | 1.05 | N/A | P12:161:KACY:EDWARDSVILLE-METRO::EDWARDSVILLE-METRO OPEN
NRIS | 15NR | 3 | 20G | N/A | EDWRDVL5 | 1.0379 | 1.0634 | 0.0255 | 161 | 0.9 | 1.05 | N/A | P12:161:WERE:EDWV-KCBPU_161::
NRIS | 8 | 3 | 20G | N/A | EDWRDVL5 | 1.0427 | 1.119 | 0.0763 | 161 | 0.9 | 1.05 | N/A | P12:161:KACY:EDWARDSVILLE-METRO::EDWARDSVILLE-METRO OPEN
NRIS | 8 | 3 | 20G | N/A | EDWRDVL5 | 1.0427 | 1.119 | 0.0763 | 161 | 0.9 | 1.05 | N/A | P12:161:WERE:EDWV-KCBPU_161::
NRIS | 15NR | 3 | 20G | N/A | RCDC.DUM-BE4 | 1.0451 | 1.0677 | 0.0226 | 230 | 0.9 | 1.05 | N/A | Base Case
NRIS | 8 | 3 | 20G | N/A | FTRANDL7 | 1.0328 | 1.0528 | 0.02 | 115 | 0.9 | 1.05 | N/A | Base Case
NRIS | 8 | 3 | 20G | N/A | FTRANDL4 | 1.0348 | 1.0552 | 0.0204 | 230 | 0.9 | 1.05 | N/A | Base Case
NRIS | 8 | 3 | 20G | N/A | FWL-WND-SWYD | 1.4677 | 1.4132 | -0.0545 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 8 | 3 | 20G | N/A | GEN-2017-040 | 1.4678 | 1.4121 | -0.0557 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 6 | 3 | 20G | N/A | C-RIVER7 | 1.0806 | 1.0601 | -0.0205 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 6 | 3 | 20G | N/A | FIREWHL-TAP | 1.1133 | 1.093 | -0.0203 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 6 | 3 | 20G | N/A | G17-092-SWYD | 1.115 | 1.0946 | -0.0204 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 6 | 3 | 20G | N/A | GEN-2017-092 | 1.115 | 1.0945 | -0.0205 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 6 | 3 | 20G | N/A | FWL-WND-SWYD | 1.4709 | 1.4365 | -0.0344 | 345 | 0.9 | 1.05 | N/A | Base Case
NRIS | 6 | 3 | 20G | N/A | GEN-2017-040 | 1.471 | 1.4365 | -0.0345 | 345 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | GEN-2017-007 | 1.0399 | 1.065 | 0.0251 | 230 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | PLSNT_HILL 6 | 1.0377 | 1.0627 | 0.025 | 230 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | SUGHLET2 | 1.0322 | 1.0557 | 0.0235 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | BANN 2 | 1.0384 | 1.0619 | 0.0235 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | SUGARHL2 | 1.0334 | 1.0569 | 0.0235 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | NW_TEXAR 2 | 1.0354 | 1.0589 | 0.0235 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | RICHMND2 | 1.0359 | 1.0594 | 0.0235 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | REDLICK2 | 1.0376 | 1.0611 | 0.0235 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | SUGHLWT2 | 1.0343 | 1.0577 | 0.0234 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | TEX39ST2 | 1.0345 | 1.0579 | 0.0234 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | KINGHWY2 | 1.0369 | 1.0603 | 0.0234 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | TEXOPER2 | 1.0359 | 1.0593 | 0.0234 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | WASHST 2 | 1.0305 | 1.0538 | 0.0233 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | TEX12ST2 | 1.0309 | 1.0542 | 0.0233 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | TAYLOR 2 | 1.0347 | 1.058 | 0.0233 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | SETEXAR2 | 1.0353 | 1.0584 | 0.0231 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | TEXARK 2 | 1.0347 | 1.0577 | 0.023 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | LSORD 2 | 1.0376 | 1.0602 | 0.0226 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | LSORDTP2 | 1.0381 | 1.0607 | 0.0226 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | DEQUEEN2 | 1.0331 | 1.0556 | 0.0225 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | HOOKS 2 | 1.0381 | 1.0604 | 0.0223 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | ECENT_1 2 | 1.0327 | 1.0548 | 0.0221 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | ECENT_2 2 | 1.0327 | 1.0548 | 0.0221 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | REDRVR-2 | 1.0358 | 1.0576 | 0.0218 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | NNBOSTN2 | 1.0386 | 1.0599 | 0.0213 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | NEWBOST2 | 1.0383 | 1.0595 | 0.0212 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | PLEASHL2 | 1.037 | 1.0579 | 0.0209 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | S_TEXARK 2 | 1.037 | 1.0579 | 0.0209 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | IPC 2 | 1.0365 | 1.0562 | 0.0197 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 08NR | 3 | 24L | N/A | IPC TAP2 | 1.0367 | 1.0563 | 0.0196 | 69 | 0.9 | 1.05 | N/A | Base Case
ERIS | 03NR | 3 | 29SP | N/A | COLBY 3 | 0.9195 | 0.8979 | 0.0216 | 115 | 0.9 | 1.05 | N/A | P12:115:SUNC-MIDW:MINGO-COLBY::
ERIS | 03NR | 3 | 29SP | N/A | COLBY 3 | 0.9195 | 0.8979 | 0.0216 | 115 | 0.9 | 1.05 | N/A | P12:115:MIDW-SUNC:COLBY-MINGO
ERIS | 04NR | 3 | 29SP | N/A | COLBY 3 | 0.9185 | 0.8934 | 0.0251 | 115 | 0.9 | 1.05 | N/A | P12:115:SUNC-MIDW:MINGO-COLBY::
ERIS | 04NR | 3 | 29SP | N/A | LOAD | 0.9196 | 0.8959 | 0.0237 | 115 | 0.9 | 1.05 | N/A | P12:115:SUNC-MIDW:MINGO-COLBY::
ERIS | 04NR | 3 | 29SP | N/A | COLBY 3 | 0.9185 | 0.8934 | 0.0251 | 115 | 0.9 | 1.05 | N/A | P12:115:MIDW-SUNC:COLBY-MINGO
ERIS | 04NR | 3 | 29SP | N/A | LOAD | 0.9196 | 0.8959 | 0.0237 | 115 | 0.9 | 1.05 | N/A | P12:115:MIDW-SUNC:COLBY-MINGO
ERIS | 08NR | 3 | 19WP | N/A | DAKOTA_5 | 0.8883 | 0.8626 | 0.0257 | 161 | 0.9 | 1.05 | N/A | P12:161:WERE:MARM-KCPL_161::FUTURE
ERIS | 08NR | 3 | 19WP | N/A | CNTRVIL5 | 0.9057 | 0.8841 | 0.0216 | 161 | 0.9 | 1.05 | N/A | P12:161:WERE:MARM-KCPL_161::FUTURE
ERIS | 08NR | 3 | 29SP | N/A | LECOMPTE 2 | 0.9012 | 0.8804 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | GALLOWAY 2 | 0.9044 | 0.8837 | 0.0207 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | BLACKMAN 2 | 0.9043 | 0.8839 | 0.0204 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | INGRAM 2 | 0.9051 | 0.8847 | 0.0204 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | PACKER 2 | 0.9055 | 0.885 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | KICKAPOO 2 | 0.9069 | 0.8858 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | S HWY 65 2 | 0.907 | 0.8862 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | NEERGARD 2 | 0.907 | 0.8862 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | HIGHWAY M 2 | 0.9071 | 0.8866 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | SEMINOLE 2 | 0.9078 | 0.8867 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | CHAD 2 | 0.9076 | 0.8872 | 0.0204 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | TWIN OAKS 2 | 0.9084 | 0.8873 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | MONROE 2 | 0.9082 | 0.8874 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | SUNSET 2 | 0.9088 | 0.8878 | 0.021 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | GRAND 2 | 0.9091 | 0.8884 | 0.0207 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | HARGISS 2 | 0.9089 | 0.8884 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | FORT 2 | 0.9099 | 0.8888 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | COX 2 | 0.9116 | 0.8905 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | MILL 2 | 0.9109 | 0.8908 | 0.0201 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | JAMES RIVER2 | 0.9137 | 0.8932 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | DAYTON 2 | 0.9152 | 0.8942 | 0.021 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | WASHINGTON 2 | 0.9152 | 0.8946 | 0.0206 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | MAIN STREET2 | 0.9151 | 0.8947 | 0.0204 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | PLAINVIEW 2 | 0.9159 | 0.8949 | 0.021 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | GOLDEN 2 | 0.9163 | 0.8953 | 0.021 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | BATTLEFIELD2 | 0.9168 | 0.8959 | 0.0209 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | NORTON 2 | 0.917 | 0.8962 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | N HWY13 2 | 0.9188 | 0.8977 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | JRPS 69B-2 2 | 0.9193 | 0.8984 | 0.0209 | 69 | 0.9 | 1.05 | N/A | P52:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | LECOMPTE 2 | 0.9012 | 0.8804 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | GALLOWAY 2 | 0.9044 | 0.8837 | 0.0207 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | BLACKMAN 2 | 0.9043 | 0.8839 | 0.0204 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | INGRAM 2 | 0.9051 | 0.8847 | 0.0204 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | PACKER 2 | 0.9055 | 0.885 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | KICKAPOO 2 | 0.9069 | 0.8858 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | S HWY 65 2 | 0.907 | 0.8862 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | NEERGARD 2 | 0.907 | 0.8862 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | HIGHWAY M 2 | 0.9071 | 0.8866 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | SEMINOLE 2 | 0.9078 | 0.8867 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | CHAD 2 | 0.9076 | 0.8872 | 0.0204 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | TWIN OAKS 2 | 0.9084 | 0.8873 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | MONROE 2 | 0.9082 | 0.8874 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | SUNSET 2 | 0.9088 | 0.8878 | 0.021 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | GRAND 2 | 0.9091 | 0.8884 | 0.0207 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | HARGISS 2 | 0.9089 | 0.8884 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | FORT 2 | 0.9099 | 0.8888 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | COX 2 | 0.9116 | 0.8905 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | MILL 2 | 0.9109 | 0.8908 | 0.0201 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | JAMES RIVER2 | 0.9137 | 0.8932 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | DAYTON 2 | 0.9152 | 0.8942 | 0.021 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | WASHINGTON 2 | 0.9152 | 0.8946 | 0.0206 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | MAIN STREET2 | 0.9151 | 0.8947 | 0.0204 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | PLAINVIEW 2 | 0.9159 | 0.8949 | 0.021 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | GOLDEN 2 | 0.9163 | 0.8953 | 0.021 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | BATTLEFIELD2 | 0.9168 | 0.8959 | 0.0209 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | NORTON 2 | 0.917 | 0.8962 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | N HWY13 2 | 0.9188 | 0.8977 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | JRPS 69B-2 2 | 0.9193 | 0.8984 | 0.0209 | 69 | 0.9 | 1.05 | N/A | P42:345:SPRM-AECI:STUCK BKR SIM17
ERIS | 08NR | 3 | 29SP | N/A | LECOMPTE 2 | 0.9012 | 0.8804 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | GALLOWAY 2 | 0.9044 | 0.8837 | 0.0207 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | BLACKMAN 2 | 0.9043 | 0.8839 | 0.0204 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | INGRAM 2 | 0.9051 | 0.8847 | 0.0204 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | PACKER 2 | 0.9055 | 0.885 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | KICKAPOO 2 | 0.9069 | 0.8858 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | S HWY 65 2 | 0.907 | 0.8862 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | NEERGARD 2 | 0.907 | 0.8862 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | HIGHWAY M 2 | 0.9071 | 0.8866 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | SEMINOLE 2 | 0.9078 | 0.8867 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | CHAD 2 | 0.9076 | 0.8872 | 0.0204 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | TWIN OAKS 2 | 0.9084 | 0.8873 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | MONROE 2 | 0.9082 | 0.8874 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | SUNSET 2 | 0.9088 | 0.8878 | 0.021 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | GRAND 2 | 0.9091 | 0.8884 | 0.0207 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | HARGISS 2 | 0.9089 | 0.8884 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | FORT 2 | 0.9099 | 0.8888 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | COX 2 | 0.9116 | 0.8905 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | MILL 2 | 0.9109 | 0.8908 | 0.0201 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | JAMES RIVER2 | 0.9137 | 0.8932 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | DAYTON 2 | 0.9152 | 0.8942 | 0.021 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | WASHINGTON 2 | 0.9152 | 0.8946 | 0.0206 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | MAIN STREET2 | 0.9151 | 0.8947 | 0.0204 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | PLAINVIEW 2 | 0.9159 | 0.8949 | 0.021 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | GOLDEN 2 | 0.9163 | 0.8953 | 0.021 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | BATTLEFIELD2 | 0.9168 | 0.8959 | 0.0209 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | NORTON 2 | 0.917 | 0.8962 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | N HWY13 2 | 0.9188 | 0.8977 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | JRPS 69B-2 2 | 0.9193 | 0.8984 | 0.0209 | 69 | 0.9 | 1.05 | N/A | P22:345:SPRM-AECI:17
ERIS | 08NR | 3 | 29SP | N/A | SSLINC2 | 0.8912 | 0.8717 | 0.0195 | 69 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | SSNORT2 | 0.8918 | 0.8722 | 0.0196 | 69 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | SSNEWN2 | 0.895 | 0.8755 | 0.0195 | 69 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | TONTITN7 | 0.9115 | 0.8918 | 0.0197 | 345 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | SPRDALE2 | 0.9124 | 0.8925 | 0.0199 | 69 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | SPRDALT2 | 0.9138 | 0.894 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | DYESS 2 | 0.9142 | 0.8944 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | BENT_SL5 | 0.9157 | 0.8961 | 0.0196 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | BENTVJ_5 | 0.9157 | 0.8961 | 0.0196 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | BEN279_5 | 0.9158 | 0.8962 | 0.0196 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | GREENHOUSE 5 | 0.916 | 0.8963 | 0.0197 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | BENT ML5 | 0.9159 | 0.8963 | 0.0196 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | ECNTRTN5 | 0.9161 | 0.8964 | 0.0197 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | ELMSPRGS 5 | 0.9168 | 0.897 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | ELMSPG_2 2 | 0.9168 | 0.897 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | WROGERS 5 | 0.9165 | 0.897 | 0.0195 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | TONTITN5 | 0.9175 | 0.8977 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | MATTISN5 | 0.9175 | 0.8977 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | BRUSHCRK_5 | 0.9176 | 0.8978 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | EFAYETVL 5 | 0.918 | 0.8982 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | EFAYVL_1 2 | 0.918 | 0.8982 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | EFAYTVL2-2 | 0.918 | 0.8982 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | SOSPRDL5 | 0.9182 | 0.8984 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | LOWELL 5 | 0.9181 | 0.8984 | 0.0197 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | OSBURN | 0.9183 | 0.8985 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | DYESS 5 | 0.9187 | 0.8989 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | ROGERS 5 | 0.9195 | 0.8999 | 0.0196 | 161 | 0.9 | 1.05 | N/A | P43:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | SSLINC2 | 0.8912 | 0.8717 | 0.0195 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | SSNORT2 | 0.8918 | 0.8722 | 0.0196 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | SSNEWN2 | 0.895 | 0.8755 | 0.0195 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | TONTITN7 | 0.9115 | 0.8918 | 0.0197 | 345 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | SPRDALE2 | 0.9124 | 0.8925 | 0.0199 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | SPRDALT2 | 0.9138 | 0.894 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | DYESS 2 | 0.9142 | 0.8944 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | BENT_SL5 | 0.9157 | 0.8961 | 0.0196 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | BENTVJ_5 | 0.9157 | 0.8961 | 0.0196 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | BEN279_5 | 0.9158 | 0.8962 | 0.0196 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | GREENHOUSE 5 | 0.916 | 0.8963 | 0.0197 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | BENT ML5 | 0.9159 | 0.8963 | 0.0196 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | ECNTRTN5 | 0.9161 | 0.8964 | 0.0197 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | ELMSPRGS 5 | 0.9168 | 0.897 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | ELMSPG_2 2 | 0.9168 | 0.897 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | WROGERS 5 | 0.9165 | 0.897 | 0.0195 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | TONTITN5 | 0.9175 | 0.8977 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | MATTISN5 | 0.9175 | 0.8977 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | BRUSHCRK_5 | 0.9176 | 0.8978 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | EFAYETVL 5 | 0.918 | 0.8982 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | EFAYVL_1 2 | 0.918 | 0.8982 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | EFAYTVL2-2 | 0.918 | 0.8982 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | SOSPRDL5 | 0.9182 | 0.8984 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | LOWELL 5 | 0.9181 | 0.8984 | 0.0197 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | OSBURN | 0.9183 | 0.8985 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | DYESS 5 | 0.9187 | 0.8989 | 0.0198 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | ROGERS 5 | 0.9195 | 0.8999 | 0.0196 | 161 | 0.9 | 1.05 | N/A | P23:345:GRDA:GRDA CB9580
ERIS | 08NR | 3 | 29SP | N/A | SSLINC2 | 0.8966 | 0.8757 | 0.0209 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:TONNECE CB9580
ERIS | 08NR | 3 | 29SP | N/A | SSNORT2 | 0.8971 | 0.8763 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:TONNECE CB9580
ERIS | 08NR | 3 | 29SP | N/A | SSNEWN2 | 0.9003 | 0.8795 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:TONNECE CB9580
ERIS | 08NR | 3 | 29SP | N/A | ARKLIN2 | 0.9069 | 0.8863 | 0.0206 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:TONNECE CB9580
ERIS | 08NR | 3 | 29SP | N/A | TONECESTR2 | 0.9077 | 0.8871 | 0.0206 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:TONNECE CB9580
ERIS | 08NR | 3 | 29SP | N/A | TONNEC2 | 0.9129 | 0.8924 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:TONNECE CB9580
ERIS | 08NR | 3 | 29SP | N/A | TONTITN7 | 0.9165 | 0.8949 | 0.0216 | 345 | 0.9 | 1.05 | N/A | P23:345:GRDA:TONNECE CB9580
ERIS | 08NR | 3 | 29SP | N/A | DYESS 2 | 0.9191 | 0.8972 | 0.0219 | 69 | 0.9 | 1.05 | N/A | P23:345:GRDA:TONNECE CB9580
ERIS | 08NR | 3 | 29SP | N/A | CHAMSPR7 | 0.9192 | 0.8981 | 0.0211 | 345 | 0.9 | 1.05 | N/A | P23:345:GRDA:TONNECE CB9580
ERIS | 08NR | 3 | 29SP | N/A | SPRDALE2 | 0.9188 | 0.8972 | 0.0216 | 69 | 0.9 | 1.05 | N/A | P12:345:GRDA:GRDA1 -TONECE
ERIS | 08NR | 3 | 29SP | N/A | PRQN_WIND5 | 0.9005 | 0.8798 | 0.0207 | 161 | 0.9 | 1.05 | N/A | P12:161:WERE:MARM-KCPL_161::FUTURE
ERIS | 08NR | 3 | 29SP | N/A | DAKOTA_5 | 0.9022 | 0.8822 | 0.02 | 161 | 0.9 | 1.05 | N/A | P12:161:WERE:MARM-KCPL_161::FUTURE
ERIS | 09NR | 3 | 19WP | N/A | MIAMI_ 5 | 0.9147 | 0.8739 | 0.0408 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 19WP | N/A | WEST---5 | 0.9149 | 0.8741 | 0.0408 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 19WP | N/A | S EAST 5 | 0.915 | 0.8742 | 0.0408 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 19WP | N/A | MRSHLJT5 | 0.9154 | 0.8746 | 0.0408 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 19WP | N/A | SEDEAST5 | 0.9056 | 0.8749 | 0.0307 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 19WP | N/A | NORTON-5 | 0.9158 | 0.875 | 0.0408 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 19WP | N/A | MALTABN5 | 0.917 | 0.8776 | 0.0394 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 19WP | N/A | SWAVRLY5 | 0.9178 | 0.8791 | 0.0387 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 19WP | N/A | SWAVCAP5 | 0.9178 | 0.8791 | 0.0387 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 19WP | N/A | SEDALIA5 | 0.915 | 0.885 | 0.03 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 24WP | N/A | MIAMI_ 5 | 0.9121 | 0.8832 | 0.0289 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 24WP | N/A | WEST---5 | 0.9122 | 0.8834 | 0.0288 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 24WP | N/A | S EAST 5 | 0.9124 | 0.8836 | 0.0288 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 24WP | N/A | SEDEAST5 | 0.9051 | 0.8837 | 0.0214 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 24WP | N/A | MRSHLJT5 | 0.9127 | 0.8839 | 0.0288 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 24WP | N/A | NORTON-5 | 0.9131 | 0.8843 | 0.0288 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 24WP | N/A | MALTABN5 | 0.9155 | 0.8877 | 0.0278 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 24WP | N/A | SWAVRLY5 | 0.9168 | 0.8895 | 0.0273 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 24WP | N/A | SWAVCAP5 | 0.9168 | 0.8895 | 0.0273 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 09NR | 3 | 24WP | N/A | SEDALIA5 | 0.9156 | 0.895 | 0.0206 | 161 | 0.9 | 1.05 | N/A | P24:345:AMMO::MCCREDIE:1
ERIS | 03NR | 3 | 20SP | N/A | GRANNIS 2 | 1.0305 | 1.05 | 0.0195 | 69 | 0.9 | 1.05 | N/A | P11:HV:EES::TURKCOAL:1
ERIS | 03NR | 3 | 20SP | N/A | GRANNIS 2 | 1.0305 | 1.05 | 0.0195 | 69 | 0.9 | 1.05 | N/A | P11:24:AEPW:TURKCOAL
ERIS | 03NR | 3 | 20SP | N/A | DEQUEEN2 | 1.0306 | 1.0501 | 0.0195 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:MENA2:DEQUEEN2
ERIS | 03NR | 3 | 20SP | N/A | LUDDEN -CP7 | 1.0306 | 1.0504 | 0.0198 | 115 | 0.9 | 1.05 | N/A | P12:230:OTP:AUTO-SINGLE:HANKSON4:WAHPETN4:1
ERIS | 03NR | 3 | 20SP | N/A | DEVAUL -MG7 | 1.0301 | 1.0504 | 0.0203 | 115 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 268 #: AVS IN ND. ANTELOPE VALLEY LINE REACTOR
ERIS | 03NR | 3 | 24WP | N/A | GEN-2017-031 | 1.0724 | 1.0506 | 0.0218 | 115 | 0.9 | 1.05 | N/A | P12:115:TSGT-BEPC_659:::W.HORSE_-TS7-B.SPRGS7
ERIS | 03NR | 3 | 24WP | N/A | G17-031-TAP | 1.0724 | 1.0506 | 0.0218 | 115 | 0.9 | 1.05 | N/A | P12:115:TSGT-BEPC_659:::W.HORSE_-TS7-B.SPRGS7
ERIS | 03NR | 3 | 20SP | N/A | SOLCHPL2 | 1.0307 | 1.0508 | 0.0201 | 69 | 0.9 | 1.05 | N/A | P12:138:AEPW:HARRISN4:PERDUE4
ERIS | 03NR | 3 | 20SP | N/A | DEVAUL -MG7 | 1.0311 | 1.0508 | 0.0197 | 115 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 283 #: LO2 IN ND. LELAND OLDS-GROTON LINE REACTOR
ERIS | 03NR | 3 | 20SP | N/A | GLENWOD2 | 1.0313 | 1.051 | 0.0197 | 69 | 0.9 | 1.05 | N/A | P12:138:AEPW:LSSOUTH4:DIANA4
ERIS | 03NR | 3 | 20SP | N/A | HECLA-ER8 | 1.0308 | 1.0514 | 0.0206 | 69 | 0.9 | 1.05 | N/A | P11:115:UMZB:# 35 #: GGS1 IN SD. GROTON 1
ERIS | 03NR | 3 | 20SP | N/A | DEVAUL -MG7 | 1.0319 | 1.0515 | 0.0196 | 115 | 0.9 | 1.05 | N/A | P14:014:UMZB:# 282 #: LO2 IN ND. LELAND OLDS TERTIARY REACTOR
ERIS | 03NR | 3 | 20SP | N/A | MCALEST2 | 1.0302 | 1.0522 | 0.022 | 69 | 0.9 | 1.05 | N/A | P12:138:AEPW:MCALEST4:LONEOAK4
ERIS | 03NR | 3 | 20SP | N/A | CLAREMNT-ER8 | 1.0323 | 1.0522 | 0.0199 | 69 | 0.9 | 1.05 | N/A | P11:115:UMZB:# 35 #: GGS1 IN SD. GROTON 1
ERIS | 03NR | 3 | 20SP | N/A | WESSINGTON 4 | 1.0314 | 1.0522 | 0.0208 | 230 | 0.9 | 1.05 | N/A | P11:230:UMZB:# 40 #: CRW IN SD. SD PRAIRIE WIND
ERIS | 03NR | 3 | 20SP | N/A | A.DEPOT2 | 1.0327 | 1.0522 | 0.0195 | 69 | 0.9 | 1.05 | N/A | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
ERIS | 03NR | 3 | 20SP | N/A | A.DEPOT2 | 1.0327 | 1.0522 | 0.0195 | 69 | 0.9 | 1.05 | N/A | P23:345:AEPW:PITTSBURG CB 3441A NBTB
ERIS | 03NR | 3 | 20SP | N/A | EVENSID2 | 1.032 | 1.0523 | 0.0203 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:BECKVIL2:POYNTER2
ERIS | 03NR | 3 | 20SP | N/A | SD.PW1__-BE4 | 1.0317 | 1.0525 | 0.0208 | 230 | 0.9 | 1.05 | N/A | P11:230:UMZB:# 40 #: CRW IN SD. SD PRAIRIE WIND
ERIS | 03NR | 3 | 20SP | N/A | CLARKSV7 | 1.0304 | 1.0528 | 0.0224 | 345 | 0.9 | 1.05 | N/A | P42:345:OKGE:SB_CRER7309
ERIS | 03NR | 3 | 20SP | N/A | WICKES 2 | 1.0321 | 1.0529 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::TURK 4%:1(1)
ERIS | 03NR | 3 | 20SP | N/A | WICKES 2 | 1.0321 | 1.0529 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:TURK 4
ERIS | 03NR | 3 | 20SP | N/A | GRANNIS 2 | 1.0317 | 1.0541 | 0.0224 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::TURK 4%:1(1)
ERIS | 08NR | 3 | 24L | N/A | JGWALKR2 | 1.031 | 1.0541 | 0.0231 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 06NR | 3 | 19WP | N/A | BUSHLAND 3 | 1.0308 | 1.0541 | 0.0233 | 115 | 0.9 | 1.05 | N/A | P12:115:SPS:V52.1.COLTR.BSHLND
ERIS | 03NR | 3 | 20SP | N/A | PINEYWD2 | 1.0305 | 1.0541 | 0.0236 | 69 | 0.9 | 1.05 | N/A | P12:138:AEPW:PERDUE4:EXXONM4
ERIS | 08NR | 3 | 24L | N/A | JGWALKR2 | 1.031 | 1.0541 | 0.0231 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | GRANNIS 2 | 1.0317 | 1.0541 | 0.0224 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:TURK 4
ERIS | 03NR | 3 | 24SP | N/A | KEYSTON3 | 1.0761 | 1.0543 | 0.0218 | 345 | 0.9 | 1.05 | N/A | P42:345:NPPD:BKR-KEY-3310
ERIS | 03NR | 3 | 20SP | N/A | SOLCHPL2 | 1.0331 | 1.055 | 0.0219 | 69 | 0.9 | 1.05 | N/A | P12:138:AEPW:PERDUE4:EXXONM4
ERIS | 07NR | 3 | 29SP | N/A | LUDDEN -CP7 | 1.0346 | 1.055 | 0.0204 | 115 | 0.9 | 1.05 | N/A | P12:115:MDU:ND:BISCENTRYCE7:CENTURY7:1
ERIS | 08NR | 3 | 24L | N/A | COVEREC2 | 1.03 | 1.0553 | 0.0253 | 69 | 0.9 | 1.05 | N/A | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
ERIS | 08NR | 3 | 24L | N/A | COVEREC2 | 1.03 | 1.0553 | 0.0253 | 69 | 0.9 | 1.05 | N/A | P23:345:AEPW:WELSH CB 11990 NBTB
ERIS | 03NR | 3 | 20SP | N/A | HOLYLAK2 | 1.0346 | 1.0554 | 0.0208 | 69 | 0.9 | 1.05 | N/A | P12:138:AEPW:PERDUE4:EXXONM4
ERIS | 08NR | 3 | 24L | N/A | EOBROWN2 | 1.0325 | 1.0555 | 0.023 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | EOBROWN2 | 1.0325 | 1.0555 | 0.023 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | HALLSVL2 | 1.0305 | 1.0558 | 0.0253 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | HOLOX 2 | 1.0309 | 1.0558 | 0.0249 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:PATTERS2:NEKOOSA2
ERIS | 03NR | 3 | 20SP | N/A | HALLSVL2 | 1.0305 | 1.0558 | 0.0253 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | CALEDON7 | 1.0309 | 1.0558 | 0.0249 | 115 | 0.9 | 1.05 | N/A | P14:013:UMZW:# 2232 #: FA IN ND. LOSS OF SHUNT (KW6A, KW7A, KW8A)
ERIS | 08NR | 3 | 24L | N/A | NEKOSAT2 | 1.031 | 1.0559 | 0.0249 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:PATTERS2:NEKOOSA2
ERIS | 03NR | 3 | 24WP | N/A | GEN-2017-031 | 1.0773 | 1.0559 | 0.0214 | 115 | 0.9 | 1.05 | N/A | P12:115:NPPD:TSGT2:W.HORSE7:B.SPRGS7:BTB
ERIS | 03NR | 3 | 24WP | N/A | G17-031-TAP | 1.0773 | 1.0559 | 0.0214 | 115 | 0.9 | 1.05 | N/A | P12:115:NPPD:TSGT2:W.HORSE7:B.SPRGS7:BTB
ERIS | 03NR | 3 | 20SP | N/A | LTLMOND2 | 1.0364 | 1.0561 | 0.0197 | 69 | 0.9 | 1.05 | N/A | P12:138:AEPW:PERDUE4:EXXONM4
ERIS | 03NR | 3 | 24WP | N/A | W.HORSE_-TS7 | 1.0775 | 1.0561 | 0.0214 | 115 | 0.9 | 1.05 | N/A | P12:115:NPPD:TSGT2:W.HORSE7:B.SPRGS7:BTB
ERIS | 03NR | 3 | 20SP | N/A | DEQUEEN2 | 1.0305 | 1.0564 | 0.0259 | 69 | 0.9 | 1.05 | N/A | P11:HV:EES::TURKCOAL:1
ERIS | 03NR | 3 | 20SP | N/A | DEQUEEN2 | 1.0305 | 1.0564 | 0.0259 | 69 | 0.9 | 1.05 | N/A | P11:24:AEPW:TURKCOAL
ERIS | 03NR | 3 | 20SP | N/A | PICKERT4 | 1.0319 | 1.0565 | 0.0246 | 230 | 0.9 | 1.05 | N/A | P13:69-230:OTP:PICKERT4:T1
ERIS | 06NR | 3 | 19WP | N/A | REDOK-4 | 1.0301 | 1.0565 | 0.0264 | 138 | 0.9 | 1.05 | N/A | P12:138:AEPW-SWPA:REDOK-4:EUFAULA4
ERIS | 03NR | 3 | 20SP | N/A | GRANITF8 | 1.0313 | 1.0565 | 0.0252 | 69 | 0.9 | 1.05 | N/A | P13:230:UMZW:# 237 #: GF IN MN. LOSS OF TRANSFORMER (KV8A).
ERIS | 06NR | 3 | 20G | N/A | REDOK-4 | 1.0309 | 1.0568 | 0.0259 | 138 | 0.9 | 1.05 | N/A | P12:138:AEPW-SWPA:REDOK-4:EUFAULA4
ERIS | 02NR | 3 | 24L | N/A | MEMPHIS2 | 1.0305 | 1.0569 | 0.0264 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:NWMEMPH2:CLARDON2
ERIS | 03NR | 3 | 20SP | N/A | GRANITF8 | 1.0316 | 1.0569 | 0.0253 | 69 | 0.9 | 1.05 | N/A | P13:230:UMZW:# 236 #: GF IN MN. LOSS OF TRANSFORMER (KV3A).
ERIS | 03NR | 3 | 20SP | N/A | FORMAN 7 | 1.0302 | 1.0571 | 0.0269 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZ:# 5563 #: IN . PROPER N-1 (LINE) FOR 652454-652638-1
ERIS | 08NR | 3 | 24L | N/A | NICHOLS2 | 1.0343 | 1.0572 | 0.0229 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | NICHOLS2 | 1.0343 | 1.0572 | 0.0229 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | WINNSBO2 | 1.0355 | 1.0582 | 0.0227 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | WINNSBO2 | 1.0355 | 1.0582 | 0.0227 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 02NR | 3 | 24L | N/A | NWMEMPH2 | 1.0305 | 1.0586 | 0.0281 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:NWMEMPH2:CLARDON2
ERIS | 03NR | 3 | 20SP | N/A | MCALEST2 | 1.0389 | 1.0587 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P23:345:AEPW:PITTSBURG CB 3441A NBTB
ERIS | 08NR | 3 | 24L | N/A | NEWHOPE2 | 1.0365 | 1.0596 | 0.0231 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | NEWHOPE2 | 1.0365 | 1.0596 | 0.0231 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | GROTON__-BE3 | 1.0388 | 1.0599 | 0.0211 | 345 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 276 #: GRT IN SD. GROTON-LELAND OLDS LINE REACTOR
ERIS | 03NR | 3 | 20SP | N/A | GR.LS-LO-BE3 | 1.0388 | 1.0599 | 0.0211 | 345 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 276 #: GRT IN SD. GROTON-LELAND OLDS LINE REACTOR
ERIS | 08NR | 3 | 20G | N/A | G16133_345CS | 1.0384 | 1.0599 | 0.0215 | 345 | 0.9 | 1.05 | N/A | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
ERIS | 08NR | 3 | 20G | N/A | G16133_345CS | 1.0384 | 1.0599 | 0.0215 | 345 | 0.9 | 1.05 | N/A | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
ERIS | 08NR | 3 | 24L | N/A | EBENTON2 | 1.0372 | 1.06 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | MTVRN R2 | 1.0366 | 1.06 | 0.0234 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | EBENTON2 | 1.0372 | 1.06 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | MTVRN R2 | 1.0366 | 1.06 | 0.0234 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | MOBLTEX2 | 1.037 | 1.0602 | 0.0232 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | MOBLTXT2 | 1.0369 | 1.0602 | 0.0233 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | MOBLTEX2 | 1.037 | 1.0602 | 0.0232 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | MOBLTXT2 | 1.0369 | 1.0602 | 0.0233 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | MORISGR2 | 1.037 | 1.0603 | 0.0233 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | MORISGR2 | 1.037 | 1.0603 | 0.0233 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | ASHDOWN2 | 1.0366 | 1.0604 | 0.0238 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:ASHDOWN2:PATTERS2
ERIS | 03NR | 3 | 20SP | N/A | DEQUEEN2 | 1.0318 | 1.0606 | 0.0288 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::TURK 4%:1(1)
ERIS | 08NR | 3 | 24L | N/A | MTVERNT2 | 1.0372 | 1.0606 | 0.0234 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | NEKOSAT2 | 1.0369 | 1.0606 | 0.0237 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:ASHDOWN2:PATTERS2
ERIS | 08NR | 3 | 24L | N/A | HOLOX 2 | 1.0368 | 1.0606 | 0.0238 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:ASHDOWN2:PATTERS2
ERIS | 08NR | 3 | 24L | N/A | MTVERNT2 | 1.0372 | 1.0606 | 0.0234 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | DEQUEEN2 | 1.0318 | 1.0606 | 0.0288 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:TURK 4
ERIS | 08NR | 3 | 24L | N/A | HILWLSN2 | 1.0377 | 1.0607 | 0.023 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | HILWLSN2 | 1.0377 | 1.0607 | 0.023 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | JARDWLM2 | 1.038 | 1.0609 | 0.0229 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | JARDWLM2 | 1.038 | 1.0609 | 0.0229 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | GEN-2017-031 | 1.0335 | 1.0611 | 0.0276 | 115 | 0.9 | 1.05 | N/A | P12:115:NPPD:TSGT2:W.HORSE7:B.SPRGS7:BTB
ERIS | 03NR | 3 | 20SP | N/A | G17-031-TAP | 1.0335 | 1.0611 | 0.0276 | 115 | 0.9 | 1.05 | N/A | P12:115:NPPD:TSGT2:W.HORSE7:B.SPRGS7:BTB
ERIS | 08NR | 3 | 24L | N/A | FORSTHL2 | 1.0386 | 1.0613 | 0.0227 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | FORSTHL2 | 1.0386 | 1.0613 | 0.0227 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | W.HORSE_-TS7 | 1.0327 | 1.0613 | 0.0286 | 115 | 0.9 | 1.05 | N/A | P12:115:NPPD:TSGT2:W.HORSE7:B.SPRGS7:BTB
ERIS | 03NR | 3 | 20SP | N/A | S-MCALT4 | 1.041 | 1.0614 | 0.0204 | 138 | 0.9 | 1.05 | N/A | P23:345:AEPW:PITTSBURG CB 3441A NBTB
ERIS | 08NR | 3 | 20G | N/A | ZONE-3 SUB | 1.0402 | 1.0615 | 0.0213 | 345 | 0.9 | 1.05 | N/A | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
ERIS | 08NR | 3 | 20G | N/A | ZONE-3 SUB | 1.0402 | 1.0615 | 0.0213 | 345 | 0.9 | 1.05 | N/A | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
ERIS | 08NR | 3 | 20G | N/A | ZONE-4 SUB | 1.041 | 1.0616 | 0.0206 | 345 | 0.9 | 1.05 | N/A | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
ERIS | 08NR | 3 | 20G | N/A | ZONE-4 SUB | 1.041 | 1.0616 | 0.0206 | 345 | 0.9 | 1.05 | N/A | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
ERIS | 08NR | 3 | 24L | N/A | MORISCH2 | 1.0388 | 1.0617 | 0.0229 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | VBSHAW 2 | 1.0388 | 1.0617 | 0.0229 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | MORISCH2 | 1.0388 | 1.0617 | 0.0229 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | VBSHAW 2 | 1.0388 | 1.0617 | 0.0229 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | DALDRDG2 | 1.0389 | 1.0618 | 0.0229 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | DALDRDG2 | 1.0389 | 1.0618 | 0.0229 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | CATHEY 2 | 1.0391 | 1.0619 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | CATHEY 2 | 1.0391 | 1.0619 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | SCROGNS2 | 1.0392 | 1.062 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | SCROGNS2 | 1.0392 | 1.062 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | HOPEWEL2 | 1.0385 | 1.0622 | 0.0237 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | HOPEWEL2 | 1.0385 | 1.0622 | 0.0237 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 20G | N/A | ZONE-5 SUB | 1.0409 | 1.0623 | 0.0214 | 345 | 0.9 | 1.05 | N/A | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
ERIS | 08NR | 3 | 20G | N/A | ZONE-5 SUB | 1.0409 | 1.0623 | 0.0214 | 345 | 0.9 | 1.05 | N/A | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
ERIS | 08NR | 3 | 24L | N/A | VBSHAWT2 | 1.0397 | 1.0625 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | VBSHAWT2 | 1.0397 | 1.0625 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | PILGRST2 | 1.0398 | 1.0626 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | ALBA 2 | 1.0398 | 1.0626 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | PILGRST2 | 1.0398 | 1.0626 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | ALBA 2 | 1.0398 | 1.0626 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 20G | N/A | ZONE-6 SUB | 1.0415 | 1.0626 | 0.0211 | 345 | 0.9 | 1.05 | N/A | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
ERIS | 08NR | 3 | 20G | N/A | ZONE-6 SUB | 1.0415 | 1.0626 | 0.0211 | 345 | 0.9 | 1.05 | N/A | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
ERIS | 03NR | 3 | 20SP | N/A | MPSNE 7 | 1.0354 | 1.0626 | 0.0272 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZS:# 4820 #: IN . CENTENNIAL-MPSNE LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | ZONE-2 SUB | 1.0416 | 1.0628 | 0.0212 | 345 | 0.9 | 1.05 | N/A | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
ERIS | 08NR | 3 | 20G | N/A | ZONE-1 SUB | 1.0416 | 1.0628 | 0.0212 | 345 | 0.9 | 1.05 | N/A | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
ERIS | 08NR | 3 | 20G | N/A | ZONE-2 SUB | 1.0416 | 1.0628 | 0.0212 | 345 | 0.9 | 1.05 | N/A | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
ERIS | 08NR | 3 | 20G | N/A | ZONE-1 SUB | 1.0416 | 1.0628 | 0.0212 | 345 | 0.9 | 1.05 | N/A | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
ERIS | 08NR | 3 | 24L | N/A | TEXARK 2 | 1.04 | 1.0631 | 0.0231 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:ASHDOWN2:PATTERS2
ERIS | 08NR | 3 | 24L | N/A | MTVERNN2 | 1.0393 | 1.0633 | 0.024 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | MTVERNN2 | 1.0393 | 1.0633 | 0.024 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | WESTWD 2 | 1.0407 | 1.0635 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | QUITMAN2 | 1.0407 | 1.0635 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 07NR | 3 | 19WP | N/A | NMINEOL2 | 1.0315 | 1.0635 | 0.032 | 69 | 0.9 | 1.05 | N/A | P12:138:AEPW:NMINEOL4:EXXONM4
ERIS | 08NR | 3 | 24L | N/A | WESTWD 2 | 1.0407 | 1.0635 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | QUITMAN2 | 1.0407 | 1.0635 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | SETEXAR2 | 1.0404 | 1.0636 | 0.0232 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:ASHDOWN2:PATTERS2
ERIS | 03NR | 3 | 20SP | N/A | MPSOPP 7 | 1.038 | 1.0636 | 0.0256 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZS:# 4820 #: IN . CENTENNIAL-MPSNE LINE FAULT
ERIS | 08NR | 3 | 24L | N/A | WINFIEL2 | 1.0399 | 1.0638 | 0.0239 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | WINFIEL2 | 1.0399 | 1.0638 | 0.0239 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | CALAMS 7 | 1.1091 | 1.0638 | 0.0453 | 115 | 0.9 | 1.05 | N/A | P12:115:NPPD:1167A:BASSETT:ONEILL 7:BTB
ERIS | 03NR | 3 | 20SP | N/A | MANFIELD-ER8 | 1.0308 | 1.0638 | 0.033 | 69 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 276 #: GRT IN SD. GROTON-LELAND OLDS LINE REACTOR
ERIS | 03NR | 3 | 20SP | N/A | MOS-MNFD-ER8 | 1.0308 | 1.0638 | 0.033 | 69 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 276 #: GRT IN SD. GROTON-LELAND OLDS LINE REACTOR
ERIS | 08NR | 3 | 24L | N/A | GRDSALR2 | 1.0412 | 1.0639 | 0.0227 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | GRDSALR2 | 1.0412 | 1.0639 | 0.0227 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 07NR | 3 | 29SP | N/A | FORMAN 7 | 1.0441 | 1.0642 | 0.0201 | 115 | 0.9 | 1.05 | N/A | P12:115:MDU:ND:BISCENTRYCE7:CENTURY7:1
ERIS | 08NR | 3 | 24L | N/A | GRANDSL2 | 1.0416 | 1.0643 | 0.0227 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | GRANDSL2 | 1.0416 | 1.0643 | 0.0227 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | RODESSA2 | 1.042 | 1.0646 | 0.0226 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | GODFREYRDTP2 | 1.042 | 1.0646 | 0.0226 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | RICHMND2 | 1.041 | 1.0646 | 0.0236 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:ASHDOWN2:PATTERS2
ERIS | 08NR | 3 | 24L | N/A | RODESSA2 | 1.042 | 1.0646 | 0.0226 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | GODFREYRDTP2 | 1.042 | 1.0646 | 0.0226 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | HOSSTON2 | 1.0453 | 1.065 | 0.0197 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | GEN-2017-057 | 1.0453 | 1.065 | 0.0197 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | HOSSTON2 | 1.0453 | 1.065 | 0.0197 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | GEN-2017-057 | 1.0453 | 1.065 | 0.0197 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | MCALEST4 | 1.0448 | 1.065 | 0.0202 | 138 | 0.9 | 1.05 | N/A | P23:345:AEPW:PITTSBURG CB 3441A NBTB
ERIS | 03NR | 3 | 20SP | N/A | MOORHED7 | 1.043 | 1.0652 | 0.0222 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZS:# 4820 #: IN . CENTENNIAL-MPSNE LINE FAULT
ERIS | 08NR | 3 | 24L | N/A | AVINGER2 | 1.0441 | 1.0653 | 0.0212 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | AVINGER2 | 1.0441 | 1.0653 | 0.0212 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | ADORA 2 | 1.0415 | 1.0657 | 0.0242 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | FARMRAC2 | 1.0415 | 1.0657 | 0.0242 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | ADORA 2 | 1.0415 | 1.0657 | 0.0242 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | FARMRAC2 | 1.0415 | 1.0657 | 0.0242 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | BSSESHUNT | 1.0303 | 1.0658 | 0.0355 | 345 | 0.9 | 1.05 | N/A | P13:014-115-345:MDU::COYOTE::1::::
ERIS | 03NR | 3 | 20SP | N/A | BSSESHUNT3 | 1.0303 | 1.0658 | 0.0355 | 345 | 0.9 | 1.05 | N/A | P13:014-115-345:MDU::COYOTE::1::::
ERIS | 03NR | 3 | 20SP | N/A | ELLENDLMVP3 | 1.0302 | 1.0658 | 0.0356 | 345 | 0.9 | 1.05 | N/A | P13:014-115-345:MDU::COYOTE::1::::
ERIS | 03NR | 3 | 20SP | N/A | BSSESHUNT | 1.0303 | 1.0658 | 0.0355 | 345 | 0.9 | 1.05 | N/A | P14:014:MDU::HETTINGER::SWREACT::::
ERIS | 03NR | 3 | 20SP | N/A | BSSESHUNT3 | 1.0303 | 1.0658 | 0.0355 | 345 | 0.9 | 1.05 | N/A | P14:014:MDU::HETTINGER::SWREACT::::
ERIS | 03NR | 3 | 20SP | N/A | ELLENDLMVP3 | 1.0302 | 1.0658 | 0.0356 | 345 | 0.9 | 1.05 | N/A | P14:014:MDU::HETTINGER::SWREACT::::
ERIS | 03NR | 3 | 20SP | N/A | FARGO 8 | 1.0429 | 1.0658 | 0.0229 | 69 | 0.9 | 1.05 | N/A | P14:013:UMZW:# 2232 #: FA IN ND. LOSS OF SHUNT (KW6A, KW7A, KW8A)
ERIS | 08NR | 3 | 24L | N/A | PILGPRD2 | 1.0419 | 1.0662 | 0.0243 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | PILGPRD2 | 1.0419 | 1.0662 | 0.0243 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 06NR | 3 | 24SP | N/A | JERIC2WT | 1.0303 | 1.0662 | 0.0359 | 69 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:CHLDR2WT
ERIS | 08NR | 3 | 24L | N/A | ADORA T2 | 1.0421 | 1.0664 | 0.0243 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | ADORA T2 | 1.0421 | 1.0664 | 0.0243 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | DUNCNRD2 | 1.0332 | 1.0667 | 0.0335 | 69 | 0.9 | 1.05 | N/A | P12:69:KCPL-INDN:BLUVLY-LAKCTYJ2::
ERIS | 08NR | 3 | 24L | N/A | WMTPLES2 | 1.0426 | 1.0669 | 0.0243 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | WMTPLES2 | 1.0426 | 1.0669 | 0.0243 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 06NR | 3 | 20G | N/A | XIT_INTG 3 | 1.0338 | 1.067 | 0.0332 | 115 | 0.9 | 1.05 | N/A | P12:115:SPS:W80.1.DALLAM.XIT
ERIS | 08NR | 3 | 24L | N/A | CITYLAKE 2 | 1.0428 | 1.0672 | 0.0244 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | CITYLAKE 2 | 1.0428 | 1.0672 | 0.0244 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | BASSETT 7 | 1.1269 | 1.0675 | 0.0594 | 115 | 0.9 | 1.05 | N/A | P12:115:NPPD:1167A:BASSETT:ONEILL 7:BTB
ERIS | 08NR | 3 | 24L | N/A | STEEL 2 | 1.0465 | 1.0676 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | STEEL 2 | 1.0465 | 1.0676 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | ORECITY2 | 1.0465 | 1.0677 | 0.0212 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | MTPLEAS2 | 1.0432 | 1.0677 | 0.0245 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | ORECITY2 | 1.0465 | 1.0677 | 0.0212 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | MTPLEAS2 | 1.0432 | 1.0677 | 0.0245 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 06NR | 3 | 20G | N/A | DAKOTA_5 | 1.0415 | 1.0677 | 0.0262 | 161 | 0.9 | 1.05 | N/A | P12:161:WERE:MARM-KCPL_161::FUTURE
ERIS | 03NR | 3 | 20SP | N/A | MPSSE 7 | 1.0378 | 1.0679 | 0.0301 | 115 | 0.9 | 1.05 | N/A | P14:013:UMZW:# 2232 #: FA IN ND. LOSS OF SHUNT (KW6A, KW7A, KW8A)
ERIS | 03NR | 3 | 20SP | N/A | MPSBROOK | 1.0386 | 1.068 | 0.0294 | 115 | 0.9 | 1.05 | N/A | P14:013:UMZW:# 2232 #: FA IN ND. LOSS OF SHUNT (KW6A, KW7A, KW8A)
ERIS | 03NR | 3 | 20SP | N/A | MPSCENT7 | 1.0374 | 1.068 | 0.0306 | 115 | 0.9 | 1.05 | N/A | P14:013:UMZW:# 2232 #: FA IN ND. LOSS OF SHUNT (KW6A, KW7A, KW8A)
ERIS | 08NR | 3 | 24L | N/A | FERNDTP2 | 1.0452 | 1.0681 | 0.0229 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | FERNDAL2 | 1.0452 | 1.0681 | 0.0229 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | FERNDTP2 | 1.0452 | 1.0681 | 0.0229 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | FERNDAL2 | 1.0452 | 1.0681 | 0.0229 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | EASTMNT2 | 1.0471 | 1.0682 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | PETTY 2 | 1.044 | 1.0682 | 0.0242 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 03NR | 3 | 20SP | N/A | MERRCRT4 | 1.0305 | 1.0682 | 0.0377 | 230 | 0.9 | 1.05 | N/A | P12:115:MDU::NORTH DICKINSON:DICKINSON WEST:1::::
ERIS | 08NR | 3 | 24L | N/A | EASTMNT2 | 1.0471 | 1.0682 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | PETTY 2 | 1.044 | 1.0682 | 0.0242 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | AINSWRT7 | 1.1207 | 1.0683 | 0.0524 | 115 | 0.9 | 1.05 | N/A | P12:115:NPPD:1167A:BASSETT:ONEILL 7:BTB
ERIS | 03NR | 3 | 20SP | N/A | MPSNE 7 | 1.0385 | 1.0687 | 0.0302 | 115 | 0.9 | 1.05 | N/A | P14:013:UMZW:# 2232 #: FA IN ND. LOSS OF SHUNT (KW6A, KW7A, KW8A)
ERIS | 08NR | 3 | 24L | N/A | GLENWOD2 | 1.0479 | 1.069 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 03NR | 3 | 20SP | N/A | MERRCRT4 | 1.0325 | 1.069 | 0.0365 | 230 | 0.9 | 1.05 | N/A | P13:014-115-345:MDU::COYOTE::1::::
ERIS | 08NR | 3 | 24L | N/A | GLENWOD2 | 1.0479 | 1.069 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | G16133_765R2 | 1.0406 | 1.0697 | 0.0291 | 765 | 0.9 | 1.05 | N/A | P42:345:OKGE:SB_CRER7309
ERIS | 08NR | 3 | 24L | N/A | BETHLHM2 | 1.0489 | 1.07 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 06NR | 3 | 29SP | N/A | JERIC2WT | 1.0433 | 1.07 | 0.0267 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 06NR | 3 | 24SP | N/A | JERIC2WT | 1.039 | 1.07 | 0.031 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 08NR | 3 | 24L | N/A | BETHLHM2 | 1.0489 | 1.07 | 0.0211 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 06NR | 3 | 24SP | N/A | HWRDWCK2 | 1.0304 | 1.07 | 0.0396 | 69 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:CHLDR2WT
ERIS | 06NR | 3 | 20G | N/A | PRQN_WIND5 | 1.0441 | 1.0704 | 0.0263 | 161 | 0.9 | 1.05 | N/A | P12:161:WERE:MARM-KCPL_161::FUTURE
ERIS | 03NR | 3 | 20SP | N/A | FARGO 7 | 1.0494 | 1.0705 | 0.0211 | 115 | 0.9 | 1.05 | N/A | P14:013:UMZW:# 2232 #: FA IN ND. LOSS OF SHUNT (KW6A, KW7A, KW8A)
ERIS | 08NR | 3 | 24L | N/A | COOKVIL2 | 1.0453 | 1.0707 | 0.0254 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | COOKVTP2 | 1.0453 | 1.0707 | 0.0254 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | COOKVIL2 | 1.0453 | 1.0707 | 0.0254 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | COOKVTP2 | 1.0453 | 1.0707 | 0.0254 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | MPSOPP 7 | 1.0434 | 1.0712 | 0.0278 | 115 | 0.9 | 1.05 | N/A | P14:013:UMZW:# 2232 #: FA IN ND. LOSS OF SHUNT (KW6A, KW7A, KW8A)
ERIS | 08NR | 3 | 24L | N/A | MVLONG 2 | 1.0509 | 1.0713 | 0.0204 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | MVLONG 2 | 1.0509 | 1.0713 | 0.0204 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | DIAN 2 | 1.0505 | 1.0715 | 0.021 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | DIAN 2 | 1.0505 | 1.0715 | 0.021 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | LETRNST2 | 1.0517 | 1.0719 | 0.0202 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | HAWKINS2 | 1.0506 | 1.0719 | 0.0213 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | HAWKREC2 | 1.0504 | 1.0719 | 0.0215 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | HOARD R2 | 1.0498 | 1.0719 | 0.0221 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | LETRNST2 | 1.0517 | 1.0719 | 0.0202 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | HAWKINS2 | 1.0506 | 1.0719 | 0.0213 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | HAWKREC2 | 1.0504 | 1.0719 | 0.0215 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | HOARD R2 | 1.0498 | 1.0719 | 0.0221 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | VALENTN7 | 1.0948 | 1.072 | 0.0228 | 115 | 0.9 | 1.05 | N/A | P12:115:NPPD:1091:VALENTN7:MISSION7:BTB
ERIS | 08NR | 3 | 24L | N/A | REDRVR-2 | 1.0418 | 1.0721 | 0.0303 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 03NR | 3 | 20SP | N/A | ELLENDLMVP3 | 1.0339 | 1.0721 | 0.0382 | 345 | 0.9 | 1.05 | N/A | P12:115:MDU::NORTH DICKINSON:DICKINSON WEST:1::::
ERIS | 08NR | 3 | 24L | N/A | REDRVR-2 | 1.0418 | 1.0721 | 0.0303 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | BSSESHUNT | 1.034 | 1.0722 | 0.0382 | 345 | 0.9 | 1.05 | N/A | P12:115:MDU::NORTH DICKINSON:DICKINSON WEST:1::::
ERIS | 03NR | 3 | 20SP | N/A | BSSESHUNT3 | 1.034 | 1.0722 | 0.0382 | 345 | 0.9 | 1.05 | N/A | P12:115:MDU::NORTH DICKINSON:DICKINSON WEST:1::::
ERIS | 08NR | 3 | 24L | N/A | MINEOLA2 | 1.0499 | 1.0723 | 0.0224 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | ATLANTA2 | 1.0461 | 1.0723 | 0.0262 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | MINEOLA2 | 1.0499 | 1.0723 | 0.0224 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | ATLANTA2 | 1.0461 | 1.0723 | 0.0262 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | MORRIS 4 | 1.0328 | 1.0724 | 0.0396 | 230 | 0.9 | 1.05 | N/A | P12:230:UMZS:# 2932 #: MDOE IN MN. LINE FAULT BTWN MOORHEAD-FARGO
ERIS | 08NR | 3 | 24L | N/A | BIGSNDY2 | 1.0515 | 1.0725 | 0.021 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | BIGSNDY2 | 1.0515 | 1.0725 | 0.021 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | VALTN.W7 | 1.0945 | 1.0725 | 0.022 | 115 | 0.9 | 1.05 | N/A | P12:115:NPPD:1091:VALENTN7:MISSION7:BTB
ERIS | 08NR | 3 | 24L | N/A | BUFORDR2 | 1.0468 | 1.0727 | 0.0259 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | NAPLES 2 | 1.0468 | 1.0727 | 0.0259 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 03NR | 3 | 20SP | N/A | CLARKSV7 | 1.0463 | 1.0727 | 0.0264 | 345 | 0.9 | 1.05 | N/A | P12:EHV:EES::CLARKSV7!:ONETA--7:1
ERIS | 03NR | 3 | 20SP | N/A | CLARKSV7 | 1.0463 | 1.0727 | 0.0264 | 345 | 0.9 | 1.05 | N/A | P12:345:AEPW:CLARKSV7:ONETA--7
ERIS | 08NR | 3 | 24L | N/A | BUFORDR2 | 1.0468 | 1.0727 | 0.0259 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | NAPLES 2 | 1.0468 | 1.0727 | 0.0259 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | CLARKSV7 | 1.0463 | 1.0727 | 0.0264 | 345 | 0.9 | 1.05 | N/A | P42:345:AEPW:ONETA CB 3401A NBTB+FAULT
ERIS | 03NR | 3 | 20SP | N/A | CLARKSV7 | 1.0463 | 1.0727 | 0.0264 | 345 | 0.9 | 1.05 | N/A | P23:345:AEPW:ONETA CB 3401A NBTB
ERIS | 08NR | 3 | 24L | N/A | LETOURN2 | 1.0529 | 1.073 | 0.0201 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | PERDUE 2 | 1.0523 | 1.073 | 0.0207 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | LETOURN2 | 1.0529 | 1.073 | 0.0201 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | PERDUE 2 | 1.0523 | 1.073 | 0.0207 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | NETTLTN2 | 1.0528 | 1.0731 | 0.0203 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | NETTLTN2 | 1.0528 | 1.0731 | 0.0203 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | GILMER 2 | 1.0518 | 1.0732 | 0.0214 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | GILMER 2 | 1.0518 | 1.0732 | 0.0214 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | NMINEOL2 | 1.0508 | 1.0733 | 0.0225 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | NMINEOL2 | 1.0508 | 1.0733 | 0.0225 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | PITTSTL2 | 1.0506 | 1.0734 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | PITTSTL2 | 1.0506 | 1.0734 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | ELLENDLMVP3 | 1.0303 | 1.0735 | 0.0432 | 345 | 0.9 | 1.05 | N/A | P12:230:MDU::MERRICOURT:WISHEK:1::::
ERIS | 03NR | 3 | 20SP | N/A | BSSESHUNT | 1.0303 | 1.0735 | 0.0432 | 345 | 0.9 | 1.05 | N/A | P12:230:MDU::MERRICOURT:WISHEK:1::::
ERIS | 03NR | 3 | 20SP | N/A | BSSESHUNT3 | 1.0303 | 1.0735 | 0.0432 | 345 | 0.9 | 1.05 | N/A | P12:230:MDU::MERRICOURT:WISHEK:1::::
ERIS | 08NR | 3 | 24L | N/A | CLARKSV2 | 1.0533 | 1.0738 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | CLARKSV2 | 1.0533 | 1.0738 | 0.0205 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | BIG 3 2 | 1.0539 | 1.0739 | 0.02 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | NETTLTP2 | 1.0536 | 1.0739 | 0.0203 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | BIG 3 2 | 1.0539 | 1.0739 | 0.02 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | NETTLTP2 | 1.0536 | 1.0739 | 0.0203 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | PITTSTP2 | 1.0515 | 1.0743 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | PITTSTP2 | 1.0515 | 1.0743 | 0.0228 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | GREGGTN2 | 1.0542 | 1.0744 | 0.0202 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | NEWBOST2 | 1.0444 | 1.0744 | 0.03 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | GREGGTN2 | 1.0542 | 1.0744 | 0.0202 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | NEWBOST2 | 1.0444 | 1.0744 | 0.03 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | SVCPIPE2 | 1.0543 | 1.0745 | 0.0202 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | SPIPETP2 | 1.0543 | 1.0745 | 0.0202 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | SVCPIPE2 | 1.0543 | 1.0745 | 0.0202 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | SPIPETP2 | 1.0543 | 1.0745 | 0.0202 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | WATLANT2 | 1.0483 | 1.0746 | 0.0263 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | WATLANT2 | 1.0483 | 1.0746 | 0.0263 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | NNBOSTN2 | 1.0448 | 1.0747 | 0.0299 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | NNBOSTN2 | 1.0448 | 1.0747 | 0.0299 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | DAINGER2 | 1.0505 | 1.0748 | 0.0243 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | DAINGER2 | 1.0505 | 1.0748 | 0.0243 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | BIG3TAP2 | 1.055 | 1.075 | 0.02 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | BIG3TAP2 | 1.055 | 1.075 | 0.02 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | AINSWND7 | 1.1187 | 1.075 | 0.0437 | 115 | 0.9 | 1.05 | N/A | P12:115:NPPD:1167A:BASSETT:ONEILL 7:BTB
ERIS | 08NR | 3 | 24L | N/A | PITTSB_2 | 1.0521 | 1.0751 | 0.023 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | JENKNST2 | 1.0508 | 1.0751 | 0.0243 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | PITTSB_2 | 1.0521 | 1.0751 | 0.023 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | JENKNST2 | 1.0508 | 1.0751 | 0.0243 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | MOORHED7 | 1.0521 | 1.0751 | 0.023 | 115 | 0.9 | 1.05 | N/A | P14:013:UMZW:# 2232 #: FA IN ND. LOSS OF SHUNT (KW6A, KW7A, KW8A)
ERIS | 08NR | 3 | 24L | N/A | SABINE 2 | 1.0552 | 1.0752 | 0.02 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | SABINE 2 | 1.0552 | 1.0752 | 0.02 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | PINEYWD2 | 1.0536 | 1.0753 | 0.0217 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | PINEYWD2 | 1.0536 | 1.0753 | 0.0217 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | LINDEN 2 | 1.0495 | 1.0754 | 0.0259 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | LINDEN 2 | 1.0495 | 1.0754 | 0.0259 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | AIRLINE2 | 1.0557 | 1.0757 | 0.02 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | AIRLINE2 | 1.0557 | 1.0757 | 0.02 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | CRESBARD-ER8 | 1.0388 | 1.0757 | 0.0369 | 69 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 276 #: GRT IN SD. GROTON-LELAND OLDS LINE REACTOR
ERIS | 03NR | 3 | 20SP | N/A | MOS-CRSB-ER8 | 1.0388 | 1.0757 | 0.0369 | 69 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 276 #: GRT IN SD. GROTON-LELAND OLDS LINE REACTOR
ERIS | 03NR | 3 | 20SP | N/A | CLARKSV7 | 1.0456 | 1.0757 | 0.0301 | 345 | 0.9 | 1.05 | N/A | P23:345:AEPW:ONETA CB 3405A NBTB
ERIS | 08NR | 3 | 24L | N/A | LLAMOND2 | 1.0557 | 1.0758 | 0.0201 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | LLAMOND2 | 1.0557 | 1.0758 | 0.0201 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | LONGVHT2 | 1.0561 | 1.0759 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | LONGVHT2 | 1.0561 | 1.0759 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | HOWELL 2 | 1.0562 | 1.076 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | HOWELL 2 | 1.0562 | 1.076 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | GEN-2016-174 | 1.0305 | 1.076 | 0.0455 | 345 | 0.9 | 1.05 | N/A | P23:345:WERE:STRA_345-95::
ERIS | 08NR | 3 | 24L | N/A | SOLCHPL2 | 1.0545 | 1.0762 | 0.0217 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | JENKINS2 | 1.0521 | 1.0762 | 0.0241 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | SOLCHPL2 | 1.0545 | 1.0762 | 0.0217 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | JENKINS2 | 1.0521 | 1.0762 | 0.0241 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | GATES 2 | 1.0563 | 1.0764 | 0.0201 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | GATES 2 | 1.0563 | 1.0764 | 0.0201 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | HOLYLAK2 | 1.0549 | 1.0766 | 0.0217 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | HOLYLAK2 | 1.0549 | 1.0766 | 0.0217 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | CRESBARD-ER8 | 1.0329 | 1.0766 | 0.0437 | 69 | 0.9 | 1.05 | N/A | P11:115:UMZB:# 35 #: GGS1 IN SD. GROTON 1
ERIS | 03NR | 3 | 20SP | N/A | MOS-CRSB-ER8 | 1.0329 | 1.0766 | 0.0437 | 69 | 0.9 | 1.05 | N/A | P11:115:UMZB:# 35 #: GGS1 IN SD. GROTON 1
ERIS | 06NR | 3 | 24SP | N/A | CLARDON2 | 1.0344 | 1.0767 | 0.0423 | 69 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:CHLDR2WT
ERIS | 08NR | 3 | 24L | N/A | LONGVUE2 | 1.057 | 1.077 | 0.02 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | LONGVUE2 | 1.057 | 1.077 | 0.02 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | BURKMERE-ER8 | 1.0392 | 1.077 | 0.0378 | 69 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 276 #: GRT IN SD. GROTON-LELAND OLDS LINE REACTOR
ERIS | 08NR | 3 | 24L | N/A | KILGORE2 | 1.0575 | 1.0771 | 0.0196 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | KILGORE2 | 1.0575 | 1.0771 | 0.0196 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | HUGHES 2 | 1.0529 | 1.0772 | 0.0243 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | HUGHES 2 | 1.0529 | 1.0772 | 0.0243 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | SELONGV2 | 1.0575 | 1.0773 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | LETOURT2 | 1.0574 | 1.0773 | 0.0199 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | LTLMOND2 | 1.0556 | 1.0773 | 0.0217 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | SELONGV2 | 1.0575 | 1.0773 | 0.0198 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | LETOURT2 | 1.0574 | 1.0773 | 0.0199 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | LTLMOND2 | 1.0556 | 1.0773 | 0.0217 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | PECANCK7 | 1.0563 | 1.0774 | 0.0211 | 345 | 0.9 | 1.05 | N/A | P42:345:OKGE:SB_PECK7382
ERIS | 08NR | 3 | 24L | N/A | MONROCR2 | 1.0579 | 1.0776 | 0.0197 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | AIRPRD-2 | 1.0537 | 1.0776 | 0.0239 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | AIRPRDT2 | 1.0537 | 1.0776 | 0.0239 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 03NR | 3 | 20SP | N/A | ELLENDL4 | 1.0411 | 1.0776 | 0.0365 | 230 | 0.9 | 1.05 | N/A | P13:014-115-345:MDU::COYOTE::1::::
ERIS | 03NR | 3 | 20SP | N/A | ELLENDLMVP4 | 1.0411 | 1.0776 | 0.0365 | 230 | 0.9 | 1.05 | N/A | P13:014-115-345:MDU::COYOTE::1::::
ERIS | 03NR | 3 | 20SP | N/A | ELLENDL4 | 1.0411 | 1.0776 | 0.0365 | 230 | 0.9 | 1.05 | N/A | P14:014:MDU::HETTINGER::SWREACT::::
ERIS | 03NR | 3 | 20SP | N/A | ELLENDLMVP4 | 1.0411 | 1.0776 | 0.0365 | 230 | 0.9 | 1.05 | N/A | P14:014:MDU::HETTINGER::SWREACT::::
ERIS | 08NR | 3 | 24L | N/A | MONROCR2 | 1.0579 | 1.0776 | 0.0197 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | AIRPRD-2 | 1.0537 | 1.0776 | 0.0239 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | AIRPRDT2 | 1.0537 | 1.0776 | 0.0239 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 06NR | 3 | 24SP | N/A | CLARREC2 | 1.0347 | 1.0776 | 0.0429 | 69 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:CHLDR2WT
ERIS | 08NR | 3 | 24L | N/A | WHITNEY2 | 1.058 | 1.0779 | 0.0199 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | WHITNEY2 | 1.058 | 1.0779 | 0.0199 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | BURKMERE-ER8 | 1.0333 | 1.0779 | 0.0446 | 69 | 0.9 | 1.05 | N/A | P11:115:UMZB:# 35 #: GGS1 IN SD. GROTON 1
ERIS | 08NR | 3 | 24L | N/A | LSREC 2 | 1.0541 | 1.078 | 0.0239 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | LSREC 2 | 1.0541 | 1.078 | 0.0239 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | LSTARTP2 | 1.0545 | 1.0783 | 0.0238 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | DEKALB 2 | 1.0509 | 1.0783 | 0.0274 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | LSTARTP2 | 1.0545 | 1.0783 | 0.0238 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | DEKALB 2 | 1.0509 | 1.0783 | 0.0274 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | LONSTAR2 | 1.0548 | 1.0786 | 0.0238 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | LONSTAR2 | 1.0548 | 1.0786 | 0.0238 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 06NR | 3 | 29SP | N/A | HWRDWCK2 | 1.0499 | 1.0787 | 0.0288 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 06NR | 3 | 24SP | N/A | HWRDWCK2 | 1.0462 | 1.0787 | 0.0325 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 06NR | 3 | 29SP | N/A | EDWRDVL5 | 1.0376 | 1.0791 | 0.0415 | 161 | 0.9 | 1.05 | N/A | P12:161:WERE:EDWV-KCBPU_161::
ERIS | 06NR | 3 | 29SP | N/A | EDWRDVL5 | 1.0376 | 1.0791 | 0.0415 | 161 | 0.9 | 1.05 | N/A | P12:161:KACY:EDWARDSVILLE-METRO::EDWARDSVILLE-METRO OPEN
ERIS | 03NR | 3 | 20SP | N/A | GEN-2016-174 | 1.0353 | 1.0791 | 0.0438 | 345 | 0.9 | 1.05 | N/A | P23:345:WERE:STRA_345-100::
ERIS | 08NR | 3 | 24L | N/A | LSSOUTH2 | 1.0556 | 1.0793 | 0.0237 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | LSSOUTH2 | 1.0556 | 1.0793 | 0.0237 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 08NR | 3 | 24L | N/A | GILMR 2 | 1.0614 | 1.0829 | 0.0215 | 69 | 0.9 | 1.05 | N/A | P12:HV:EES::PIRKEY 4:1
ERIS | 08NR | 3 | 24L | N/A | GILMR 2 | 1.0614 | 1.0829 | 0.0215 | 69 | 0.9 | 1.05 | N/A | P13:138-24:AEPW:PIRKEY 4
ERIS | 03NR | 3 | 20SP | N/A | MUSKOGE7 | 1.063 | 1.0847 | 0.0217 | 345 | 0.9 | 1.05 | N/A | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
ERIS | 03NR | 3 | 20SP | N/A | ELLENDLMVP4 | 1.0457 | 1.0851 | 0.0394 | 230 | 0.9 | 1.05 | N/A | P12:115:MDU::NORTH DICKINSON:DICKINSON WEST:1::::
ERIS | 03NR | 3 | 20SP | N/A | FOXTAIL4 | 1.0377 | 1.0859 | 0.0482 | 230 | 0.9 | 1.05 | N/A | P12:230:MDU::MERRICOURT:WISHEK:1::::
ERIS | 03NR | 3 | 20SP | N/A | TTANKANORTH4 | 1.0369 | 1.0863 | 0.0494 | 230 | 0.9 | 1.05 | N/A | P12:230:MDU::MERRICOURT:WISHEK:1::::
ERIS | 03NR | 3 | 20SP | N/A | MERRCRT4 | 1.0355 | 1.0871 | 0.0516 | 230 | 0.9 | 1.05 | N/A | P12:230:MDU::MERRICOURT:WISHEK:1::::
ERIS | 03NR | 3 | 20SP | N/A | ELLENDL4 | 1.042 | 1.0874 | 0.0454 | 230 | 0.9 | 1.05 | N/A | P12:230:MDU::MERRICOURT:WISHEK:1::::
ERIS | 03NR | 3 | 20SP | N/A | ELLENDLMVP4 | 1.042 | 1.0874 | 0.0454 | 230 | 0.9 | 1.05 | N/A | P12:230:MDU::MERRICOURT:WISHEK:1::::
ERIS | 03NR | 3 | 20SP | N/A | ELLENDL7 | 1.0542 | 1.0879 | 0.0337 | 115 | 0.9 | 1.05 | N/A | P13:014-115-345:MDU::COYOTE::1::::
ERIS | 03NR | 3 | 20SP | N/A | ELLENDL7 | 1.0542 | 1.0879 | 0.0337 | 115 | 0.9 | 1.05 | N/A | P14:014:MDU::HETTINGER::SWREACT::::
ERIS | 03NR | 3 | 20SP | N/A | BROADLND-BE3 | 1.0669 | 1.0879 | 0.021 | 345 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 269 #: BD IN SD. BROADLAND LINE REACTOR
ERIS | 03NR | 3 | 20SP | N/A | BD.LS-AV-BE3 | 1.067 | 1.088 | 0.021 | 345 | 0.9 | 1.05 | N/A | P14:345:UMZB:# 269 #: BD IN SD. BROADLAND LINE REACTOR
ERIS | 03NR | 3 | 20SP | N/A | FTSMITH7 | 1.0635 | 1.0885 | 0.025 | 345 | 0.9 | 1.05 | N/A | P43:345-500:OKGE:SB_FTTH7306
ERIS | 06NR | 3 | 29SP | N/A | CLARDON2 | 1.0582 | 1.0886 | 0.0304 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 06NR | 3 | 24SP | N/A | CLARDON2 | 1.055 | 1.0886 | 0.0336 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 03NR | 3 | 20SP | N/A | GEN-2016-176 | 1.0382 | 1.0888 | 0.0506 | 345 | 0.9 | 1.05 | N/A | P23:345:WERE:STRA_345-100::
ERIS | 08NR | 3 | 20G | N/A | XIT_INTG 3 | 1.0488 | 1.089 | 0.0402 | 115 | 0.9 | 1.05 | N/A | P12:115:SPS:W80.1.DALLAM.XIT
ERIS | 08NR | 3 | 29SP | N/A | EDWRDVL5 | 1.0487 | 1.0893 | 0.0406 | 161 | 0.9 | 1.05 | N/A | P12:161:WERE:EDWV-KCBPU_161::
ERIS | 08NR | 3 | 29SP | N/A | EDWRDVL5 | 1.0487 | 1.0893 | 0.0406 | 161 | 0.9 | 1.05 | N/A | P12:161:KACY:EDWARDSVILLE-METRO::EDWARDSVILLE-METRO OPEN
ERIS | 06NR | 3 | 24SP | N/A | HEDLEY 2 | 1.0437 | 1.0893 | 0.0456 | 69 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:CHLDR2WT
ERIS | 06NR | 3 | 29SP | N/A | CLARREC2 | 1.0594 | 1.0901 | 0.0307 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 06NR | 3 | 24SP | N/A | CLARREC2 | 1.0562 | 1.0901 | 0.0339 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 08NR | 3 | 24L | N/A | KEYSTON3 | 1.0572 | 1.0902 | 0.033 | 345 | 0.9 | 1.05 | N/A | P42:345:NPPD:BKR-KEY-3310
ERIS | 03NR | 3 | 20SP | N/A | LEOLA 7 | 1.0551 | 1.0916 | 0.0365 | 115 | 0.9 | 1.05 | N/A | P13:014-115-345:MDU::COYOTE::1::::
ERIS | 03NR | 3 | 20SP | N/A | LEOLA 7 | 1.0551 | 1.0916 | 0.0365 | 115 | 0.9 | 1.05 | N/A | P14:014:MDU::HETTINGER::SWREACT::::
ERIS | 03NR | 3 | 20SP | N/A | GEN-2016-150 | 1.0382 | 1.092 | 0.0538 | 345 | 0.9 | 1.05 | N/A | P23:345:WERE:STRA_345-100::
ERIS | 03NR | 3 | 20SP | N/A | MOORHED4 | 1.0527 | 1.0931 | 0.0404 | 230 | 0.9 | 1.05 | N/A | P12:230:UMZS:# 2932 #: MDOE IN MN. LINE FAULT BTWN MOORHEAD-FARGO
ERIS | 06NR | 3 | 24SP | N/A | ESTELNE2 | 1.0471 | 1.0973 | 0.0502 | 69 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:CHLDR2WT
ERIS | 06NR | 3 | 24SP | N/A | CAREY 2 | 1.0464 | 1.0974 | 0.051 | 69 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:CHLDR2WT
ERIS | 06NR | 3 | 24SP | N/A | AMOCO 2 | 1.0455 | 1.0974 | 0.0519 | 69 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:CHLDR2WT
ERIS | 06NR | 3 | 24SP | N/A | AIRPORT2 | 1.0465 | 1.0982 | 0.0517 | 69 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:CHLDR2WT
ERIS | 06NR | 3 | 24SP | N/A | REDRIVR2 | 1.049 | 1.0984 | 0.0494 | 69 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:CHLDR2WT
ERIS | 06NR | 3 | 24SP | N/A | AMOCOTP2 | 1.0466 | 1.0984 | 0.0518 | 69 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:CHLDR2WT
ERIS | 06NR | 3 | 24SP | N/A | NMEMREC2 | 1.0516 | 1.099 | 0.0474 | 69 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:CHLDR2WT
ERIS | 06NR | 3 | 24SP | N/A | CHLDR2WT | 1.0496 | 1.1015 | 0.0519 | 69 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:CHLDR2WT
ERIS | 06NR | 3 | 24SP | N/A | NWMEMPH2 | 1.0545 | 1.1024 | 0.0479 | 69 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:CHLDR2WT
ERIS | 03NR | 3 | 20SP | N/A | C-RIVER4 | 1.0816 | 1.1027 | 0.0211 | 138 | 0.9 | 1.05 | N/A | P23:345:AEPW:PITTSBURG CB 3441A NBTB
ERIS | 06NR | 3 | 24SP | N/A | MEMPHIS2 | 1.0546 | 1.1028 | 0.0482 | 69 | 0.9 | 1.05 | N/A | P13:69-138:AEPW:CHLDR2WT
ERIS | 06NR | 3 | 29SP | N/A | HEDLEY 2 | 1.0733 | 1.1051 | 0.0318 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 06NR | 3 | 24SP | N/A | HEDLEY 2 | 1.0703 | 1.1051 | 0.0348 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 03NR | 3 | 20SP | N/A | C-RIVER4 | 1.0783 | 1.1063 | 0.028 | 138 | 0.9 | 1.05 | N/A | P12:345:OKGE-AEPW:BKRBKR409
ERIS | 01NR | 3 | 20G | N/A | FLANDRU7 | 1.0622 | 1.111 | 0.0488 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | FLANDRU7 | 1.0621 | 1.1113 | 0.0492 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | FLANDRU7 | 1.063 | 1.1116 | 0.0486 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | HOLLAND -LO7 | 1.0656 | 1.1144 | 0.0488 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | HOLLAND -LO7 | 1.0656 | 1.1147 | 0.0491 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | HOLLAND -LO7 | 1.0665 | 1.115 | 0.0485 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 29SP | N/A | NMEMREC2 | 1.084 | 1.1163 | 0.0323 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 06NR | 3 | 24SP | N/A | NMEMREC2 | 1.081 | 1.1163 | 0.0353 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 01NR | 3 | 20G | N/A | WARD-ER8 | 1.07 | 1.1201 | 0.0501 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 29SP | N/A | NWMEMPH2 | 1.0877 | 1.1202 | 0.0325 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 06NR | 3 | 24SP | N/A | NWMEMPH2 | 1.0848 | 1.1202 | 0.0354 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 06NR | 3 | 20G | N/A | WARD-ER8 | 1.0699 | 1.1204 | 0.0505 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | WARD-ER8 | 1.0708 | 1.1207 | 0.0499 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 29SP | N/A | MEMPHIS2 | 1.0883 | 1.1209 | 0.0326 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 06NR | 3 | 24SP | N/A | MEMPHIS2 | 1.0854 | 1.1209 | 0.0355 | 69 | 0.9 | 1.05 | N/A | P12:69:AEPW:CHLDR2WT:MEMPHIS2
ERIS | 01NR | 3 | 20G | N/A | FLANDRU8 | 1.073 | 1.123 | 0.05 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | SW234-ER8 | 1.0731 | 1.123 | 0.0499 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | FLANDRU8 | 1.073 | 1.1233 | 0.0503 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | SW234-ER8 | 1.073 | 1.1233 | 0.0503 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | EGAN-ER8 | 1.0727 | 1.1233 | 0.0506 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | FLANDRU8 | 1.0739 | 1.1236 | 0.0497 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | SW234-ER8 | 1.0739 | 1.1236 | 0.0497 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | EGAN-ER8 | 1.0726 | 1.1236 | 0.051 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | EGAN-ER8 | 1.0736 | 1.1239 | 0.0503 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | SW209-ER8 | 1.0744 | 1.1249 | 0.0505 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | SW209-ER8 | 1.0744 | 1.1253 | 0.0509 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | SW209-ER8 | 1.0753 | 1.1255 | 0.0502 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | COLEMAN-ER8 | 1.0753 | 1.1264 | 0.0511 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | COLEMAN-ER8 | 1.0752 | 1.1267 | 0.0515 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | WENTWRTH-ER8 | 1.0748 | 1.1268 | 0.052 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | COLEMAN-ER8 | 1.0762 | 1.127 | 0.0508 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | WENTWRTH-ER8 | 1.0747 | 1.1271 | 0.0524 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | MOS-CLMN-ER8 | 1.0763 | 1.1273 | 0.051 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | WENTWRTH-ER8 | 1.0757 | 1.1274 | 0.0517 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | MOS-CLMN-ER8 | 1.0762 | 1.1277 | 0.0515 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | MOS-CLMN-ER8 | 1.0772 | 1.1279 | 0.0507 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | RUTLAND-ER8 | 1.077 | 1.1285 | 0.0515 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | RUTLAND-ER8 | 1.0769 | 1.1289 | 0.052 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | MOS-LKV2-ER8 | 1.076 | 1.1289 | 0.0529 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | RUTLAND-ER8 | 1.0779 | 1.1292 | 0.0513 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | MOS-LKV2-ER8 | 1.0759 | 1.1293 | 0.0534 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | MOS-WTWR-ER8 | 1.0777 | 1.1295 | 0.0518 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | MOS-LKV2-ER8 | 1.0769 | 1.1296 | 0.0527 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | MOS-WTWR-ER8 | 1.0776 | 1.1298 | 0.0522 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | SW211-ER8 | 1.0783 | 1.1298 | 0.0515 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | MOS-WTWR-ER8 | 1.0786 | 1.1301 | 0.0515 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | SW211-ER8 | 1.0783 | 1.1301 | 0.0518 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | SW211-ER8 | 1.0792 | 1.1304 | 0.0512 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | MADISON-ER8 | 1.0779 | 1.1308 | 0.0529 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | MOS-FLDT-ER8 | 1.0779 | 1.1308 | 0.0529 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | MADISON-ER8 | 1.0779 | 1.1312 | 0.0533 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | MOS-FLDT-ER8 | 1.0779 | 1.1312 | 0.0533 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | MADISON-ER8 | 1.0789 | 1.1314 | 0.0525 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | MOS-FLDT-ER8 | 1.0789 | 1.1314 | 0.0525 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | MOS-LKV1-ER8 | 1.0789 | 1.1317 | 0.0528 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | AURORAIP-ER7 | 1.0816 | 1.1319 | 0.0503 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | MOS-LKV1-ER8 | 1.0789 | 1.1321 | 0.0532 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | AURORAIP-ER7 | 1.0815 | 1.1323 | 0.0508 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | MOS-LKV1-ER8 | 1.0799 | 1.1324 | 0.0525 | 69 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | AURORAIP-ER7 | 1.0824 | 1.1325 | 0.0501 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 01NR | 3 | 20G | N/A | AURORA 7 | 1.0825 | 1.1329 | 0.0504 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 06NR | 3 | 20G | N/A | AURORA 7 | 1.0825 | 1.1332 | 0.0507 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 08NR | 3 | 20G | N/A | AURORA 7 | 1.0834 | 1.1335 | 0.0501 | 115 | 0.9 | 1.05 | N/A | P12:115:UMZW:# 124 #: AUR IN SD. AUR-BR LINE FAULT
ERIS | 03NR | 3 | 20SP | N/A | EDWRDVL5 | 1.0791 | 1.1339 | 0.0548 | 161 | 0.9 | 1.05 | N/A | P12:161:WERE:EDWV-KCBPU_161::
ERIS | 03NR | 3 | 20SP | N/A | EDWRDVL5 | 1.0791 | 1.1339 | 0.0548 | 161 | 0.9 | 1.05 | N/A | P12:161:KACY:EDWARDSVILLE-METRO::EDWARDSVILLE-METRO OPEN
ERIS | 03NR | 3 | 20SP | N/A | FIREWHL-TAP | 1.1188 | 1.1404 | 0.0216 | 345 | 0.9 | 1.05 | N/A | P42:345:OKGE:SB_CRER7309
ERIS | 03NR | 3 | 20SP | N/A | G17-092-SWYD | 1.1205 | 1.1422 | 0.0217 | 345 | 0.9 | 1.05 | N/A | P42:345:OKGE:SB_CRER7309
ERIS | 03NR | 3 | 20SP | N/A | GEN-2017-092 | 1.1205 | 1.1422 | 0.0217 | 345 | 0.9 | 1.05 | N/A | P42:345:OKGE:SB_CRER7309
ERIS | 03NR | 3 | 20SP | N/A | C-RIVER7 | 1.1226 | 1.1443 | 0.0217 | 345 | 0.9 | 1.05 | N/A | P42:345:OKGE:SB_CRER7309

## Short Circuit Ratio
Study Request | Current Cluster | Cluster Group | Transmission Owner | Capacity | Service Type | Generation Type | Point of Interconnection | GEN Bus # | Gen ID | POI Bus # | DIS1701TC01ALL-24WP0.SAV |  | DIS1701TC01ALL-29SP0.SAV |  | DIS1701TC02ALL-24WP0.SAV |  | DIS1701TC02ALL-29SP0.SAV |  | DIS1701TC03ALL-24WP0.SAV |  | DIS1701TC03ALL-29SP0.SAV |  | DIS1701TC04ALL-24WP0.SAV |  | DIS1701TC04ALL-29SP0.SAV |  | DIS1701TC06ALL-24WP0.SAV |  | DIS1701TC06ALL-29SP0.SAV |  | DIS1701TC07ALL-24WP0.SAV |  | DIS1701TC07ALL-29SP0.SAV |  | DIS1701TC08ALL-24WP0.SAV |  | DIS1701TC08ALL-29SP0.SAV |  | DIS1701TC09ALL-24WP0.SAV |  | DIS1701TC09ALL-29SP0.SAV |  | DIS1701TC10ALL-24WP0.SAV |  | DIS1701TC10ALL-29SP0.SAV |  | DIS1701TC12ALL-24WP0.SAV |  | DIS1701TC12ALL-29SP0.SAV |  | DIS1701TC13ALL-24WP0.SAV |  | DIS1701TC13ALL-29SP0.SAV |  | DIS1701TC14ALL-24WP0.SAV |  | DIS1701TC14ALL-29SP0.SAV |  | DIS1701TC15ALL-24WP0.SAV |  | DIS1701TC15ALL-29SP0.SAV |  | DIS1701TC16ALL-24WP0.SAV |  | DIS1701TC16ALL-29SP0.SAV |  | DIS1701TC17ALL-24WP0.SAV |  | DIS1701TC17ALL-29SP0.SAV
[11 empty] | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio
ASGI-2016-001 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 2.5 | ER | Wind | Wolf Forth 115kV | 562502 | 1 | 526109 | 2005.68 | 802.272 | 2089.85 | 835.94 | 2158.27 | 863.308 | 2171.16 | 868.464 | 2158.25 | 863.3 | 2171.14 | 868.456 | 2158.25 | 863.3 | 2171.14 | 868.456 | 2160.64 | 864.256 | 2093.65 | 837.46 | 2158.23 | 863.292 | 2090.38 | 836.152 | 2005.68 | 802.272 | 2171.14 | 868.456 | 2158.25 | 863.3 | 2171.14 | 868.456 | 2158.25 | 863.3 | 2171.14 | 868.456 | 2158.25 | 863.3 | 2171.14 | 868.456 | 2158.25 | 863.3 | 2171.14 | 868.456 | 2158.25 | 863.3 | 2090.38 | 836.152 | 2158.25 | 863.3 | 2171.14 | 868.456 | 2158.25 | 863.3 | 2171.14 | 868.456 | 2158.25 | 863.3 | 2171.14 | 868.456
ASGI-2017-007 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 4.2 | ER/NR | Wind | Sp-erskine 115kV | 926103 | 1 | 526109 | 2005.68 | 477.5429 | 2089.85 | 497.5833 | 2158.27 | 513.8738 | 2171.16 | 516.9429 | 2158.25 | 513.869 | 2171.14 | 516.9381 | 2158.25 | 513.869 | 2171.14 | 516.9381 | 2160.64 | 514.4381 | 2093.65 | 498.4881 | 2158.23 | 513.8643 | 2090.38 | 497.7095 | 2005.68 | 477.5429 | 2171.14 | 516.9381 | 2158.25 | 513.869 | 2171.14 | 516.9381 | 2158.25 | 513.869 | 2171.14 | 516.9381 | 2158.25 | 513.869 | 2171.14 | 516.9381 | 2158.25 | 513.869 | 2171.14 | 516.9381 | 2158.25 | 513.869 | 2090.38 | 497.7095 | 2158.25 | 513.869 | 2171.14 | 516.9381 | 2158.25 | 513.869 | 2171.14 | 516.9381 | 2158.25 | 513.869 | 2171.14 | 516.9381
GEN-2016-005 | DISIS-2017-001 | 03 - Spearville | SUNC | 150 | ER/NR | Wind | Clark-Thistle 345kV | 587044 | 1 | 587040 | 7195.88 | 47.9725 | 7293.11 | 48.6207 | 7196.4 | 47.976 | 7295.58 | 48.6372 | 7198.47 | 47.9898 | 7293.91 | 48.6261 | 7189.48 | 47.9299 | 7285.04 | 48.5669 | 7196.27 | 47.9751 | 7294.02 | 48.6268 | 7192.32 | 47.9488 | 7295.41 | 48.6361 | 7194.88 | 47.9659 | 7297.75 | 48.6517 | 7189.59 | 47.9306 | 7282.88 | 48.5525 | 7199.72 | 47.9981 | 7297.13 | 48.6475 | 7199.72 | 47.9981 | 7297.13 | 48.6475 | 7196.3 | 47.9753 | 7294.62 | 48.6308 | 7196.29 | 47.9753 | 7295.41 | 48.6361 | 7199.7 | 47.998 | 7296.39 | 48.6426 | 7198.21 | 47.9881 | 7296.39 | 48.6426 | 7199.72 | 47.9981 | 7296.42 | 48.6428
GEN-2016-034 | DISIS-2017-001 | 09 - Nebraska | WAPA | 90 | ER | Wind | Laramie River Station-Sidney 345kV | 587223 | 1 | 587220 | 2984.32 | 33.1591 | 2993.62 | 33.2624 | 2984.57 | 33.1619 | 2993.67 | 33.263 | 2984.6 | 33.1622 | 2993.69 | 33.2632 | 2984.53 | 33.1614 | 2993.61 | 33.2623 | 2984.15 | 33.1572 | 2993.62 | 33.2624 | 2984.57 | 33.1619 | 2993.66 | 33.2629 | 2984.13 | 33.157 | 2993.72 | 33.2636 | 2984.14 | 33.1571 | 2991.56 | 33.2396 | 2984.62 | 33.1624 | 2993.71 | 33.2634 | 2984.62 | 33.1624 | 2993.71 | 33.2634 | 2984.57 | 33.1619 | 2993.65 | 33.2628 | 2984.57 | 33.1619 | 2993.66 | 33.2629 | 2984.24 | 33.1582 | 2993.42 | 33.2602 | 2984.22 | 33.158 | 2993.48 | 33.2609 | 2984.62 | 33.1624 | 2993.7 | 33.2633
GEN-2016-037 | DISIS-2017-001 | 07 - Southwestern Oklahoma | AEPW | 300 | ER/NR | Wind | Chisholm-Gracemont 345kV | 587233 | 1 | 587230 | 3693.27 | 12.3109 | 3714.57 | 12.3819 | 3695.69 | 12.319 | 3717.03 | 12.3901 | 3695.64 | 12.3188 | 3716.97 | 12.3899 | 3695.63 | 12.3188 | 3716.96 | 12.3899 | 3659.15 | 12.1972 | 3685.75 | 12.2858 | 3689.48 | 12.2983 | 3716.77 | 12.3892 | 3693.25 | 12.3108 | 3716.97 | 12.3899 | 3695.63 | 12.3188 | 3716.96 | 12.3899 | 3695.63 | 12.3188 | 3716.98 | 12.3899 | 3695.63 | 12.3188 | 3716.98 | 12.3899 | 3695.63 | 12.3188 | 3716.98 | 12.3899 | 3695.63 | 12.3188 | 3716.77 | 12.3892 | 3695.63 | 12.3188 | 3716.98 | 12.3899 | 3695.63 | 12.3188 | 3716.98 | 12.3899 | 3695.63 | 12.3188 | 3716.98 | 12.3899
GEN-2016-039 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 112 | ER | Solar | Swisher 115kV Substation | 587253 | 1 | 587250 | 2258.43 | 20.1646 | 2279.47 | 20.3524 | 2303.11 | 20.5635 | 2300.38 | 20.5391 | 2302.8 | 20.5607 | 2300.03 | 20.536 | 2302.78 | 20.5605 | 2300.03 | 20.536 | 2304.85 | 20.579 | 2291.98 | 20.4641 | 2302.77 | 20.5604 | 2287.48 | 20.4239 | 2258.43 | 20.1646 | 2300.05 | 20.5362 | 2302.78 | 20.5605 | 2300.03 | 20.536 | 2302.79 | 20.5606 | 2300.05 | 20.5362 | 2302.79 | 20.5606 | 2300.05 | 20.5362 | 2302.79 | 20.5606 | 2300.05 | 20.5362 | 2302.79 | 20.5606 | 2287.48 | 20.4239 | 2302.79 | 20.5606 | 2300.05 | 20.5362 | 2302.79 | 20.5606 | 2300.05 | 20.5362 | 2302.79 | 20.5606 | 2300.05 | 20.5362
GEN-2016-049 | DISIS-2017-001 | 03 - Spearville | SUNC | 155.1 | ER | Wind | Post Rock-Spearville 345kV | 589483 | 1 | 589480 | 5026.35 | 32.4072 | 5126.25 | 33.0513 | 5025.77 | 32.4034 | 5137.04 | 33.1208 | 5050.06 | 32.56 | 5146.85 | 33.1841 | 5040.69 | 32.4996 | 5141.15 | 33.1473 | 5026.43 | 32.4077 | 5126.37 | 33.052 | 5025.42 | 32.4012 | 5137.01 | 33.1206 | 5026.13 | 32.4057 | 5148.88 | 33.1972 | 5041.4 | 32.5042 | 5130.27 | 33.0772 | 5042.37 | 32.5104 | 5145.71 | 33.1767 | 5042.37 | 32.5104 | 5145.71 | 33.1767 | 5025.75 | 32.4033 | 5132.3 | 33.0903 | 5025.74 | 32.4032 | 5137.01 | 33.1206 | 5042.3 | 32.51 | 5141.76 | 33.1513 | 5035.1 | 32.4636 | 5141.76 | 33.1513 | 5042.37 | 32.5104 | 5141.93 | 33.1524
GEN-2016-049 | DISIS-2017-001 | 03 - Spearville | SUNC | 250.7 | ER | Wind | Post Rock-Spearville 345kV | 587353 | 1 | 587350 | 4834.17 | 19.2827 | 4887.78 | 19.4965 | 4827.29 | 19.2552 | 4891.47 | 19.5112 | 4833.57 | 19.2803 | 4894.13 | 19.5219 | 4831.83 | 19.2734 | 4893.42 | 19.519 | 4834.04 | 19.2822 | 4887.79 | 19.4966 | 4827.26 | 19.2551 | 4891.47 | 19.5112 | 4833.86 | 19.2815 | 4895.82 | 19.5286 | 4838.73 | 19.3009 | 4864.95 | 19.4055 | 4831.42 | 19.2717 | 4895.05 | 19.5255 | 4831.42 | 19.2717 | 4895.05 | 19.5255 | 4827.35 | 19.2555 | 4890.09 | 19.5057 | 4827.29 | 19.2552 | 4891.47 | 19.5112 | 4830.95 | 19.2698 | 4892.42 | 19.515 | 4829.16 | 19.2627 | 4892.43 | 19.5151 | 4831.42 | 19.2717 | 4894.14 | 19.5219
GEN-2016-072 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | OKGE | 300 | ER | Wind | Renfrow 345kV Substation | 587493 | 1 | 587490 | 7491.85 | 24.9728 | 7577.67 | 25.2589 | 7492.09 | 24.9736 | 7578.57 | 25.2619 | 7492.21 | 24.974 | 7578.53 | 25.2618 | 7492.05 | 24.9735 | 7578.45 | 25.2615 | 7481.71 | 24.939 | 7574.62 | 25.2487 | 7488.77 | 24.9626 | 7578.54 | 25.2618 | 7489.71 | 24.9657 | 7578.56 | 25.2619 | 7491.95 | 24.9732 | 7578.4 | 25.2613 | 7492.17 | 24.9739 | 7578.59 | 25.262 | 7492.17 | 24.9739 | 7578.59 | 25.262 | 7492.08 | 24.9736 | 7578.55 | 25.2618 | 7492.08 | 24.9736 | 7578.54 | 25.2618 | 7492.17 | 24.9739 | 7578.58 | 25.2619 | 7492.13 | 24.9738 | 7578.58 | 25.2619 | 7492.17 | 24.9739 | 7578.58 | 25.2619
GEN-2016-077 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 54 | ER/NR | Solar | Lakeview-Brownfield 69kV | 587693 | 1 | 587690 | 316.89 | 5.8683 | 317.43 | 5.8783 | 317.61 | 5.8817 | 317.78 | 5.8848 | 317.61 | 5.8817 | 317.78 | 5.8848 | 317.61 | 5.8817 | 317.78 | 5.8848 | 317.62 | 5.8819 | 317.45 | 5.8787 | 317.61 | 5.8817 | 317.43 | 5.8783 | 316.89 | 5.8683 | 317.78 | 5.8848 | 317.61 | 5.8817 | 317.78 | 5.8848 | 317.61 | 5.8817 | 317.78 | 5.8848 | 317.61 | 5.8817 | 317.78 | 5.8848 | 317.61 | 5.8817 | 317.78 | 5.8848 | 317.61 | 5.8817 | 317.43 | 5.8783 | 317.61 | 5.8817 | 317.78 | 5.8848 | 317.61 | 5.8817 | 317.78 | 5.8848 | 317.61 | 5.8817 | 317.78 | 5.8848
GEN-2016-078 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 108 | ER/NR | Solar | Bailey County 115kV Substation | 587703 | 1 | 587700 | 1067.41 | 9.8834 | 1308.66 | 12.1172 | 1076.21 | 9.9649 | 1311.88 | 12.147 | 1076.19 | 9.9647 | 1311.86 | 12.1469 | 1076.19 | 9.9647 | 1311.86 | 12.1469 | 1076.31 | 9.9658 | 1310.88 | 12.1378 | 1076.19 | 9.9647 | 1309.13 | 12.1216 | 1067.41 | 9.8834 | 1311.86 | 12.1469 | 1076.19 | 9.9647 | 1311.86 | 12.1469 | 1076.19 | 9.9647 | 1311.86 | 12.1469 | 1076.19 | 9.9647 | 1311.86 | 12.1469 | 1076.19 | 9.9647 | 1311.86 | 12.1469 | 1076.19 | 9.9647 | 1309.13 | 12.1216 | 1076.19 | 9.9647 | 1311.86 | 12.1469 | 1076.19 | 9.9647 | 1311.86 | 12.1469 | 1076.19 | 9.9647 | 1311.86 | 12.1469
GEN-2016-090 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 100 | ER/NR | Solar | Yoakum-Seagraves 115kV | 589463 | 1 | 589460 | 1539.25 | 15.3925 | 1557.94 | 15.5794 | 1555.71 | 15.5571 | 1567.12 | 15.6712 | 1555.71 | 15.5571 | 1567.12 | 15.6712 | 1555.71 | 15.5571 | 1567.12 | 15.6712 | 1555.95 | 15.5595 | 1558.42 | 15.5842 | 1555.71 | 15.5571 | 1558 | 15.58 | 1539.25 | 15.3925 | 1567.12 | 15.6712 | 1555.71 | 15.5571 | 1567.12 | 15.6712 | 1555.71 | 15.5571 | 1567.12 | 15.6712 | 1555.71 | 15.5571 | 1567.12 | 15.6712 | 1555.71 | 15.5571 | 1567.12 | 15.6712 | 1555.71 | 15.5571 | 1558 | 15.58 | 1555.71 | 15.5571 | 1567.12 | 15.6712 | 1555.71 | 15.5571 | 1567.12 | 15.6712 | 1555.71 | 15.5571 | 1567.12 | 15.6712
GEN-2016-093 | DISIS-2017-001 | 09 - Nebraska | NPPD | 70 | ER | Solar | Bobcat 115kV Substation | 589423 | 1 | 589420 | 1850.44 | 26.4349 | 1853.61 | 26.4801 | 1851.05 | 26.4436 | 1853.62 | 26.4803 | 1851.06 | 26.4437 | 1853.63 | 26.4804 | 1851.04 | 26.4434 | 1853.61 | 26.4801 | 1850.18 | 26.4311 | 1853.61 | 26.4801 | 1851.05 | 26.4436 | 1853.62 | 26.4803 | 1850.16 | 26.4309 | 1853.64 | 26.4806 | 1850.2 | 26.4314 | 1852.57 | 26.4653 | 1851.06 | 26.4437 | 1853.63 | 26.4804 | 1851.06 | 26.4437 | 1853.63 | 26.4804 | 1851.05 | 26.4436 | 1853.62 | 26.4803 | 1851.05 | 26.4436 | 1853.62 | 26.4803 | 1850.53 | 26.4361 | 1853.25 | 26.475 | 1850.52 | 26.436 | 1853.33 | 26.4761 | 1851.06 | 26.4437 | 1853.63 | 26.4804
GEN-2016-103 | DISIS-2017-001 | 15 - Eastern South Dakota | WAPA | 250.7 | ER/NR | Wind | Fort Thompson-Leland Olds 345kV | 587833 | 1 | 587830 | 4368.55 | 17.4254 | 4637 | 18.4962 | 4613.25 | 18.4015 | 4637.03 | 18.4963 | 4613.26 | 18.4015 | 4637.03 | 18.4963 | 4613.25 | 18.4015 | 4637.03 | 18.4963 | 4325.33 | 17.253 | 4637 | 18.4962 | 4613.25 | 18.4015 | 4637.03 | 18.4963 | 4322.81 | 17.243 | 4637.07 | 18.4965 | 4330.63 | 17.2742 | 4394.59 | 17.5293 | 4613.26 | 18.4015 | 4637.07 | 18.4965 | 4613.26 | 18.4015 | 4637.07 | 18.4965 | 4613.26 | 18.4015 | 4637.02 | 18.4963 | 4613.25 | 18.4015 | 4637.03 | 18.4963 | 4393.58 | 17.5252 | 4440.33 | 17.7117 | 4393.37 | 17.5244 | 4455 | 17.7702 | 4613.26 | 18.4015 | 4637.07 | 18.4965
GEN-2016-107 | DISIS-2017-001 | 01 - Woodward | WFEC | 75.6 | ER/NR | Wind | Okeene-Cederdale 138kV | 589443 | 1 | 589440 | 1381.19 | 18.2697 | 1382.03 | 18.2808 | 1381.2 | 18.2698 | 1382.11 | 18.2819 | 1381.2 | 18.2698 | 1382.11 | 18.2819 | 1381.2 | 18.2698 | 1382.11 | 18.2819 | 1379.83 | 18.2517 | 1381.57 | 18.2747 | 1361.7 | 18.0119 | 1382.11 | 18.2819 | 1381.18 | 18.2696 | 1382.11 | 18.2819 | 1381.2 | 18.2698 | 1382.11 | 18.2819 | 1381.2 | 18.2698 | 1382.11 | 18.2819 | 1381.2 | 18.2698 | 1382.11 | 18.2819 | 1381.2 | 18.2698 | 1382.11 | 18.2819 | 1381.2 | 18.2698 | 1382.11 | 18.2819 | 1381.2 | 18.2698 | 1382.11 | 18.2819 | 1381.2 | 18.2698 | 1382.11 | 18.2819 | 1381.2 | 18.2698 | 1382.11 | 18.2819
GEN-2016-107 | DISIS-2017-001 | 01 - Woodward | WFEC | 66.15 | ER/NR | Wind | Okeene-Cederdale 138kV | 589447 | 1 | 589440 | 1381.19 | 20.8797 | 1382.03 | 20.8924 | 1381.2 | 20.8798 | 1382.11 | 20.8936 | 1381.2 | 20.8798 | 1382.11 | 20.8936 | 1381.2 | 20.8798 | 1382.11 | 20.8936 | 1379.83 | 20.8591 | 1381.57 | 20.8854 | 1361.7 | 20.585 | 1382.11 | 20.8936 | 1381.18 | 20.8795 | 1382.11 | 20.8936 | 1381.2 | 20.8798 | 1382.11 | 20.8936 | 1381.2 | 20.8798 | 1382.11 | 20.8936 | 1381.2 | 20.8798 | 1382.11 | 20.8936 | 1381.2 | 20.8798 | 1382.11 | 20.8936 | 1381.2 | 20.8798 | 1382.11 | 20.8936 | 1381.2 | 20.8798 | 1382.11 | 20.8936 | 1381.2 | 20.8798 | 1382.11 | 20.8936 | 1381.2 | 20.8798 | 1382.11 | 20.8936
GEN-2016-109 | DISIS-2017-001 | 09 - Nebraska | NPPD | 102 | ER/NR | Wind | Fairbury 115kV Substation | 589453 | 1 | 589450 | 970.51 | 9.5148 | 1019.93 | 9.9993 | 970.29 | 9.5126 | 1020.11 | 10.0011 | 970.3 | 9.5127 | 1020.12 | 10.0012 | 970.3 | 9.5127 | 1020.12 | 10.0012 | 970.5 | 9.5147 | 1019.93 | 9.9993 | 970.29 | 9.5126 | 1020.11 | 10.0011 | 970.48 | 9.5145 | 1020.42 | 10.0041 | 970.52 | 9.5149 | 971.77 | 9.5272 | 970.3 | 9.5127 | 1020.42 | 10.0041 | 970.3 | 9.5127 | 1020.42 | 10.0041 | 970.31 | 9.5128 | 1020.07 | 10.0007 | 970.29 | 9.5126 | 1020.11 | 10.0011 | 970.28 | 9.5125 | 1020.11 | 10.0011 | 970.28 | 9.5125 | 1020.11 | 10.0011 | 970.3 | 9.5127 | 1020.42 | 10.0041
GEN-2016-127 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | AEPW | 101.2 | ER/NR | Wind | Shidler 138kV Substation | 588033 | 1 | 588030 | 2016.24 | 19.9233 | 2031.69 | 20.076 | 2016.33 | 19.9242 | 2031.78 | 20.0769 | 2016.33 | 19.9242 | 2031.78 | 20.0769 | 2016.33 | 19.9242 | 2031.78 | 20.0769 | 2015.21 | 19.9131 | 2030.99 | 20.0691 | 2016.29 | 19.9238 | 2031.78 | 20.0769 | 2015.65 | 19.9175 | 2031.74 | 20.0765 | 2016.24 | 19.9233 | 2031.78 | 20.0769 | 2016.33 | 19.9242 | 2031.78 | 20.0769 | 2016.33 | 19.9242 | 2031.78 | 20.0769 | 2016.33 | 19.9242 | 2031.78 | 20.0769 | 2016.33 | 19.9242 | 2031.78 | 20.0769 | 2016.33 | 19.9242 | 2031.78 | 20.0769 | 2016.33 | 19.9242 | 2031.78 | 20.0769 | 2016.33 | 19.9242 | 2031.78 | 20.0769
GEN-2016-127 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | AEPW | 98.9 | ER/NR | Wind | Shidler 138kV Substation | 588036 | 1 | 588030 | 2016.24 | 20.3867 | 2031.69 | 20.5429 | 2016.33 | 20.3876 | 2031.78 | 20.5438 | 2016.33 | 20.3876 | 2031.78 | 20.5438 | 2016.33 | 20.3876 | 2031.78 | 20.5438 | 2015.21 | 20.3762 | 2030.99 | 20.5358 | 2016.29 | 20.3872 | 2031.78 | 20.5438 | 2015.65 | 20.3807 | 2031.74 | 20.5434 | 2016.24 | 20.3867 | 2031.78 | 20.5438 | 2016.33 | 20.3876 | 2031.78 | 20.5438 | 2016.33 | 20.3876 | 2031.78 | 20.5438 | 2016.33 | 20.3876 | 2031.78 | 20.5438 | 2016.33 | 20.3876 | 2031.78 | 20.5438 | 2016.33 | 20.3876 | 2031.78 | 20.5438 | 2016.33 | 20.3876 | 2031.78 | 20.5438 | 2016.33 | 20.3876 | 2031.78 | 20.5438
GEN-2016-159 | DISIS-2017-001 | 09 - Nebraska | NPPD | 213.9 | ER/NR | Wind | Turtle Creek 345kV Substation | 588383 | 1 | 588380 | 2178.32 | 10.1838 | 2182.05 | 10.2013 | 2178.58 | 10.185 | 2182.33 | 10.2026 | 2178.58 | 10.185 | 2182.33 | 10.2026 | 2178.58 | 10.185 | 2182.33 | 10.2026 | 2178 | 10.1823 | 2182.05 | 10.2013 | 2178.58 | 10.185 | 2182.33 | 10.2026 | 2176.74 | 10.1764 | 2182.67 | 10.2042 | 2178.77 | 10.1859 | 2181.57 | 10.199 | 2178.58 | 10.185 | 2182.67 | 10.2042 | 2178.58 | 10.185 | 2182.67 | 10.2042 | 2178.59 | 10.1851 | 2182.26 | 10.2022 | 2178.58 | 10.185 | 2182.33 | 10.2026 | 2178.26 | 10.1835 | 2182.54 | 10.2036 | 2178.2 | 10.1833 | 2182.36 | 10.2027 | 2178.58 | 10.185 | 2182.67 | 10.2042
GEN-2016-159 | DISIS-2017-001 | 09 - Nebraska | NPPD | 213.9 | ER/NR | Wind | Turtle Creek 345kV Substation | 588386 | 1 | 588380 | 2178.32 | 10.1838 | 2182.05 | 10.2013 | 2178.58 | 10.185 | 2182.33 | 10.2026 | 2178.58 | 10.185 | 2182.33 | 10.2026 | 2178.58 | 10.185 | 2182.33 | 10.2026 | 2178 | 10.1823 | 2182.05 | 10.2013 | 2178.58 | 10.185 | 2182.33 | 10.2026 | 2176.74 | 10.1764 | 2182.67 | 10.2042 | 2178.77 | 10.1859 | 2181.57 | 10.199 | 2178.58 | 10.185 | 2182.67 | 10.2042 | 2178.58 | 10.185 | 2182.67 | 10.2042 | 2178.59 | 10.1851 | 2182.26 | 10.2022 | 2178.58 | 10.185 | 2182.33 | 10.2026 | 2178.26 | 10.1835 | 2182.54 | 10.2036 | 2178.2 | 10.1833 | 2182.36 | 10.2027 | 2178.58 | 10.185 | 2182.67 | 10.2042
GEN-2016-171 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 64 | ER | Solar | Hobbs-Yoakum 230kV | 588353 | 1 | 588350 | 3526.23 | 55.0973 | 3554.75 | 55.543 | 3762.58 | 58.7903 | 3707.24 | 57.9256 | 3762.57 | 58.7902 | 3707.23 | 57.9255 | 3762.57 | 58.7902 | 3707.23 | 57.9255 | 3763.93 | 58.8114 | 3557.41 | 55.5845 | 3762.56 | 58.79 | 3555.04 | 55.5475 | 3526.23 | 55.0973 | 3707.23 | 57.9255 | 3762.57 | 58.7902 | 3707.23 | 57.9255 | 3762.57 | 58.7902 | 3707.23 | 57.9255 | 3762.57 | 58.7902 | 3707.23 | 57.9255 | 3762.57 | 58.7902 | 3707.23 | 57.9255 | 3762.57 | 58.7902 | 3555.04 | 55.5475 | 3762.57 | 58.7902 | 3707.23 | 57.9255 | 3762.57 | 58.7902 | 3707.23 | 57.9255 | 3762.57 | 58.7902 | 3707.23 | 57.9255
GEN-2016-172 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 117 | ER | Wind | Newhart 115kV Substation | 588443 | 1 | 588440 | 3069.52 | 26.2352 | 3092.01 | 26.4274 | 3139.57 | 26.8339 | 3117.76 | 26.6475 | 3139.03 | 26.8293 | 3117.16 | 26.6424 | 3139.01 | 26.8291 | 3117.15 | 26.6423 | 3141.8 | 26.853 | 3113.38 | 26.6101 | 3138.99 | 26.829 | 3103.64 | 26.5268 | 3069.52 | 26.2352 | 3117.19 | 26.6426 | 3139.01 | 26.8291 | 3117.15 | 26.6423 | 3139.02 | 26.8292 | 3117.19 | 26.6426 | 3139.02 | 26.8292 | 3117.19 | 26.6426 | 3139.02 | 26.8292 | 3117.19 | 26.6426 | 3139.02 | 26.8292 | 3103.64 | 26.5268 | 3139.02 | 26.8292 | 3117.19 | 26.6426 | 3139.02 | 26.8292 | 3117.19 | 26.6426 | 3139.02 | 26.8292 | 3117.19 | 26.6426
GEN-2016-172 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 114 | ER | Wind | Newhart 115kV Substation | 588446 | 1 | 588440 | 3069.52 | 26.9256 | 3092.01 | 27.1229 | 3139.57 | 27.5401 | 3117.76 | 27.3488 | 3139.03 | 27.5354 | 3117.16 | 27.3435 | 3139.01 | 27.5352 | 3117.15 | 27.3434 | 3141.8 | 27.5596 | 3113.38 | 27.3104 | 3138.99 | 27.535 | 3103.64 | 27.2249 | 3069.52 | 26.9256 | 3117.19 | 27.3438 | 3139.01 | 27.5352 | 3117.15 | 27.3434 | 3139.02 | 27.5353 | 3117.19 | 27.3438 | 3139.02 | 27.5353 | 3117.19 | 27.3438 | 3139.02 | 27.5353 | 3117.19 | 27.3438 | 3139.02 | 27.5353 | 3103.64 | 27.2249 | 3139.02 | 27.5353 | 3117.19 | 27.3438 | 3139.02 | 27.5353 | 3117.19 | 27.3438 | 3139.02 | 27.5353 | 3117.19 | 27.3438
GEN-2016-173 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | WERE | 42 | ER/NR | Solar | Creswell 69kV Substation | 588423 | 1 | 588420 | 1677.42 | 39.9386 | 1719.45 | 40.9393 | 1677.43 | 39.9388 | 1719.47 | 40.9398 | 1677.43 | 39.9388 | 1719.47 | 40.9398 | 1677.43 | 39.9388 | 1719.46 | 40.9395 | 1677.32 | 39.9362 | 1719.42 | 40.9386 | 1677.38 | 39.9376 | 1719.47 | 40.9398 | 1677.27 | 39.935 | 1719.46 | 40.9395 | 1677.42 | 39.9386 | 1719.46 | 40.9395 | 1677.43 | 39.9388 | 1719.47 | 40.9398 | 1677.43 | 39.9388 | 1719.47 | 40.9398 | 1677.43 | 39.9388 | 1719.47 | 40.9398 | 1677.43 | 39.9388 | 1719.47 | 40.9398 | 1677.43 | 39.9388 | 1719.47 | 40.9398 | 1677.43 | 39.9388 | 1719.47 | 40.9398 | 1677.43 | 39.9388 | 1719.47 | 40.9398
GEN-2017-001 | DISIS-2017-001 | 09 - Nebraska | NPPD | 250 | ER/NR | Wind | Sweetwater 345kV Substation | 588373 | 1 | 588370 | 3642.49 | 14.57 | 3672.36 | 14.6894 | 3634.68 | 14.5387 | 3673.44 | 14.6938 | 3635.22 | 14.5409 | 3673.68 | 14.6947 | 3634.95 | 14.5398 | 3673.48 | 14.6939 | 3642.28 | 14.5691 | 3672.36 | 14.6894 | 3634.68 | 14.5387 | 3673.44 | 14.6938 | 3642.12 | 14.5685 | 3674.86 | 14.6994 | 3642.71 | 14.5708 | 3655.43 | 14.6217 | 3635.09 | 14.5404 | 3674.78 | 14.6991 | 3635.09 | 14.5404 | 3674.78 | 14.6991 | 3634.73 | 14.5389 | 3673.15 | 14.6926 | 3634.68 | 14.5387 | 3673.44 | 14.6938 | 3634.38 | 14.5375 | 3673.19 | 14.6928 | 3634.19 | 14.5368 | 3673.21 | 14.6928 | 3635.09 | 14.5404 | 3674.7 | 14.6988
GEN-2017-004 | DISIS-2017-001 | 04 - Northwest Kansas | SUNC | 201.6 | ER/NR | Wind | Elm Creek-Summit 345kV | 588493 | 1 | 588490 | 5519.46 | 27.3783 | 5763.27 | 28.5876 | 5519.48 | 27.3784 | 5763.89 | 28.5907 | 5521.38 | 27.3878 | 5764.51 | 28.5938 | 5520.88 | 27.3853 | 5764.4 | 28.5933 | 5519.37 | 27.3778 | 5763.27 | 28.5876 | 5519.33 | 27.3776 | 5763.88 | 28.5907 | 5516.21 | 27.3622 | 5764.56 | 28.594 | 5520.88 | 27.3853 | 5763.37 | 28.5881 | 5520.7 | 27.3844 | 5764.39 | 28.5932 | 5520.7 | 27.3844 | 5764.39 | 28.5932 | 5519.49 | 27.3784 | 5763.63 | 28.5894 | 5519.48 | 27.3784 | 5763.88 | 28.5907 | 5520.7 | 27.3844 | 5764.16 | 28.5921 | 5520.17 | 27.3818 | 5764.16 | 28.5921 | 5520.7 | 27.3844 | 5764.17 | 28.5921
GEN-2017-005 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | WERE | 195 | ER | Wind | Marmaton-Litchfield 161kV | 588503 | 1 | 588500 | 1832.06 | 9.3952 | 1852.59 | 9.5005 | 1838.78 | 9.4296 | 1852.59 | 9.5005 | 1838.78 | 9.4296 | 1852.59 | 9.5005 | 1838.78 | 9.4296 | 1852.59 | 9.5005 | 1832.02 | 9.395 | 1852.55 | 9.5003 | 1838.78 | 9.4296 | 1852.59 | 9.5005 | 1830.15 | 9.3854 | 1847.39 | 9.4738 | 1832.06 | 9.3952 | 1852.59 | 9.5005 | 1838.78 | 9.4296 | 1852.59 | 9.5005 | 1838.78 | 9.4296 | 1852.59 | 9.5005 | 1838.78 | 9.4296 | 1852.6 | 9.5005 | 1838.78 | 9.4296 | 1852.59 | 9.5005 | 1838.78 | 9.4296 | 1852.59 | 9.5005 | 1838.78 | 9.4296 | 1852.59 | 9.5005 | 1838.78 | 9.4296 | 1852.59 | 9.5005
GEN-2017-006 | DISIS-2017-001 | 09 - Nebraska | NPPD | 73.6 | ER | Wind | Moore (GEN-2015-088 Tap)-PauLine 345kV | 588513 | 1 | 587780 | 6066.07 | 82.4194 | 6201.57 | 84.2605 | 6056.69 | 82.292 | 6221.94 | 84.5372 | 6057.07 | 82.2971 | 6222.09 | 84.5393 | 6056.94 | 82.2954 | 6222.02 | 84.5383 | 6065.71 | 82.4145 | 6201.57 | 84.2605 | 6056.69 | 82.292 | 6221.94 | 84.5372 | 6064.88 | 82.4033 | 6250.29 | 84.9224 | 6067.06 | 82.4329 | 6121.95 | 83.1787 | 6056.95 | 82.2955 | 6250.24 | 84.9217 | 6056.95 | 82.2955 | 6250.24 | 84.9217 | 6057.86 | 82.3079 | 6217.59 | 84.4781 | 6056.69 | 82.292 | 6221.94 | 84.5372 | 6055.84 | 82.2804 | 6221.77 | 84.5349 | 6055.66 | 82.278 | 6221.68 | 84.5337 | 6056.95 | 82.2955 | 6250.19 | 84.9211
GEN-2017-007 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 147.5 | ER | Wind | Pleasant Hill 230kV Substation | 588523 | 1 | 588520 | 1474.69 | 9.9979 | 1478.46 | 10.0235 | 1485.35 | 10.0702 | 1483.53 | 10.0578 | 1485.34 | 10.0701 | 1483.52 | 10.0578 | 1485.34 | 10.0701 | 1483.52 | 10.0578 | 1485.45 | 10.0708 | 1480.04 | 10.0342 | 1485.34 | 10.0701 | 1478.72 | 10.0252 | 1474.69 | 9.9979 | 1483.52 | 10.0578 | 1485.34 | 10.0701 | 1483.52 | 10.0578 | 1485.34 | 10.0701 | 1483.52 | 10.0578 | 1485.34 | 10.0701 | 1483.52 | 10.0578 | 1485.34 | 10.0701 | 1483.52 | 10.0578 | 1485.34 | 10.0701 | 1478.72 | 10.0252 | 1485.34 | 10.0701 | 1483.52 | 10.0578 | 1485.34 | 10.0701 | 1483.52 | 10.0578 | 1485.34 | 10.0701 | 1483.52 | 10.0578
GEN-2017-007 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 150 | ER | Wind | Pleasant Hill 230kV Substation | 588527 | 1 | 588520 | 1474.69 | 9.8313 | 1478.46 | 9.8564 | 1485.35 | 9.9023 | 1483.53 | 9.8902 | 1485.34 | 9.9023 | 1483.52 | 9.8901 | 1485.34 | 9.9023 | 1483.52 | 9.8901 | 1485.45 | 9.903 | 1480.04 | 9.8669 | 1485.34 | 9.9023 | 1478.72 | 9.8581 | 1474.69 | 9.8313 | 1483.52 | 9.8901 | 1485.34 | 9.9023 | 1483.52 | 9.8901 | 1485.34 | 9.9023 | 1483.52 | 9.8901 | 1485.34 | 9.9023 | 1483.52 | 9.8901 | 1485.34 | 9.9023 | 1483.52 | 9.8901 | 1485.34 | 9.9023 | 1478.72 | 9.8581 | 1485.34 | 9.9023 | 1483.52 | 9.8901 | 1485.34 | 9.9023 | 1483.52 | 9.8901 | 1485.34 | 9.9023 | 1483.52 | 9.8901
GEN-2017-008 | DISIS-2017-001 | 09 - Nebraska | NPPD | 155 | ER | Solar | Moore (GEN-2016-096 Tap)-PauLine 345kV | 588533 | 1 | 588530 | 4644.5 | 29.9645 | 4705.36 | 30.3572 | 4634.93 | 29.9028 | 4711.45 | 30.3965 | 4635.63 | 29.9073 | 4711.74 | 30.3983 | 4635.4 | 29.9058 | 4711.62 | 30.3975 | 4644.29 | 29.9632 | 4705.36 | 30.3572 | 4634.93 | 29.9028 | 4711.45 | 30.3965 | 4643.95 | 29.961 | 4719.82 | 30.4505 | 4645.16 | 29.9688 | 4667.65 | 30.1139 | 4635.41 | 29.9059 | 4719.74 | 30.4499 | 4635.41 | 29.9059 | 4719.74 | 30.4499 | 4635.27 | 29.905 | 4710.08 | 30.3876 | 4634.93 | 29.9028 | 4711.45 | 30.3965 | 4634.73 | 29.9015 | 4711.36 | 30.3959 | 4634.5 | 29.9 | 4711.34 | 30.3957 | 4635.41 | 29.9059 | 4719.64 | 30.4493
GEN-2017-008 | DISIS-2017-001 | 09 - Nebraska | NPPD | 150 | ER | Solar | Moore (GEN-2016-096 Tap)-PauLine 345kV | 588537 | 1 | 588530 | 4644.5 | 30.9633 | 4705.36 | 31.3691 | 4634.93 | 30.8995 | 4711.45 | 31.4097 | 4635.63 | 30.9042 | 4711.74 | 31.4116 | 4635.4 | 30.9027 | 4711.62 | 31.4108 | 4644.29 | 30.9619 | 4705.36 | 31.3691 | 4634.93 | 30.8995 | 4711.45 | 31.4097 | 4643.95 | 30.9597 | 4719.82 | 31.4655 | 4645.16 | 30.9677 | 4667.65 | 31.1177 | 4635.41 | 30.9027 | 4719.74 | 31.4649 | 4635.41 | 30.9027 | 4719.74 | 31.4649 | 4635.27 | 30.9018 | 4710.08 | 31.4005 | 4634.93 | 30.8995 | 4711.45 | 31.4097 | 4634.73 | 30.8982 | 4711.36 | 31.4091 | 4634.5 | 30.8967 | 4711.34 | 31.4089 | 4635.41 | 30.9027 | 4719.64 | 31.4643
GEN-2017-009 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | WERE | 121 | ER | Wind | Neosho-Caney River 345kV | 588543 | 1 | 588540 | 6654.54 | 54.9962 | 6699.84 | 55.3706 | 6666.69 | 55.0966 | 6699.92 | 55.3712 | 6666.71 | 55.0968 | 6699.92 | 55.3712 | 6666.7 | 55.0967 | 6699.91 | 55.3712 | 6652.74 | 54.9813 | 6697.89 | 55.3545 | 6666.59 | 55.0958 | 6699.92 | 55.3712 | 6609.3 | 54.6223 | 6690.91 | 55.2968 | 6654.55 | 54.9963 | 6699.9 | 55.3711 | 6666.71 | 55.0968 | 6699.92 | 55.3712 | 6666.71 | 55.0968 | 6699.92 | 55.3712 | 6666.7 | 55.0967 | 6699.92 | 55.3712 | 6666.69 | 55.0966 | 6699.92 | 55.3712 | 6666.71 | 55.0968 | 6699.92 | 55.3712 | 6666.7 | 55.0967 | 6699.92 | 55.3712 | 6666.71 | 55.0968 | 6699.92 | 55.3712
GEN-2017-009 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | WERE | 30 | ER | Wind | Neosho-Caney River 345kV | 588543 | 2 | 588540 | 6654.54 | 221.818 | 6699.84 | 223.328 | 6666.69 | 222.223 | 6699.92 | 223.3307 | 6666.71 | 222.2237 | 6699.92 | 223.3307 | 6666.7 | 222.2233 | 6699.91 | 223.3303 | 6652.74 | 221.758 | 6697.89 | 223.263 | 6666.59 | 222.2197 | 6699.92 | 223.3307 | 6609.3 | 220.31 | 6690.91 | 223.0303 | 6654.55 | 221.8183 | 6699.9 | 223.33 | 6666.71 | 222.2237 | 6699.92 | 223.3307 | 6666.71 | 222.2237 | 6699.92 | 223.3307 | 6666.7 | 222.2233 | 6699.92 | 223.3307 | 6666.69 | 222.223 | 6699.92 | 223.3307 | 6666.71 | 222.2237 | 6699.92 | 223.3307 | 6666.7 | 222.2233 | 6699.92 | 223.3307 | 6666.71 | 222.2237 | 6699.92 | 223.3307
GEN-2017-009 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | WERE | 121 | ER | Wind | Neosho-Caney River 345kV | 588547 | 1 | 588540 | 6654.54 | 54.9962 | 6699.84 | 55.3706 | 6666.69 | 55.0966 | 6699.92 | 55.3712 | 6666.71 | 55.0968 | 6699.92 | 55.3712 | 6666.7 | 55.0967 | 6699.91 | 55.3712 | 6652.74 | 54.9813 | 6697.89 | 55.3545 | 6666.59 | 55.0958 | 6699.92 | 55.3712 | 6609.3 | 54.6223 | 6690.91 | 55.2968 | 6654.55 | 54.9963 | 6699.9 | 55.3711 | 6666.71 | 55.0968 | 6699.92 | 55.3712 | 6666.71 | 55.0968 | 6699.92 | 55.3712 | 6666.7 | 55.0967 | 6699.92 | 55.3712 | 6666.69 | 55.0966 | 6699.92 | 55.3712 | 6666.71 | 55.0968 | 6699.92 | 55.3712 | 6666.7 | 55.0967 | 6699.92 | 55.3712 | 6666.71 | 55.0968 | 6699.92 | 55.3712
GEN-2017-009 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | WERE | 30.5 | ER | Wind | Neosho-Caney River 345kV | 588547 | 2 | 588540 | 6654.54 | 218.1816 | 6699.84 | 219.6669 | 6666.69 | 218.58 | 6699.92 | 219.6695 | 6666.71 | 218.5807 | 6699.92 | 219.6695 | 6666.7 | 218.5803 | 6699.91 | 219.6692 | 6652.74 | 218.1226 | 6697.89 | 219.603 | 6666.59 | 218.5767 | 6699.92 | 219.6695 | 6609.3 | 216.6984 | 6690.91 | 219.3741 | 6654.55 | 218.182 | 6699.9 | 219.6689 | 6666.71 | 218.5807 | 6699.92 | 219.6695 | 6666.71 | 218.5807 | 6699.92 | 219.6695 | 6666.7 | 218.5803 | 6699.92 | 219.6695 | 6666.69 | 218.58 | 6699.92 | 219.6695 | 6666.71 | 218.5807 | 6699.92 | 219.6695 | 6666.7 | 218.5803 | 6699.92 | 219.6695 | 6666.71 | 218.5807 | 6699.92 | 219.6695
GEN-2017-010 | DISIS-2017-001 | 16 - Western North Dakota | WAPA | 200.1 | ER | Wind | Rhame 230kV Substation | 588553 | 1 | 588550 | 1600.79 | 8 | 1667.99 | 8.3358 | 1602.12 | 8.0066 | 1667.99 | 8.3358 | 1602.12 | 8.0066 | 1667.99 | 8.3358 | 1602.12 | 8.0066 | 1667.99 | 8.3358 | 1588.53 | 7.9387 | 1667.99 | 8.3358 | 1602.12 | 8.0066 | 1667.99 | 8.3358 | 1571.31 | 7.8526 | 1667.99 | 8.3358 | 1600.17 | 7.9969 | 1666.95 | 8.3306 | 1602.12 | 8.0066 | 1667.99 | 8.3358 | 1602.12 | 8.0066 | 1667.99 | 8.3358 | 1602.12 | 8.0066 | 1667.99 | 8.3358 | 1602.12 | 8.0066 | 1667.99 | 8.3358 | 1601.19 | 8.0019 | 1671.88 | 8.3552 | 1601.22 | 8.0021 | 1672.07 | 8.3562 | 1602.12 | 8.0066 | 1667.99 | 8.3358
GEN-2017-011 | DISIS-2017-001 | 01 - Woodward | OKGE | 151.8 | ER/NR | Solar | Badger-Woodward EHV Dbl Ckt 345kV | 588563 | 1 | 588560 | 8470.5 | 55.8004 | 8510.4 | 56.0632 | 8484.59 | 55.8932 | 8522.19 | 56.1409 | 8484.58 | 55.8931 | 8514.68 | 56.0914 | 8479.17 | 55.8575 | 8512.45 | 56.0767 | 8488.63 | 55.9198 | 8530.61 | 56.1964 | 8457.91 | 55.7175 | 8518.22 | 56.1148 | 8470.25 | 55.7987 | 8519.71 | 56.1246 | 8479.16 | 55.8574 | 8512.33 | 56.076 | 8482.13 | 55.877 | 8519.68 | 56.1244 | 8482.13 | 55.877 | 8519.68 | 56.1244 | 8481.96 | 55.8759 | 8519.57 | 56.1236 | 8481.96 | 55.8759 | 8518.22 | 56.1148 | 8482.13 | 55.877 | 8519.65 | 56.1242 | 8482.06 | 55.8765 | 8519.65 | 56.1242 | 8482.13 | 55.877 | 8519.65 | 56.1242
GEN-2017-012 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 100.8 | ER/NR | Wind | Newhart-Potter County 230kV | 588573 | 1 | 588570 | 2881.39 | 28.5852 | 2891.35 | 28.684 | 2936.41 | 29.1311 | 2925.9 | 29.0268 | 2934.71 | 29.1142 | 2924.05 | 29.0084 | 2934.63 | 29.1134 | 2924.03 | 29.0082 | 2940.57 | 29.1723 | 2928.4 | 29.0516 | 2934.62 | 29.1133 | 2918.56 | 28.954 | 2881.39 | 28.5852 | 2924.15 | 29.0094 | 2934.63 | 29.1134 | 2924.03 | 29.0082 | 2934.67 | 29.1138 | 2924.15 | 29.0094 | 2934.67 | 29.1138 | 2924.15 | 29.0094 | 2934.67 | 29.1138 | 2924.15 | 29.0094 | 2934.67 | 29.1138 | 2918.56 | 28.954 | 2934.67 | 29.1138 | 2924.15 | 29.0094 | 2934.67 | 29.1138 | 2924.15 | 29.0094 | 2934.67 | 29.1138 | 2924.15 | 29.0094
GEN-2017-012 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 100.8 | ER/NR | Wind | Newhart-Potter County 230kV | 588577 | 1 | 588570 | 2881.39 | 28.5852 | 2891.35 | 28.684 | 2936.41 | 29.1311 | 2925.9 | 29.0268 | 2934.71 | 29.1142 | 2924.05 | 29.0084 | 2934.63 | 29.1134 | 2924.03 | 29.0082 | 2940.57 | 29.1723 | 2928.4 | 29.0516 | 2934.62 | 29.1133 | 2918.56 | 28.954 | 2881.39 | 28.5852 | 2924.15 | 29.0094 | 2934.63 | 29.1134 | 2924.03 | 29.0082 | 2934.67 | 29.1138 | 2924.15 | 29.0094 | 2934.67 | 29.1138 | 2924.15 | 29.0094 | 2934.67 | 29.1138 | 2924.15 | 29.0094 | 2934.67 | 29.1138 | 2918.56 | 28.954 | 2934.67 | 29.1138 | 2924.15 | 29.0094 | 2934.67 | 29.1138 | 2924.15 | 29.0094 | 2934.67 | 29.1138 | 2924.15 | 29.0094
GEN-2017-013 | DISIS-2017-001 | 04 - Northwest Kansas | SUNC | 200 | ER/NR | Wind | Mingo 345kV Substation | 588583 | 1 | 588580 | 3546.05 | 17.7303 | 3611.45 | 18.0572 | 3545.83 | 17.7292 | 3613.06 | 18.0653 | 3538.37 | 17.6918 | 3613.68 | 18.0684 | 3525.64 | 17.6282 | 3594.23 | 17.9712 | 3546.16 | 17.7308 | 3611.57 | 18.0579 | 3545.71 | 17.7285 | 3613.02 | 18.0651 | 3545.98 | 17.7299 | 3615.76 | 18.0788 | 3526.01 | 17.6301 | 3587.81 | 17.939 | 3548.19 | 17.741 | 3614.26 | 18.0713 | 3548.19 | 17.741 | 3614.26 | 18.0713 | 3545.79 | 17.729 | 3612.38 | 18.0619 | 3545.78 | 17.7289 | 3613.02 | 18.0651 | 3548.1 | 17.7405 | 3613.64 | 18.0682 | 3547.05 | 17.7353 | 3613.64 | 18.0682 | 3548.19 | 17.741 | 3613.74 | 18.0687
GEN-2017-014 | DISIS-2017-001 | 17 - Western South Dakota | WAPA | 138 | ER/NR | Wind | Underwood-Philip Tap 230kV | 588593 | 1 | 588590 | 1590.51 | 11.5254 | 1652.77 | 11.9766 | 1645.18 | 11.9216 | 1652.77 | 11.9766 | 1645.18 | 11.9216 | 1652.77 | 11.9766 | 1645.18 | 11.9216 | 1652.77 | 11.9766 | 1569.87 | 11.3759 | 1652.77 | 11.9766 | 1645.18 | 11.9216 | 1652.77 | 11.9766 | 1569.47 | 11.373 | 1652.77 | 11.9766 | 1570.61 | 11.3812 | 1602.33 | 11.6111 | 1645.18 | 11.9216 | 1652.77 | 11.9766 | 1645.18 | 11.9216 | 1652.77 | 11.9766 | 1645.18 | 11.9216 | 1652.77 | 11.9766 | 1645.18 | 11.9216 | 1652.77 | 11.9766 | 1601.57 | 11.6056 | 1619.14 | 11.7329 | 1601.56 | 11.6055 | 1627.44 | 11.793 | 1645.18 | 11.9216 | 1652.77 | 11.9766
GEN-2017-014 | DISIS-2017-001 | 17 - Western South Dakota | WAPA | 162 | ER/NR | Wind | Underwood-Philip Tap 230kV | 588597 | 1 | 588590 | 1590.51 | 9.818 | 1652.77 | 10.2023 | 1645.18 | 10.1554 | 1652.77 | 10.2023 | 1645.18 | 10.1554 | 1652.77 | 10.2023 | 1645.18 | 10.1554 | 1652.77 | 10.2023 | 1569.87 | 9.6906 | 1652.77 | 10.2023 | 1645.18 | 10.1554 | 1652.77 | 10.2023 | 1569.47 | 9.6881 | 1652.77 | 10.2023 | 1570.61 | 9.6951 | 1602.33 | 9.8909 | 1645.18 | 10.1554 | 1652.77 | 10.2023 | 1645.18 | 10.1554 | 1652.77 | 10.2023 | 1645.18 | 10.1554 | 1652.77 | 10.2023 | 1645.18 | 10.1554 | 1652.77 | 10.2023 | 1601.57 | 9.8862 | 1619.14 | 9.9947 | 1601.56 | 9.8862 | 1627.44 | 10.0459 | 1645.18 | 10.1554 | 1652.77 | 10.2023
GEN-2017-016 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 33 | ER/NR | Solar | Norton 115kV Switching Station | 588613 | 1 | 588610 | 637.34 | 19.3133 | 637.6 | 19.3212 | 637.71 | 19.3245 | 756.92 | 22.937 | 637.71 | 19.3245 | 756.92 | 22.937 | 637.71 | 19.3245 | 756.92 | 22.937 | 637.71 | 19.3245 | 637.66 | 19.323 | 637.71 | 19.3245 | 637.61 | 19.3215 | 637.34 | 19.3133 | 756.92 | 22.937 | 637.71 | 19.3245 | 756.92 | 22.937 | 637.71 | 19.3245 | 756.92 | 22.937 | 637.71 | 19.3245 | 756.92 | 22.937 | 637.71 | 19.3245 | 756.92 | 22.937 | 637.71 | 19.3245 | 637.61 | 19.3215 | 637.71 | 19.3245 | 756.92 | 22.937 | 637.71 | 19.3245 | 756.92 | 22.937 | 637.71 | 19.3245 | 756.92 | 22.937
GEN-2017-018 | DISIS-2017-001 | 03 - Spearville | SUNC | 95 | ER/NR | Solar | Thistle 345kV Substation | 588633 | 1 | 588630 | 9713.6 | 102.2484 | 9916.59 | 104.3852 | 9715.41 | 102.2675 | 9919.04 | 104.4109 | 9717.28 | 102.2872 | 9917.35 | 104.3932 | 9712.1 | 102.2326 | 9913.08 | 104.3482 | 9714.42 | 102.2571 | 9920.1 | 104.4221 | 9697.04 | 102.0741 | 9918.52 | 104.4055 | 9709.48 | 102.2051 | 9919.97 | 104.4207 | 9712.06 | 102.2322 | 9911.97 | 104.3365 | 9717.13 | 102.2856 | 9919.7 | 104.4179 | 9717.13 | 102.2856 | 9919.7 | 104.4179 | 9715.21 | 102.2654 | 9918.41 | 104.4043 | 9715.2 | 102.2653 | 9918.52 | 104.4055 | 9717.12 | 102.2855 | 9919.31 | 104.4138 | 9716.29 | 102.2767 | 9919.31 | 104.4138 | 9717.13 | 102.2856 | 9919.33 | 104.414
GEN-2017-018 | DISIS-2017-001 | 03 - Spearville | SUNC | 95 | ER/NR | Solar | Thistle 345kV Substation | 588637 | 1 | 588630 | 9713.6 | 102.2484 | 9916.59 | 104.3852 | 9715.41 | 102.2675 | 9919.04 | 104.4109 | 9717.28 | 102.2872 | 9917.35 | 104.3932 | 9712.1 | 102.2326 | 9913.08 | 104.3482 | 9714.42 | 102.2571 | 9920.1 | 104.4221 | 9697.04 | 102.0741 | 9918.52 | 104.4055 | 9709.48 | 102.2051 | 9919.97 | 104.4207 | 9712.06 | 102.2322 | 9911.97 | 104.3365 | 9717.13 | 102.2856 | 9919.7 | 104.4179 | 9717.13 | 102.2856 | 9919.7 | 104.4179 | 9715.21 | 102.2654 | 9918.41 | 104.4043 | 9715.2 | 102.2653 | 9918.52 | 104.4055 | 9717.12 | 102.2855 | 9919.31 | 104.4138 | 9716.29 | 102.2767 | 9919.31 | 104.4138 | 9717.13 | 102.2856 | 9919.33 | 104.414
GEN-2017-021 | DISIS-2017-001 | 03 - Spearville | SUNC | 200 | ER/NR | Wind | Post Rock-Spearville 345kV | 588653 | 1 | 588650 | 6084.58 | 30.4229 | 6197.16 | 30.9858 | 6084.5 | 30.4225 | 6203.69 | 31.0184 | 6095.29 | 30.4764 | 6205.59 | 31.028 | 6081.26 | 30.4063 | 6192.24 | 30.9612 | 6084.83 | 30.4242 | 6197.48 | 30.9874 | 6083.57 | 30.4178 | 6203.6 | 31.018 | 6084.25 | 30.4213 | 6210.63 | 31.0532 | 6081.68 | 30.4084 | 6185.65 | 30.9282 | 6094.55 | 30.4728 | 6208.73 | 31.0436 | 6094.55 | 30.4728 | 6208.73 | 31.0436 | 6084.43 | 30.4222 | 6200.86 | 31.0043 | 6084.42 | 30.4221 | 6203.6 | 31.018 | 6094.5 | 30.4725 | 6206.41 | 31.032 | 6090.12 | 30.4506 | 6206.41 | 31.032 | 6094.55 | 30.4728 | 6206.51 | 31.0326
GEN-2017-022 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | WERE | 65 | ER/NR | Solar | Altoona-NE Parson 138kV | 588663 | 1 | 588660 | 2011.67 | 30.9488 | 2066.01 | 31.7848 | 2013.59 | 30.9783 | 2066.02 | 31.7849 | 2013.59 | 30.9783 | 2066.02 | 31.7849 | 2013.59 | 30.9783 | 2066.02 | 31.7849 | 2011.42 | 30.9449 | 2065.81 | 31.7817 | 2013.58 | 30.9782 | 2066.02 | 31.7849 | 2009.04 | 30.9083 | 2064.7 | 31.7646 | 2011.67 | 30.9488 | 2066.02 | 31.7849 | 2013.59 | 30.9783 | 2066.02 | 31.7849 | 2013.59 | 30.9783 | 2066.02 | 31.7849 | 2013.59 | 30.9783 | 2066.02 | 31.7849 | 2013.59 | 30.9783 | 2066.02 | 31.7849 | 2013.59 | 30.9783 | 2066.02 | 31.7849 | 2013.59 | 30.9783 | 2066.02 | 31.7849 | 2013.59 | 30.9783 | 2066.02 | 31.7849
GEN-2017-023 | DISIS-2017-001 | 14 - South Central Oklahoma | WFEC | 85 | ER/NR | Solar | Hugo Power Plant 138kV Substation | 588673 | 1 | 588670 | 5357.71 | 63.0319 | 5388.07 | 63.3891 | 5357.77 | 63.0326 | 5388.41 | 63.3931 | 5357.77 | 63.0326 | 5388.41 | 63.3931 | 5357.77 | 63.0326 | 5388.41 | 63.3931 | 5359.4 | 63.0518 | 5369.77 | 63.1738 | 5357.37 | 63.0279 | 5388.4 | 63.3929 | 5357.65 | 63.0312 | 5388.41 | 63.3931 | 5357.77 | 63.0326 | 5388.41 | 63.3931 | 5357.77 | 63.0326 | 5388.41 | 63.3931 | 5357.77 | 63.0326 | 5388.41 | 63.3931 | 5357.77 | 63.0326 | 5388.41 | 63.3931 | 5357.77 | 63.0326 | 5388.4 | 63.3929 | 5357.77 | 63.0326 | 5388.41 | 63.3931 | 5357.77 | 63.0326 | 5388.41 | 63.3931 | 5357.77 | 63.0326 | 5388.41 | 63.3931
GEN-2017-024 | DISIS-2017-001 | 14 - South Central Oklahoma | WFEC | 50 | ER/NR | Solar | Frogville 138kV Substation | 588683 | 1 | 588680 | 2588.66 | 51.7732 | 2595.87 | 51.9174 | 2588.67 | 51.7734 | 2595.96 | 51.9192 | 2588.67 | 51.7734 | 2595.96 | 51.9192 | 2588.67 | 51.7734 | 2595.96 | 51.9192 | 2589.21 | 51.7842 | 2591.95 | 51.839 | 2588.55 | 51.771 | 2595.95 | 51.919 | 2588.64 | 51.7728 | 2595.96 | 51.9192 | 2588.67 | 51.7734 | 2595.96 | 51.9192 | 2588.67 | 51.7734 | 2595.96 | 51.9192 | 2588.67 | 51.7734 | 2595.96 | 51.9192 | 2588.67 | 51.7734 | 2595.96 | 51.9192 | 2588.67 | 51.7734 | 2595.95 | 51.919 | 2588.67 | 51.7734 | 2595.96 | 51.9192 | 2588.67 | 51.7734 | 2595.96 | 51.9192 | 2588.67 | 51.7734 | 2595.96 | 51.9192
GEN-2017-026 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 117.5 | ER/NR | Wind | Tolk 230kV Substation | 588703 | 1 | 588700 | 9773.1 | 83.1753 | 9928.22 | 84.4955 | 10691.08 | 90.9879 | 10064.38 | 85.6543 | 10690.37 | 90.9819 | 10063.54 | 85.6471 | 10690.33 | 90.9815 | 10063.53 | 85.6471 | 10699.78 | 91.062 | 10044.09 | 85.4816 | 10690.26 | 90.9809 | 9944.02 | 84.63 | 9773.1 | 83.1753 | 10063.59 | 85.6476 | 10690.33 | 90.9815 | 10063.53 | 85.6471 | 10690.35 | 90.9817 | 10063.59 | 85.6476 | 10690.35 | 90.9817 | 10063.59 | 85.6476 | 10690.35 | 90.9817 | 10063.59 | 85.6476 | 10690.35 | 90.9817 | 9944.02 | 84.63 | 10690.35 | 90.9817 | 10063.59 | 85.6476 | 10690.35 | 90.9817 | 10063.59 | 85.6476 | 10690.35 | 90.9817 | 10063.59 | 85.6476
GEN-2017-026 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 117.5 | ER/NR | Wind | Tolk 230kV Substation | 588707 | 1 | 588700 | 9773.1 | 83.1753 | 9928.22 | 84.4955 | 10691.08 | 90.9879 | 10064.38 | 85.6543 | 10690.37 | 90.9819 | 10063.54 | 85.6471 | 10690.33 | 90.9815 | 10063.53 | 85.6471 | 10699.78 | 91.062 | 10044.09 | 85.4816 | 10690.26 | 90.9809 | 9944.02 | 84.63 | 9773.1 | 83.1753 | 10063.59 | 85.6476 | 10690.33 | 90.9815 | 10063.53 | 85.6471 | 10690.35 | 90.9817 | 10063.59 | 85.6476 | 10690.35 | 90.9817 | 10063.59 | 85.6476 | 10690.35 | 90.9817 | 10063.59 | 85.6476 | 10690.35 | 90.9817 | 9944.02 | 84.63 | 10690.35 | 90.9817 | 10063.59 | 85.6476 | 10690.35 | 90.9817 | 10063.59 | 85.6476 | 10690.35 | 90.9817 | 10063.59 | 85.6476
GEN-2017-027 | DISIS-2017-001 | 14 - South Central Oklahoma | OKGE | 140 | ER/NR | Wind | Pooleville-Ratliff (Carter County) 138kV | 588713 | 1 | 588710 | 2946.08 | 21.0434 | 2966.42 | 21.1887 | 2946.2 | 21.0443 | 2966.96 | 21.1926 | 2946.2 | 21.0443 | 2966.96 | 21.1926 | 2946.2 | 21.0443 | 2966.96 | 21.1926 | 2947.08 | 21.0506 | 2961.84 | 21.156 | 2945.51 | 21.0394 | 2966.93 | 21.1924 | 2946.05 | 21.0432 | 2966.96 | 21.1926 | 2946.2 | 21.0443 | 2966.96 | 21.1926 | 2946.2 | 21.0443 | 2966.96 | 21.1926 | 2946.2 | 21.0443 | 2966.96 | 21.1926 | 2946.2 | 21.0443 | 2966.96 | 21.1926 | 2946.2 | 21.0443 | 2966.93 | 21.1924 | 2946.2 | 21.0443 | 2966.96 | 21.1926 | 2946.2 | 21.0443 | 2966.96 | 21.1926 | 2946.2 | 21.0443 | 2966.96 | 21.1926
GEN-2017-028 | DISIS-2017-001 | 01 - Woodward | WFEC | 50 | ER/NR | Solar | El Reno SW 138kV Switch Station | 588723 | 1 | 588720 | 3428.19 | 68.5638 | 3454.5 | 69.09 | 3428.3 | 68.566 | 3456.73 | 69.1346 | 3428.3 | 68.566 | 3456.72 | 69.1344 | 3428.3 | 68.566 | 3456.72 | 69.1344 | 3349.37 | 66.9874 | 3430.65 | 68.613 | 3419.65 | 68.393 | 3456.71 | 69.1342 | 3428.14 | 68.5628 | 3456.72 | 69.1344 | 3428.29 | 68.5658 | 3456.72 | 69.1344 | 3428.3 | 68.566 | 3456.73 | 69.1346 | 3428.3 | 68.566 | 3456.73 | 69.1346 | 3428.3 | 68.566 | 3456.73 | 69.1346 | 3428.3 | 68.566 | 3456.71 | 69.1342 | 3428.3 | 68.566 | 3456.73 | 69.1346 | 3428.3 | 68.566 | 3456.73 | 69.1346 | 3428.3 | 68.566 | 3456.73 | 69.1346
GEN-2017-030 | DISIS-2017-001 | 13 - Northeast Kansas/Northwest Missouri | KCPL | 200 | ER/NR | Wind | Eastown-Iatan 345kV | 588733 | 1 | 588730 | 1510.68 | 7.5534 | 1514.59 | 7.5729 | 1510.68 | 7.5534 | 1514.6 | 7.573 | 1510.68 | 7.5534 | 1514.6 | 7.573 | 1510.68 | 7.5534 | 1514.6 | 7.573 | 1510.68 | 7.5534 | 1514.59 | 7.5729 | 1510.68 | 7.5534 | 1514.6 | 7.573 | 1509.69 | 7.5484 | 1514.62 | 7.5731 | 1510.69 | 7.5535 | 1514.57 | 7.5728 | 1510.68 | 7.5534 | 1514.62 | 7.5731 | 1510.68 | 7.5534 | 1514.62 | 7.5731 | 1510.72 | 7.5536 | 1514.65 | 7.5733 | 1510.68 | 7.5534 | 1514.6 | 7.573 | 1510.68 | 7.5534 | 1514.6 | 7.573 | 1510.68 | 7.5534 | 1514.6 | 7.573 | 1510.68 | 7.5534 | 1514.62 | 7.5731
GEN-2017-031 | DISIS-2017-001 | 09 - Nebraska | NPPD | 100 | ER | Wind | Wildhorse-Covalt 115kV | 588743 | 1 | 588740 | 495.78 | 4.9578 | 496.47 | 4.9647 | 495.81 | 4.9581 | 496.47 | 4.9647 | 495.81 | 4.9581 | 496.48 | 4.9648 | 495.81 | 4.9581 | 496.47 | 4.9647 | 495.77 | 4.9577 | 496.47 | 4.9647 | 495.81 | 4.9581 | 496.47 | 4.9647 | 495.76 | 4.9576 | 496.48 | 4.9648 | 495.77 | 4.9577 | 496.37 | 4.9637 | 495.81 | 4.9581 | 496.48 | 4.9648 | 495.81 | 4.9581 | 496.48 | 4.9648 | 495.81 | 4.9581 | 496.47 | 4.9647 | 495.81 | 4.9581 | 496.47 | 4.9647 | 495.78 | 4.9578 | 496.46 | 4.9646 | 495.78 | 4.9578 | 496.46 | 4.9646 | 495.81 | 4.9581 | 496.48 | 4.9648
GEN-2017-032 | DISIS-2017-001 | 03 - Spearville | SWPS | 200 | ER/NR | Wind | Finney-Lamar 345kV | 588753 | 1 | 588750 | 1801.86 | 9.0093 | 1828.09 | 9.1404 | 1801.98 | 9.0099 | 1828.34 | 9.1417 | 1796.41 | 8.9821 | 1826.86 | 9.1343 | 1788.7 | 8.9435 | 1815.5 | 9.0775 | 1801.98 | 9.0099 | 1828.2 | 9.141 | 1801.9 | 9.0095 | 1828.31 | 9.1416 | 1801.85 | 9.0092 | 1828.51 | 9.1425 | 1788.72 | 8.9436 | 1815.19 | 9.076 | 1802.2 | 9.011 | 1828.43 | 9.1422 | 1802.2 | 9.011 | 1828.43 | 9.1422 | 1801.95 | 9.0098 | 1828.25 | 9.1412 | 1801.95 | 9.0098 | 1828.31 | 9.1416 | 1802.2 | 9.011 | 1828.38 | 9.1419 | 1802.09 | 9.0104 | 1828.38 | 9.1419 | 1802.2 | 9.011 | 1828.38 | 9.1419
GEN-2017-033 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | AEPW | 100 | ER/NR | Wind | Oklaunion 345kV Substation | 588763 | 1 | 588760 | 2414.99 | 24.1499 | 2435.44 | 24.3544 | 2423.28 | 24.2328 | 2439.03 | 24.3903 | 2423.27 | 24.2327 | 2439.02 | 24.3902 | 2423.27 | 24.2327 | 2439.02 | 24.3902 | 2443.58 | 24.4358 | 2479.15 | 24.7915 | 2422.25 | 24.2225 | 2435.68 | 24.3568 | 2414.98 | 24.1498 | 2439.03 | 24.3903 | 2423.27 | 24.2327 | 2439.02 | 24.3902 | 2423.27 | 24.2327 | 2439.03 | 24.3903 | 2423.27 | 24.2327 | 2439.03 | 24.3903 | 2423.27 | 24.2327 | 2439.03 | 24.3903 | 2423.27 | 24.2327 | 2435.68 | 24.3568 | 2423.27 | 24.2327 | 2439.03 | 24.3903 | 2423.27 | 24.2327 | 2439.03 | 24.3903 | 2423.27 | 24.2327 | 2439.03 | 24.3903
GEN-2017-033 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | AEPW | 100 | ER/NR | Wind | Oklaunion 345kV Substation | 588767 | 1 | 588760 | 2414.99 | 24.1499 | 2435.44 | 24.3544 | 2423.28 | 24.2328 | 2439.03 | 24.3903 | 2423.27 | 24.2327 | 2439.02 | 24.3902 | 2423.27 | 24.2327 | 2439.02 | 24.3902 | 2443.58 | 24.4358 | 2479.15 | 24.7915 | 2422.25 | 24.2225 | 2435.68 | 24.3568 | 2414.98 | 24.1498 | 2439.03 | 24.3903 | 2423.27 | 24.2327 | 2439.02 | 24.3902 | 2423.27 | 24.2327 | 2439.03 | 24.3903 | 2423.27 | 24.2327 | 2439.03 | 24.3903 | 2423.27 | 24.2327 | 2439.03 | 24.3903 | 2423.27 | 24.2327 | 2435.68 | 24.3568 | 2423.27 | 24.2327 | 2439.03 | 24.3903 | 2423.27 | 24.2327 | 2439.03 | 24.3903 | 2423.27 | 24.2327 | 2439.03 | 24.3903
GEN-2017-036 | DISIS-2017-001 | 07 - Southwestern Oklahoma | AEPW | 100 | ER/NR | Solar | Snyder-Cache 138kV | 588783 | 1 | 588780 | 1657.92 | 16.5792 | 1662.87 | 16.6287 | 1658.09 | 16.5809 | 1663.03 | 16.6303 | 1658.08 | 16.5808 | 1663.03 | 16.6303 | 1658.08 | 16.5808 | 1663.03 | 16.6303 | 1623.06 | 16.2306 | 1651.66 | 16.5166 | 1655.8 | 16.558 | 1663 | 16.63 | 1657.91 | 16.5791 | 1663.03 | 16.6303 | 1658.08 | 16.5808 | 1663.03 | 16.6303 | 1658.08 | 16.5808 | 1663.03 | 16.6303 | 1658.08 | 16.5808 | 1663.03 | 16.6303 | 1658.08 | 16.5808 | 1663.03 | 16.6303 | 1658.08 | 16.5808 | 1663 | 16.63 | 1658.08 | 16.5808 | 1663.03 | 16.6303 | 1658.08 | 16.5808 | 1663.03 | 16.6303 | 1658.08 | 16.5808 | 1663.03 | 16.6303
GEN-2017-037 | DISIS-2017-001 | 09 - Nebraska | NPPD | 20 | ER | Solar | Bobcat 115kV Substation | 588933 | 1 | 589420 | 1850.44 | 92.522 | 1853.61 | 92.6805 | 1851.05 | 92.5525 | 1853.62 | 92.681 | 1851.06 | 92.553 | 1853.63 | 92.6815 | 1851.04 | 92.552 | 1853.61 | 92.6805 | 1850.18 | 92.509 | 1853.61 | 92.6805 | 1851.05 | 92.5525 | 1853.62 | 92.681 | 1850.16 | 92.508 | 1853.64 | 92.682 | 1850.2 | 92.51 | 1852.57 | 92.6285 | 1851.06 | 92.553 | 1853.63 | 92.6815 | 1851.06 | 92.553 | 1853.63 | 92.6815 | 1851.05 | 92.5525 | 1853.62 | 92.681 | 1851.05 | 92.5525 | 1853.62 | 92.681 | 1850.53 | 92.5265 | 1853.25 | 92.6625 | 1850.52 | 92.526 | 1853.33 | 92.6665 | 1851.06 | 92.553 | 1853.63 | 92.6815
GEN-2017-038 | DISIS-2017-001 | 13 - Northeast Kansas/Northwest Missouri | KCPL | 200 | ER/NR | Wind | Eastown-Iatan 345kV | 588793 | 1 | 588790 | 1427.63 | 7.1382 | 1431.1 | 7.1555 | 1427.63 | 7.1382 | 1431.11 | 7.1555 | 1427.63 | 7.1382 | 1431.11 | 7.1555 | 1427.63 | 7.1382 | 1431.11 | 7.1555 | 1427.63 | 7.1382 | 1431.1 | 7.1555 | 1427.63 | 7.1382 | 1431.11 | 7.1555 | 1426.76 | 7.1338 | 1431.12 | 7.1556 | 1427.64 | 7.1382 | 1431.08 | 7.1554 | 1427.63 | 7.1382 | 1431.12 | 7.1556 | 1427.63 | 7.1382 | 1431.12 | 7.1556 | 1427.67 | 7.1383 | 1431.15 | 7.1558 | 1427.63 | 7.1382 | 1431.11 | 7.1555 | 1427.63 | 7.1382 | 1431.11 | 7.1555 | 1427.63 | 7.1382 | 1431.11 | 7.1555 | 1427.63 | 7.1382 | 1431.12 | 7.1556
GEN-2017-039 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 200.1 | ER | Wind | Needmore 230kV Substation | 588803 | 1 | 588800 | 4425.31 | 22.1155 | 4464.06 | 22.3091 | 4562.09 | 22.7991 | 4491.82 | 22.4479 | 4562 | 22.7986 | 4491.7 | 22.4473 | 4562 | 22.7986 | 4491.7 | 22.4473 | 4563.58 | 22.8065 | 4480.25 | 22.3901 | 4561.98 | 22.7985 | 4466.27 | 22.3202 | 4425.31 | 22.1155 | 4491.71 | 22.4473 | 4562 | 22.7986 | 4491.7 | 22.4473 | 4562 | 22.7986 | 4491.71 | 22.4473 | 4562 | 22.7986 | 4491.71 | 22.4473 | 4562 | 22.7986 | 4491.71 | 22.4473 | 4562 | 22.7986 | 4466.27 | 22.3202 | 4562 | 22.7986 | 4491.71 | 22.4473 | 4562 | 22.7986 | 4491.71 | 22.4473 | 4562 | 22.7986 | 4491.71 | 22.4473
GEN-2017-040 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | OKGE | 96.6 | ER | Wind | Canadian River-Muskogee and Muskogee-Seminole 345kV | 588813 | 1 | 588810 | 1378.08 | 14.2658 | 1387.62 | 14.3646 | 1378.09 | 14.2659 | 1387.66 | 14.365 | 1378.09 | 14.2659 | 1387.66 | 14.365 | 1378.09 | 14.2659 | 1387.66 | 14.365 | 1385.9 | 14.3468 | 1387.29 | 14.3612 | 1378.08 | 14.2658 | 1387.66 | 14.365 | 1377.99 | 14.2649 | 1387.66 | 14.365 | 1378.08 | 14.2658 | 1387.66 | 14.365 | 1378.09 | 14.2659 | 1387.66 | 14.365 | 1378.09 | 14.2659 | 1387.66 | 14.365 | 1378.09 | 14.2659 | 1387.66 | 14.365 | 1378.09 | 14.2659 | 1387.66 | 14.365 | 1378.09 | 14.2659 | 1387.66 | 14.365 | 1378.09 | 14.2659 | 1387.66 | 14.365 | 1378.09 | 14.2659 | 1387.66 | 14.365
GEN-2017-040 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | OKGE | 103.5 | ER | Wind | Canadian River-Muskogee and Muskogee-Seminole 345kV | 588817 | 1 | 588810 | 1378.08 | 13.3148 | 1387.62 | 13.407 | 1378.09 | 13.3149 | 1387.66 | 13.4073 | 1378.09 | 13.3149 | 1387.66 | 13.4073 | 1378.09 | 13.3149 | 1387.66 | 13.4073 | 1385.9 | 13.3903 | 1387.29 | 13.4038 | 1378.08 | 13.3148 | 1387.66 | 13.4073 | 1377.99 | 13.3139 | 1387.66 | 13.4073 | 1378.08 | 13.3148 | 1387.66 | 13.4073 | 1378.09 | 13.3149 | 1387.66 | 13.4073 | 1378.09 | 13.3149 | 1387.66 | 13.4073 | 1378.09 | 13.3149 | 1387.66 | 13.4073 | 1378.09 | 13.3149 | 1387.66 | 13.4073 | 1378.09 | 13.3149 | 1387.66 | 13.4073 | 1378.09 | 13.3149 | 1387.66 | 13.4073 | 1378.09 | 13.3149 | 1387.66 | 13.4073
GEN-2017-041 | DISIS-2017-001 | 13 - Northeast Kansas/Northwest Missouri | KCPL | 200 | ER/NR | Wind | Eastown-Iatan 345kV Substation | 588823 | 1 | 588820 | 1386.35 | 6.9317 | 1389.55 | 6.9478 | 1386.35 | 6.9317 | 1389.56 | 6.9478 | 1386.35 | 6.9317 | 1389.56 | 6.9478 | 1386.35 | 6.9317 | 1389.56 | 6.9478 | 1386.35 | 6.9317 | 1389.55 | 6.9478 | 1386.35 | 6.9317 | 1389.56 | 6.9478 | 1385.54 | 6.9277 | 1389.57 | 6.9478 | 1386.35 | 6.9317 | 1389.53 | 6.9476 | 1386.35 | 6.9317 | 1389.57 | 6.9478 | 1386.35 | 6.9317 | 1389.57 | 6.9478 | 1386.38 | 6.9319 | 1389.59 | 6.9479 | 1386.35 | 6.9317 | 1389.56 | 6.9478 | 1386.35 | 6.9317 | 1389.56 | 6.9478 | 1386.35 | 6.9317 | 1389.56 | 6.9478 | 1386.35 | 6.9317 | 1389.57 | 6.9478
GEN-2017-047 | DISIS-2017-001 | 02 - Hitchland | SWPS | 102 | ER/NR | Wind | Cole 115kV Substation | 588863 | 1 | 588860 | 885.96 | 8.6859 | 887.14 | 8.6975 | 886.94 | 8.6955 | 888.07 | 8.7066 | 886.83 | 8.6944 | 887.05 | 8.6966 | 886.54 | 8.6916 | 887 | 8.6961 | 886.71 | 8.6932 | 887.85 | 8.7044 | 886.6 | 8.6922 | 887.74 | 8.7033 | 885.96 | 8.6859 | 887.75 | 8.7034 | 886.54 | 8.6916 | 886.99 | 8.696 | 886.62 | 8.6924 | 887.75 | 8.7034 | 886.62 | 8.6924 | 887.75 | 8.7034 | 886.62 | 8.6924 | 887.75 | 8.7034 | 886.62 | 8.6924 | 887.74 | 8.7033 | 886.62 | 8.6924 | 887.75 | 8.7034 | 886.62 | 8.6924 | 887.75 | 8.7034 | 886.62 | 8.6924 | 887.75 | 8.7034
GEN-2017-048 | DISIS-2017-001 | 16 - Western North Dakota | BEPC | 300 | ER/NR | Wind | Neset 230kV Substation | 588873 | 1 | 588870 | 3352.12 | 11.1737 | 3393.03 | 11.3101 | 3354.05 | 11.1802 | 3393.03 | 11.3101 | 3354.05 | 11.1802 | 3393.03 | 11.3101 | 3354.05 | 11.1802 | 3393.03 | 11.3101 | 3344.87 | 11.1496 | 3393.03 | 11.3101 | 3354.05 | 11.1802 | 3393.03 | 11.3101 | 3334.53 | 11.1151 | 3393.03 | 11.3101 | 3350.15 | 11.1672 | 3392.74 | 11.3091 | 3354.05 | 11.1802 | 3393.03 | 11.3101 | 3354.05 | 11.1802 | 3393.03 | 11.3101 | 3354.05 | 11.1802 | 3393.03 | 11.3101 | 3354.05 | 11.1802 | 3393.03 | 11.3101 | 3353.77 | 11.1792 | 3394.42 | 11.3147 | 3353.89 | 11.1796 | 3394.63 | 11.3154 | 3354.05 | 11.1802 | 3393.03 | 11.3101
GEN-2017-049 | DISIS-2017-001 | 03 - Spearville | MIDW | 50 | ER | Solar | Tap Pawnee Valley-Hanston 69kV | 588883 | 1 | 588880 | 301.47 | 6.0294 | 303.99 | 6.0798 | 301.47 | 6.0294 | 304.01 | 6.0802 | 301.5 | 6.03 | 304.02 | 6.0804 | 301.48 | 6.0296 | 304 | 6.08 | 301.47 | 6.0294 | 303.99 | 6.0798 | 301.47 | 6.0294 | 304.01 | 6.0802 | 301.47 | 6.0294 | 304.02 | 6.0804 | 301.48 | 6.0296 | 303.98 | 6.0796 | 301.5 | 6.03 | 304.01 | 6.0802 | 301.5 | 6.03 | 304.01 | 6.0802 | 301.47 | 6.0294 | 304 | 6.08 | 301.47 | 6.0294 | 304.01 | 6.0802 | 301.5 | 6.03 | 304.01 | 6.0802 | 301.49 | 6.0298 | 304.01 | 6.0802 | 301.5 | 6.03 | 304.01 | 6.0802
GEN-2017-050 | DISIS-2017-001 | 12 - Northwest Arkansas | WERE | 25 | ER | Solar | Tap Neosho-Crawford 69kV | 588893 | 1 | 588890 | 984.02 | 39.3608 | 987.98 | 39.5192 | 985.32 | 39.4128 | 987.98 | 39.5192 | 985.32 | 39.4128 | 987.98 | 39.5192 | 985.32 | 39.4128 | 987.98 | 39.5192 | 983.99 | 39.3596 | 987.95 | 39.518 | 985.32 | 39.4128 | 987.98 | 39.5192 | 983.28 | 39.3312 | 987.01 | 39.4804 | 984.02 | 39.3608 | 987.98 | 39.5192 | 985.32 | 39.4128 | 987.98 | 39.5192 | 985.32 | 39.4128 | 987.98 | 39.5192 | 985.32 | 39.4128 | 987.98 | 39.5192 | 985.32 | 39.4128 | 987.98 | 39.5192 | 985.32 | 39.4128 | 987.98 | 39.5192 | 985.32 | 39.4128 | 987.98 | 39.5192 | 985.32 | 39.4128 | 987.98 | 39.5192
GEN-2017-051 | DISIS-2017-001 | 07 - Southwestern Oklahoma | WFEC | 30 | ER | Solar | Tap Lake Creek SW-Russell SW 69kV | 588903 | 1 | 588900 | 416.5 | 13.8833 | 416.68 | 13.8893 | 416.51 | 13.8837 | 416.69 | 13.8897 | 416.51 | 13.8837 | 416.69 | 13.8897 | 416.51 | 13.8837 | 416.69 | 13.8897 | 415.77 | 13.859 | 416.27 | 13.8757 | 416.41 | 13.8803 | 416.69 | 13.8897 | 416.5 | 13.8833 | 416.69 | 13.8897 | 416.51 | 13.8837 | 416.69 | 13.8897 | 416.51 | 13.8837 | 416.69 | 13.8897 | 416.51 | 13.8837 | 416.69 | 13.8897 | 416.51 | 13.8837 | 416.69 | 13.8897 | 416.51 | 13.8837 | 416.69 | 13.8897 | 416.51 | 13.8837 | 416.69 | 13.8897 | 416.51 | 13.8837 | 416.69 | 13.8897 | 416.51 | 13.8837 | 416.69 | 13.8897
GEN-2017-052 | DISIS-2017-001 | 03 - Spearville | SUNC | 25 | ER | Solar | Tap Bear Creek-Johnson Corner 115kV | 588913 | 1 | 588910 | 593.06 | 23.7224 | 612.54 | 24.5016 | 593.08 | 23.7232 | 612.55 | 24.502 | 604.8 | 24.192 | 612.69 | 24.5076 | 590.43 | 23.6172 | 610.82 | 24.4328 | 593.08 | 23.7232 | 612.54 | 24.5016 | 593.07 | 23.7228 | 612.55 | 24.502 | 593.06 | 23.7224 | 612.56 | 24.5024 | 590.44 | 23.6176 | 610.8 | 24.432 | 593.09 | 23.7236 | 612.56 | 24.5024 | 593.09 | 23.7236 | 612.56 | 24.5024 | 593.07 | 23.7228 | 612.55 | 24.502 | 593.07 | 23.7228 | 612.55 | 24.502 | 593.09 | 23.7236 | 612.55 | 24.502 | 593.08 | 23.7232 | 612.55 | 24.502 | 593.09 | 23.7236 | 612.55 | 24.502
GEN-2017-053 | DISIS-2017-001 | 07 - Southwestern Oklahoma | WFEC | 50 | ER | Solar | Tap Hollister SW-PSO Walters 69kV | 588923 | 1 | 588920 | 607.12 | 12.1424 | 607.68 | 12.1536 | 607.13 | 12.1426 | 607.69 | 12.1538 | 607.13 | 12.1426 | 607.69 | 12.1538 | 607.13 | 12.1426 | 607.69 | 12.1538 | 600.12 | 12.0024 | 606.4 | 12.128 | 606.8 | 12.136 | 607.69 | 12.1538 | 607.12 | 12.1424 | 607.69 | 12.1538 | 607.13 | 12.1426 | 607.69 | 12.1538 | 607.13 | 12.1426 | 607.69 | 12.1538 | 607.13 | 12.1426 | 607.69 | 12.1538 | 607.13 | 12.1426 | 607.69 | 12.1538 | 607.13 | 12.1426 | 607.69 | 12.1538 | 607.13 | 12.1426 | 607.69 | 12.1538 | 607.13 | 12.1426 | 607.69 | 12.1538 | 607.13 | 12.1426 | 607.69 | 12.1538
GEN-2017-055 | DISIS-2017-001 | 09 - Nebraska | LES | 228.25 | ER/NR | Solar | Wagener 115kV Substation | 588943 | 1 | 588940 | 5624.3 | 24.641 | 5845.57 | 25.6104 | 5621.01 | 24.6265 | 6071.27 | 26.5992 | 5621.07 | 24.6268 | 6071.29 | 26.5993 | 5621.05 | 24.6267 | 6071.27 | 26.5992 | 5623.96 | 24.6395 | 5845.57 | 25.6104 | 5621.01 | 24.6265 | 6071.27 | 26.5992 | 5623.09 | 24.6357 | 6293.86 | 27.5744 | 5625.55 | 24.6464 | 5766.56 | 25.2642 | 5621.05 | 24.6267 | 6293.86 | 27.5744 | 5621.05 | 24.6267 | 6293.86 | 27.5744 | 5622.1 | 24.6313 | 6008.68 | 26.325 | 5621.01 | 24.6265 | 6071.27 | 26.5992 | 5620.11 | 24.6226 | 6071.25 | 26.5991 | 5619.99 | 24.6221 | 6071.08 | 26.5984 | 5621.05 | 24.6267 | 6293.85 | 27.5744
GEN-2017-057 | DISIS-2017-001 | 10 - Southeast Oklahoma/Northeast Texas | AEPW | 72.5 | ER/NR | Solar | Hosston 69kV Substation | 588953 | 1 | 588950 | 725.88 | 10.0121 | 727.42 | 10.0334 | 725.88 | 10.0121 | 727.42 | 10.0334 | 725.88 | 10.0121 | 727.42 | 10.0334 | 725.88 | 10.0121 | 727.42 | 10.0334 | 722.57 | 9.9665 | 725.21 | 10.0029 | 725.88 | 10.0121 | 727.42 | 10.0334 | 725.88 | 10.0121 | 727.42 | 10.0334 | 725.88 | 10.0121 | 727.42 | 10.0334 | 725.88 | 10.0121 | 727.42 | 10.0334 | 725.88 | 10.0121 | 727.42 | 10.0334 | 725.88 | 10.0121 | 727.42 | 10.0334 | 725.88 | 10.0121 | 727.42 | 10.0334 | 725.88 | 10.0121 | 727.42 | 10.0334 | 725.88 | 10.0121 | 727.42 | 10.0334 | 725.88 | 10.0121 | 727.42 | 10.0334
GEN-2017-058 | DISIS-2017-001 | 02 - Hitchland | SWPS | 135 | ER | Solar | Hereford Northeast 115kV Substation | 588963 | 1 | 588960 | 1959.19 | 14.5125 | 1963.06 | 14.5412 | 1986.81 | 14.7171 | 1974.15 | 14.6233 | 1986.4 | 14.7141 | 1973.7 | 14.62 | 1986.39 | 14.714 | 1973.69 | 14.6199 | 1987.76 | 14.7241 | 1999.62 | 14.812 | 1986.38 | 14.7139 | 1971.22 | 14.6016 | 1959.19 | 14.5125 | 1973.72 | 14.6201 | 1986.39 | 14.714 | 1973.69 | 14.6199 | 1986.39 | 14.714 | 1973.72 | 14.6201 | 1986.39 | 14.714 | 1973.72 | 14.6201 | 1986.39 | 14.714 | 1973.72 | 14.6201 | 1986.39 | 14.714 | 1971.22 | 14.6016 | 1986.39 | 14.714 | 1973.72 | 14.6201 | 1986.39 | 14.714 | 1973.72 | 14.6201 | 1986.39 | 14.714 | 1973.72 | 14.6201
GEN-2017-059 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 90 | ER/NR | Solar | TUCO 230kV Substation | 588973 | 1 | 588970 | 6868.72 | 76.3191 | 7758.34 | 86.2038 | 7822.5 | 86.9167 | 8286.68 | 92.0742 | 7822.09 | 86.9121 | 8286.18 | 92.0687 | 7822.04 | 86.9116 | 8286.16 | 92.0684 | 7899.16 | 87.7684 | 7850.66 | 87.2296 | 7821.52 | 86.9058 | 7768.37 | 86.3152 | 6868.72 | 76.3191 | 8286.23 | 92.0692 | 7822.04 | 86.9116 | 8286.16 | 92.0684 | 7822.07 | 86.9119 | 8286.23 | 92.0692 | 7822.07 | 86.9119 | 8286.23 | 92.0692 | 7822.06 | 86.9118 | 8286.23 | 92.0692 | 7822.06 | 86.9118 | 7768.37 | 86.3152 | 7822.07 | 86.9119 | 8286.23 | 92.0692 | 7822.06 | 86.9118 | 8286.23 | 92.0692 | 7822.07 | 86.9119 | 8286.23 | 92.0692
GEN-2017-060 | DISIS-2017-001 | 12 - Northwest Arkansas | EDE | 24 | ER | Wind | LaRussell Energy Center 161kV Substation | 588983 | 1 | 588980 | 1534.71 | 63.9462 | 1556.23 | 64.8429 | 1544.75 | 64.3646 | 1556.23 | 64.8429 | 1544.75 | 64.3646 | 1556.23 | 64.8429 | 1544.75 | 64.3646 | 1556.23 | 64.8429 | 1534.7 | 63.9458 | 1556.21 | 64.8421 | 1544.75 | 64.3646 | 1556.23 | 64.8429 | 1533.71 | 63.9046 | 1548.16 | 64.5067 | 1534.71 | 63.9462 | 1556.23 | 64.8429 | 1544.75 | 64.3646 | 1556.23 | 64.8429 | 1544.75 | 64.3646 | 1556.23 | 64.8429 | 1544.75 | 64.3646 | 1556.23 | 64.8429 | 1544.75 | 64.3646 | 1556.23 | 64.8429 | 1544.75 | 64.3646 | 1556.23 | 64.8429 | 1544.75 | 64.3646 | 1556.23 | 64.8429 | 1544.75 | 64.3646 | 1556.23 | 64.8429
GEN-2017-060 | DISIS-2017-001 | 12 - Northwest Arkansas | EDE | 125.4 | ER | Wind | LaRussell Energy Center 161kV Substation | 588984 | 1 | 588980 | 1534.71 | 12.2385 | 1556.23 | 12.4101 | 1544.75 | 12.3186 | 1556.23 | 12.4101 | 1544.75 | 12.3186 | 1556.23 | 12.4101 | 1544.75 | 12.3186 | 1556.23 | 12.4101 | 1534.7 | 12.2384 | 1556.21 | 12.41 | 1544.75 | 12.3186 | 1556.23 | 12.4101 | 1533.71 | 12.2305 | 1548.16 | 12.3458 | 1534.71 | 12.2385 | 1556.23 | 12.4101 | 1544.75 | 12.3186 | 1556.23 | 12.4101 | 1544.75 | 12.3186 | 1556.23 | 12.4101 | 1544.75 | 12.3186 | 1556.23 | 12.4101 | 1544.75 | 12.3186 | 1556.23 | 12.4101 | 1544.75 | 12.3186 | 1556.23 | 12.4101 | 1544.75 | 12.3186 | 1556.23 | 12.4101 | 1544.75 | 12.3186 | 1556.23 | 12.4101
GEN-2017-061 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | GRDA | 101.5 | ER/NR | Solar | GRDA1 to CLARMR 5 161kV | 588993 | 1 | 588990 | 6770.41 | 66.7035 | 6910.07 | 68.0795 | 6777.93 | 66.7776 | 6910.19 | 68.0807 | 6777.93 | 66.7776 | 6910.19 | 68.0807 | 6777.93 | 66.7776 | 6910.19 | 68.0807 | 6766.57 | 66.6657 | 6903.65 | 68.0163 | 6777.9 | 66.7773 | 6910.19 | 68.0807 | 6480.5 | 63.8473 | 6905.09 | 68.0304 | 6770.41 | 66.7035 | 6910.19 | 68.0807 | 6777.93 | 66.7776 | 6910.19 | 68.0807 | 6777.93 | 66.7776 | 6910.19 | 68.0807 | 6777.93 | 66.7776 | 6910.19 | 68.0807 | 6777.93 | 66.7776 | 6910.19 | 68.0807 | 6777.93 | 66.7776 | 6910.19 | 68.0807 | 6777.93 | 66.7776 | 6910.19 | 68.0807 | 6777.93 | 66.7776 | 6910.19 | 68.0807
GEN-2017-064 | DISIS-2017-001 | 17 - Western South Dakota | WAPA | 49.6 | ER/NR | Solar | Underwood-Wayside 230kV | 589023 | 1 | 589020 | 1290.01 | 26.0083 | 1299.64 | 26.2024 | 1297.92 | 26.1677 | 1299.64 | 26.2024 | 1297.92 | 26.1677 | 1299.64 | 26.2024 | 1297.92 | 26.1677 | 1299.64 | 26.2024 | 1286.81 | 25.9437 | 1299.64 | 26.2024 | 1297.92 | 26.1677 | 1299.64 | 26.2024 | 1286.6 | 25.9395 | 1299.64 | 26.2024 | 1287.06 | 25.9488 | 1292.4 | 26.0565 | 1297.92 | 26.1677 | 1299.64 | 26.2024 | 1297.92 | 26.1677 | 1299.64 | 26.2024 | 1297.92 | 26.1677 | 1299.64 | 26.2024 | 1297.92 | 26.1677 | 1299.64 | 26.2024 | 1291.64 | 26.0411 | 1294.95 | 26.1079 | 1291.64 | 26.0411 | 1296.12 | 26.1315 | 1297.92 | 26.1677 | 1299.64 | 26.2024
GEN-2017-064 | DISIS-2017-001 | 17 - Western South Dakota | WAPA | 60.4 | ER/NR | Solar | Underwood-Wayside 230kV | 589027 | 1 | 589020 | 1290.01 | 21.3578 | 1299.64 | 21.5172 | 1297.92 | 21.4887 | 1299.64 | 21.5172 | 1297.92 | 21.4887 | 1299.64 | 21.5172 | 1297.92 | 21.4887 | 1299.64 | 21.5172 | 1286.81 | 21.3048 | 1299.64 | 21.5172 | 1297.92 | 21.4887 | 1299.64 | 21.5172 | 1286.6 | 21.3013 | 1299.64 | 21.5172 | 1287.06 | 21.3089 | 1292.4 | 21.3974 | 1297.92 | 21.4887 | 1299.64 | 21.5172 | 1297.92 | 21.4887 | 1299.64 | 21.5172 | 1297.92 | 21.4887 | 1299.64 | 21.5172 | 1297.92 | 21.4887 | 1299.64 | 21.5172 | 1291.64 | 21.3848 | 1294.95 | 21.4396 | 1291.64 | 21.3848 | 1296.12 | 21.4589 | 1297.92 | 21.4887 | 1299.64 | 21.5172
GEN-2017-065 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | AEPW | 99 | ER/NR | Solar | Oklaunion 345kV Substation | 589033 | 1 | 589030 | 3338.87 | 33.726 | 3379.9 | 34.1404 | 3355.46 | 33.8935 | 3387.13 | 34.2134 | 3355.45 | 33.8934 | 3387.12 | 34.2133 | 3355.44 | 33.8933 | 3387.11 | 34.2132 | 3396.31 | 34.3062 | 3468.61 | 35.0365 | 3353.41 | 33.8728 | 3380.37 | 34.1452 | 3338.86 | 33.7259 | 3387.12 | 34.2133 | 3355.44 | 33.8933 | 3387.11 | 34.2132 | 3355.44 | 33.8933 | 3387.12 | 34.2133 | 3355.44 | 33.8933 | 3387.12 | 34.2133 | 3355.44 | 33.8933 | 3387.12 | 34.2133 | 3355.44 | 33.8933 | 3380.37 | 34.1452 | 3355.44 | 33.8933 | 3387.12 | 34.2133 | 3355.44 | 33.8933 | 3387.12 | 34.2133 | 3355.44 | 33.8933 | 3387.12 | 34.2133
GEN-2017-066 | DISIS-2017-001 | 14 - South Central Oklahoma | WFEC | 150.75 | ER/NR | Solar | Oney 138kV Substation | 589043 | 1 | 589040 | 2597.42 | 17.23 | 2656.78 | 17.6237 | 2597.6 | 17.2312 | 2657.11 | 17.6259 | 2597.6 | 17.2312 | 2657.1 | 17.6259 | 2597.59 | 17.2311 | 2657.1 | 17.6259 | 2478.68 | 16.4423 | 2504.3 | 16.6123 | 2582.88 | 17.1335 | 2657.07 | 17.6257 | 2597.41 | 17.2299 | 2657.1 | 17.6259 | 2597.59 | 17.2311 | 2657.1 | 17.6259 | 2597.6 | 17.2312 | 2657.1 | 17.6259 | 2597.6 | 17.2312 | 2657.1 | 17.6259 | 2597.6 | 17.2312 | 2657.1 | 17.6259 | 2597.6 | 17.2312 | 2657.07 | 17.6257 | 2597.6 | 17.2312 | 2657.1 | 17.6259 | 2597.6 | 17.2312 | 2657.1 | 17.6259 | 2597.6 | 17.2312 | 2657.1 | 17.6259
GEN-2017-067 | DISIS-2017-001 | 01 - Woodward | OKGE | 99 | ER/NR | Solar | Minco 345kV Substation | 589053 | 1 | 589050 | 9378.97 | 94.7371 | 9563.05 | 96.5965 | 9382.52 | 94.7729 | 9571.28 | 96.6796 | 9382.48 | 94.7725 | 9571.2 | 96.6788 | 9382.44 | 94.7721 | 9571.19 | 96.6787 | 9077.92 | 91.6962 | 9400.56 | 94.9552 | 9352.6 | 94.4707 | 9570.37 | 96.6704 | 9378.71 | 94.7344 | 9571.22 | 96.679 | 9382.41 | 94.7718 | 9571.18 | 96.6786 | 9382.46 | 94.7723 | 9571.23 | 96.6791 | 9382.46 | 94.7723 | 9571.23 | 96.6791 | 9382.46 | 94.7723 | 9571.23 | 96.6791 | 9382.46 | 94.7723 | 9570.37 | 96.6704 | 9382.46 | 94.7723 | 9571.23 | 96.6791 | 9382.46 | 94.7723 | 9571.23 | 96.6791 | 9382.46 | 94.7723 | 9571.23 | 96.6791
GEN-2017-067 | DISIS-2017-001 | 01 - Woodward | OKGE | 101.25 | ER/NR | Solar | Minco 345kV Substation | 589057 | 1 | 589050 | 9378.97 | 92.6318 | 9563.05 | 94.4499 | 9382.52 | 92.6669 | 9571.28 | 94.5312 | 9382.48 | 92.6665 | 9571.2 | 94.5304 | 9382.44 | 92.6661 | 9571.19 | 94.5303 | 9077.92 | 89.6585 | 9400.56 | 92.845 | 9352.6 | 92.3714 | 9570.37 | 94.5222 | 9378.71 | 92.6292 | 9571.22 | 94.5306 | 9382.41 | 92.6658 | 9571.18 | 94.5302 | 9382.46 | 92.6663 | 9571.23 | 94.5307 | 9382.46 | 92.6663 | 9571.23 | 94.5307 | 9382.46 | 92.6663 | 9571.23 | 94.5307 | 9382.46 | 92.6663 | 9570.37 | 94.5222 | 9382.46 | 92.6663 | 9571.23 | 94.5307 | 9382.46 | 92.6663 | 9571.23 | 94.5307 | 9382.46 | 92.6663 | 9571.23 | 94.5307
GEN-2017-068 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | WERE | 103.5 | ER/NR | Solar | Wichita 345kV Substation | 589063 | 1 | 589060 | 11448.01 | 110.6088 | 12320.2 | 119.0357 | 11448.9 | 110.6174 | 12321.2 | 119.0454 | 11450.33 | 110.6312 | 12321.17 | 119.0451 | 11448.96 | 110.618 | 12320.28 | 119.0365 | 11444.84 | 110.5782 | 12319.71 | 119.031 | 11444.29 | 110.5729 | 12321.1 | 119.0444 | 11426.41 | 110.4001 | 12321.44 | 119.0477 | 11448.46 | 110.6131 | 12319.73 | 119.0312 | 11449.94 | 110.6274 | 12321.56 | 119.0489 | 11449.94 | 110.6274 | 12321.56 | 119.0489 | 11448.87 | 110.6171 | 12320.97 | 119.0432 | 11448.86 | 110.617 | 12321.1 | 119.0444 | 11449.93 | 110.6273 | 12321.38 | 119.0471 | 11449.46 | 110.6228 | 12321.38 | 119.0471 | 11449.94 | 110.6274 | 12321.39 | 119.0472
GEN-2017-069 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 25 | ER/NR | Solar | Norton 115kV Switching Station | 524491 | 1 | 588610 | 637.34 | 25.4936 | 637.6 | 25.504 | 637.71 | 25.5084 | 756.92 | 30.2768 | 637.71 | 25.5084 | 756.92 | 30.2768 | 637.71 | 25.5084 | 756.92 | 30.2768 | 637.71 | 25.5084 | 637.66 | 25.5064 | 637.71 | 25.5084 | 637.61 | 25.5044 | 637.34 | 25.4936 | 756.92 | 30.2768 | 637.71 | 25.5084 | 756.92 | 30.2768 | 637.71 | 25.5084 | 756.92 | 30.2768 | 637.71 | 25.5084 | 756.92 | 30.2768 | 637.71 | 25.5084 | 756.92 | 30.2768 | 637.71 | 25.5084 | 637.61 | 25.5044 | 637.71 | 25.5084 | 756.92 | 30.2768 | 637.71 | 25.5084 | 756.92 | 30.2768 | 637.71 | 25.5084 | 756.92 | 30.2768
GEN-2017-071 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | OKGE | 124.7 | ER/NR | Solar | Greenwood 138kV Substation | 589093 | 1 | 589090 | 2010.42 | 16.1221 | 2025.17 | 16.2403 | 2010.46 | 16.1224 | 2027.13 | 16.2561 | 2010.46 | 16.1224 | 2027.13 | 16.2561 | 2010.46 | 16.1224 | 2027.13 | 16.2561 | 2004.29 | 16.0729 | 2018.53 | 16.1871 | 2010.37 | 16.1217 | 2027.13 | 16.2561 | 2010.13 | 16.1197 | 2027.12 | 16.256 | 2010.43 | 16.1221 | 2027.13 | 16.2561 | 2010.46 | 16.1224 | 2027.13 | 16.2561 | 2010.46 | 16.1224 | 2027.13 | 16.2561 | 2010.46 | 16.1224 | 2027.13 | 16.2561 | 2010.46 | 16.1224 | 2027.13 | 16.2561 | 2010.46 | 16.1224 | 2027.13 | 16.2561 | 2010.46 | 16.1224 | 2027.13 | 16.2561 | 2010.46 | 16.1224 | 2027.13 | 16.2561
GEN-2017-072 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | OKGE | 52.2 | ER/NR | Solar | Greenwood 138kV Substation | 589103 | 1 | 589100 | 2010.42 | 38.5138 | 2025.17 | 38.7964 | 2010.46 | 38.5146 | 2027.13 | 38.8339 | 2010.46 | 38.5146 | 2027.13 | 38.8339 | 2010.46 | 38.5146 | 2027.13 | 38.8339 | 2004.29 | 38.3964 | 2018.53 | 38.6692 | 2010.37 | 38.5128 | 2027.13 | 38.8339 | 2010.13 | 38.5082 | 2027.12 | 38.8337 | 2010.43 | 38.514 | 2027.13 | 38.8339 | 2010.46 | 38.5146 | 2027.13 | 38.8339 | 2010.46 | 38.5146 | 2027.13 | 38.8339 | 2010.46 | 38.5146 | 2027.13 | 38.8339 | 2010.46 | 38.5146 | 2027.13 | 38.8339 | 2010.46 | 38.5146 | 2027.13 | 38.8339 | 2010.46 | 38.5146 | 2027.13 | 38.8339 | 2010.46 | 38.5146 | 2027.13 | 38.8339
GEN-2017-073 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | GRDA | 72.5 | ER/NR | Solar | Dry Gulch 161kV Substation | 589113 | 1 | 589110 | 3808.08 | 52.5252 | 3857.96 | 53.2132 | 3814.22 | 52.6099 | 3857.99 | 53.2137 | 3814.22 | 52.6099 | 3857.99 | 53.2137 | 3814.22 | 52.6099 | 3857.99 | 53.2137 | 3807.01 | 52.5105 | 3856.28 | 53.1901 | 3814.21 | 52.6098 | 3857.99 | 53.2137 | 3640.14 | 50.2088 | 3853.61 | 53.1532 | 3808.08 | 52.5252 | 3857.99 | 53.2137 | 3814.22 | 52.6099 | 3857.99 | 53.2137 | 3814.22 | 52.6099 | 3857.99 | 53.2137 | 3814.22 | 52.6099 | 3857.99 | 53.2137 | 3814.22 | 52.6099 | 3857.99 | 53.2137 | 3814.22 | 52.6099 | 3857.99 | 53.2137 | 3814.22 | 52.6099 | 3857.99 | 53.2137 | 3814.22 | 52.6099 | 3857.99 | 53.2137
GEN-2017-074 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | AEPW | 72.5 | ER/NR | Solar | Pryor Junction 138kV Substation | 589123 | 1 | 589120 | 1548.27 | 21.3554 | 1562.17 | 21.5472 | 1549.49 | 21.3723 | 1562.18 | 21.5473 | 1549.49 | 21.3723 | 1562.18 | 21.5473 | 1549.49 | 21.3723 | 1562.18 | 21.5473 | 1547.7 | 21.3476 | 1561.6 | 21.5393 | 1549.49 | 21.3723 | 1562.18 | 21.5473 | 1537.98 | 21.2135 | 1561.32 | 21.5354 | 1548.27 | 21.3554 | 1562.18 | 21.5473 | 1549.49 | 21.3723 | 1562.18 | 21.5473 | 1549.49 | 21.3723 | 1562.18 | 21.5473 | 1549.49 | 21.3723 | 1562.18 | 21.5473 | 1549.49 | 21.3723 | 1562.18 | 21.5473 | 1549.49 | 21.3723 | 1562.18 | 21.5473 | 1549.49 | 21.3723 | 1562.18 | 21.5473 | 1549.49 | 21.3723 | 1562.18 | 21.5473
GEN-2017-075 | DISIS-2017-001 | 14 - South Central Oklahoma | OKGE | 200 | ER/NR | Solar | Hugo-Sunnyside 345kV Substation | 589133 | 1 | 589130 | 4067.48 | 20.3374 | 4095.24 | 20.4762 | 4067.72 | 20.3386 | 4095.77 | 20.4789 | 4067.72 | 20.3386 | 4095.77 | 20.4789 | 4067.72 | 20.3386 | 4095.77 | 20.4789 | 4062.29 | 20.3115 | 4084.51 | 20.4226 | 4066.76 | 20.3338 | 4095.7 | 20.4785 | 4067.43 | 20.3371 | 4095.77 | 20.4789 | 4067.71 | 20.3386 | 4095.77 | 20.4789 | 4067.72 | 20.3386 | 4095.77 | 20.4789 | 4067.72 | 20.3386 | 4095.77 | 20.4789 | 4067.72 | 20.3386 | 4095.77 | 20.4789 | 4067.72 | 20.3386 | 4095.7 | 20.4785 | 4067.72 | 20.3386 | 4095.77 | 20.4789 | 4067.72 | 20.3386 | 4095.77 | 20.4789 | 4067.72 | 20.3386 | 4095.77 | 20.4789
GEN-2017-076 | DISIS-2017-001 | 12 - Northwest Arkansas | AEPW | 52.2 | ER/NR | Solar | Chamber Springs 161kV Substation | 589143 | 1 | 589140 | 6097.31 | 116.8067 | 6142.64 | 117.6751 | 6104.93 | 116.9527 | 6142.71 | 117.6764 | 6104.93 | 116.9527 | 6142.71 | 117.6764 | 6104.93 | 116.9527 | 6142.71 | 117.6764 | 6105.06 | 116.9552 | 6139.11 | 117.6075 | 6104.91 | 116.9523 | 6142.71 | 117.6764 | 6070.44 | 116.292 | 6137.01 | 117.5672 | 6097.31 | 116.8067 | 6142.71 | 117.6764 | 6104.93 | 116.9527 | 6142.71 | 117.6764 | 6104.93 | 116.9527 | 6142.71 | 117.6764 | 6104.93 | 116.9527 | 6142.71 | 117.6764 | 6104.93 | 116.9527 | 6142.71 | 117.6764 | 6104.93 | 116.9527 | 6142.71 | 117.6764 | 6104.93 | 116.9527 | 6142.71 | 117.6764 | 6104.93 | 116.9527 | 6142.71 | 117.6764
GEN-2017-077 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | AEPW | 124.7 | ER/NR | Solar | Explorer Claremore Tap EXCLART4 | 589153 | 1 | 589150 | 1444.44 | 11.5833 | 1459.12 | 11.701 | 1445.22 | 11.5896 | 1459.12 | 11.701 | 1445.22 | 11.5896 | 1459.12 | 11.701 | 1445.22 | 11.5896 | 1459.12 | 11.701 | 1443.73 | 11.5776 | 1458.44 | 11.6956 | 1445.22 | 11.5896 | 1459.12 | 11.701 | 1437.57 | 11.5282 | 1458.6 | 11.6969 | 1444.44 | 11.5833 | 1459.12 | 11.701 | 1445.22 | 11.5896 | 1459.12 | 11.701 | 1445.22 | 11.5896 | 1459.12 | 11.701 | 1445.22 | 11.5896 | 1459.12 | 11.701 | 1445.22 | 11.5896 | 1459.12 | 11.701 | 1445.22 | 11.5896 | 1459.12 | 11.701 | 1445.22 | 11.5896 | 1459.12 | 11.701 | 1445.22 | 11.5896 | 1459.12 | 11.701
GEN-2017-078 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 150 | ER/NR | Wind | Eddy County-Tolk (Crossroads) 345kV | 589163 | 1 | 589160 | 3206.49 | 21.3766 | 3212.62 | 21.4175 | 3269.04 | 21.7936 | 3235.73 | 21.5715 | 3269.02 | 21.7935 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3235.69 | 21.5713 | 3269.52 | 21.7968 | 3217.67 | 21.4511 | 3269.01 | 21.7934 | 3213.32 | 21.4221 | 3206.49 | 21.3766 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3213.32 | 21.4221 | 3269.01 | 21.7934 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3235.69 | 21.5713
GEN-2017-078 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 150 | ER/NR | Wind | Eddy County-Tolk (Crossroads) 345kV | 589167 | 1 | 589160 | 3206.49 | 21.3766 | 3212.62 | 21.4175 | 3269.04 | 21.7936 | 3235.73 | 21.5715 | 3269.02 | 21.7935 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3235.69 | 21.5713 | 3269.52 | 21.7968 | 3217.67 | 21.4511 | 3269.01 | 21.7934 | 3213.32 | 21.4221 | 3206.49 | 21.3766 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3213.32 | 21.4221 | 3269.01 | 21.7934 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3235.69 | 21.5713 | 3269.01 | 21.7934 | 3235.69 | 21.5713
GEN-2017-079 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 26.25 | ER | Solar | Hart Industrial 115kV Substation | 589173 | 1 | 589170 | 1597.96 | 60.8747 | 1604.27 | 61.115 | 1616.05 | 61.5638 | 1610.51 | 61.3528 | 1615.94 | 61.5596 | 1610.39 | 61.3482 | 1615.94 | 61.5596 | 1610.39 | 61.3482 | 1616.56 | 61.5832 | 1608.97 | 61.2941 | 1615.93 | 61.5592 | 1606.63 | 61.205 | 1597.96 | 60.8747 | 1610.4 | 61.3486 | 1615.94 | 61.5596 | 1610.39 | 61.3482 | 1615.94 | 61.5596 | 1610.4 | 61.3486 | 1615.94 | 61.5596 | 1610.4 | 61.3486 | 1615.94 | 61.5596 | 1610.4 | 61.3486 | 1615.94 | 61.5596 | 1606.63 | 61.205 | 1615.94 | 61.5596 | 1610.4 | 61.3486 | 1615.94 | 61.5596 | 1610.4 | 61.3486 | 1615.94 | 61.5596 | 1610.4 | 61.3486
GEN-2017-079 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 23.63 | ER | Solar | Hart Industrial 115kV Substation | 589177 | 1 | 589170 | 1597.96 | 67.6242 | 1604.27 | 67.8912 | 1616.05 | 68.3898 | 1610.51 | 68.1553 | 1615.94 | 68.3851 | 1610.39 | 68.1502 | 1615.94 | 68.3851 | 1610.39 | 68.1502 | 1616.56 | 68.4113 | 1608.97 | 68.0901 | 1615.93 | 68.3847 | 1606.63 | 67.9911 | 1597.96 | 67.6242 | 1610.4 | 68.1507 | 1615.94 | 68.3851 | 1610.39 | 68.1502 | 1615.94 | 68.3851 | 1610.4 | 68.1507 | 1615.94 | 68.3851 | 1610.4 | 68.1507 | 1615.94 | 68.3851 | 1610.4 | 68.1507 | 1615.94 | 68.3851 | 1606.63 | 67.9911 | 1615.94 | 68.3851 | 1610.4 | 68.1507 | 1615.94 | 68.3851 | 1610.4 | 68.1507 | 1615.94 | 68.3851 | 1610.4 | 68.1507
GEN-2017-080 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 213.1 | ER | Solar | Tolk 230kV Substation | 589183 | 1 | 589180 | 9773.1 | 45.8616 | 9928.22 | 46.5895 | 10691.08 | 50.1693 | 10064.38 | 47.2284 | 10690.37 | 50.166 | 10063.54 | 47.2245 | 10690.33 | 50.1658 | 10063.53 | 47.2244 | 10699.78 | 50.2101 | 10044.09 | 47.1332 | 10690.26 | 50.1655 | 9944.02 | 46.6636 | 9773.1 | 45.8616 | 10063.59 | 47.2247 | 10690.33 | 50.1658 | 10063.53 | 47.2244 | 10690.35 | 50.1659 | 10063.59 | 47.2247 | 10690.35 | 50.1659 | 10063.59 | 47.2247 | 10690.35 | 50.1659 | 10063.59 | 47.2247 | 10690.35 | 50.1659 | 9944.02 | 46.6636 | 10690.35 | 50.1659 | 10063.59 | 47.2247 | 10690.35 | 50.1659 | 10063.59 | 47.2247 | 10690.35 | 50.1659 | 10063.59 | 47.2247
GEN-2017-080 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 311.9 | ER | Solar | Tolk 230kV Substation | 589187 | 1 | 589180 | 9773.1 | 31.3341 | 9928.22 | 31.8314 | 10691.08 | 34.2773 | 10064.38 | 32.268 | 10690.37 | 34.275 | 10063.54 | 32.2653 | 10690.33 | 34.2749 | 10063.53 | 32.2652 | 10699.78 | 34.3052 | 10044.09 | 32.2029 | 10690.26 | 34.2746 | 9944.02 | 31.8821 | 9773.1 | 31.3341 | 10063.59 | 32.2654 | 10690.33 | 34.2749 | 10063.53 | 32.2652 | 10690.35 | 34.2749 | 10063.59 | 32.2654 | 10690.35 | 34.2749 | 10063.59 | 32.2654 | 10690.35 | 34.2749 | 10063.59 | 32.2654 | 10690.35 | 34.2749 | 9944.02 | 31.8821 | 10690.35 | 34.2749 | 10063.59 | 32.2654 | 10690.35 | 34.2749 | 10063.59 | 32.2654 | 10690.35 | 34.2749 | 10063.59 | 32.2654
GEN-2017-081 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 151.3 | ER | Solar | Amarillo South-Swisher 230kV | 589193 | 1 | 589190 | 2872.09 | 18.9827 | 2889.14 | 19.0954 | 2934.53 | 19.3954 | 2932.63 | 19.3829 | 2933.49 | 19.3886 | 2931.48 | 19.3753 | 2933.44 | 19.3882 | 2931.47 | 19.3752 | 2937.34 | 19.414 | 2928.75 | 19.3572 | 2933.41 | 19.388 | 2922.38 | 19.3151 | 2872.09 | 18.9827 | 2931.54 | 19.3757 | 2933.44 | 19.3882 | 2931.47 | 19.3752 | 2933.46 | 19.3884 | 2931.54 | 19.3757 | 2933.46 | 19.3884 | 2931.54 | 19.3757 | 2933.46 | 19.3884 | 2931.54 | 19.3757 | 2933.46 | 19.3884 | 2922.38 | 19.3151 | 2933.46 | 19.3884 | 2931.54 | 19.3757 | 2933.46 | 19.3884 | 2931.54 | 19.3757 | 2933.46 | 19.3884 | 2931.54 | 19.3757
GEN-2017-081 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 148.7 | ER | Solar | Amarillo South-Swisher 230kV | 589197 | 1 | 589190 | 2872.09 | 19.3147 | 2889.14 | 19.4293 | 2934.53 | 19.7346 | 2932.63 | 19.7218 | 2933.49 | 19.7276 | 2931.48 | 19.7141 | 2933.44 | 19.7272 | 2931.47 | 19.714 | 2937.34 | 19.7535 | 2928.75 | 19.6957 | 2933.41 | 19.727 | 2922.38 | 19.6529 | 2872.09 | 19.3147 | 2931.54 | 19.7145 | 2933.44 | 19.7272 | 2931.47 | 19.714 | 2933.46 | 19.7274 | 2931.54 | 19.7145 | 2933.46 | 19.7274 | 2931.54 | 19.7145 | 2933.46 | 19.7274 | 2931.54 | 19.7145 | 2933.46 | 19.7274 | 2922.38 | 19.6529 | 2933.46 | 19.7274 | 2931.54 | 19.7145 | 2933.46 | 19.7274 | 2931.54 | 19.7145 | 2933.46 | 19.7274 | 2931.54 | 19.7145
GEN-2017-082 | DISIS-2017-001 | 12 - Northwest Arkansas | EDE | 24 | ER | Wind | Asbury Plant 161kV Substation | 589203 | 1 | 589200 | 2113.49 | 88.0621 | 2176.58 | 90.6908 | 2140.46 | 89.1858 | 2176.58 | 90.6908 | 2140.46 | 89.1858 | 2176.58 | 90.6908 | 2140.46 | 89.1858 | 2176.58 | 90.6908 | 2113.45 | 88.0604 | 2176.53 | 90.6888 | 2140.46 | 89.1858 | 2176.58 | 90.6908 | 2110.92 | 87.955 | 2154.75 | 89.7812 | 2113.49 | 88.0621 | 2176.58 | 90.6908 | 2140.46 | 89.1858 | 2176.58 | 90.6908 | 2140.46 | 89.1858 | 2176.58 | 90.6908 | 2140.46 | 89.1858 | 2176.58 | 90.6908 | 2140.46 | 89.1858 | 2176.58 | 90.6908 | 2140.46 | 89.1858 | 2176.58 | 90.6908 | 2140.46 | 89.1858 | 2176.58 | 90.6908 | 2140.46 | 89.1858 | 2176.58 | 90.6908
GEN-2017-082 | DISIS-2017-001 | 12 - Northwest Arkansas | EDE | 125.4 | ER | Wind | Asbury Plant 161kV Substation | 589204 | 1 | 589200 | 2113.49 | 16.854 | 2176.58 | 17.3571 | 2140.46 | 17.0691 | 2176.58 | 17.3571 | 2140.46 | 17.0691 | 2176.58 | 17.3571 | 2140.46 | 17.0691 | 2176.58 | 17.3571 | 2113.45 | 16.8537 | 2176.53 | 17.3567 | 2140.46 | 17.0691 | 2176.58 | 17.3571 | 2110.92 | 16.8335 | 2154.75 | 17.183 | 2113.49 | 16.854 | 2176.58 | 17.3571 | 2140.46 | 17.0691 | 2176.58 | 17.3571 | 2140.46 | 17.0691 | 2176.58 | 17.3571 | 2140.46 | 17.0691 | 2176.58 | 17.3571 | 2140.46 | 17.0691 | 2176.58 | 17.3571 | 2140.46 | 17.0691 | 2176.58 | 17.3571 | 2140.46 | 17.0691 | 2176.58 | 17.3571 | 2140.46 | 17.0691 | 2176.58 | 17.3571
GEN-2017-083 | DISIS-2017-001 | 04 - Northwest Kansas | SUNC | 100 | ER/NR | Wind | Mingo 115kV Substation | 589213 | 1 | 589210 | 2291.53 | 22.9153 | 2323.82 | 23.2382 | 2291.45 | 22.9145 | 2324.85 | 23.2485 | 2289.8 | 22.898 | 2326.41 | 23.2641 | 2284.31 | 22.8431 | 2318.81 | 23.1881 | 2291.57 | 22.9157 | 2323.86 | 23.2386 | 2291.4 | 22.914 | 2324.84 | 23.2484 | 2291.5 | 22.915 | 2327.2 | 23.272 | 2284.45 | 22.8445 | 2315.35 | 23.1535 | 2293.04 | 22.9304 | 2325.67 | 23.2567 | 2293.04 | 22.9304 | 2325.67 | 23.2567 | 2291.43 | 22.9143 | 2324.4 | 23.244 | 2291.43 | 22.9143 | 2324.84 | 23.2484 | 2293.01 | 22.9301 | 2325.27 | 23.2527 | 2292.31 | 22.9231 | 2325.27 | 23.2527 | 2293.04 | 22.9304 | 2325.31 | 23.2531
GEN-2017-084 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 89.25 | ER | Solar | Newhart-Swisher 230kV Substation | 589223 | 1 | 589220 | 3876.79 | 43.4374 | 3920.65 | 43.9289 | 4000.28 | 44.8211 | 3970.54 | 44.4878 | 3999.22 | 44.8092 | 3969.37 | 44.4747 | 3999.17 | 44.8086 | 3969.36 | 44.4746 | 4004.89 | 44.8727 | 3959.03 | 44.3589 | 3999.13 | 44.8082 | 3943.91 | 44.1895 | 3876.79 | 43.4374 | 3969.44 | 44.4755 | 3999.17 | 44.8086 | 3969.36 | 44.4746 | 3999.19 | 44.8089 | 3969.44 | 44.4755 | 3999.19 | 44.8089 | 3969.44 | 44.4755 | 3999.19 | 44.8089 | 3969.44 | 44.4755 | 3999.19 | 44.8089 | 3943.91 | 44.1895 | 3999.19 | 44.8089 | 3969.44 | 44.4755 | 3999.19 | 44.8089 | 3969.44 | 44.4755 | 3999.19 | 44.8089 | 3969.44 | 44.4755
GEN-2017-085 | DISIS-2017-001 | 09 - Nebraska | NPPD | 73.4 | ER/NR | Wind | Friend 115kV Substation | 562547 | 1 | 562545 | 1198.18 | 16.324 | 1207.69 | 16.4535 | 1197.54 | 16.3153 | 1208.37 | 16.4628 | 1197.55 | 16.3154 | 1208.38 | 16.4629 | 1197.55 | 16.3154 | 1208.37 | 16.4628 | 1198.17 | 16.3238 | 1207.69 | 16.4535 | 1197.54 | 16.3153 | 1208.37 | 16.4628 | 1198.15 | 16.3236 | 1209.54 | 16.4787 | 1198.2 | 16.3243 | 1200.18 | 16.3512 | 1197.55 | 16.3154 | 1209.54 | 16.4787 | 1197.55 | 16.3154 | 1209.54 | 16.4787 | 1197.57 | 16.3157 | 1208.21 | 16.4606 | 1197.54 | 16.3153 | 1208.37 | 16.4628 | 1197.5 | 16.3147 | 1208.36 | 16.4627 | 1197.5 | 16.3147 | 1208.36 | 16.4627 | 1197.55 | 16.3154 | 1209.54 | 16.4787
GEN-2017-086 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | WERE | 20 | ER/NR | Wind | Viola 345kV Substation | 589243 | 1 | 589240 | 8154.89 | 407.7445 | 8385.68 | 419.284 | 8155.23 | 407.7615 | 8386.26 | 419.313 | 8155.58 | 407.779 | 8386.21 | 419.3105 | 8155.2 | 407.76 | 8385.99 | 419.2995 | 8150.07 | 407.5035 | 8384.35 | 419.2175 | 8152.52 | 407.626 | 8386.22 | 419.311 | 8149.15 | 407.4575 | 8386.28 | 419.314 | 8155.01 | 407.7505 | 8385.87 | 419.2935 | 8155.48 | 407.774 | 8386.33 | 419.3165 | 8155.48 | 407.774 | 8386.33 | 419.3165 | 8155.22 | 407.761 | 8386.2 | 419.31 | 8155.22 | 407.761 | 8386.22 | 419.311 | 8155.48 | 407.774 | 8386.29 | 419.3145 | 8155.36 | 407.768 | 8386.29 | 419.3145 | 8155.48 | 407.774 | 8386.29 | 419.3145
GEN-2017-086 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | WERE | 130 | ER/NR | Wind | Viola 345kV Substation | 589245 | 1 | 589240 | 8154.89 | 62.7299 | 8385.68 | 64.5052 | 8155.23 | 62.7325 | 8386.26 | 64.5097 | 8155.58 | 62.7352 | 8386.21 | 64.5093 | 8155.2 | 62.7323 | 8385.99 | 64.5076 | 8150.07 | 62.6928 | 8384.35 | 64.495 | 8152.52 | 62.7117 | 8386.22 | 64.5094 | 8149.15 | 62.6858 | 8386.28 | 64.5098 | 8155.01 | 62.7308 | 8385.87 | 64.5067 | 8155.48 | 62.7345 | 8386.33 | 64.5102 | 8155.48 | 62.7345 | 8386.33 | 64.5102 | 8155.22 | 62.7325 | 8386.2 | 64.5092 | 8155.22 | 62.7325 | 8386.22 | 64.5094 | 8155.48 | 62.7345 | 8386.29 | 64.5099 | 8155.36 | 62.7335 | 8386.29 | 64.5099 | 8155.48 | 62.7345 | 8386.29 | 64.5099
GEN-2017-087 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 64 | ER/NR | Solar | Clovis Interchange 115kV Substation | 589253 | 1 | 589250 | 1485.73 | 23.2145 | 1492.2 | 23.3156 | 1495.64 | 23.3694 | 1501.02 | 23.4534 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.74 | 23.3709 | 1493.83 | 23.3411 | 1495.62 | 23.3691 | 1492.49 | 23.3202 | 1485.73 | 23.2145 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1492.49 | 23.3202 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1501.01 | 23.4533
GEN-2017-087 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 64 | ER/NR | Solar | Clovis Interchange 115kV Substation | 589257 | 1 | 589250 | 1485.73 | 23.2145 | 1492.2 | 23.3156 | 1495.64 | 23.3694 | 1501.02 | 23.4534 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.74 | 23.3709 | 1493.83 | 23.3411 | 1495.62 | 23.3691 | 1492.49 | 23.3202 | 1485.73 | 23.2145 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1492.49 | 23.3202 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1501.01 | 23.4533 | 1495.63 | 23.3692 | 1501.01 | 23.4533
GEN-2017-090 | DISIS-2017-001 | 13 - Northeast Kansas/Northwest Missouri | KCPL | 76 | ER | Solar | Adrian 161kV Substation | 589283 | 1 | 589280 | 2235.61 | 29.4159 | 2337.55 | 30.7572 | 2235.84 | 29.4189 | 2337.55 | 30.7572 | 2235.84 | 29.4189 | 2337.55 | 30.7572 | 2235.84 | 29.4189 | 2337.55 | 30.7572 | 2235.61 | 29.4159 | 2337.54 | 30.7571 | 2235.84 | 29.4189 | 2337.55 | 30.7572 | 2229.75 | 29.3388 | 2337.41 | 30.7554 | 2235.62 | 29.4161 | 2337.55 | 30.7572 | 2235.84 | 29.4189 | 2337.56 | 30.7574 | 2235.84 | 29.4189 | 2337.56 | 30.7574 | 2235.86 | 29.4192 | 2337.56 | 30.7574 | 2235.84 | 29.4189 | 2337.55 | 30.7572 | 2235.84 | 29.4189 | 2337.55 | 30.7572 | 2235.84 | 29.4189 | 2337.55 | 30.7572 | 2235.84 | 29.4189 | 2337.56 | 30.7574
GEN-2017-090 | DISIS-2017-001 | 13 - Northeast Kansas/Northwest Missouri | KCPL | 74 | ER | Solar | Adrian 161kV Substation | 589287 | 1 | 589280 | 2235.61 | 30.2109 | 2337.55 | 31.5885 | 2235.84 | 30.2141 | 2337.55 | 31.5885 | 2235.84 | 30.2141 | 2337.55 | 31.5885 | 2235.84 | 30.2141 | 2337.55 | 31.5885 | 2235.61 | 30.2109 | 2337.54 | 31.5884 | 2235.84 | 30.2141 | 2337.55 | 31.5885 | 2229.75 | 30.1318 | 2337.41 | 31.5866 | 2235.62 | 30.2111 | 2337.55 | 31.5885 | 2235.84 | 30.2141 | 2337.56 | 31.5886 | 2235.84 | 30.2141 | 2337.56 | 31.5886 | 2235.86 | 30.2143 | 2337.56 | 31.5886 | 2235.84 | 30.2141 | 2337.55 | 31.5885 | 2235.84 | 30.2141 | 2337.55 | 31.5885 | 2235.84 | 30.2141 | 2337.55 | 31.5885 | 2235.84 | 30.2141 | 2337.56 | 31.5886
GEN-2017-091 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 26.25 | ER | Solar | Lamton 115kV Substation | 589293 | 1 | 589290 | 1532.66 | 58.387 | 1540.86 | 58.6994 | 1553.02 | 59.1627 | 1547.34 | 58.9463 | 1552.96 | 59.1604 | 1547.26 | 58.9432 | 1552.95 | 59.16 | 1547.26 | 58.9432 | 1553.5 | 59.181 | 1544.67 | 58.8446 | 1552.95 | 59.16 | 1542.39 | 58.7577 | 1532.66 | 58.387 | 1547.27 | 58.9436 | 1552.95 | 59.16 | 1547.26 | 58.9432 | 1552.95 | 59.16 | 1547.27 | 58.9436 | 1552.95 | 59.16 | 1547.27 | 58.9436 | 1552.95 | 59.16 | 1547.27 | 58.9436 | 1552.95 | 59.16 | 1542.39 | 58.7577 | 1552.95 | 59.16 | 1547.27 | 58.9436 | 1552.95 | 59.16 | 1547.27 | 58.9436 | 1552.95 | 59.16 | 1547.27 | 58.9436
GEN-2017-092 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | OKGE | 80.6 | ER | Solar | Canadian River-Muskogee and Muskogee-Seminole 345kV | 589303 | 1 | 589300 | 8283.24 | 102.7697 | 8733.72 | 108.3588 | 8283.79 | 102.7766 | 8735.6 | 108.3821 | 8283.79 | 102.7766 | 8735.6 | 108.3821 | 8283.79 | 102.7766 | 8735.6 | 108.3821 | 8649.56 | 107.3146 | 8717.07 | 108.1522 | 8283.03 | 102.7671 | 8735.59 | 108.382 | 8279.15 | 102.719 | 8735.35 | 108.379 | 8283.3 | 102.7705 | 8735.6 | 108.3821 | 8283.79 | 102.7766 | 8735.6 | 108.3821 | 8283.79 | 102.7766 | 8735.6 | 108.3821 | 8283.79 | 102.7766 | 8735.6 | 108.3821 | 8283.79 | 102.7766 | 8735.59 | 108.382 | 8283.79 | 102.7766 | 8735.6 | 108.3821 | 8283.79 | 102.7766 | 8735.6 | 108.3821 | 8283.79 | 102.7766 | 8735.6 | 108.3821
GEN-2017-092 | DISIS-2017-001 | 08 - North Oklahoma/South Central Kansas | OKGE | 119.4 | ER | Solar | Canadian River-Muskogee and Muskogee-Seminole 345kV | 589307 | 1 | 589300 | 8283.24 | 69.3739 | 8733.72 | 73.1467 | 8283.79 | 69.3785 | 8735.6 | 73.1625 | 8283.79 | 69.3785 | 8735.6 | 73.1625 | 8283.79 | 69.3785 | 8735.6 | 73.1625 | 8649.56 | 72.4419 | 8717.07 | 73.0073 | 8283.03 | 69.3721 | 8735.59 | 73.1624 | 8279.15 | 69.3396 | 8735.35 | 73.1604 | 8283.3 | 69.3744 | 8735.6 | 73.1625 | 8283.79 | 69.3785 | 8735.6 | 73.1625 | 8283.79 | 69.3785 | 8735.6 | 73.1625 | 8283.79 | 69.3785 | 8735.6 | 73.1625 | 8283.79 | 69.3785 | 8735.59 | 73.1624 | 8283.79 | 69.3785 | 8735.6 | 73.1625 | 8283.79 | 69.3785 | 8735.6 | 73.1625 | 8283.79 | 69.3785 | 8735.6 | 73.1625
GEN-2017-094 | DISIS-2017-001 | 15 - Eastern South Dakota | WAPA | 100 | ER/NR | Wind | Fort Thompson-Huron 230kV | 589323 | 1 | 589320 | 4039.91 | 40.3991 | 4309.45 | 43.0945 | 4286.9 | 42.869 | 4309.47 | 43.0947 | 4286.9 | 42.869 | 4309.47 | 43.0947 | 4286.9 | 42.869 | 4309.47 | 43.0947 | 3996.64 | 39.9664 | 4309.45 | 43.0945 | 4286.9 | 42.869 | 4309.47 | 43.0947 | 3993.86 | 39.9386 | 4309.5 | 43.095 | 4002.51 | 40.0251 | 4065.03 | 40.6503 | 4286.9 | 42.869 | 4309.5 | 43.095 | 4286.9 | 42.869 | 4309.5 | 43.095 | 4286.9 | 42.869 | 4309.47 | 43.0947 | 4286.9 | 42.869 | 4309.47 | 43.0947 | 4066.38 | 40.6638 | 4114.33 | 41.1433 | 4065 | 40.65 | 4127.07 | 41.2707 | 4286.9 | 42.869 | 4309.5 | 43.095
GEN-2017-094 | DISIS-2017-001 | 15 - Eastern South Dakota | WAPA | 100 | ER/NR | Wind | Fort Thompson-Huron 230kV | 589327 | 1 | 589320 | 4039.91 | 40.3991 | 4309.45 | 43.0945 | 4286.9 | 42.869 | 4309.47 | 43.0947 | 4286.9 | 42.869 | 4309.47 | 43.0947 | 4286.9 | 42.869 | 4309.47 | 43.0947 | 3996.64 | 39.9664 | 4309.45 | 43.0945 | 4286.9 | 42.869 | 4309.47 | 43.0947 | 3993.86 | 39.9386 | 4309.5 | 43.095 | 4002.51 | 40.0251 | 4065.03 | 40.6503 | 4286.9 | 42.869 | 4309.5 | 43.095 | 4286.9 | 42.869 | 4309.5 | 43.095 | 4286.9 | 42.869 | 4309.47 | 43.0947 | 4286.9 | 42.869 | 4309.47 | 43.0947 | 4066.38 | 40.6638 | 4114.33 | 41.1433 | 4065 | 40.65 | 4127.07 | 41.2707 | 4286.9 | 42.869 | 4309.5 | 43.095
GEN-2017-095 | DISIS-2017-001 | 13 - Northeast Kansas/Northwest Missouri | KCPL | 200 | ER/NR | Wind | Eastown-Iatan 345kV | 589333 | 1 | 589330 | 1350.68 | 6.7534 | 1353.7 | 6.7685 | 1350.68 | 6.7534 | 1353.71 | 6.7686 | 1350.68 | 6.7534 | 1353.71 | 6.7686 | 1350.68 | 6.7534 | 1353.71 | 6.7686 | 1350.68 | 6.7534 | 1353.7 | 6.7685 | 1350.68 | 6.7534 | 1353.71 | 6.7686 | 1349.91 | 6.7496 | 1353.72 | 6.7686 | 1350.68 | 6.7534 | 1353.69 | 6.7685 | 1350.68 | 6.7534 | 1353.72 | 6.7686 | 1350.68 | 6.7534 | 1353.72 | 6.7686 | 1350.71 | 6.7536 | 1353.75 | 6.7687 | 1350.68 | 6.7534 | 1353.71 | 6.7686 | 1350.68 | 6.7534 | 1353.71 | 6.7686 | 1350.68 | 6.7534 | 1353.71 | 6.7686 | 1350.68 | 6.7534 | 1353.72 | 6.7686
GEN-2017-097 | DISIS-2017-001 | 17 - Western South Dakota | WAPA | 64 | ER/NR | Solar | Underwood 115kV Substation | 589353 | 1 | 589350 | 1431.08 | 22.3606 | 1452.37 | 22.6933 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1423.95 | 22.2492 | 1452.37 | 22.6933 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1423.49 | 22.242 | 1452.37 | 22.6933 | 1424.45 | 22.257 | 1436.1 | 22.4391 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1434.74 | 22.4178 | 1441.72 | 22.5269 | 1434.74 | 22.4178 | 1444.38 | 22.5684 | 1448.87 | 22.6386 | 1452.37 | 22.6933
GEN-2017-097 | DISIS-2017-001 | 17 - Western South Dakota | WAPA | 64 | ER/NR | Solar | Underwood 115kV Substation | 589357 | 1 | 589350 | 1431.08 | 22.3606 | 1452.37 | 22.6933 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1423.95 | 22.2492 | 1452.37 | 22.6933 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1423.49 | 22.242 | 1452.37 | 22.6933 | 1424.45 | 22.257 | 1436.1 | 22.4391 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1448.87 | 22.6386 | 1452.37 | 22.6933 | 1434.74 | 22.4178 | 1441.72 | 22.5269 | 1434.74 | 22.4178 | 1444.38 | 22.5684 | 1448.87 | 22.6386 | 1452.37 | 22.6933
GEN-2017-099 | DISIS-2017-001 | 03 - Spearville | SUNC | 200 | ER/NR | Wind | Post Rock-Spearville 345kV | 589373 | 1 | 589370 | 6084.58 | 30.4229 | 6197.16 | 30.9858 | 6084.5 | 30.4225 | 6203.69 | 31.0184 | 6095.29 | 30.4764 | 6205.59 | 31.028 | 6081.26 | 30.4063 | 6192.24 | 30.9612 | 6084.83 | 30.4242 | 6197.48 | 30.9874 | 6083.57 | 30.4178 | 6203.6 | 31.018 | 6084.25 | 30.4213 | 6210.63 | 31.0532 | 6081.68 | 30.4084 | 6185.65 | 30.9282 | 6094.55 | 30.4728 | 6208.73 | 31.0436 | 6094.55 | 30.4728 | 6208.73 | 31.0436 | 6084.43 | 30.4222 | 6200.86 | 31.0043 | 6084.42 | 30.4221 | 6203.6 | 31.018 | 6094.5 | 30.4725 | 6206.41 | 31.032 | 6090.12 | 30.4506 | 6206.41 | 31.032 | 6094.55 | 30.4728 | 6206.51 | 31.0326
GEN-2017-100 | DISIS-2017-001 | 02 - Hitchland | SWPS | 102.6 | ER/NR | Solar | Texas County 115kV Substation | 589383 | 1 | 589380 | 1781.7 | 17.3655 | 1793.95 | 17.4849 | 1785.44 | 17.4019 | 1797.5 | 17.5195 | 1785.84 | 17.4058 | 1787.51 | 17.4221 | 1783.26 | 17.3807 | 1787.14 | 17.4185 | 1784.11 | 17.389 | 1796.2 | 17.5068 | 1783.7 | 17.385 | 1795.82 | 17.5031 | 1781.7 | 17.3655 | 1795.87 | 17.5036 | 1783.26 | 17.3807 | 1787.13 | 17.4184 | 1783.8 | 17.386 | 1795.87 | 17.5036 | 1783.8 | 17.386 | 1795.87 | 17.5036 | 1783.79 | 17.3859 | 1795.86 | 17.5035 | 1783.79 | 17.3859 | 1795.82 | 17.5031 | 1783.8 | 17.386 | 1795.87 | 17.5036 | 1783.8 | 17.386 | 1795.87 | 17.5036 | 1783.8 | 17.386 | 1795.87 | 17.5036
GEN-2017-104 | DISIS-2017-001 | 06 - South Texas Panhandle/New Mexico | SWPS | 240 | ER/NR | Solar | Hobbs 230kV Substation | 589403 | 1 | 589400 | 5449.16 | 22.7048 | 5317.97 | 22.1582 | 6548.14 | 27.2839 | 5980.28 | 24.9178 | 6548.12 | 27.2838 | 5980.25 | 24.9177 | 6548.12 | 27.2838 | 5980.25 | 24.9177 | 6551.04 | 27.296 | 5322.98 | 22.1791 | 6548.1 | 27.2838 | 5318.52 | 22.1605 | 5449.16 | 22.7048 | 5980.25 | 24.9177 | 6548.12 | 27.2838 | 5980.25 | 24.9177 | 6548.12 | 27.2838 | 5980.25 | 24.9177 | 6548.12 | 27.2838 | 5980.25 | 24.9177 | 6548.12 | 27.2838 | 5980.25 | 24.9177 | 6548.12 | 27.2838 | 5318.52 | 22.1605 | 6548.12 | 27.2838 | 5980.25 | 24.9177 | 6548.12 | 27.2838 | 5980.25 | 24.9177 | 6548.12 | 27.2838 | 5980.25 | 24.9177