## Measures
Basic Info | [9 empty] | Level-2 Attributes
Measure Reference Number | Measure Category | Measure Type | Measure Sub Type | Measure Name | Measure Description | Version Number | Active Indicator | Effective Start Date | Effective End Date | Baseline Description | Baseline Value | Baseline Value Unit | Begin Gross Average Annual Demand Reduction_kW | Begin Gross Incremental Annual Electric Savings_kWh | Cost Attribute Notes | Cost Unit | Demand savings calculation method | Efficiency Requirement Description | Efficient Case Unit | Efficient Case Value | Eligibility Requirement Description | End Gross Average Annual Demand Reduction_kW | End Gross Incremental Annual Electric Savings_kWh | Energy Savings calculation method | General Attribute Notes | Gross Incremental Annual Gas Savings_MMBTU | Incremental Cost per Unit | kWReduction | Measure Life | MEEIA Cycle | Non_Energy Benefits _ Other | Non_Energy Benefits _ Other Units | Non_Energy Benefits _ Water | Program Name | Review Date | Savings Attributes Notes | Savings Unit | Total Gross Average Annual Demand Reduction_kW | Total Gross Incremental Annual Electric Savings_kWh | Vintage | WaterSavings
972 | HVAC | Space Cooling | Room AC | AC - Energy Star Room - Thru-Wall_MF: Low Income | Energy Star Room thru-wall AC | 1 | InActive | 2013-01-02 | 2015-12-31 | 9.8 EER AC unit | 9.8 | EER |  |  |  | per measure | Algorithm | Energy Star Room thru-wall AC | EER | 10.8 | Energy Star Room thru-wall AC |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 50 |  | 12 | 2013-15 |  |  |  | Low Income |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.290 | 274.0
972 | HVAC | Space Cooling | Room AC | AC - Energy Star Room - Thru-Wall_MF: Low Income | Energy Star Room thru-wall AC | 2 | InActive | 2016-01-01 | 2016-12-31 | 9.8 EER AC unit | 9.8 | EER |  |  |  | per measure | Algorithm | Energy Star Room thru-wall AC | EER | 10.8 | Energy Star Room thru-wall AC |  |  | Algorithm | HVAC applications can either be applied as an “early replacement” or as a “replace on fail”. A “replace on fail” analysis is relatively simple, when contrasted with an “early replacement” analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 637 |  | 12 | 2016-18 |  |  |  | Low Income |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.259 | 273
972 | HVAC | Space Cooling | Room AC | AC - Energy Star Room - Thru-Wall_MF: Low Income | Energy Star Room thru-wall AC | 3 | Active | 2017-01-01 |  | 9.8 EER AC unit | 9.8 | EER |  |  |  | per measure | Algorithm | Energy Star Room thru-wall AC | EER | 10.8 | Energy Star Room thru-wall AC |  |  | Algorithm | HVAC applications can either be applied as an “early replacement” or as a “replace on fail”. A “replace on fail” analysis is relatively simple, when contrasted with an “early replacement” analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 637 |  | 12 | 2016-18 |  |  |  | Low Income |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.473 | 499.0
973 | HVAC | Space Cooling | Room AC | AC - Energy Star Room - Thru-Wall_SF: Low Income | Energy Star Room thru-wall AC | 1 | InActive | 2013-01-01 | 2015-12-30 | 9.8 EER AC unit | 9.8 | EER |  |  |  | per measure | Algorithm | Energy Star Room thru-wall AC | EER | 10.8 | Energy Star Room thru-wall AC |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 50 |  | 12 | 2013-15 |  |  |  | Low Income |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.094 | 274
973 | HVAC | Space Cooling | Room AC | AC - Energy Star Room - Thru-Wall_SF: Low Income | Energy Star Room thru-wall AC | 2 | Active | 2016-01-01 |  | 9.8 EER AC unit | 9.8 | EER |  |  |  | per measure | Algorithm | Energy Star Room thru-wall AC | EER | 10.8 | Energy Star Room thru-wall AC |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 641 |  | 12 | 2016-18 |  |  |  | Low Income |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.259 | 273
974 | HVAC | Space Cooling | Room AC | AC - Energy Star Room_MF: Low Income | Energy Star Room AC | 1 | InActive | 2013-01-02 | 2015-12-31 | 9.8 EER A/C unit | 9.8 | EER |  |  |  | per measure | Algorithm | Energy Star Room AC | EER | 10.8 | Energy Star Room AC |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 50 |  | 12 | 2013-15 |  |  |  | Low Income |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.290 | 273.0
974 | HVAC | Space Cooling | Room AC | AC - Energy Star Room_MF: Low Income | Energy Star Room AC | 2 | InActive | 2016-01-01 | 2016-12-31 | 9.8 EER A/C unit | 9.8 | EER |  |  |  | per measure | Algorithm | Energy Star Room AC | EER | 10.8 | Energy Star Room AC |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 442 |  | 12 | 2016-18 |  |  |  | Low Income |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.259 | 273
974 | HVAC | Space Cooling | Room AC | AC - Energy Star Room_MF: Low Income | Energy Star Room AC | 3 | Active | 2017-01-01 |  | 9.8 EER A/C unit | 9.8 | EER |  |  |  | per measure | Algorithm | Energy Star Room AC | EER | 10.8 | Energy Star Room AC |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 442 |  | 12 | 2016-18 |  |  |  | Low Income |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.473 | 499.0
975 | HVAC | Space Cooling | Room AC | AC - Energy Star Room_SF: Low Income | Energy Star Room AC | 1 | InActive | 2013-01-01 | 2015-12-30 | 9.8 EER A/C unit | 9.8 | EER |  |  |  | per measure | Algorithm | 10.8 EER Energy Star Room AC | EER | 10.8 | 10.8 EER Energy Star Room AC |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 50 |  | 12 | 2013-15 |  |  |  | Low Income |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.094 | 115.0
975 | HVAC | Space Cooling | Room AC | AC - Energy Star Room_SF: Low Income | Energy Star Room AC | 2 | Active | 2016-01-01 |  | 9.8 EER A/C unit | 9.8 | EER |  |  |  | per measure | Algorithm | 10.8 EER Energy Star Room AC | EER | 10.8 | 10.8 EER Energy Star Room AC |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 445 |  | 12 | 2016-18 |  |  |  | Low Income |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.259 | 273
857 | HVAC | Space Cooling | Room AC | AC - Energy Star Room: Efficient Products | Energy Star Room AC: Efficient Products | 1 | InActive | 2013-01-02 | 2015-12-31 | 9.8 EER Room AC | 9.8 | EER |  |  |  | per measure | Algorithm | 10.8 EER Energy Star Room AC | EER | 10.8 | 10.8 EER Energy Star Room AC |  |  | Algorithm |  |  | 50 |  | 12 | 2013-15 |  |  |  | Efficient Products |  |  | per measure | 0.094 | 115.0
857 | HVAC | Space Cooling | Room AC | AC - Energy Star Room: Efficient Products | Energy Star Room AC: Efficient Products | 2 | Active | 2016-01-01 |  | 9.8 EER Room AC | 9.8 | EER |  |  |  | per measure | Algorithm | 10.8 EER Energy Star Room AC | EER | 10.8 | 10.8 EER Energy Star Room AC |  |  | Algorithm |  |  | 50 |  | 12 | 2016-18 |  |  |  | Efficient Products |  |  | per measure | 0.047 | 49.6
857 | HVAC | Space Cooling | Room AC | AC - Energy Star Room: Efficient Products | Energy Star Room AC: Efficient Products | 3 | InActive |  |  | 9.8 EER Room AC | 9.8 | EER |  |  |  | per measure | Algorithm | 10.8 EER Energy Star Room AC | EER | 10.8 | 10.8 EER Energy Star Room AC |  |  | Algorithm |  |  | 50 |  | 12 | 2016-18 |  |  |  | Efficient Products |  |  | per measure | 0.047 | 50.0
873 | Building Shell | Air Sealing | Air Sealing/Infiltration | Air Sealing (Infiltration reduction) - 30%_SF: Home Energy Performance | Various air sealing measure with infiltration reduction of 30% | 1 | InActive | 2013-01-02 | 2015-12-31 | Varies by vintage | [5 empty] | per home | Algorithm | Reduce Air leakage 30% | [5 empty] | Algorithm |  |  | 264 |  | 13 | 2013-15 |  |  |  | Home Energy Performance |  | Key Assumptions: Tons = 2.2 | per home | 0.070 | 448.0
1042 | Building Shell | Air Sealing | Air Sealing/Infiltration | Air Sealing (Infiltration reduction) - 30%_SF: New Home Construction | Various air sealing measure with infiltration reduction of 30% | 1 | InActive | 2013-01-02 | 2014-12-31 | Varies by vintage | [5 empty] | per home | Algorithm | Reduce Air leakage 30% | [5 empty] | Algorithm |  |  | 264 |  | 13 | 2013-15 |  |  |  | New Home Construction |  | Key Assumptions: Tons = 2.2 | per home | 0.070 | 448.0
1220 | Building Shell | Air Sealing | Air Sealing/Infiltration | Air Sealing (Infiltration reduction) - 50%_MF: Low Income | Various air sealing measure with infiltration reduction of 50% | 1 | Active | 2016-01-01 | [7 empty] | per home | Algorithm | [6 empty] | Algorithm |  |  | 400 |  | 13 | 2016-18 |  |  |  | Low Income |  |  | per home | 0.1864 | 400
874 | Building Shell | Air Sealing | Air Sealing/Infiltration | Air Sealing (Infiltration reduction) - 50%_SF: Efficient Products | Various air sealing measure with infiltration reduction of 50% | 2 | Active | 2016-01-01 |  | Varies by vintage | [5 empty] | per home | Algorithm | Reduce Air leakage 50% | [5 empty] | Algorithm |  |  | 264 |  | 13 | 2016-18 |  |  |  | Efficient Products |  | Key Assumptions, Tons = 2.2 | per home | 0.345 | 739.8
874 | Building Shell | Air Sealing | Air Sealing/Infiltration | Air Sealing (Infiltration reduction) - 50%_SF: Home Energy Performance | Various air sealing measure with infiltration reduction of 50% | 1 | InActive | 2013-01-02 | 2015-12-31 | Varies by vintage | [5 empty] | per home | Algorithm | Reduce Air leakage 50% | [5 empty] | Algorithm |  |  | 264 |  | 13 | 2013-15 |  |  |  | Home Energy Performance |  | Key Assumptions, Tons = 2.2 | per home | 0.120 | 740.0
1207 | Building Shell | Air Sealing | Air Sealing/Infiltration | Air Sealing (Infiltration reduction) - 50%_SF: Low Income | Various air sealing measure with infiltration reduction of 50% | 1 | Active | 2016-01-01 | [7 empty] | per home | Algorithm | [6 empty] | Algorithm |  |  | 500 |  | 10 | 2016-18 |  |  |  | Low Income |  |  | per home | 0.233 | 500
1043 | Building Shell | Air Sealing | Air Sealing/Infiltration | Air Sealing (Infiltration reduction) - 50%_SF: New Home Construction | Various air sealing measure with infiltration reduction of 50% | 1 | InActive | 2013-01-02 | 2014-12-31 | Varies by vintage | [5 empty] | per home | Algorithm | Reduce Air leakage 50% | [5 empty] | Algorithm |  |  | 264 |  | 13 | 2013-15 |  |  |  | New Home Construction |  | Key Assumptions, Tons = 2.2 | per home | 0.120 | 740.0
1007 | Lighting | Interior Lighting | Can Lights/Infiltration | Airtight Can Lights_MF: Low Income | Airtight Can Bulb for Multi Family | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Can Light Bulb | N/A |  |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per measure | Algorithm | Airtight Can Bulb for Multifamily |  | N/A | Airtight Can Bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. The following table summarizes individual measure level energy savings, demand savings, incremental cost, and effective useful life. |  | 150 |  | 15 | 2013-15 |  |  |  | Low Income |  | Assumed 6 can lights per measure | per measure | 0.030 | 85.0
915 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 14 ER Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 14 Electric Resistance Base Unit Early Replacement | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 8 Air Source Heat Pump | 8 | SEER | 1.173 | 14917 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 14 Air Source Heat Pump | SEER | 14 | SEER 14 Air Source Heat Pump | 0.252 | 13426 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1496 |  | 18 | 2013-15 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.173 | 14917.0 | Early Replacement
915 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 14 ER Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 14 Electric Resistance Base Unit Early Replacement | 2 | InActive |  |  | Electric Resistance Furnace SEER 7.2 | 7.2 | SEER | 1.672 | 12905 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 14 Air Source Heat Pump | SEER | 14.14 | SEER 14 Air Source Heat Pump | .129 | 12173 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1496 |  | 18 |  |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.560 | 12905.0 | Early Replacement
916 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 14 ER with ASHP: HVAC | Air Source Heat Pump SEER 14 ASHP Base Unit Early Replacement | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 8 Air Source Heat Pump | 8 | SEER | 1.173 | 4201.5 |  | per measure | Algorithm | SEER 14 Air Source Heat Pump | SEER | 14 | SEER 14 | .252 | 1157 | Algorithm | Existing Unit RUL: 6 years ; New ASHP EUL: 18 years ; REL after RUL: 12 years |  | 1073 |  | 18 | 2013-15 |  |  |  | HVAC |  |  | per measure | 1.173 | 4201.5 | Early Replacement
916 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 14 ER with ASHP: HVAC | Air Source Heat Pump SEER 14 ASHP Base Unit Early Replacement | 2 | InActive |  |  | SEER 7.2 Air Source Heat Pump | 7.2 | SEER | 1.863 | 4530 |  | per measure | Algorithm | SEER 14 Air Source Heat Pump | SEER | 14.14 | SEER 14 | .158 | 1059 | Algorithm | Existing Unit RUL: 6 years ; New ASHP EUL: 18 years ; REL after RUL: 12 years |  | 1073 |  | 18 |  |  |  |  | HVAC |  |  | per measure | 1.560 | 4530.0 | Early Replacement
918 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 14 Replace at Fail with ASHP: HVAC | Air Source Heat Pump SEER 14 ASHP Base Unit Replace on Fail | 1 | InActive | 2013-01-02 | 2015-12-31 | Air Source Heat Pump SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 14 | SEER | 14 | Air Source Heat Pump SEER 14 |  |  | Algorithm |  |  | 411 |  | 18 | 2013-15 |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.300 | 1157.0 | Replace at Fail
918 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 14 Replace at Fail with ASHP: HVAC | Air Source Heat Pump SEER 14 ASHP Base Unit Replace on Fail | 2 | InActive |  |  | Air Source Heat Pump SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 14 | SEER | 14.14 | Air Source Heat Pump SEER 14 |  |  | Algorithm |  |  | 411 |  | 18 |  |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 1.560 | 1059.0 | Replace at Fail
981 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 14_MF: Low Income | Air Source Heat Pump SEER 14 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 14 | SEER | 14 | Air Source Heat Pump SEER 14 |  |  | Algorithm |  |  | 147 |  | 12 | 2013-15 |  |  |  | Low Income |  | Multifamily Tons = 1.5; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.320 | 244.0
919 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 15 ER Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 15 Electric Resistance Base Unit Early Replacement | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 8 Air Source Heat Pump | 8 | SEER | 1.27 | 15398 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 15 Air Source Heat Pump | SEER | 15 | SEER 15 Air Source Heat Pump | 0.349 | 13907 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1607 |  | 18 | 2013-15 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.270 | 15398.0 | Early Replacement
919 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 15 ER Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 15 Electric Resistance Base Unit Early Replacement | 2 | InActive | 2016-01-01 | 2016-12-31 |  |  | SEER |  |  | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm |  | SEER |  |  |  |  | Algorithm |  |  | 1607 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 7.062 | 15151.63 | Early Replacement
919 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 15 ER Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 15 Electric Resistance Base Unit Early Replacement | 3 | Active | 2017-01-27 |  | SEER 8 Air Source Heat Pump | 8 | SEER |  |  | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 15 Air Source Heat Pump | SEER | 15 | SEER 15 Air Source Heat Pump |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 2376 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 6.48 | 13903 | Early Replacement
1048 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 15 ER Elec Resist Furnace: New Home Construction | Air Source Heat Pump SEER 15 Electric Resistance Base Unit Early Replacement | 1 | InActive | 2013-01-02 | 2014-12-31 | SEER 8 Air Source Heat Pump | 8 | SEER | 1.27 | 15398 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 15 Air Source Heat Pump | SEER | 15 | SEER 15 Air Source Heat Pump | 0.349 | 13907 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1607 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.270 | 15398.0 | Early Replacement
920 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 15 ER with ASHP: HVAC | Air Source Heat Pump SEER 15 ASHP Base Unit Early Replacement | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 8 ASHP | 8 | SEER | 1.27 | 4682.6 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 15 ASHP | SEER | 15 | SEER 15 ASHP | 0.349 | 1638.6 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1184 |  | 18 | 2013-15 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.270 | 4682.6 | Early Replacement
920 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 15 ER with ASHP: HVAC | Air Source Heat Pump SEER 15 ASHP Base Unit Early Replacement | 2 | InActive | 2016-01-01 | 2016-12-31 | [5 empty] | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm |  |  |  | SEER 15 ASHP |  |  | Algorithm |  |  | 1184 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 2.322 | 4982.71 | Early Replacement
920 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 15 ER with ASHP: HVAC | Air Source Heat Pump SEER 15 ASHP Base Unit Early Replacement | 3 | Active | 2017-01-01 |  |  |  | SEER |  |  | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 15 ASHP | SEER | 15 | SEER 15 ASHP |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1184 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 2.266 | 4862 | Early Replacement
1049 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 15 ER with ASHP: New Home Construction | Air Source Heat Pump SEER 15 ASHP Base Unit Early Replacement | 1 | InActive | 2013-01-02 | 2014-12-31 | SEER 8 ASHP | 8 | SEER | 1.27 | 4682.6 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 15 ASHP | SEER | 15 | SEER 15 ASHP | 0.349 | 1638.6 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1184 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.270 | 4683.0 | Early Replacement
922 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 15 Replace at Fail with ASHP: HVAC | Air Source Heat Pump SEER 15 ASHP Base Unit Replace on Fail | 1 | InActive | 2013-01-02 | 2015-12-31 | Air Source Heat Pump SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 15 | SEER | 15 | Air Source Heat Pump SEER 15 |  |  | Algorithm |  |  | 522 |  | 18 | 2013-15 |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.300 | 1639.0 | Replace at Fail
922 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 15 Replace at Fail with ASHP: HVAC | Air Source Heat Pump SEER 15 ASHP Base Unit Replace on Fail | 2 | InActive | 2016-01-01 | 2016-12-31 |  |  | SEER |  |  |  | per measure | Algorithm |  | SEER |  | Air Source Heat Pump SEER 15 |  |  | Algorithm |  |  | 522 |  | 18 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.709 | 1520.99 | Replace at Fail
922 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 15 Replace at Fail with ASHP: HVAC | Air Source Heat Pump SEER 15 ASHP Base Unit Replace on Fail | 3 | Active | 2017-01-01 |  | Air Source Heat Pump SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 15 | SEER | 15 | Air Source Heat Pump SEER 15 |  |  | Algorithm |  |  | 111 |  | 18 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.401 | 860 | Replace at Fail
1051 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 15 Replace at Fail with ASHP: New Home Construction | Air Source Heat Pump SEER 15 ASHP Base Unit Replace on Fail | 1 | InActive | 2013-01-02 | 2014-12-31 | Air Source Heat Pump SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 15 | SEER | 15 | Air Source Heat Pump SEER 15 |  |  | Algorithm |  |  | 522 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.300 | 1639.0 | Replace at Fail
1051 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 15 Replace at Fail with ASHP: New Home Construction | Air Source Heat Pump SEER 15 Replace on Fail | 2 | InActive |  |  | SEER 13 Air Source Heat Pump | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 15 | SEER | 15 | Air Source Heat Pump SEER 15 |  |  | Algorithm |  |  | 522 |  | 18 |  |  |  |  | New Home Construction |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.300 | 546.0 | Replace at Fail
982 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 15_MF: Low Income | Air Source Heat Pump SEER 15 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 15 | SEER | 15 | Air Source Heat Pump SEER 15 |  |  | Algorithm |  |  | 294 |  | 12 | 2013-15 |  |  |  | Low Income |  | Multifamily Tons = 1.5; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.410 | 437.0
983 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 16_MF: Low Income | Air Source Heat Pump SEER 16 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 16 | SEER | 16 | Air Source Heat Pump SEER 16 |  |  | Algorithm |  |  | 441 |  | 12 | 2013-15 |  |  |  | Low Income |  | Multifamily Tons = 1.5; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.300 | 316.0
923 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 16+ ER Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 16+ Electric Resistance Base Unit Early Replacement | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 8 Air Source Heat Pump | 8 | SEER | 1.359 | 15841 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 16 Air Source Heat Pump | SEER | 16 | SEER 16 Air Source Heat Pump | 0.439 | 14350 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 2018 |  | 18 | 2013-15 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.359 | 15841.0 | Early Replacement
923 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 16+ ER Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 16+ Electric Resistance Base Unit Early Replacement | 2 | InActive | 2016-01-01 | 2016-12-31 |  |  | SEER |  |  | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm |  | SEER |  |  |  |  | Algorithm |  |  | 2018 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 7.752 | 16633.05 | Early Replacement
923 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 16+ ER Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 16+ Electric Resistance Base Unit Early Replacement | 3 | Active | 2017-01-01 |  |  |  | SEER |  |  | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm |  | SEER |  |  |  |  | Algorithm |  |  | 2018 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 7.666 | 16448 | Early Replacement
1052 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 16+ ER Elec Resist Furnace: New Home Construction | Air Source Heat Pump SEER 16+ Electric Resistance Base Unit Early Replacement | 1 | InActive | 2013-01-02 | 2014-12-31 | SEER 8 Air Source Heat Pump | 8 | SEER | 1.359 | 15841 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 16 Air Source Heat Pump | SEER | 16 | SEER 16 Air Source Heat Pump | 0.439 | 14350 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 2018 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.359 | 15841.0 | Early Replacement
924 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 16+ ER with ASHP: HVAC | Air Source Heat Pump SEER 16+ ASHP Base Unit Early Replacement | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 8 ASHP | 8 | SEER | 1.359 | 5125.8 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 16+ ASHP | SEER | 16 | SEER 16+ ASHP | 0.439 | 2081.8 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1595 |  | 18 | 2013-15 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.359 | 5125.8 | Early Replacement
924 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 16+ ER with ASHP: HVAC | Air Source Heat Pump SEER 16+ ASHP Base Unit Early Replacement | 2 | InActive | 2016-01-01 | 2016-12-31 | [5 empty] | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm |  | SEER |  | SEER 16+ ASHP |  |  | Algorithm |  |  | 1595 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 3.029 | 6499.77 | Early Replacement
924 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 16+ ER with ASHP: HVAC | Air Source Heat Pump SEER 16+ ASHP Base Unit Early Replacement | 3 | Active | 2017-01-01 |  |  |  | SEER |  |  | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm |  | SEER |  | SEER 16+ ASHP |  |  | Algorithm |  |  | 1595 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 3.023 | 6487 | Early Replacement
1053 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 16+ ER with ASHP: New Home Construction | Air Source Heat Pump SEER 16+ ASHP Base Unit Early Replacement | 1 | InActive | 2013-01-02 | 2014-12-31 | SEER 8 ASHP | 8 | SEER | 1.359 | 5125.8 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 16+ ASHP | SEER | 16 | SEER 16+ ASHP | 0.439 | 2081.8 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1595 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.359 | 5126.0 | Early Replacement
926 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 16+ Replace at Fail with ASHP: HVAC | Air Source Heat Pump SEER 16+ ASHP Base Unit Replace on Fail | 1 | InActive | 2013-01-02 | 2015-12-31 | Air Source Heat Pump SEER 13 | 13 | SEER |  |  |  |  | Algorithm | Air Source Heat Pump SEER 16+ | SEER | 16 | Air Source Heat Pump SEER 16+ |  |  | Algorithm |  |  | 933 |  | 18 | 2013-15 |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.400 | 2082.0 | Replace at Fail
926 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 16+ Replace at Fail with ASHP: HVAC | Air Source Heat Pump SEER 16+ ASHP Base Unit Replace on Fail | 2 | InActive | 2016-01-01 | 2016-12-31 |  |  | SEER |  |  |  | per measure | Algorithm |  | SEER |  | Air Source Heat Pump SEER 16+ |  |  | Algorithm |  |  | 522 |  | 18 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.86 | 1844.65 | Replace at Fail
926 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 16+ Replace at Fail with ASHP: HVAC | Air Source Heat Pump SEER 16+ ASHP Base Unit Replace on Fail | 3 | Active | 2017-01-01 |  |  |  | SEER |  |  |  | per measure | Algorithm |  | SEER |  | Air Source Heat Pump SEER 16+ |  |  | Algorithm |  |  | 522 |  | 18 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.825 | 1770 | Replace at Fail
1055 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 16+ Replace at Fail with ASHP: New Home Construction | Air Source Heat Pump SEER 16+ ASHP Base Unit Replace on Fail | 1 | InActive | 2013-01-02 | 2014-12-31 | Air Source Heat Pump SEER 13 | 13 | SEER |  |  |  |  | Algorithm | Air Source Heat Pump SEER 16+ | SEER | 16 | Air Source Heat Pump SEER 16+ |  |  | Algorithm |  |  | 933 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.400 | 2082.0 | Replace at Fail
984 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 17_MF: Low Income | Air Source Heat Pump SEER 17 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 17 | SEER | 17 | Air Source Heat Pump SEER 17 |  |  | Algorithm |  |  | 588 |  | 12 | 2013-15 |  |  |  | Low Income |  | Multifamily Tons = 1.5; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.340 | 414.0
985 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP - SEER 18_MF: Low Income | Air Source Heat Pump SEER 18 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 18 | SEER | 18 | Air Source Heat Pump SEER 18 |  |  | Algorithm |  |  | 735 |  | 12 | 2013-15 |  |  |  | Low Income |  | Multifamily Tons = 1.5; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.360 | 454.0
1239 | HVAC | Space Cooling | Central Air | ASHP SEER 15 MF ER Replace ASHP: HVAC | ASHP SEER 15 MF | 2 | Active | 2017-01-01 |  | 14 SEER ASHP | [5 empty] | per measure |  | 15 SEER ASHP | [8 empty] | 147 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 1.115 | 2392.5
1266 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP SEER 15 MF ER Replace Elec Resist Furnace: HVAC | ASHP SEER 15 MF ER Replace Elec Resist Furnace: HVAC | 1 | Active | 2017-01-01 | [7 empty] | per measure |  | 15 SEER ASHP | [8 empty] | 803 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 3.366 | 7222.5
1268 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP SEER 15 MF Replace at Fail Elec Resist Furnace: HVAC | ASHP SEER 15 MF Replace at Fail Elec Resist Furnace | 1 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 537 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 3.153 | 6764
1239 | HVAC | Space Cooling | Central Air | ASHP SEER 15 MF: HVAC | ASHP SEER 15 MF | 1 | InActive | 2016-01-01 | 2016-12-31 | 14 SEER ASHP | [5 empty] | per measure |  | 15 SEER ASHP | [8 empty] | 147 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 3.018 | 6475.5
1240 | HVAC | Space Cooling | Central Air | ASHP SEER 16 MF ER Replace ASHP: HVAC | ASHP SEER 16 MF | 2 | Active | 2017-01-01 |  | 14 SEER | [5 empty] | per measure |  | 16+ SEER | [8 empty] | 294 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 1.473 | 3161
1270 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP SEER 16 MF Replace at Fail ASHP: HVAC | ASHP SEER 16 MF Replace at Fail ASHP | 1 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 467 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.44 | 944
1271 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP SEER 16 MF Replace at Fail Elec Resist Furnace: HVAC | ASHP SEER 16 MF Replace at Fail Elec Resist Furnace | 1 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 743 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 3.057 | 6560
1269 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP SEER 16 MF Replace Elec Resist Furnace: HVAC | ASHP SEER 16 MF Replace Elec Resist Furnace | 1 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 1009 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 3.535 | 7584.5
1240 | HVAC | Space Cooling | Central Air | ASHP SEER 16 MF: HVAC | ASHP SEER 16 MF | 1 | InActive | 2016-01-01 | 2016-12-31 | 14 SEER | [5 empty] | per measure |  | 16+ SEER | [8 empty] | 294 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 3.759 | 8065.8
1267 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP SEER15 MF Replace at Fail ASHP: HVAC | ASHP SEER 15 MF Replace at Fail ASHP | 1 | Active | 2017-01-01 |  | 14 SEER | [5 empty] | per measure |  | 15 SEER | [8 empty] | 261 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.343 | 735
917 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP- SEER 14 Replace at Fail Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 14 Electric Resistance Base Unit Replace on Fail | 1 | InActive | 2013-01-02 | 2015-12-31 | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 14 | SEER | 14 | Air Source Heat Pump SEER 14 |  |  | Algorithm |  |  | 963 |  | 18 | 2013-15 |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.300 | 13426.0 | Replace at Fail
917 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP- SEER 14 Replace at Fail Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 14 Electric Resistance Base Unit Replace on Fail | 2 | InActive |  |  | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 14 | SEER | 14.2 | Air Source Heat Pump SEER 14 |  |  | Algorithm |  |  | 963 |  | 18 |  |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 1.560 | 12173.0 | Replace at Fail
921 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP- SEER 15 Replace at Fail Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 15 Electric Resistance Base Unit Replace on Fail | 1 | InActive | 2013-01-02 | 2015-12-31 | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 15 | SEER | 15 | Air Source Heat Pump SEER 15 |  |  | Algorithm |  |  | 1074 |  | 18 | 2013-15 |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.300 | 13907.0 | Replace at Fail
921 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP- SEER 15 Replace at Fail Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 15 Electric Resistance Base Unit Replace on Fail | 2 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per measure | Algorithm | [6 empty] | Algorithm |  |  | 1074 |  | 18 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 6.514 | 13976.54 | Replace at Fail
921 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP- SEER 15 Replace at Fail Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 15 Electric Resistance Base Unit Replace on Fail | 3 | Active | 2017-01-01 |  | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 15 | SEER | 15 | Air Source Heat Pump SEER 15 |  |  | Algorithm |  |  | 1264 |  | 18 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 5.389 | 11562 | Replace at Fail
1050 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP- SEER 15 Replace at Fail Elec Resist Furnace: New Home Construction | Air Source Heat Pump SEER 15 Electric Resistance Base Unit Replace on Fail | 1 | InActive | 2013-01-02 | 2014-12-31 | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Air Source Heat Pump SEER 15 | SEER | 15 | Air Source Heat Pump SEER 15 |  |  | Algorithm |  |  | 1074 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.300 | 13907.0 | Replace at Fail
925 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP- SEER 16+ Replace at Fail Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 16+ Electric Resistance Base Unit Replace on Fail | 1 | InActive | 2013-01-02 | 2015-12-31 | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  |  | Algorithm | Air Source Heat Pump SEER 16+ | SEER | 16 | Air Source Heat Pump SEER 16+ |  |  | Algorithm |  |  | 1485 |  | 18 | 2013-15 |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.400 | 14350.0 | Replace at Fail
925 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP- SEER 16+ Replace at Fail Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 16+ Electric Resistance Base Unit Replace on Fail | 2 | InActive | 2016-01-01 | 2016-12-31 |  |  | SEER |  |  |  | per measure | Algorithm |  | SEER |  | Air Source Heat Pump SEER 16+ |  |  | Algorithm |  |  | 1485 |  | 18 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 7.518 | 16129.4 | Replace at Fail
925 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP- SEER 16+ Replace at Fail Elec Resist Furnace: HVAC | Air Source Heat Pump SEER 16+ Electric Resistance Base Unit Replace on Fail | 3 | Active | 2017-01-01 |  |  |  | SEER |  |  |  | per measure | Algorithm |  | SEER |  | Air Source Heat Pump SEER 16+ |  |  | Algorithm |  |  | 1074 |  | 18 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 6.134 | 13160 | Replace at Fail
1054 | HVAC | Heat Pumps | Heat Pump, Air Source | ASHP- SEER 16+ Replace at Fail Elec Resist Furnace: New Home Construction | Air Source Heat Pump SEER 16+ Electric Resistance Base Unit Replace on Fail | 1 | InActive | 2013-01-02 | 2014-12-31 | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  |  | Algorithm | Air Source Heat Pump SEER 16+ | SEER | 16 | Air Source Heat Pump SEER 16+ |  |  | Algorithm |  |  | 1485 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | Single Family Tons = 3.0; Equivalent Full Load Hours (EFLH) Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.400 | 14350.0 | Replace at Fail
945 | HVAC | Space Cooling | Central Air | CAC - SEER 14 ER: HVAC | Central Air Conditioner SEER 14 Early Replacement | 1 | InActive | 2013-01-01 | 2015-12-30 | Central Air Conditioner (CAC) SEER 8 | 8 | SEER | 1.173 | 1899.6 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 14 Central Air Conditioner | SEER | 14 | Central Air Conditioner (CAC) SEER 14 | 0.252 | 408.5 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 890 |  | 18 | 2013-15 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.173 | 1899.6 | Early Replacement
945 | HVAC | Space Cooling | Central Air | CAC - SEER 14 ER: HVAC | Central Air Conditioner SEER 14 Early Replacement | 2 | InActive | 2016-01-01 | 2016-12-31 | Central Air Conditioner (CAC) SEER 8 | 7.2 | SEER |  |  | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 14 Central Air Conditioner | SEER | 14 | Central Air Conditioner (CAC) SEER 14 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 890 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.555 | 1641.6 | Early Replacement
945 | HVAC | Space Cooling | Central Air | CAC - SEER 14 ER: HVAC | Central Air Conditioner SEER 14 Early Replacement | 3 | Active | 2017-01-01 |  | Central Air Conditioner (CAC) SEER 8 | 7.2 | SEER |  |  | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 14 Central Air Conditioner | SEER | 14 | Central Air Conditioner (CAC) SEER 14 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 890 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.55 | 1636 | Early Replacement
944 | HVAC | Space Cooling | Central Air | CAC - SEER 14 Replace at Fail: HVAC | Central Air Conditioner SEER 14 Replace at Fail | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 13 Central Air Conditioner | 13 | SEER |  |  |  | per measure | Algorithm | SEER 14 Central Air Conditioner | SEER | 14 | SEER 14 Central Air Conditioner |  |  | Algorithm |  |  | 357 |  | 18 | 2013-15 |  |  |  | HVAC |  | Single Family Tons = 3.0; EFLH Cooling = 1215; EFLH Heating = 2009 | per measure | 0.250 | 409.0 | Replace at Fail
944 | HVAC | Space Cooling | Central Air | CAC - SEER 14 Replace at Fail: HVAC | Central Air Conditioner SEER 14 Replace at Fail | 2 | InActive | 2016-01-01 | 2016-12-31 | SEER 13 Central Air Conditioner | 13 | SEER |  |  |  | per measure | Algorithm | SEER 14 Central Air Conditioner | SEER | 14 | SEER 14 Central Air Conditioner |  |  | Algorithm |  |  | 357 |  | 18 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 3.0; EFLH Cooling = 1215; EFLH Heating = 2009 | per measure | 0.31 | 327.61 | Replace at Fail
944 | HVAC | Space Cooling | Central Air | CAC - SEER 14 Replace at Fail: HVAC | Central Air Conditioner SEER 14 Replace at Fail | 3 | Active | 2017-01-01 |  | SEER 13 Central Air Conditioner | 13 | SEER |  |  |  | per measure | Algorithm | SEER 14 Central Air Conditioner | SEER | 14 | SEER 14 Central Air Conditioner |  |  | Algorithm |  |  | 357 |  | 18 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 3.0; EFLH Cooling = 1215; EFLH Heating = 2009 | per measure | 0.306 | 323 | Replace at Fail
1069 | HVAC | Space Cooling | Central Air | CAC - SEER 14 Replace at Fail: New Home Construction | Central Air Conditioner SEER 14 | 1 | InActive | 2013-01-02 | 2014-12-31 | SEER 13 Central Air Conditioner | 13 | SEER |  |  |  | per measure | Algorithm | SEER 14 Central Air Conditioner | SEER | 14 | SEER 14 Central Air Conditioner |  |  | Algorithm |  |  | 357 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | Single Family Tons = 3.0; EFLH Cooling = 1215; EFLH Heating = 2009 | per measure | 0.250 | 409.0 | Replace at Fail
1069 | HVAC | Space Cooling | Central Air | CAC - SEER 14 Replace at Fail: New Home Construction | Central Air Conditioner SEER 14 | 2 | InActive |  |  | SEER 13 Central Air Conditioner | 13 | SEER |  |  |  | per measure | Algorithm | SEER 14 Central Air Conditioner | SEER | 14 | SEER 14 Central Air Conditioner |  |  | Algorithm |  |  | 357 |  | 18 |  |  |  |  | New Home Construction |  | Single Family Tons = 3.0; EFLH Cooling = 1215; EFLH Heating = 2009 | per measure | 0.250 | 193.0 | Replace at Fail
1001 | HVAC | Space Cooling | Central Air | CAC - SEER 14_MF: Low Income | Central Air Conditioner SEER 14 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Central Air Conditioner SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Central Air Conditioner SEER 14 | SEER | 14 | Central Air Conditioner SEER 14 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 139 |  | 12 | 2013-15 |  |  |  | Low Income |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. Multifamily Tons = 1.5; EFLH Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.260 | 294.0
1070 | HVAC | Space Cooling | Central Air | CAC - SEER 14: New Home Construction | Central Air Conditioner (CAC) SEER 14 | 1 | InActive | 2013-01-02 | 2014-12-31 | Central Air Conditioner (CAC) SEER 8 | 8 | SEER | 1.173 | 1899.6 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 14 Central Air Conditioner | SEER | 14 | Central Air Conditioner (CAC) SEER 14 | 0.252 | 408.5 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 890 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.173 | 1900.0 | Early Replacement
947 | HVAC | Space Cooling | Central Air | CAC - SEER 15 ER: HVAC | Central Air Conditioner SEER 15 Early Replacement | 2 | InActive | 2016-01-01 | 2016-12-31 | Central Air Conditioner (CAC) SEER 8 | 7.2 | SEER |  |  | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 15 Central Air Conditioner | SEER | 15 | Central Air Conditioner (CAC) SEER 15 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1247 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.824 | 1925.35 | Early Replacement
947 | HVAC | Space Cooling | Central Air | CAC - SEER 15 ER: HVAC | Central Air Conditioner SEER 15 Early Replacement | 3 | Active | 2017-01-01 |  | Central Air Conditioner (CAC) SEER 8 | 7.2 | SEER |  |  | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 15 Central Air Conditioner | SEER | 15 | Central Air Conditioner (CAC) SEER 15 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1247 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.826 | 1927 | Early Replacement
946 | HVAC | Space Cooling | Central Air | CAC - SEER 15 Replace at Fail: HVAC | Central Air Conditioner SEER 15 Replace at Fail | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 13 Central Air Conditioner | 13 | SEER |  |  |  | per measure | Algorithm | SEER 15 Central Air Conditioner | SEER | 15 | SEER 15 Central Air Conditioner |  |  | Algorithm |  |  | 714 |  | 18 | 2013-15 |  |  |  | HVAC |  | Single Family Tons = 3.0; EFLH Cooling = 1215; EFLH Heating = 2009 | per measure | 0.350 | 566.0 | Replace at Fail
946 | HVAC | Space Cooling | Central Air | CAC - SEER 15 Replace at Fail: HVAC | Central Air Conditioner SEER 15 Replace at Fail | 2 | InActive | 2016-01-01 | 2016-12-31 | SEER 13 Central Air Conditioner | 13 | SEER |  |  |  | per measure | Algorithm | SEER 15 Central Air Conditioner | SEER | 15 | SEER 15 Central Air Conditioner |  |  | Algorithm |  |  | 714 |  | 18 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 3.0; EFLH Cooling = 1215; EFLH Heating = 2009 | per measure | 0.364 | 383.75 | Replace at Fail
946 | HVAC | Space Cooling | Central Air | CAC - SEER 15 Replace at Fail: HVAC | Central Air Conditioner SEER 15 Replace at Fail | 3 | Active | 2017-01-01 |  | SEER 13 Central Air Conditioner | 13 | SEER |  |  |  | per measure | Algorithm | SEER 15 Central Air Conditioner | SEER | 15 | SEER 15 Central Air Conditioner |  |  | Algorithm |  |  | 714 |  | 18 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 3.0; EFLH Cooling = 1215; EFLH Heating = 2009 | per measure | 0.357 | 377 | Replace at Fail
1071 | HVAC | Space Cooling | Central Air | CAC - SEER 15 Replace at Fail: New Home Construction | Central Air Conditioner SEER 15 | 1 | InActive | 2013-01-02 | 2014-12-31 | SEER 13 Central Air Conditioner | 13 | SEER |  |  |  | per measure | Algorithm | SEER 15 Central Air Conditioner | SEER | 15 | SEER 15 Central Air Conditioner |  |  | Algorithm |  |  | 714 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | Single Family Tons = 3.0; EFLH Cooling = 1215; EFLH Heating = 2009 | per measure | 0.350 | 566.0 | Replace at Fail
1071 | HVAC | Space Cooling | Central Air | CAC - SEER 15 Replace at Fail: New Home Construction | Central Air Conditioner SEER 15 | 2 | InActive |  |  | SEER 13 Central Air Conditioner | 13 | SEER |  |  |  | per measure | Algorithm | SEER 15 Central Air Conditioner | SEER | 15 | SEER 15 Central Air Conditioner |  |  | Algorithm |  |  | 714 |  | 18 |  |  |  |  | New Home Construction |  | Single Family Tons = 3.0; EFLH Cooling = 1215; EFLH Heating = 2009 | per measure | 0.350 | 267.0 | Replace at Fail
1002 | HVAC | Space Cooling | Central Air | CAC - SEER 15_MF: Low Income | Central Air Conditioner SEER 15 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Central Air Conditioner SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Central Air Conditioner SEER 15 | SEER | 15 | Central Air Conditioner SEER 15 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 278 |  | 12 | 2013-15 |  |  |  | Low Income |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. Multifamily Tons = 1.5; EFLH Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.280 | 310.0
947 | HVAC | Space Cooling | Central Air | CAC - SEER 15: HVAC | Central Air Conditioner SEER 15 Early Replacement | 1 | InActive | 2013-01-02 | 2015-12-31 | Central Air Conditioner (CAC) SEER 8 | 8 | SEER | 1.27 | 2057.3 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 15 Central Air Conditioner | SEER | 15 | Central Air Conditioner (CAC) SEER 15 | 0.349 | 566.1 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1247 |  | 18 | 2013-15 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.270 | 2057.3 | Early Replacement
1072 | HVAC | Space Cooling | Central Air | CAC - SEER 15: New Home Construction | Central Air Conditioner (CAC) SEER 15 | 1 | InActive | 2013-01-02 | 2014-12-31 | Central Air Conditioner (CAC) SEER 8 | 8 | SEER | 1.27 | 2057.3 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 15 Central Air Conditioner | SEER | 15 | Central Air Conditioner (CAC) SEER 15 | 0.349 | 566.1 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1247 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.270 | 2057.0 | Early Replacement
1003 | HVAC | Space Cooling | Central Air | CAC - SEER 16_MF: Low Income | Central Air Conditioner SEER 16 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Central Air Conditioner SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Central Air Conditioner SEER 16 | SEER | 16 | Central Air Conditioner SEER 16 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 417 |  | 12 | 2013-15 |  |  |  | Low Income |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. Multifamily Tons = 1.5; EFLH Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.180 | 268.0
949 | HVAC | Space Cooling | Central Air | CAC - SEER 16+ ER: HVAC | Central Air Conditioner SEER 16+ Early Replacement | 2 | InActive | 2016-01-01 | 2016-12-31 | Central Air Conditioner (CAC) SEER 8 | 7.2 | SEER |  |  | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 16 Central Air Conditioner | SEER | 16 | Central Air Conditioner (CAC) SEER 16+ |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1304 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.823 | 1924.55 | Early Replacement
949 | HVAC | Space Cooling | Central Air | CAC - SEER 16+ ER: HVAC | Central Air Conditioner SEER 16+ Early Replacement | 3 | Active | 2017-01-01 |  | Central Air Conditioner (CAC) SEER 8 | 7.2 | SEER |  |  | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 16 Central Air Conditioner | SEER | 16 | Central Air Conditioner (CAC) SEER 16+ |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1304 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.828 | 1929 | Early Replacement
948 | HVAC | Space Cooling | Central Air | CAC - SEER 16+ Replace at Fail: HVAC | Central Air Conditioner SEER 16+ Replace at Fail | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 13 Central Air Conditioner | 13 | SEER |  |  |  | per measure | Algorithm | SEER 16 Central Air Conditioner | SEER | 16 | SEER 16 Central Air Conditioner |  |  | Algorithm |  |  | 771 |  | 18 | 2013-15 |  |  |  | HVAC |  | Single Family Tons = 3.0; EFLH Cooling = 1215; EFLH Heating = 2009 | per measure | 0.440 | 710.0 | Replace at Fail
948 | HVAC | Space Cooling | Central Air | CAC - SEER 16+ Replace at Fail: HVAC | Central Air Conditioner SEER 16+ Replace at Fail | 2 | InActive | 2016-01-01 | 2016-12-31 | SEER 13 Central Air Conditioner | 13 | SEER |  |  |  | per measure | Algorithm | SEER 16 Central Air Conditioner | SEER | 16 | SEER 16 Central Air Conditioner |  |  | Algorithm |  |  | 771 |  | 18 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 3.0; EFLH Cooling = 1215; EFLH Heating = 2009 | per measure | 0.363 | 383.4 | Replace at Fail
948 | HVAC | Space Cooling | Central Air | CAC - SEER 16+ Replace at Fail: HVAC | Central Air Conditioner SEER 16+ Replace at Fail | 3 | Active | 2017-01-01 |  | SEER 13 Central Air Conditioner | 13 | SEER |  |  |  | per measure | Algorithm | SEER 16 Central Air Conditioner | SEER | 16 | SEER 16 Central Air Conditioner |  |  | Algorithm |  |  | 771 |  | 18 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 3.0; EFLH Cooling = 1215; EFLH Heating = 2009 | per measure | 0.333 | 351 | Replace at Fail
1073 | HVAC | Space Cooling | Central Air | CAC - SEER 16+ Replace at Fail: New Home Construction | Central Air Conditioner SEER 16+ | 1 | InActive | 2013-01-02 | 2014-12-31 | SEER 13 Central Air Conditioner | 13 | SEER |  |  |  | per measure | Algorithm | SEER 16 Central Air Conditioner | SEER | 16 | SEER 16 Central Air Conditioner |  |  | Algorithm |  |  | 771 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | Single Family Tons = 3.0; EFLH Cooling = 1215; EFLH Heating = 2009 | per measure | 0.440 | 710.0 | Replace at Fail
1073 | HVAC | Space Cooling | Central Air | CAC - SEER 16+ Replace at Fail: New Home Construction | Central Air Conditioner SEER 16+ | 2 | InActive |  |  | SEER 13 Central Air Conditioner | 13 | SEER |  |  |  | per measure | Algorithm | SEER 16 Central Air Conditioner | SEER | 16 | SEER 16 Central Air Conditioner |  |  | Algorithm |  |  | 714 |  | 18 |  |  |  |  | New Home Construction |  | Single Family Tons = 3.0; EFLH Cooling = 1215; EFLH Heating = 2009 | per measure | 0.440 | 335.0 | Replace at Fail
949 | HVAC | Space Cooling | Central Air | CAC - SEER 16+: HVAC | Central Air Conditioner SEER 16+ Early Replacement | 1 | InActive | 2013-01-02 | 2015-12-31 | Central Air Conditioner (CAC) SEER 8 | 8 | SEER | 1.359 | 2201.5 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 16 Central Air Conditioner | SEER | 16 | Central Air Conditioner (CAC) SEER 16+ | 0.439 | 710.4 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1304 |  | 18 | 2013-15 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.359 | 2201.5 | Early Replacement
1074 | HVAC | Space Cooling | Central Air | CAC - SEER 16+: New Home Construction | Central Air Conditioner (CAC) SEER 16+ | 1 | InActive | 2013-01-02 | 2014-12-31 | Central Air Conditioner (CAC) SEER 8 | 8 | SEER | 1.359 | 2201.5 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | SEER 16 Central Air Conditioner | SEER | 16 | Central Air Conditioner (CAC) SEER 16+ | 0.439 | 710.4 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 1304 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.359 | 2202.0 | Early Replacement
1004 | HVAC | Space Cooling | Central Air | CAC - SEER 17_MF: Low Income | Central Air Conditioner SEER 17 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Central Air Conditioner SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Central Air Conditioner SEER 17 | SEER | 17 | Central Air Conditioner SEER 17 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 556 |  | 12 | 2013-15 |  |  |  | Low Income |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. Multifamily Tons = 1.5; EFLH Cooling = 1215 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet); • EFLH Heating = 2009 (Used by Proctor Engineering Group in their calculations - Sourced from DOE, EPA, Energy Star Calculation Sheet) | per measure | 0.320 | 401.0
875 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R11-R30: Home Energy Performance | Residential Ceiling Insulation, R11-R30 | 1 | InActive | 2013-01-02 | 2015-12-31 | R-11 level of existing insulation | 11 | R-value |  |  | Cost value is the electric incremental cost. Full incremental cost is $420. Missouri insulation contractors participating in Ameren Missouri's natural gas incentive program. This measure is intended to be included within Ameren Missouri's Home Energy Performance program. Since this program seeks to glean both electric and natural gas savings from Ameren Missouri customers receiving both fuel services from the Company, the incremental costs are parsed on a source BTU basis between natural gas and electric fuels. This is done by multiplying annual CCF savings by 100,000 and electric annual kWh savings by 10,000. As an example, ceiling insulation with a baseline of R-5 and an efficient of R-30 saves 433.9 kWh and 227.6 therms. Multiply therm savings by 1.024 to convert to CCF, 227.5*1.024 = 233. This yields 4,339,268 source BTU electric and 23,303,097 source BTU gas, or 15.7% electric and 84.3% gas. Multiplying the full incremental cost of $475 * 15.7% = $75. Incremental cost is assuming 950 square feet times the appropriate R-value differential in "Insulation Cost Table". These cost estimates were gathered from Missouri based insulation contractors. | per home | Algorithm | Adding insulation to a R-30 level | R-value | 30 | Minimum R-30 or above |  |  | Algorithm |  |  | 66 |  | 25 | 2013-15 |  |  |  | Home Energy Performance |  | In order to appropriately parse costs and savings, the following natural gas savings equations can be utilized. Savings = [(1/R_old - 1/R_attic) x A_attic x (1-Framing_factor/2) x 24 x HDD] / (100,067 x nHeat) nHeat = Efficiency of heating system. Use actual, if unknown assume 70%. See savings parameters for variable inputs. The savings values represented below were developed using building simulations. See Building Simulation Protocols section for further details. | per home | 0.100 | 150.0
876 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R11-R38: Home Energy Performance | Residential Ceiling Insulation, R11-R38 | 1 | InActive | 2013-01-02 | 2015-12-31 | R-11 level of existing insulation | 11 | R-value |  |  | Cost value is the electric incremental cost. Full incremental cost is $495. Missouri insulation contractors participating in Ameren Missouri's natural gas incentive program. This measure is intended to be included within Ameren Missouri's Home Energy Performance program. Since this program seeks to glean both electric and natural gas savings from Ameren Missouri customers receiving both fuel services from the Company, the incremental costs are parsed on a source BTU basis between natural gas and electric fuels. This is done by multiplying annual CCF savings by 100,000 and electric annual kWh savings by 10,000. As an example, ceiling insulation with a baseline of R-5 and an efficient of R-30 saves 433.9 kWh and 227.6 therms. Multiply therm savings by 1.024 to convert to CCF, 227.5*1.024 = 233. This yields 4,339,268 source BTU electric and 23,303,097 source BTU gas, or 15.7% electric and 84.3% gas. Multiplying the full incremental cost of $475 * 15.7% = $75. Incremental cost is assuming 950 square feet times the appropriate R-value differential in "Insulation Cost Table". These cost estimates were gathered from Missouri based insulation contractors. | per home | Algorithm | Adding insulation to a R-38 level | R-value | 38 | Minimum R-38 or above |  |  | Algorithm |  |  | 78 |  | 25 | 2013-15 |  |  |  | Home Energy Performance |  | In order to appropriately parse costs and savings, the following natural gas savings equations can be utilized. Savings = [(1/R_old - 1/R_attic) x A_attic x (1-Framing_factor/2) x 24 x HDD] / (100,067 x nHeat) nHeat = Efficiency of heating system. Use actual, if unknown assume 70%. See savings parameters for variable inputs. The savings values represented below were developed using building simulations. See Building Simulation Protocols section for further details. | per home | 0.100 | 168.0
1044 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R11-R38: New Home Construction | Residential Ceiling Insulation, R11-R38 | 1 | InActive | 2013-01-02 | 2014-12-31 | R-11 level of existing insulation | 11 | R-value |  |  |  | per home | Algorithm | Adding insulation to a R-38 level | R-value | 38 | Minimum R-30 or above |  |  | Algorithm |  |  | 495 |  | 25 | 2013-15 |  |  |  | New Home Construction |  | In order to appropriately parse costs and savings, the following natural gas savings equations can be utilized. Savings = [(1/R_old - 1/R_attic) x A_attic x (1-Framing_factor/2) x 24 x HDD] / (100,067 x nHeat) nHeat = Efficiency of heating system. Use actual, if unknown assume 70%. See savings parameters for variable inputs. The savings values represented below were developed using building simulations. See Building Simulation Protocols section for further details. | per home | 0.100 | 168.0
877 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R11-R49: Home Energy Performance | Residential Ceiling Insulation, R11-R49 | 1 | InActive | 2013-01-02 | 2015-12-31 | R-11 level of existing insulation | 11 | R-value |  |  | Cost value is the electric incremental cost. Full incremental cost is $420. Missouri insulation contractors participating in Ameren Missouri's natural gas incentive program. This measure is intended to be included within Ameren Missouri's Home Energy Performance program. Since this program seeks to glean both electric and natural gas savings from Ameren Missouri customers receiving both fuel services from the Company, the incremental costs are parsed on a source BTU basis between natural gas and electric fuels. This is done by multiplying annual CCF savings by 100,000 and electric annual kWh savings by 10,000. As an example, ceiling insulation with a baseline of R-5 and an efficient of R-30 saves 433.9 kWh and 227.6 therms. Multiply therm savings by 1.024 to convert to CCF, 227.5*1.024 = 233. This yields 4,339,268 source BTU electric and 23,303,097 source BTU gas, or 15.7% electric and 84.3% gas. Multiplying the full incremental cost of $475 * 15.7% = $75. Incremental cost is assuming 950 square feet times the appropriate R-value differential in "Insulation Cost Table". These cost estimates were gathered from Missouri based insulation contractors. | per home | Algorithm | Adding insulation to a R-49 level | R-value | 49 | Minimum R-49 or above |  |  | Algorithm |  |  | 94 |  | 25 | 2013-15 |  |  |  | Home Energy Performance |  | In order to appropriately parse costs and savings, the following natural gas savings equations can be utilized. Savings = [(1/R_old - 1/R_attic) x A_attic x (1-Framing_factor/2) x 24 x HDD] / (100,067 x nHeat) nHeat = Efficiency of heating system. Use actual, if unknown assume 70%. See savings parameters for variable inputs. The savings values represented below were developed using building simulations. See Building Simulation Protocols section for further details. | per home | 0.100 | 183.6
877 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R11-R49: Home Energy Performance | Residential Ceiling Insulation, R11-R49 | 2 | InActive | 2015-12-31 | 2015-12-31 | R-11 level of existing insulation | 11 | R-value |  |  | Cost value is the electric incremental cost. Full incremental cost is $420. Missouri insulation contractors participating in Ameren Missouri's natural gas incentive program. This measure is intended to be included within Ameren Missouri's Home Energy Performance program. Since this program seeks to glean both electric and natural gas savings from Ameren Missouri customers receiving both fuel services from the Company, the incremental costs are parsed on a source BTU basis between natural gas and electric fuels. This is done by multiplying annual CCF savings by 100,000 and electric annual kWh savings by 10,000. As an example, ceiling insulation with a baseline of R-5 and an efficient of R-30 saves 433.9 kWh and 227.6 therms. Multiply therm savings by 1.024 to convert to CCF, 227.5*1.024 = 233. This yields 4,339,268 source BTU electric and 23,303,097 source BTU gas, or 15.7% electric and 84.3% gas. Multiplying the full incremental cost of $475 * 15.7% = $75. Incremental cost is assuming 950 square feet times the appropriate R-value differential in 'Insulation Cost Table'. These cost estimates were gathered from Missouri based insulation contractors. | per home | Algorithm | Adding insulation to a R-49 level | R-value | 49 | Minimum R-49 or above |  |  | Algorithm |  | 74.7 therms | 94 |  | 25 |  |  |  |  | Home Energy Performance |  |  | per home | 0.100 | 133.0
878 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R19-R30: Home Energy Performance | Residential Ceiling Insulation, R19-R30 | 1 | InActive | 2013-01-02 | 2015-12-31 | R-19 level of existing insulation | 19 | R-value |  |  | Cost value is the electric incremental cost. Full incremental cost is $600. Missouri insulation contractors participating in Ameren Missouri's natural gas incentive program. This measure is intended to be included within Ameren Missouri's Home Energy Performance program. Since this program seeks to glean both electric and natural gas savings from Ameren Missouri customers receiving both fuel services from the Company, the incremental costs are parsed on a source BTU basis between natural gas and electric fuels. This is done by multiplying annual CCF savings by 100,000 and electric annual kWh savings by 10,000. As an example, ceiling insulation with a baseline of R-5 and an efficient of R-30 saves 433.9 kWh and 227.6 therms. Multiply therm savings by 1.024 to convert to CCF, 227.5*1.024 = 233. This yields 4,339,268 source BTU electric and 23,303,097 source BTU gas, or 15.7% electric and 84.3% gas. Multiplying the full incremental cost of $475 * 15.7% = $75. Incremental cost is assuming 950 square feet times the appropriate R-value differential in "Insulation Cost Table". These cost estimates were gathered from Missouri based insulation contractors. | per home | Algorithm | Adding insulation to a R-30 level | R-value | 30 | Minimum R-30 or above |  |  | Algorithm |  |  | 54 |  | 25 | 2013-15 |  |  |  | Home Energy Performance |  | In order to appropriately parse costs and savings, the following natural gas savings equations can be utilized. Savings = [(1/R_old - 1/R_attic) x A_attic x (1-Framing_factor/2) x 24 x HDD] / (100,067 x nHeat) nHeat = Efficiency of heating system. Use actual, if unknown assume 70%. See savings parameters for variable inputs. The savings values represented below were developed using building simulations. See Building Simulation Protocols section for further details. | per home | 0.000 | 50.0
879 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R19-R38: Home Energy Performance | Residential Ceiling Insulation, R19-R38 | 1 | InActive | 2013-01-02 | 2015-12-31 | R-19 level of existing insulation | 19 | R-value |  |  | Cost value is the electric incremental cost. Full incremental cost is $345. Missouri insulation contractors participating in Ameren Missouri's natural gas incentive program. This measure is intended to be included within Ameren Missouri's Home Energy Performance program. Since this program seeks to glean both electric and natural gas savings from Ameren Missouri customers receiving both fuel services from the Company, the incremental costs are parsed on a source BTU basis between natural gas and electric fuels. This is done by multiplying annual CCF savings by 100,000 and electric annual kWh savings by 10,000. As an example, ceiling insulation with a baseline of R-5 and an efficient of R-30 saves 433.9 kWh and 227.6 therms. Multiply therm savings by 1.024 to convert to CCF, 227.5*1.024 = 233. This yields 4,339,268 source BTU electric and 23,303,097 source BTU gas, or 15.7% electric and 84.3% gas. Multiplying the full incremental cost of $475 * 15.7% = $75. Incremental cost is assuming 950 square feet times the appropriate R-value differential in "Insulation Cost Table". These cost estimates were gathered from Missouri based insulation contractors. | per home | Algorithm | Adding insulation to a R-38 level | R-value | 38 | Minimum R-38 or above |  |  | Algorithm |  |  | 66 |  | 25 | 2013-15 |  |  |  | Home Energy Performance |  | In order to appropriately parse costs and savings, the following natural gas savings equations can be utilized. Savings = [(1/R_old - 1/R_attic) x A_attic x (1-Framing_factor/2) x 24 x HDD] / (100,067 x nHeat) nHeat = Efficiency of heating system. Use actual, if unknown assume 70%. See savings parameters for variable inputs. The savings values represented below were developed using building simulations. See Building Simulation Protocols section for further details. | per home | 0.100 | 69.0
880 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R19-R49: Home Energy Performance | Residential Ceiling Insulation, R19-R49 | 1 | InActive | 2013-01-02 | 2015-12-31 | R-19 level of existing insulation | 19 | R-value |  |  | Cost value is the electric incremental cost. Full incremental cost is $525. Missouri insulation contractors participating in Ameren Missouri's natural gas incentive program. This measure is intended to be included within Ameren Missouri's Home Energy Performance program. Since this program seeks to glean both electric and natural gas savings from Ameren Missouri customers receiving both fuel services from the Company, the incremental costs are parsed on a source BTU basis between natural gas and electric fuels. This is done by multiplying annual CCF savings by 100,000 and electric annual kWh savings by 10,000. As an example, ceiling insulation with a baseline of R-5 and an efficient of R-30 saves 433.9 kWh and 227.6 therms. Multiply therm savings by 1.024 to convert to CCF, 227.5*1.024 = 233. This yields 4,339,268 source BTU electric and 23,303,097 source BTU gas, or 15.7% electric and 84.3% gas. Multiplying the full incremental cost of $475 * 15.7% = $75. Incremental cost is assuming 950 square feet times the appropriate R-value differential in "Insulation Cost Table". These cost estimates were gathered from Missouri based insulation contractors. | per home | Algorithm | Adding insulation to a R-49 level | R-value | 49 | Minimum R-49 or above |  |  | Algorithm |  |  | 82 |  | 25 | 2013-15 |  |  |  | Home Energy Performance |  | In order to appropriately parse costs and savings, the following natural gas savings equations can be utilized. Savings = [(1/R_old - 1/R_attic) x A_attic x (1-Framing_factor/2) x 24 x HDD] / (100,067 x nHeat) nHeat = Efficiency of heating system. Use actual, if unknown assume 70%. See savings parameters for variable inputs. The savings values represented below were developed using building simulations. See Building Simulation Protocols section for further details. | per home | 0.100 | 83.9
880 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R19-R49: Home Energy Performance | Residential Ceiling Insulation, R19-R49 | 2 | InActive |  |  | R-19 level of existing insulation | 19 | R-value |  |  | Cost value is the electric incremental cost. Full incremental cost is $525. Missouri insulation contractors participating in Ameren Missouri's natural gas incentive program. This measure is intended to be included within Ameren Missouri's Home Energy Performance program. Since this program seeks to glean both electric and natural gas savings from Ameren Missouri customers receiving both fuel services from the Company, the incremental costs are parsed on a source BTU basis between natural gas and electric fuels. This is done by multiplying annual CCF savings by 100,000 and electric annual kWh savings by 10,000. As an example, ceiling insulation with a baseline of R-5 and an efficient of R-30 saves 433.9 kWh and 227.6 therms. Multiply therm savings by 1.024 to convert to CCF, 227.5*1.024 = 233. This yields 4,339,268 source BTU electric and 23,303,097 source BTU gas, or 15.7% electric and 84.3% gas. Multiplying the full incremental cost of $475 * 15.7% = $75. Incremental cost is assuming 950 square feet times the appropriate R-value differential in "Insulation Cost Table". These cost estimates were gathered from Missouri based insulation contractors. | per home | Algorithm | Adding insulation to a R-49 level | R-value | 49 | Minimum R-49 or above |  |  | Algorithm |  | 57.9 therms | 82 |  | 25 |  |  |  |  | Home Energy Performance |  |  | per home | 0.100 | 123.0
1209 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R5-R30 All Electric_MF: Low Income | Residential Ceiling Insulation, R5-R30 | 1 | Active | 2016-01-01 | [7 empty] | per sq ft | Algorithm | [6 empty] | Algorithm |  |  | 1.37 |  | 25 | 2016-18 |  |  |  | Low Income |  | Assumed 437.5 sq ft for batchtool | per sq ft | 2.0E-4 | 0.46
1208 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R5-R30 All Electric_SF: Low Income | Residential Ceiling Insulation, R5-R30 | 1 | Active | 2016-01-01 | [7 empty] | per sq ft | Algorithm | [9 empty] | 1.47 |  | 10 | 2016-18 |  |  |  | Low Income |  | Assumed 475 sq ft for batchtool | per sq ft | 2.0E-4 | 0.46
1208 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R5-R30 All Electric_SF: Low Income | Residential Ceiling Insulation, R5-R30 | 2 | Proposed | 2017-01-01 | [7 empty] | per sq ft | Algorithm | [9 empty] | 0.74 |  | 25 |  |  |  |  | Low Income |  | Assumed 950 sq ft for batchtool | per sq ft | 2.0E-4 | 0.46
875 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R5-R30 All Electric: Efficient Products | Residential Ceiling Insulation, R5-R30 | 2 | Active | 2016-01-01 |  | R-5 level of existing insulation | 5 | R-value |  |  | Cost value is the electric incremental cost. Full incremental cost is $420. Missouri insulation contractors participating in Ameren Missouri's natural gas incentive program. This measure is intended to be included within Ameren Missouri's Home Energy Performance program. Since this program seeks to glean both electric and natural gas savings from Ameren Missouri customers receiving both fuel services from the Company, the incremental costs are parsed on a source BTU basis between natural gas and electric fuels. This is done by multiplying annual CCF savings by 100,000 and electric annual kWh savings by 10,000. As an example, ceiling insulation with a baseline of R-5 and an efficient of R-30 saves 433.9 kWh and 227.6 therms. Multiply therm savings by 1.024 to convert to CCF, 227.5*1.024 = 233. This yields 4,339,268 source BTU electric and 23,303,097 source BTU gas, or 15.7% electric and 84.3% gas. Multiplying the full incremental cost of $475 * 15.7% = $75. Incremental cost is assuming 950 square feet times the appropriate R-value differential in "Insulation Cost Table". These cost estimates were gathered from Missouri based insulation contractors. | per sq ft | Algorithm | Adding insulation to a R-30 level | R-value | 30 | Minimum R-30 or above |  |  | Algorithm |  |  | .46 |  | 25 | 2016-18 |  |  |  | Efficient Products |  | For batchtool, assumed average attic was 950 sq ft | per sq ft | 2.0E-4 | 0.46
876 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R5-R38 All Electric: Efficient Products | Residential Ceiling Insulation, R5-R38 | 2 | Active | 2016-01-01 |  | R-5 level of existing insulation | 5 | R-value |  |  | Cost value is the electric incremental cost. Full incremental cost is $495. Missouri insulation contractors participating in Ameren Missouri's natural gas incentive program. This measure is intended to be included within Ameren Missouri's Home Energy Performance program. Since this program seeks to glean both electric and natural gas savings from Ameren Missouri customers receiving both fuel services from the Company, the incremental costs are parsed on a source BTU basis between natural gas and electric fuels. This is done by multiplying annual CCF savings by 100,000 and electric annual kWh savings by 10,000. As an example, ceiling insulation with a baseline of R-5 and an efficient of R-30 saves 433.9 kWh and 227.6 therms. Multiply therm savings by 1.024 to convert to CCF, 227.5*1.024 = 233. This yields 4,339,268 source BTU electric and 23,303,097 source BTU gas, or 15.7% electric and 84.3% gas. Multiplying the full incremental cost of $475 * 15.7% = $75. Incremental cost is assuming 950 square feet times the appropriate R-value differential in "Insulation Cost Table". These cost estimates were gathered from Missouri based insulation contractors. | per sq ft | Algorithm | Adding insulation to a R-38 level | R-value | 38 | Minimum R-38 or above |  |  | Algorithm |  |  | 0.58 |  | 25 | 2016-18 |  |  |  | Efficient Products |  | Assumed 950 sq ft in the batchtool | per sq ft | 2.0E-4 | 0.48
881 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R5-R49 All Electric: Efficient Products | Residential Ceiling Insulation, R5-R49 | 2 | Active | 2016-01-01 |  | R-5 level of existing insulation | 5 | R-value |  |  | Cost value is the electric incremental cost. Full incremental cost is $665. Missouri insulation contractors participating in Ameren Missouri's natural gas incentive program. This measure is intended to be included within Ameren Missouri's Home Energy Performance program. Since this program seeks to glean both electric and natural gas savings from Ameren Missouri customers receiving both fuel services from the Company, the incremental costs are parsed on a source BTU basis between natural gas and electric fuels. This is done by multiplying annual CCF savings by 100,000 and electric annual kWh savings by 10,000. As an example, ceiling insulation with a baseline of R-5 and an efficient of R-30 saves 433.9 kWh and 227.6 therms. Multiply therm savings by 1.024 to convert to CCF, 227.5*1.024 = 233. This yields 4,339,268 source BTU electric and 23,303,097 source BTU gas, or 15.7% electric and 84.3% gas. Multiplying the full incremental cost of $475 * 15.7% = $75. Incremental cost is assuming 950 square feet times the appropriate R-value differential in "Insulation Cost Table". These cost estimates were gathered from Missouri based insulation contractors. | per sq ft | Algorithm | Adding insulation to a R-49 level | R-value | 49 | Minimum R-49 or above |  |  | Algorithm |  | 0 | 0.70 |  | 25 | 2016-18 |  |  |  | Efficient Products |  | Assumed 950 sq ft in batchtool | per sq ft | 2.0E-4 | 0.49
1210 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R5-R49 All Electric: Low Income | Residential Ceiling Insulation, R5-R49 | 1 | InActive | 2015-12-31 | [7 empty] | per home | Algorithm | [6 empty] | Algorithm |  |  | 665 |  | 25 |  |  |  |  | Low Income |  |  | per home | .400 | 467.6
881 | Building Shell | Insulation | Ceiling Insulation | Ceiling Insulation R5-R49: Home Energy Performance | Residential Ceiling Insulation, R5-R49 | 1 | InActive | 2013-01-02 | 2015-12-31 | R-5 level of existing insulation | 5 | R-value |  |  | Cost value is the electric incremental cost. Full incremental cost is $665. Missouri insulation contractors participating in Ameren Missouri's natural gas incentive program. This measure is intended to be included within Ameren Missouri's Home Energy Performance program. Since this program seeks to glean both electric and natural gas savings from Ameren Missouri customers receiving both fuel services from the Company, the incremental costs are parsed on a source BTU basis between natural gas and electric fuels. This is done by multiplying annual CCF savings by 100,000 and electric annual kWh savings by 10,000. As an example, ceiling insulation with a baseline of R-5 and an efficient of R-30 saves 433.9 kWh and 227.6 therms. Multiply therm savings by 1.024 to convert to CCF, 227.5*1.024 = 233. This yields 4,339,268 source BTU electric and 23,303,097 source BTU gas, or 15.7% electric and 84.3% gas. Multiplying the full incremental cost of $475 * 15.7% = $75. Incremental cost is assuming 950 square feet times the appropriate R-value differential in "Insulation Cost Table". These cost estimates were gathered from Missouri based insulation contractors. | per home | Algorithm | Adding insulation to a R-49 level | R-value | 49 | Minimum R-49 or above |  |  | Algorithm |  |  | 104 |  | 25 | 2013-15 |  |  |  | Home Energy Performance |  | In order to appropriately parse costs and savings, the following natural gas savings equations can be utilized. Savings = [(1/R_old - 1/R_attic) x A_attic x (1-Framing_factor/2) x 24 x HDD] / (100,067 x nHeat) nHeat = Efficiency of heating system. Use actual, if unknown assume 70%. See savings parameters for variable inputs. The savings values represented below were developed using building simulations. See Building Simulation Protocols section for further details. | per home | 0.400 | 467.6
858 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W (60W incand equiv) POST-EISA: Efficient Products | CFL - 13W POST-EISA | 1 | InActive | 2013-01-02 | 2015-12-31 | EISA Compliant Bulb | 45 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 13 Watt | watts | 13 | 13 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Efficient Products |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per bulb | 0.003 | 31.5
858 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W (60W incand equiv) POST-EISA: Efficient Products | CFL - 13W POST-EISA | 2 | InActive |  |  | EISA Compliant Bulb | 60 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 13 Watt | watts | 13 | 13 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 |  |  |  |  | Efficient Products |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per bulb | 0.003 | 49.0
883 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W (60W incand equiv) POST-EISA: Home Energy Performance | CFL - 13W POST-EISA | 1 | InActive | 2013-01-02 | 2015-12-31 | EISA Compliant Bulb | 45 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 13 Watt | watts | 13 | 13 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Home Energy Performance |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per bulb | 0.003 | 31.5
883 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W (60W incand equiv) POST-EISA: Home Energy Performance | CFL - 13W POST-EISA | 2 | InActive |  |  | EISA Compliant Bulb | 43 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 13 Watt | watts | 13 | 13 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 |  |  |  |  | Home Energy Performance |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per bulb | 0.003 | 27.0
954 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W (60W incand equiv) POST-EISA: Lighting | CFL - 13W POST-EISA | 1 | InActive | 2013-01-02 | 2015-12-31 | EISA Compliant Bulb | 45 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 13 Watt | watts | 13 | 13 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Lighting |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per bulb | 0.003 | 31.5
954 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W (60W incand equiv) POST-EISA: Lighting | CFL - 13W POST-EISA | 2 | InActive |  |  | EISA Compliant Bulb | 59.3 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 13 Watt | watts | 13.3 | 13 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 |  |  |  |  | Lighting |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per bulb | 0.006 | 57.0
1078 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W (60W incand equiv) POST-EISA: New Home Construction | CFL - 13W POST-EISA | 1 | InActive | 2013-01-02 | 2014-12-31 | EISA Compliant Bulb | 45 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 13 Watt | watts | 13 | 13 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | New Home Construction |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per bulb | 0.003 | 32.0
1188 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W (60W incand equiv) PRE-EISA_MF: Low Income | CFL 13W PRE-EISA Multi Family | 1 | InActive | 2013-01-02 | 2013-12-31 | Incandescent Bulb | 59.1 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | algorithm | CFL PRE-EISA 13 Watt | watts | 13.5 | 13 watt CFL bulb |  |  | algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Low Income |  | Assumed same parameter as comparable 13W CFLs for single families | per bulb | 0.008 | 48.4
1189 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W (60W incand equiv) PRE-EISA_SF: Low Income | CFL 13W PRE-EISA Single Family | 1 | InActive | 2013-01-02 | 2013-12-31 | Incandescent Bulb | 58.6 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | algorithm | CFL PRE-EISA 13 Watt | watts | 13 | 13 watt CFL bulb |  |  | algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.008 | 48.4
1186 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W (60W incand equiv) PRE-EISA: Home Energy Performance | CFL 13W PRE-EISA | 1 | InActive | 2013-01-02 | 2013-12-31 | Incandescent Bulb | 58.6 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | algorithm | CFL PRE-EISA 13 Watt | watts | 13 | 13 watt CFL bulb |  |  | algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Home Energy Performance |  |  | per bulb | 0.008 | 48.4
1187 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W (60W incand equiv) PRE-EISA: Lighting | CFL 13W PRE-EISA | 1 | InActive | 2013-01-02 | 2013-12-31 | Incandescent Bulb | 58.6 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | algorithm | CFL PRE-EISA 13 Watt | watts | 13 | 13 watt CFL bulb |  |  | algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Lighting |  |  | per bulb | 0.008 | 48.4
1190 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W (60W incand equiv) PRE-EISA: New Home Construction | CFL 13W PRE-EISA | 1 | InActive | 2013-01-02 | 2013-12-31 | Incandescent Bulb | 58.6 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | algorithm | CFL PRE-EISA 13 Watt | watts | 13 | 13 watt CFL bulb |  |  | algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | New Home Construction |  |  | per bulb | 0.008 | 48.4
1008 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W_MF POST-EISA_MF: Low Income | CFL - 13W POST-EISA MultiFamily | 1 | InActive | 2013-01-02 | 2015-12-31 | EISA Compliant Bulb | 45 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 13 Watt | watts | 13 | 13 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per bulb | 0.003 | 32.0
1008 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W_MF POST-EISA_MF: Low Income | CFL - 13W POST-EISA MultiFamily | 2 | InActive |  |  | EISA Compliant Bulb | 45 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 13 Watt | watts | 13 | 13 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 |  |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per bulb | 0.003 | 32.0
1009 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W_MF POST-EISA_SF: Low Income | CFL - 13W POST-EISA Single Family | 1 | InActive | 2013-01-02 | 2015-12-31 | EISA Compliant Bulb | 45 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 13 Watt | watts | 13 | 13 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per bulb | 0.003 | 32.0
1009 | Lighting | Interior Lighting | CFL, screw base | CFL - 13W_MF POST-EISA_SF: Low Income | CFL - 13W POST-EISA Single Family | 2 | InActive |  |  | EISA Compliant Bulb | 45 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 13 Watt | watts | 13 | 13 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 |  |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per bulb | 0.003 | 32.0
1010 | Lighting | Interior Lighting | CFL, screw base | CFL - 18W (75W incand equiv) POST-EISA_MF: Low Income | CFL - 18W POST-EISA Multi Family | 1 | InActive | 2013-01-02 | 2015-12-31 | EISA Compliant Bulb | 56 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 18 Watt | watts | 18 | 18 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.003 | 37.4
1010 | Lighting | Interior Lighting | CFL, screw base | CFL - 18W (75W incand equiv) POST-EISA_MF: Low Income | CFL - 18W POST-EISA Multi Family | 2 | InActive |  |  | EISA Compliant Bulb | 63 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 18 Watt | watts | 18 | 18 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 |  |  |  |  | Low Income |  |  | per bulb | 0.001 | 37.0
1011 | Lighting | Interior Lighting | CFL, screw base | CFL - 18W (75W incand equiv) POST-EISA_SF: Low Income | CFL - 18W POST-EISA Single Family | 1 | InActive | 2013-01-02 | 2015-12-31 | EISA Compliant Bulb | 56 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 18 Watt | watts | 18 | 18 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.003 | 37.4
1011 | Lighting | Interior Lighting | CFL, screw base | CFL - 18W (75W incand equiv) POST-EISA_SF: Low Income | CFL - 18W POST-EISA Single Family | 2 | InActive |  |  | EISA Compliant Bulb | 63 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 18 Watt | watts | 18 | 18 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 |  |  |  |  | Low Income |  |  | per bulb | 0.001 | 37.0
884 | Lighting | Interior Lighting | CFL, screw base | CFL - 18W (75W incand equiv) POST-EISA: Home Energy Performance | CFL - 18W POST-EISA | 1 | InActive | 2013-01-02 | 2015-12-31 | EISA Compliant Bulb | 56 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 18 Watt | watts | 18 | 18 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Home Energy Performance |  |  | per bulb | 0.003 | 37.4
884 | Lighting | Interior Lighting | CFL, screw base | CFL - 18W (75W incand equiv) POST-EISA: Home Energy Performance | CFL - 18W POST-EISA | 2 | InActive |  |  | EISA Compliant Bulb | 53 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 18 Watt | watts | 18 | 18 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 |  |  |  |  | Home Energy Performance |  |  | per bulb | 0.003 | 31.0
955 | Lighting | Interior Lighting | CFL, screw base | CFL - 18W (75W incand equiv) POST-EISA: Lighting | CFL - 18W POST-EISA | 1 | InActive | 2013-01-02 | 2015-12-31 | EISA Compliant Bulb | 56 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 18 Watt | watts | 18 | 18 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Lighting |  |  | per bulb | 0.003 | 37.4
955 | Lighting | Interior Lighting | CFL, screw base | CFL - 18W (75W incand equiv) POST-EISA: Lighting | CFL - 18W POST-EISA | 2 | InActive |  |  | EISA Compliant Bulb | 53 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 18 Watt | watts | 18.6 | 18 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 |  |  |  |  | Lighting |  |  | per bulb | 0.006 | 60.0
1079 | Lighting | Interior Lighting | CFL, screw base | CFL - 18W (75W incand equiv) POST-EISA: New Home Construction | CFL - 18W POST-EISA | 1 | InActive | 2013-01-02 | 2014-12-31 | EISA Compliant Bulb | 56 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 18 Watt | watts | 18 | 18 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | New Home Construction |  |  | per bulb | 0.003 | 37.0
1012 | Lighting | Interior Lighting | CFL, screw base | CFL - 23W (100W incand equiv) POST-EISA_MF: Low Income | CFL 23W POST-EISA Multi Family | 1 | InActive | 2013-01-02 | 2015-12-31 | EISA Compliant Bulb | 75 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 23 Watt | watts | 23 | 23 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.004 | 51.2
1012 | Lighting | Interior Lighting | CFL, screw base | CFL - 23W (100W incand equiv) POST-EISA_MF: Low Income | CFL 23W POST-EISA Multi Family | 2 | InActive |  |  | EISA Compliant Bulb | 72 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 23 Watt | watts | 23 | 23 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 |  |  |  |  | Low Income |  |  | per bulb | 0.002 | 40.0
1013 | Lighting | Interior Lighting | CFL, screw base | CFL - 23W (100W incand equiv) POST-EISA_SF: Low Income | CFL 23W POST-EISA Single Family | 1 | InActive | 2013-01-02 | 2015-12-31 | EISA Compliant Bulb | 75 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 23 Watt | watts | 23 | 23 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.004 | 51.2
1013 | Lighting | Interior Lighting | CFL, screw base | CFL - 23W (100W incand equiv) POST-EISA_SF: Low Income | CFL 23W POST-EISA Single Family | 2 | InActive |  |  | EISA Compliant Bulb | 72 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 23 Watt | watts | 23 | 23 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 |  |  |  |  | Low Income |  |  | per bulb | 0.002 | 40.3
885 | Lighting | Interior Lighting | CFL, screw base | CFL - 23W (100W incand equiv) POST-EISA: Home Energy Performance | CFL 23W POST-EISA | 1 | InActive | 2013-01-02 | 2015-12-31 | EISA Compliant Bulb | 75 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 23 Watt | watts | 23 | 23 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Home Energy Performance |  |  | per bulb | 0.004 | 51.2
885 | Lighting | Interior Lighting | CFL, screw base | CFL - 23W (100W incand equiv) POST-EISA: Home Energy Performance | CFL 23W POST-EISA | 2 | InActive |  |  | EISA Compliant Bulb | 72 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 23 Watt | watts | 23 | 23 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 |  |  |  |  | Home Energy Performance |  |  | per bulb | 0.004 | 43.0
956 | Lighting | Interior Lighting | CFL, screw base | CFL - 23W (100W incand equiv) POST-EISA: Lighting | CFL 23W POST-EISA | 1 | InActive | 2013-01-02 | 2015-12-31 | EISA Compliant Bulb | 75 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 23 Watt | watts | 23 | 23 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | Lighting |  |  | per bulb | 0.004 | 51.2
956 | Lighting | Interior Lighting | CFL, screw base | CFL - 23W (100W incand equiv) POST-EISA: Lighting | CFL 23W POST-EISA | 2 | InActive |  |  | EISA Compliant Bulb | 72 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 23 Watt | watts | 23.4 | 23 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 |  |  |  |  | Lighting |  |  | per bulb | 0.006 | 60.0
1080 | Lighting | Interior Lighting | CFL, screw base | CFL - 23W (100W incand equiv) POST-EISA: New Home Construction | CFL 23W POST-EISA | 1 | InActive | 2013-01-02 | 2014-12-31 | EISA Compliant Bulb | 75 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL POST-EISA 23 Watt | watts | 23 | 23 watt CFL bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 9 | 2013-15 |  |  |  | New Home Construction |  |  | per bulb | 0.004 | 51.0
1014 | Lighting | Interior Lighting | CFL Fixtures | CFL - Fixtures_MF: Low Income | CFL Fixtures Multi Family | 1 | InActive | 2013-01-02 | 2015-12-31 | N/A | 156 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per fixture | Algorithm | CFL - Fixture | watts | 39 | CFL Fixture |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 25 |  | 20 | 2013-15 |  |  |  | Low Income |  |  | per fixture | 0.014 | 124.0
886 | Lighting | Interior Lighting | CFL Fixtures | CFL - Fixtures: Home Energy Performance | CFL Fixtures | 1 | InActive | 2013-01-02 | 2015-12-31 | N/A | 156 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per fixture | Algorithm | CFL - Fixture | watts | 39 | CFL Fixture |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 25 |  | 20 | 2013-15 |  |  |  | Home Energy Performance |  |  | per fixture | 0.014 | 124.0
957 | Lighting | Interior Lighting | CFL Fixtures | CFL - Fixtures: Lighting | CFL Fixtures | 1 | InActive | 2013-01-02 | 2015-12-31 | N/A | 156 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per fixture | Algorithm | CFL - Fixture | watts | 39 | CFL Fixture |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 25 |  | 20 | 2013-15 |  |  |  | Lighting |  |  | per fixture | 0.014 | 124.3
1081 | Lighting | Interior Lighting | CFL Fixtures | CFL - Fixtures: New Home Construction | CFL Fixtures | 1 | InActive | 2013-01-02 | 2014-12-31 | N/A | 156 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per fixture | Algorithm | CFL - Fixture | watts | 39 | CFL Fixture |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 25 |  | 20 | 2013-15 |  |  |  | New Home Construction |  |  | per fixture | 0.014 | 124.0
887 | Lighting | Interior Lighting | CFL, screw base | CFL - High Wattage Bulbs : Home Energy Performance | CFL - High Wattage Bulbs | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Bulb | 199.6 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL High Wattage | watts | 65 | CFL - High Watt |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 15 |  | 9 | 2013-15 |  |  |  | Home Energy Performance |  |  | per bulb | 0.011 | 113.0
887 | Lighting | Interior Lighting | CFL, screw base | CFL - High Wattage Bulbs : Home Energy Performance | CFL - High Wattage Bulbs | 2 | InActive |  |  | Incandescent Bulb | 199.6 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL High Wattage | watts | 42 | CFL - High Watt |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 15 |  | 9 |  |  |  |  | Home Energy Performance |  |  | per bulb | 0.011 | 140.0
958 | Lighting | Interior Lighting | CFL, screw base | CFL - High Wattage Bulbs : Lighting | CFL - High Wattage Bulbs | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Bulb | 199.6 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL High Wattage | watts | 65 | CFL - High Watt |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 15 |  | 9 | 2013-15 |  |  |  | Lighting |  |  | per bulb | 0.011 | 113.0
958 | Lighting | Interior Lighting | CFL, screw base | CFL - High Wattage Bulbs : Lighting | CFL - High Wattage Bulbs | 2 | InActive | 2016-01-01 |  | Incandescent Bulb | 187.8 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL High Wattage | watts | 47.6 | CFL - High Watt |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 15 |  | 9 |  |  |  |  | Lighting |  |  | per bulb | 0.011 | 173.1
1082 | Lighting | Interior Lighting | CFL, screw base | CFL - High Wattage Bulbs : New Home Construction | CFL - High Wattage Bulbs | 1 | InActive | 2013-01-02 | 2014-12-31 | Incandescent Bulb | 199.6 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL High Wattage | watts | 65 | CFL - High Watt |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 15 |  | 9 | 2013-15 |  |  |  | New Home Construction |  |  | per bulb | 0.011 | 113.0
1015 | Lighting | Interior Lighting | CFL, screw base | CFL - High Wattage Bulbs_MF: Low Income | CFL - High Wattage Bulbs Multi Family | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Bulb | 199.6 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL High Wattage | watts | 65 | CFL - High Watt |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 15 |  | 9 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.011 | 113.0
1016 | Lighting | Interior Lighting | CFL, screw base | CFL - Reflector_MF: Low Income | CFL Reflector Multi Family | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Bulb w/ Reflector | 72.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per measure | Algorithm | CFL - Reflector | watts | 20 | CFL reflector |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 13 |  | 9 | 2013-15 |  |  |  | Low Income |  |  | per measure | 0.004 | 44.0
888 | Lighting | Interior Lighting | CFL, screw base | CFL - Reflector: Home Energy Performance | CFL Reflector | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Bulb w/ Reflector | 72.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per measure | Algorithm | CFL - Reflector | watts | 20 | CFL reflector |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 13 |  | 9 | 2013-15 |  |  |  | Home Energy Performance |  |  | per measure | 0.004 | 44.1
888 | Lighting | Interior Lighting | CFL, screw base | CFL - Reflector: Home Energy Performance | CFL Reflector | 2 | InActive |  |  | Incandescent Bulb w/ Reflector | 63 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per measure | Algorithm | CFL - Reflector | watts | 20 | CFL reflector |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 13 |  | 9 |  |  |  |  | Home Energy Performance |  |  | per measure | 0.004 | 38.0
959 | Lighting | Interior Lighting | CFL, screw base | CFL - Reflector: Lighting | CFL Reflector | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Bulb w/ Reflector | 72.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per measure | Algorithm | CFL - Reflector | watts | 20 | CFL reflector |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 13 |  | 9 | 2013-15 |  |  |  | Lighting |  |  | per measure | 0.004 | 44.1
959 | Lighting | Interior Lighting | CFL, screw base | CFL - Reflector: Lighting | CFL Reflector | 2 | InActive |  |  | Incandescent Bulb w/ Reflector | 60.9 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per measure | Algorithm | CFL - Reflector | watts | 15.8 | CFL reflector |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 13 |  | 9 |  |  |  |  | Lighting |  |  | per measure | 0.006 | 56.0
1083 | Lighting | Interior Lighting | CFL, screw base | CFL - Reflector: New Home Construction | CFL Reflector | 1 | InActive | 2013-01-02 | 2014-12-31 | Incandescent Bulb w/ Reflector | 72.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per measure | Algorithm | CFL - Reflector | watts | 20 | CFL reflector |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 13 |  | 9 | 2013-15 |  |  |  | New Home Construction |  |  | per measure | 0.004 | 44.0
1017 | Lighting | Interior Lighting | CFL, screw base | CFL - Specialty Bulbs_MF: Low Income | CFL - Specialty Bulb Multi Family | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Bulb | 79 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL - Specialty | watts | 26.5 | CFL - Specialty bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 10 |  | 9 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.004 | 44.0
889 | Lighting | Interior Lighting | CFL, screw base | CFL - Specialty Bulbs: Home Energy Performance | CFL - Specialty Bulb | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Bulb | 79 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL - Specialty | watts | 26.5 | CFL - Specialty bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 10 |  | 9 | 2013-15 |  |  |  | Home Energy Performance |  |  | per bulb | 0.004 | 44.1
889 | Lighting | Interior Lighting | CFL, screw base | CFL - Specialty Bulbs: Home Energy Performance | CFL - Specialty Bulb | 2 | InActive |  |  | Incandescent Bulb | 52.7 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL - Specialty | watts | 12.9 | CFL - Specialty bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 10 |  | 9 |  |  |  |  | Home Energy Performance |  |  | per bulb | 0.004 | 35.0
960 | Lighting | Interior Lighting | CFL, screw base | CFL - Specialty Bulbs: Lighting | CFL - Specialty Bulb | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Bulb | 79 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL - Specialty | watts | 26.5 | CFL - Specialty bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 10 |  | 9 | 2013-15 |  |  |  | Lighting |  |  | per bulb | 0.004 | 44.1
960 | Lighting | Interior Lighting | CFL, screw base | CFL - Specialty Bulbs: Lighting | CFL - Specialty Bulb | 2 | InActive |  |  | Incandescent Bulb | 52.6 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL - Specialty | watts | 12.8 | CFL - Specialty bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 10 |  | 9 |  |  |  |  | Lighting |  |  | per bulb | 0.005 | 49.0
1084 | Lighting | Interior Lighting | CFL, screw base | CFL - Specialty Bulbs: New Home Construction | CFL - Specialty Bulb | 1 | InActive | 2013-01-02 | 2014-12-31 | Incandescent Bulb | 79 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | CFL - Specialty | watts | 26.5 | CFL - Specialty bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 10 |  | 9 | 2013-15 |  |  |  | New Home Construction |  |  | per bulb | 0.004 | 44.0
961 | Lighting | Interior Lighting | CFL, screw base | CFL - Torchiere Floor Lamps: Lighting | CFL Torchiere Floor Lamps | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Torchiere | 250.4 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per lamp | Algorithm | CFL - Torchiere Floor Lamps | watts | 55 | CFL - Torchiere Floor Lamps |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 50 |  | 12 | 2013-15 |  |  |  | Lighting |  |  | per lamp | 0.016 | 164.0
1 | Appliances | Dehumidifiers | Recycling | Dehumidifier recycling: Appliance Recycle | Recycling of a dehumidifier unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Old Operating Unit | N/A |  |  |  | The incremental cost for each appliance recycling measure is the actual cost associated with the removal and recycling of the retired unit. | per measure | Algorithm | Assumes complete removal of the base characteristic | [5 empty] | Algorithm | Ameren Missouri considered 3 measures for an Appliance Recycling program. All 3 measures were associated with different residential end uses: refrigeration, freezer, and miscellaneous. These measures are different than other measures in the TRM because the efficient characteristics assume a complete removal of the base characteristic |  | 49 |  | 8 | 2013-15 |  |  |  | Appliance Recycle |  |  | per measure | 0.035 | 139.0
1 | Appliances | Dehumidifiers | Recycling | Dehumidifier recycling: Appliance Recycle | Recycling of a dehumidifier unit | 2 | InActive |  |  | Old Operating Unit | N/A |  |  |  | The incremental cost for each appliance recycling measure is the actual cost associated with the removal and recycling of the retired unit. | per measure | Algorithm | Assumes complete removal of the base characteristic | [5 empty] | Algorithm | Ameren Missouri considered 3 measures for an Appliance Recycling program. All 3 measures were associated with different residential end uses: refrigeration, freezer, and miscellaneous. These measures are different than other measures in the TRM because the efficient characteristics assume a complete removal of the base characteristic |  | 49 |  | 8 |  |  |  |  | Appliance Recycle |  |  | per measure | 0.113 | 964.0
986 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 14_MF: Low Income | Dual Fuel Heat Pump (DFHP) SEER 14 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 14 | SEER | 14 | Dual Fuel Heat Pump (DFHP) SEER 14 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 139 |  | 12 | 2013-15 |  |  |  | Low Income |  | Multifamily Tons = 1.5; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.320 | 302.0
927 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 14_SF: HVAC | Dual Fuel Heat Pump (DFHP) SEER 14 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 14 | SEER | 14 | Dual Fuel Heat Pump (DFHP) SEER 14 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 254 |  | 12 | 2013-15 |  |  |  | HVAC |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.760 | 650.0
927 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 14_SF: HVAC | Dual Fuel Heat Pump (DFHP) SEER 14 Replacing SEER 13 unit | 2 | InActive | 2016-01-01 | 2016-12-31 |  |  | SEER |  |  |  | per measure | Algorithm |  | SEER |  |  |  |  | Algorithm |  |  | 254 |  | 12 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.539 | 1157.43
927 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 14_SF: HVAC | Dual Fuel Heat Pump (DFHP) SEER 14 Replacing SEER 13 unit | 3 | InActive |  |  |  |  | SEER |  |  |  | per measure | Algorithm |  | SEER |  |  |  |  | Algorithm |  |  | 254 |  | 12 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.297 | 637
987 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 15_MF: Low Income | Dual Fuel Heat Pump (DFHP) SEER 15 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 15 | SEER | 15 | Dual Fuel Heat Pump (DFHP) SEER 15 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 278 |  | 12 | 2013-15 |  |  |  | Low Income |  | Multifamily Tons = 1.5; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.410 | 590.0
928 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 15_SF: HVAC | Dual Fuel Heat Pump (DFHP) SEER 15 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 15 | SEER | 15 | Dual Fuel Heat Pump (DFHP) SEER 15 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 508 |  | 12 | 2013-15 |  |  |  | HVAC |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.574 | 1230.5
928 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 15_SF: HVAC | Dual Fuel Heat Pump (DFHP) SEER 15 Replacing SEER 13 unit | 2 | InActive | 2016-01-01 | 2016-12-31 |  |  | SEER |  |  |  | per measure | Algorithm |  | SEER |  |  |  |  | Algorithm |  |  | 508 |  | 12 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.628 | 1348.34
928 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 15_SF: HVAC | Dual Fuel Heat Pump (DFHP) SEER 15 Replacing SEER 13 unit | 3 | Active | 2017-01-01 |  |  |  | SEER |  |  |  | per measure | Algorithm |  | SEER |  |  |  |  | Algorithm |  |  | 508 |  | 12 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.172 | 370
1056 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 15_SF: New Home Construction | Dual Fuel Heat Pump (DFHP) SEER 15 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2014-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 15 | SEER | 15 | Dual Fuel Heat Pump (DFHP) SEER 15 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 508 |  | 12 | 2013-15 |  |  |  | New Home Construction |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.800 | 1230.0
988 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 16_MF: Low Income | Dual Fuel Heat Pump (DFHP) SEER 16 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 16 | SEER | 16 | Dual Fuel Heat Pump (DFHP) SEER 16 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 417 |  | 12 | 2013-15 |  |  |  | Low Income |  | Multifamily Tons = 1.5; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.300 | 492.0
929 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 16_SF: HVAC | Dual Fuel Heat Pump (DFHP) SEER 16 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 16 | SEER | 16 | Dual Fuel Heat Pump (DFHP) SEER 16 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 763 |  | 12 | 2013-15 |  |  |  | HVAC |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.671 | 1439.0
929 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 16_SF: HVAC | Dual Fuel Heat Pump (DFHP) SEER 16 Replacing SEER 13 unit | 2 | InActive | 2016-01-01 | 2016-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 16 | SEER | 16 | Dual Fuel Heat Pump (DFHP) SEER 16 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 763 |  | 12 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.566 | 1213.49
929 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 16_SF: HVAC | Dual Fuel Heat Pump (DFHP) SEER 16 Replacing SEER 13 unit | 3 | Active | 2017-01-01 |  | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 16 | SEER | 16 | Dual Fuel Heat Pump (DFHP) SEER 16 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 763 |  | 12 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.253 | 542
1057 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 16_SF: New Home Construction | Dual Fuel Heat Pump (DFHP) SEER 16 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2014-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 16 | SEER | 16 | Dual Fuel Heat Pump (DFHP) SEER 16 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 763 |  | 12 | 2013-15 |  |  |  | New Home Construction |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.830 | 1439.0
989 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 17_MF: Low Income | Dual Fuel Heat Pump (DFHP) SEER 17 Replacing SEER 13 unit | 1 | InActive | 2013-01-01 | 2015-12-30 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 17 | SEER | 17 | Dual Fuel Heat Pump (DFHP) SEER 17 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 556 |  | 12 | 2013-15 |  |  |  | Low Income |  | Multifamily Tons = 1.5; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.340 | 667.0
930 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 17_SF: HVAC | Dual Fuel Heat Pump (DFHP) SEER 17 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 17 | SEER | 17 | Dual Fuel Heat Pump (DFHP) SEER 17 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 1017 |  | 12 | 2013-15 |  |  |  | HVAC |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.769 | 1651.0
930 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 17_SF: HVAC | Dual Fuel Heat Pump (DFHP) SEER 17 Replacing SEER 13 unit | 2 | InActive | 2016-01-01 | 2016-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 17 | SEER | 17 | Dual Fuel Heat Pump (DFHP) SEER 17 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 1017 |  | 12 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.713 | 1529.89
930 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 17_SF: HVAC | Dual Fuel Heat Pump (DFHP) SEER 17 Replacing SEER 13 unit | 3 | Active | 2017-01-01 |  | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 17 | SEER | 17 | Dual Fuel Heat Pump (DFHP) SEER 17 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 1017 |  | 12 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.483 | 1037
1058 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 17_SF: New Home Construction | Dual Fuel Heat Pump (DFHP) SEER 17 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2014-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 17 | SEER | 17 | Dual Fuel Heat Pump (DFHP) SEER 17 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 1017 |  | 12 | 2013-15 |  |  |  | New Home Construction |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.810 | 1651.0
990 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 18_MF: Low Income | Dual Fuel Heat Pump (DFHP) SEER 18 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 18 | SEER | 18 | Dual Fuel Heat Pump (DFHP) SEER 18 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 734 |  | 12 | 2013-15 |  |  |  | Low Income |  | Multifamily Tons = 1.5; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.360 | 681.0
931 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 18_SF: HVAC | Dual Fuel Heat Pump (DFHP) SEER 18 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 18 | SEER | 18 | Dual Fuel Heat Pump (DFHP) SEER 18 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 1342 |  | 12 | 2013-15 |  |  |  | HVAC |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.763 | 1638.0
931 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 18_SF: HVAC | Dual Fuel Heat Pump (DFHP) SEER 18 Replacing SEER 13 unit | 2 | InActive | 2016-01-01 | 2016-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 18 | SEER | 18 | Dual Fuel Heat Pump (DFHP) SEER 18 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 1342 |  | 12 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.485 | 1040.13
931 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 18_SF: HVAC | Dual Fuel Heat Pump (DFHP) SEER 18 Replacing SEER 13 unit | 3 | Active | 2017-01-01 |  | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 18 | SEER | 18 | Dual Fuel Heat Pump (DFHP) SEER 18 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 1342 |  | 12 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.503 | 1079
1059 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP - SEER 18_SF: New Home Construction | Dual Fuel Heat Pump (DFHP) SEER 18 Replacing SEER 13 unit | 1 | InActive | 2013-01-02 | 2014-12-31 | SEER 13; 78 Annual Fuel Utilization Efficiency ( AFUE) | 13 | SEER |  |  |  | per measure | Algorithm | Dual Fuel Heat Pump (DFHP) SEER 18 | SEER | 18 | Dual Fuel Heat Pump (DFHP) SEER 18 |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". A "replace on fail" analysis is relatively simple, when contrasted with an "early replacement" analysis, as the analysis is a calculation of the energy and demand savings associated with the use of the efficient equipment when compared with the base equipment energy. In addition, the incremental cost for using the efficient equipment is the difference between the cost of the installed efficient equipment versus the installed base equipment. |  | 1342 |  | 12 | 2013-15 |  |  |  | New Home Construction |  | Single Family Tons = 2.7; To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used. | per measure | 0.880 | 1638.0
1242 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP SEER 16_MF: HVAC | DFHP SEER 16_MF | 1 | InActive | 2016-01-01 | 2016-12-31 | 13 SEER | [5 empty] | per measure |  | 16 SEER | [8 empty] | 278 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.335 | 719.4
1242 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP SEER 16_MF: HVAC | DFHP SEER 16_MF | 2 | Active | 2017-01-01 |  | 13 SEER | [5 empty] | per measure |  | 16 SEER | [8 empty] | 382 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.126 | 271
1243 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP SEER 17+_MF: HVAC | DFHP SEER 17+_MF | 1 | InActive | 2016-01-01 | 2016-12-31 | 13 SEER | [5 empty] | per measure |  | 17 SEER | [8 empty] | 417 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.385 | 825.5
1243 | HVAC | Heat Pumps | Heat Pump, Dual Fuel | DFHP SEER 17+_MF: HVAC | DFHP SEER 17+_MF | 2 | Active | 2017-01-01 |  | 13 SEER | [5 empty] | per measure |  | 17 SEER | [8 empty] | 508.5 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.242 | 518.5
1264 | HVAC | HVAC O&M | HVAC Tune Up | Dirty filter alarm_LI: Kits | Dirty filter alarm | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 5 |  | 14 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.051 | 110
1225 | HVAC | HVAC O&M | HVAC Tune Up | Dirty filter alarm_MF: Kits | Dirty filter alarm_MF | 1 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per measure | [10 empty] | 5 |  | 14 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.051 | 110
1225 | HVAC | HVAC O&M | HVAC Tune Up | Dirty filter alarm_MF: Kits | Dirty filter alarm_MF | 2 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 5 |  | 14 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.091 | 195.8
1260 | HVAC | HVAC O&M | HVAC Tune Up | Dirty Filter Alarm_MF: Low Income | Dirty Filter Alarm | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 5 |  | 14 | 2016-18 |  |  |  | Low Income |  |  | per measure | 0.051 | 110
1224 | HVAC | HVAC O&M | HVAC Tune Up | Dirty filter alarm_SF: Kits | Dirty filter alarm_SF | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 5 |  | 14 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.051 | 110
1259 | HVAC | HVAC O&M | HVAC Tune Up | Dirty Filter Alarm_SF: Low Income | Dirty Filter Alarm | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 5 |  | 14 | 2016-18 |  |  |  | Low Income |  |  | per measure | 0.051 | 110
1226 | HVAC | HVAC O&M | HVAC Tune Up | Dirty filter alarm_SK: Kits | Dirty filter alarm | 1 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per measure | [10 empty] | 5 |  | 14 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.051 | 110
1226 | HVAC | HVAC O&M | HVAC Tune Up | Dirty filter alarm_SK: Kits | Dirty filter alarm | 2 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 5 |  | 14 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.091 | 195.8
1226 | HVAC | HVAC O&M | HVAC Tune Up | Dirty filter alarm_SK: Kits | Dirty filter alarm | 3 | Proposed | 2018-01-01 | [7 empty] | per measure | [10 empty] | 5 |  | 14 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.039 | 83.37
976 | HVAC | Ducting | Duct Insulation | Duct Insulation_MF: Low Income | Insulate ducts | 1 | InActive | 2013-01-02 | 2015-12-31 | Ducts not insulated | [5 empty] | per building | Algorithm |  |  |  | Insulate ducts |  |  | Algorithm |  |  | 528 |  | 20 | 2013-15 |  |  |  | Low Income |  | Assume 2,200 square feet | per building | 0.150 | 460.0
977 | HVAC | Ducting | Duct Location | Duct location_MF: Low Income | Recolate ducts to conditioned space | 1 | InActive | 2013-01-02 | 2015-12-31 | Ducts outside conditioned space | [5 empty] | per building | Algorithm |  |  |  | Relocate ducts |  |  | Algorithm |  |  | 1650 |  | 20 | 2013-15 |  |  |  | Low Income |  | Assume 2,200 square feet | per building | 0.430 | 852.0
978 | HVAC | Ducting | Duct Sealing | Duct sealing 20% leakage base_MF: Low Income | Duct sealing to 20% duct leakage improvement | 1 | InActive | 2013-01-02 | 2015-12-31 | Substantial leakage | [5 empty] | per home | Algorithm | 20% duct leakage improvement | percent improvement | 20 | 20% duct leakage improvement |  |  | Algorithm |  |  | 475 |  | 18 | 2013-15 |  |  |  | Low Income |  | Assume 2,200 sq ft house | per measure | 0.080 | 250.0
979 | HVAC | Ducting | Duct Sealing | Duct sealing 25% leakage base_MF: Low Income | Duct sealing to 25% duct leakage improvement | 1 | InActive | 2013-01-02 | 2015-12-31 | Substantial Leakage | [5 empty] | total building | Algorithm | 25% Duct leakage improvement | percent improvement | 25 | 25% Duct leakage improvement |  |  | Algorithm |  |  | 475 |  | 18 | 2013-15 |  |  |  | Low Income |  | Assume 2,200 sq ft house | per measure | 0.100 | 338.0
980 | HVAC | Ducting | Duct Sealing | Duct sealing 30% leakage base_MF: Low Income | Duct sealing to 30% duct leakage improvement | 1 | InActive | 2013-01-02 | 2015-12-31 | Substantial Leakage | [5 empty] | total building | Algorithm | 30% Duct leakage improvement | percent improvement | 30 | 30% Duct leakage improvement |  |  | Algorithm |  |  | 475 |  | 18 | 2013-15 |  |  |  | Low Income |  | Assume 2,200 sq ft house | per measure | 0.130 | 424.0
905 | HVAC | Ducting | Duct Sealing | Duct Sealing Level 1: HVAC | Duct Sealing to 14% Duct leakage improvement | 1 | InActive | 2013-01-02 | 2015-12-31 | Substantial leakage | [5 empty] | per home | Algorithm | 14% duct leakage improvement | percent improvement | 14 |  |  |  | Algorithm |  |  | 325 |  | 20 | 2013-15 |  |  |  | HVAC |  | Assume 2,200 sq ft house | per home | 0.240 | 1352.0
905 | HVAC | Ducting | Duct Sealing | Duct Sealing Level 1: HVAC | Duct Sealing to 14% Duct leakage improvement | 2 | Active | 2016-01-01 |  | Substantial leakage | [5 empty] | per home | Algorithm | 14% duct leakage improvement | percent improvement | 14 |  |  |  | Algorithm |  |  | 325 |  | 20 | 2016-18 |  |  |  | HVAC |  | Assume 2,200 sq ft house | per home | 0.299 | 641.1
1046 | HVAC | Ducting | Duct Sealing | Duct Sealing Level 1: New Home Construction | Duct Sealing to 14% Duct leakage improvement | 1 | InActive | 2013-01-02 | 2014-12-31 | Substantial Leakage | [5 empty] | per home | Algorithm | 14% duct leakage improvement | percent improvement | 14 |  |  |  | Algorithm |  |  | 325 |  | 20 | 2013-15 |  |  |  | New Home Construction |  | Assume 2,200 sq ft house | per home | 0.240 | 1352.0
1046 | HVAC | Ducting | Duct Sealing | Duct Sealing Level 1: New Home Construction | Duct Sealing to 14% Duct leakage improvement | 2 | InActive |  |  | Substantial Leakage | [5 empty] | per home | Algorithm | 14% duct leakage improvement | percent improvement | 14 |  |  |  | Algorithm |  |  | 325 |  | 20 |  |  |  |  | New Home Construction |  | Assume 2,200 sq ft house | per home | 0.240 | 638.0
906 | HVAC | Ducting | Duct Sealing | Duct Sealing Level 2: HVAC | Duct Sealing to 50% Duct leakage improvement | 1 | InActive | 2013-01-02 | 2015-12-31 | Substantial Leakage | [5 empty] | per home | Algorithm | 50% Duct leakage improvement | percent improvement | 50 |  |  |  | Algorithm |  |  | 325 |  | 20 | 2013-15 |  |  |  | HVAC |  | Assume 2,200 sq ft house | per home | 0.420 | 2347.0
906 | HVAC | Ducting | Duct Sealing | Duct Sealing Level 2: HVAC | Duct Sealing to 50% Duct leakage improvement | 2 | Active | 2016-01-01 |  | Standard Leakage | [5 empty] | per home | Algorithm | 50% Duct leakage improvement | percent improvement | 50 |  |  |  | Algorithm |  |  | 325 |  | 20 | 2016-18 |  |  |  | HVAC |  | Assume 2,200 sq ft house | per home | 0.519 | 1113.1
1047 | HVAC | Ducting | Duct Sealing | Duct Sealing Level 2: New Home Construction | Duct Sealing to 50% Duct leakage improvement | 1 | InActive | 2013-01-02 | 2014-12-31 | Substantial Leakage | [5 empty] | per home | Algorithm | 50% Duct leakage improvement | percent improvement | 50 |  |  |  | Algorithm |  |  | 325 |  | 20 | 2013-15 |  |  |  | New Home Construction |  | Assume 2,200 sq ft house | per home | 0.420 | 2347.0
1047 | HVAC | Ducting | Duct Sealing | Duct Sealing Level 2: New Home Construction | Duct Sealing to 50% Duct leakage improvement | 2 | InActive |  |  | Substantial Leakage | [5 empty] | per home | Algorithm | 50% Duct leakage improvement | percent improvement | 50 |  |  |  | Algorithm |  |  | 325 |  | 20 |  |  |  |  | New Home Construction |  | Assume 2,200 sq ft house | per home | 0.420 | 1107.0
1250 | HVAC | Heat Pumps | Heat Pump, Air Source | Ductless ASHP ER: HVAC | Ductless ASHP ER | 1 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per measure | [10 empty] | 1982 |  | 18 | 2016-18 |  |  |  | HVAC |  |  | per measure | 1.718 | 3686
1250 | HVAC | Heat Pumps | Heat Pump, Air Source | Ductless ASHP ER: HVAC | Ductless ASHP ER | 2 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 1982 |  | 18 | 2016-18 |  |  |  | HVAC |  |  | per measure | 2.141 | 4594
1252 | HVAC | Heat Pumps | Heat Pump, Air Source | Ductless ASHP Replace Electric Resistance ER: HVAC | Ductless ASHP Replace Electric Resistance ER | 1 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per measure | [10 empty] | 2108 |  | 18 | 2016-18 |  |  |  | HVAC |  |  | per measure | 2.668 | 5725
1252 | HVAC | Heat Pumps | Heat Pump, Air Source | Ductless ASHP Replace Electric Resistance ER: HVAC | Ductless ASHP Replace Electric Resistance ER | 2 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 2108 |  | 18 | 2016-18 |  |  |  | HVAC |  |  | per measure | 3.479 | 7465
1253 | HVAC | Heat Pumps | Heat Pump, Air Source | Ductless ASHP Replace Electric Resistance ROF: HVAC | Ductless ASHP Replace Electric Resistance ROF | 1 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per measure | [10 empty] | 1051 |  | 18 | 2016-18 |  |  |  | HVAC |  |  | per measure | 2.037 | 4370
1253 | HVAC | Heat Pumps | Heat Pump, Air Source | Ductless ASHP Replace Electric Resistance ROF: HVAC | Ductless ASHP Replace Electric Resistance ROF | 2 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 1051 |  | 18 | 2016-18 |  |  |  | HVAC |  |  | per measure | 3.685 | 7906
1251 | HVAC | Heat Pumps | Heat Pump, Air Source | Ductless ASHP ROF: HVAC | Ductless ASHP ROF | 1 | InActive | 2016-01-01 | 2016-12-31 | Standard leakage | [5 empty] | per measure |  | 14% duct leakage improvement | [8 empty] | 888 |  | 18 | 2016-18 |  |  |  | HVAC |  |  | per measure | 1.031 | 2211
1251 | HVAC | Heat Pumps | Heat Pump, Air Source | Ductless ASHP ROF: HVAC | Ductless ASHP ROF | 2 | Active | 2017-01-01 |  | Standard leakage | [5 empty] | per measure |  | 14% duct leakage improvement | [8 empty] | 888 |  | 18 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.814 | 1746
908 | HVAC | Fans | Auto Fan | ECM Auto Fan Early Replacement: HVAC | ECM Installations Auto Fan Early Replacement for RUL replacement | 2 | InActive | 2016-01-01 | 2016-12-31 | PSC Motor (Permanent Split Capacitor) for 8 SEER AC | [5 empty] | per measure | Algorithm | Intermittent ECM blower |  |  | Intermittent ECM blower |  |  | Algorithm | Existing Unit RUL: 6 years ; New Motor EUL: 18 years ; REL after RUL: 12 years |  | 168 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.302 | 647.51 | Early Replacement
908 | HVAC | Fans | Auto Fan | ECM Auto Fan Early Replacement: HVAC | ECM Installations Auto Fan Early Replacement for RUL replacement | 3 | Active | 2017-01-01 |  | PSC Motor (Permanent Split Capacitor) for 8 SEER AC | [5 empty] | per measure | Algorithm | Intermittent ECM blower |  |  | Intermittent ECM blower |  |  | Algorithm | Existing Unit RUL: 6 years ; New Motor EUL: 18 years ; REL after RUL: 12 years |  | 168 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.37 | 794 | Early Replacement
1257 | HVAC | Fans | Auto Fan | ECM Auto Fan MF: HVAC | ECM Auto Fan MF | 1 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per measure | [10 empty] | 263 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.172 | 368.9
1257 | HVAC | Fans | Auto Fan | ECM Auto Fan MF: HVAC | ECM Auto Fan MF | 2 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 263 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.183 | 392.5
907 | HVAC | Fans | Auto Fan | ECM Auto Fan Replace at Fail: HVAC | ECM Auto Fan Replace at Fail: HVAC | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard motor auto fan | [5 empty] | per measure | Algorithm | Intermittent ECM blower |  |  | Intermittent ECM blower |  |  | Algorithm |  |  | 125 |  | 15 | 2013-15 |  |  |  | HVAC |  | For ECM measures the evaluation team determined ex post demand savings were 0 kW. There are no demand savings for ECM fan measures because the efficiency rating of the HVAC unit includes the efficiency improvement from the ECM fan | per measure | 0.270 | 929.0 | Replace at Fail
907 | HVAC | Fans | Auto Fan | ECM Auto Fan Replace at Fail: HVAC | ECM Auto Fan Replace at Fail: HVAC | 2 | InActive | 2016-01-01 | 2016-12-31 | Standard motor continuous operation | [5 empty] | per measure | Algorithm | Intermittent ECM blower |  |  | Intermittent ECM blower |  |  | Algorithm |  |  | 263 |  | 15 | 2016-18 |  |  |  | HVAC |  | For ECM measures the evaluation team determined ex post demand savings were 0 kW. There are no demand savings for ECM fan measures because the efficiency rating of the HVAC unit includes the efficiency improvement from the ECM fan | per measure | 0.31 | 665.16 | Replace at Fail
907 | HVAC | Fans | Auto Fan | ECM Auto Fan Replace at Fail: HVAC | ECM Auto Fan Replace at Fail: HVAC | 3 | Active | 2017-01-01 |  | Standard motor continuous operation | [5 empty] | per measure | Algorithm | Intermittent ECM blower |  |  | Intermittent ECM blower |  |  | Algorithm |  |  | 263 |  | 15 | 2016-18 |  |  |  | HVAC |  | For ECM measures the evaluation team determined ex post demand savings were 0 kW. There are no demand savings for ECM fan measures because the efficiency rating of the HVAC unit includes the efficiency improvement from the ECM fan | per measure | 0.366 | 785 | Replace at Fail
1028 | HVAC | Fans | Continuous Fan | ECM blower - continuous_MF: Low Income | ECM blower - continuous_MF | 1 | InActive | 2013-01-01 | 2015-12-30 | Electronically Commutated Motor Blower – Continuous | [5 empty] | per measure | Algorithm | Standard motor continuous operation |  |  | Continuous ECM blower |  |  | Algorithm |  |  | 263 |  | 15 | 2013-15 |  |  |  | Low Income |  | Multifamily Tons = 1.5 | per measure | 0.140 | 794.0
1029 | HVAC | Fans | Intermittent Fan | ECM blower - intermittent_MF: Low Income | ECM blower - intermittent_MF | 1 | InActive | 2013-01-01 | 2015-12-30 | Electronically Commutated Motor Blower – Intermittent | [5 empty] | per measure | Algorithm | Standard motor continuous operation |  |  | Intermittent ECM blower |  |  | Algorithm |  |  | 263 |  | 15 | 2013-15 |  |  |  | Low Income |  | Multifamily Tons = 1.5 | per measure | 0.110 | 190.0
911 | HVAC | Fans | Continuous Fan | ECM Continuous Fan Early Replacement: HVAC | ECM Installations Continuous Fan Early Replacement for RUL replacement | 2 | InActive | 2016-01-01 | 2016-12-31 | PSC Motor (Permanent Split Capacitor) for 8 SEER AC |  |  | 0 | 3488 |  | per measure | Algorithm | Continuous ECM blower |  |  | Continuous ECM blower | 0 | 3488 | Algorithm | Existing Unit RUL: 6 years ; New Motor EUL: 18 years ; REL after RUL: 12 years |  | 168 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 1.626 | 3488.5 | Early Replacement
911 | HVAC | Fans | Continuous Fan | ECM Continuous Fan Early Replacement: HVAC | ECM Installations Continuous Fan Early Replacement for RUL replacement | 3 | Active | 2017-01-01 |  | PSC Motor (Permanent Split Capacitor) for 8 SEER AC |  |  | 0 | 3488 |  | per measure | Algorithm | Continuous ECM blower |  |  | Continuous ECM blower | 0 | 3488 | Algorithm | Existing Unit RUL: 6 years ; New Motor EUL: 18 years ; REL after RUL: 12 years |  | 168 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 1.533 | 3289 | Early Replacement
1244 | HVAC | Fans | Continuous Fan | ECM Continuous Fan MF: HVAC | ECM Continuous Fan MF | 1 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per measure | [10 empty] | 263 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.813 | 1744
1244 | HVAC | Fans | Continuous Fan | ECM Continuous Fan MF: HVAC | ECM Continuous Fan MF | 2 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 263 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.766 | 1644.5
910 | HVAC | Fans | Continuous Fan | ECM Continuous Fan Replace at Fail: HVAC | ECM Continuous Fan Replace at Fail: HVAC | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard motor continuous operation | [5 empty] | per measure | Algorithm | Continuous ECM blower |  |  | Continuous ECM blower |  |  | Algorithm |  |  | 125 |  | 15 | 2013-15 |  |  |  | HVAC |  |  | per measure | 0.270 | 3597.0 | Replace at Fail
910 | HVAC | Fans | Continuous Fan | ECM Continuous Fan Replace at Fail: HVAC | ECM Continuous Fan Replace at Fail: HVAC | 2 | InActive | 2016-01-01 | 2016-12-31 | Standard motor continuous operation | [5 empty] | per measure | Algorithm | Continuous ECM blower |  |  | Continuous ECM blower |  |  | Algorithm |  |  | 125 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 1.626 | 3488.5 | Replace at Fail
910 | HVAC | Fans | Continuous Fan | ECM Continuous Fan Replace at Fail: HVAC | ECM Continuous Fan Replace at Fail: HVAC | 3 | Active | 2017-01-01 |  | Standard motor continuous operation | [5 empty] | per measure | Algorithm | Continuous ECM blower |  |  | Continuous ECM blower |  |  | Algorithm |  |  | 125 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 1.533 | 3289 | Replace at Fail
908 | HVAC | Fans | Auto Fan | ECM Installations Auto Fan: HVAC: Early Replacement | ECM Installations Auto Fan Early Replacement for RUL replacement | 1 | InActive | 2013-01-02 | 2015-12-31 | PSC Motor (Permanent Split Capacitor) for 13 SEER AC |  |  | 0.268 | 928.6 |  | per measure | Algorithm | Intermittent ECM blower |  |  | Intermittent ECM blower | 0.268 | 928.6 | Algorithm | Existing Unit RUL: 6 years ; New Motor EUL: 18 years ; REL after RUL: 12 years |  | 168 |  | 15 | 2013-15 |  |  |  | HVAC |  |  | per measure | 0.268 | 928.6 | Early Replacement
911 | HVAC | Fans | Continuous Fan | ECM Installations Continuous Fan: HVAC: Early Replacement | ECM Installations Continuous Fan Early Replacement for RUL replacement | 1 | InActive | 2013-01-02 | 2015-12-31 | PSC Motor (Permanent Split Capacitor) for 8 SEER AC |  |  | 0.268 | 3596.6 |  | per measure | Algorithm | Continuous ECM blower |  |  | Continuous ECM blower | 0.268 | 3596.6 | Algorithm | Existing Unit RUL: 6 years ; New Motor EUL: 18 years ; REL after RUL: 12 years |  | 168 |  | 15 | 2013-15 |  |  |  | HVAC |  |  | per measure | 0.268 | 3596.6 | Early Replacement
1179 | Appliances | Miscellaneous | Air Purifier | Energy Star Air Purifier: Home Energy Performance | Energy Star Air Purifier | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Air Purifier | [5 empty] | per measure | Algorithm | Energy Star Air Purifier |  |  | Energy Star Air Purifier |  |  | Algorithm |  |  | 70 |  | 9 | 2013-15 |  |  |  | Home Energy Performance |  |  | per measure | 0.081 | 482.0
1171 | Appliances | Miscellaneous | Air Purifier | Energy Star Air Purifier: Low Income | Energy Star Air Purifier | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Air Purifier | [5 empty] | per measure | Algorithm | Energy Star Air Purifier |  |  | Energy Star Air Purifier |  |  | Algorithm |  |  | 70 |  | 9 | 2013-15 |  |  |  | Low Income |  |  | per measure | 0.081 | 482.0
1177 | Appliances | Miscellaneous | Air Purifier | Energy Star Air Purifier:Efficient Products | Energy Star Air Purifier | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Air Purifier | [5 empty] | per measure | Algorithm | Energy Star Air Purifier |  |  | Energy Star Air Purifier |  |  | Algorithm |  |  | 70 |  | 9 | 2013-15 |  |  |  | Efficient Products |  |  | per measure | 0.081 | 482.0
1177 | Appliances | Miscellaneous | Air Purifier | Energy Star Air Purifier:Efficient Products | Energy Star Air Purifier | 2 | InActive | 2016-01-01 | 2016-12-31 | Standard Air Purifier | [5 empty] | per measure | Algorithm | Energy Star Air Purifier |  |  | Energy Star Air Purifier |  |  | Algorithm |  |  | 70 |  | 9 | 2016-18 |  |  |  | Efficient Products |  |  | per measure | 0.225 | 482
1177 | Appliances | Miscellaneous | Air Purifier | Energy Star Air Purifier:Efficient Products | Energy Star Air Purifier | 3 | Active | 2017-01-01 |  | Standard Air Purifier | [5 empty] | per measure | Algorithm | Energy Star Air Purifier |  |  | Energy Star Air Purifier |  |  | Algorithm |  |  | 70 |  | 9 | 2016-18 |  |  |  | Efficient Products |  |  | per measure | 0.24 | 515.0
1175 | Appliances | Freezers | Freezer, residential | Energy Star Freezer: Efficient Products | Energy Star Freezer | 1 | InActive | 2013-01-01 | 2015-12-30 | Standard Freezer | [5 empty] | per measure | Algorithm | Energy Star Freezer |  |  | Energy Star Freezer |  |  | Algorithm |  |  | 33 |  | 11 | 2013-15 |  |  |  | Efficient Products |  |  | per measure | 0.004 | 61.0
1176 | Appliances | Freezers | Freezer, residential | Energy Star Freezer: Home Energy Performance | Energy Star Freezer | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Freezer | [5 empty] | per measure | Algorithm | Energy Star Freezer |  |  | Energy Star Freezer |  |  | Algorithm |  |  | 33 |  | 11 | 2013-15 |  |  |  | Home Energy Performance |  |  | per measure | 0.004 | 61.0
1170 | Appliances | Freezers | Freezer, residential | Energy Star Freezer: Low Income | Energy Star Freezer | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Freezer | [5 empty] | per measure | Algorithm | Energy Star Freezer |  |  | Energy Star Freezer |  |  | Algorithm |  |  | 33 |  | 11 | 2013-15 |  |  |  | Low Income |  |  | per measure | 0.004 | 61.0
968 | Appliances | Refrigerators | Refrigerator, residential | Energy Star Refrigerator_MF: Low Income | Energy Star Refrigerator in Multifamily Unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Operating unit with top freezer (15, 18, or 21 ft3) manufactured before 2000 | 1495 | kWh |  |  |  | per measure | Algorithm | Energy Star Refrigerator | kWh | 369 | Energy Star Refrigerator in Multifamily units |  |  | Algorithm |  |  | 680 |  | 10 | 2013-15 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.; Note, this savings value is only for multi-family units, savings for single family units, while similar, may be slightly different due to various factors including as household size, location of unit, or climate. Another tool to help estimate savings is the Energy Star website which provides various unit models and associated energy consumption. http://www.energystar.gov/index.cfm?fuseaction=find_a_product.showProductGroup&pgw_code=RF | per measure | 0.178 | 1126.0
968 | Appliances | Refrigerators | Refrigerator, residential | Energy Star Refrigerator_MF: Low Income | Energy Star Refrigerator in Multifamily Unit | 2 | InActive | 2016-01-01 | 2016-12-31 | Operating unit with top freezer (15, 18, or 21 ft3) manufactured before 2000 | 1268 | kWh |  |  |  | per measure | Algorithm | Energy Star Refrigerator | kWh | 362 | Energy Star Refrigerator in Multifamily units |  |  | Algorithm |  |  | 750 |  | 10 | 2016-18 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.; Note, this savings value is only for multi-family units, savings for single family units, while similar, may be slightly different due to various factors including as household size, location of unit, or climate. Another tool to help estimate savings is the Energy Star website which provides various unit models and associated energy consumption. http://www.energystar.gov/index.cfm?fuseaction=find_a_product.showProductGroup&pgw_code=RF | per measure | 0.104 | 807
968 | Appliances | Refrigerators | Refrigerator, residential | Energy Star Refrigerator_MF: Low Income | Energy Star Refrigerator in Multifamily Unit | 3 | Active | 2017-01-01 |  | Operating unit with top freezer (15, 18, or 21 ft3) manufactured before 2000 | 1268 | kWh |  |  |  | per measure | Algorithm | Energy Star Refrigerator | kWh | 362 | Energy Star Refrigerator in Multifamily units |  |  | Algorithm |  |  | 750 |  | 10 | 2016-18 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.; Note, this savings value is only for multi-family units, savings for single family units, while similar, may be slightly different due to various factors including as household size, location of unit, or climate. Another tool to help estimate savings is the Energy Star website which provides various unit models and associated energy consumption. http://www.energystar.gov/index.cfm?fuseaction=find_a_product.showProductGroup&pgw_code=RF | per measure | 0.114 | 888.0
1221 | Appliances | Refrigerators | Refrigerator, residential | Energy Star Refrigerator_SF: Low Income | Energy Star Refrigerator in low income single family Unit | 1 | Active | 2016-01-01 | [7 empty] | per measure | Algorithm | [6 empty] | Algorithm |  |  | 750 |  | 10 | 2016-18 |  |  |  | Low Income |  |  | per measure | 0.104 | 807
1221 | Appliances | Refrigerators | Refrigerator, residential | Energy Star Refrigerator_SF: Low Income | Energy Star Refrigerator in low income single family Unit | 2 | Proposed | 2017-01-01 | [7 empty] | per measure | Algorithm | [6 empty] | Algorithm |  |  | 750 |  | 10 |  |  |  |  | Low Income |  |  | per measure | 0.116 | 906.0
1180 | Appliances | Refrigerators | Water Cooler | Energy Star Water Cooler - Cold Only: Efficient Products | Energy Star Water Cooler | 1 | Active | 2013-01-02 |  | Standard Water Cooler | [5 empty] | per measure | Algorithm | Energy Star Water Cooler |  |  | Energy Star Water Cooler |  |  | Algorithm |  |  | 17 |  | 10 | 2013-15, 2016-18 |  |  |  | Efficient Products |  | Key Assumptions: • 365 days per year • Conventional Hot and Cold energy consumption = 2.19 kWh/day • Conventional Cold Water Only energy consumption = 0.29 kWh per day • Efficient Hot and Cold energy consumption = 1.2 kWh per day. • Efficient Cold Water Only energy consumption = 0.16 kWh per day • Blend of hot and cold, and cold only water coolers. 98% are assumed to be combination and 2% are cold only. | per measure | 0.006 | 47.4
1182 | Appliances | Refrigerators | Water Cooler | Energy Star Water Cooler - Cold Only: Home Energy Performance | Energy Star Water Cooler | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Water Cooler | [5 empty] | per measure | Algorithm | Energy Star Water Cooler |  |  | Energy Star Water Cooler |  |  | Algorithm |  |  | 17 |  | 10 | 2013-15 |  |  |  | Home Energy Performance |  | Key Assumptions: • 365 days per year • Conventional Hot and Cold energy consumption = 2.19 kWh/day • Conventional Cold Water Only energy consumption = 0.29 kWh per day • Efficient Hot and Cold energy consumption = 1.2 kWh per day. • Efficient Cold Water Only energy consumption = 0.16 kWh per day • Blend of hot and cold, and cold only water coolers. 98% are assumed to be combination and 2% are cold only. | per measure | 0.233 | 47.0
1173 | Appliances | Refrigerators | Water Cooler | Energy Star Water Cooler - Cold Only: Low Income | Energy Star Water Cooler | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Water Cooler | [5 empty] | per measure | Algorithm | Energy Star Water Cooler |  |  | Energy Star Water Cooler |  |  | Algorithm |  |  | 17 |  | 10 | 2013-15 |  |  |  | Low Income |  | Key Assumptions: • 365 days per year • Conventional Hot and Cold energy consumption = 2.19 kWh/day • Conventional Cold Water Only energy consumption = 0.29 kWh per day • Efficient Hot and Cold energy consumption = 1.2 kWh per day. • Efficient Cold Water Only energy consumption = 0.16 kWh per day • Blend of hot and cold, and cold only water coolers. 98% are assumed to be combination and 2% are cold only. | per measure | 0.233 | 47.0
1181 | Appliances | Refrigerators | Water Cooler | Energy Star Water Cooler - Hot and Cold: Efficient Products | Energy Star Water Cooler | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Water Cooler | [5 empty] | per measure | Algorithm | Energy Star Water Cooler |  |  | Energy Star Water Cooler |  |  | Algorithm |  |  | 17 |  | 10 | 2013-15 |  |  |  | Efficient Products |  | Key Assumptions: • 365 days per year • Conventional Hot and Cold energy consumption = 2.19 kWh/day • Conventional Cold Water Only energy consumption = 0.29 kWh per day • Efficient Hot and Cold energy consumption = 1.2 kWh per day. • Efficient Cold Water Only energy consumption = 0.16 kWh per day • Blend of hot and cold, and cold only water coolers. 98% are assumed to be combination and 2% are cold only. | per measure | 0.001 | 361.0
1181 | Appliances | Refrigerators | Water Cooler | Energy Star Water Cooler - Hot and Cold: Efficient Products | Energy Star Water Cooler | 2 | InActive | 2016-01-01 | 2016-12-31 | Standard Water Cooler | [5 empty] | per measure | Algorithm | Energy Star Water Cooler |  |  | Energy Star Water Cooler |  |  | Algorithm |  |  | 17 |  | 10 | 2016-18 |  |  |  | Efficient Products |  | Key Assumptions: • 365 days per year • Conventional Hot and Cold energy consumption = 2.19 kWh/day • Conventional Cold Water Only energy consumption = 0.29 kWh per day • Efficient Hot and Cold energy consumption = 1.2 kWh per day. • Efficient Cold Water Only energy consumption = 0.16 kWh per day • Blend of hot and cold, and cold only water coolers. 98% are assumed to be combination and 2% are cold only. | per measure | 0.046 | 361
1181 | Appliances | Refrigerators | Water Cooler | Energy Star Water Cooler - Hot and Cold: Efficient Products | Energy Star Water Cooler | 3 | Active | 2017-01-01 |  | Standard Water Cooler | [5 empty] | per measure | Algorithm | Energy Star Water Cooler |  |  | Energy Star Water Cooler |  |  | Algorithm |  |  | 17 |  | 10 | 2016-18 |  |  |  | Efficient Products |  | Key Assumptions: • 365 days per year • Conventional Hot and Cold energy consumption = 2.19 kWh/day • Conventional Cold Water Only energy consumption = 0.29 kWh per day • Efficient Hot and Cold energy consumption = 1.2 kWh per day. • Efficient Cold Water Only energy consumption = 0.16 kWh per day • Blend of hot and cold, and cold only water coolers. 98% are assumed to be combination and 2% are cold only. | per measure | 0.018 | 140.0
1183 | Appliances | Refrigerators | Water Cooler | Energy Star Water Cooler - Hot and Cold: Home Energy Performance | Energy Star Water Cooler | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Water Cooler | [5 empty] | per measure | Algorithm | Energy Star Water Cooler |  |  | Energy Star Water Cooler |  |  | Algorithm |  |  | 17 |  | 10 | 2013-15 |  |  |  | Home Energy Performance |  | Key Assumptions: • 365 days per year • Conventional Hot and Cold energy consumption = 2.19 kWh/day • Conventional Cold Water Only energy consumption = 0.29 kWh per day • Efficient Hot and Cold energy consumption = 1.2 kWh per day. • Efficient Cold Water Only energy consumption = 0.16 kWh per day • Blend of hot and cold, and cold only water coolers. 98% are assumed to be combination and 2% are cold only. | per measure | 0.001 | 361.0
1174 | Appliances | Refrigerators | Water Cooler | Energy Star Water Cooler - Hot and Cold: Low Income | Energy Star Water Cooler | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Water Cooler | [5 empty] | per measure | Algorithm | Energy Star Water Cooler |  |  | Energy Star Water Cooler |  |  | Algorithm |  |  | 17 |  | 10 | 2013-15 |  |  |  | Low Income |  | Key Assumptions: • 365 days per year • Conventional Hot and Cold energy consumption = 2.19 kWh/day • Conventional Cold Water Only energy consumption = 0.29 kWh per day • Efficient Hot and Cold energy consumption = 1.2 kWh per day. • Efficient Cold Water Only energy consumption = 0.16 kWh per day • Blend of hot and cold, and cold only water coolers. 98% are assumed to be combination and 2% are cold only. | per measure | 0.001 | 361.0
2 | Appliances | Freezers | Recycling | Freezer Recycling: Appliance Recycle | Recycling of a room air conditioner unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Operating Unit (10-27 cubic ft) | 1664 | UEC |  |  | The incremental cost for each appliance recycling measure is the actual cost associated with the removal and recycling of the retired unit. | per measure | Algorithm | Assumes complete removal of the base characteristic | [5 empty] | Algorithm | Ameren Missouri considered 3 measures for an Appliance Recycling program. All 3 measures were associated with different residential end uses: refrigeration, freezer, and miscellaneous. These measures are different than other measures in the TRM because the efficient characteristics assume a complete removal of the base characteristic |  | 84 |  | 8 | 2013-15 |  |  |  | Appliance Recycle |  | The energy and demand savings for the freezer and refrigerator recycling measures can be calculated using the following formula: Delta kWh=(Base UEC-Efficient UEC)× In-situ factor where UEC = average unit energy consumption. In-situ factor = factor considering appliances not plugged in year-round (also known as part-use). If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.203 | 1429.0
2 | Appliances | Freezers | Recycling | Freezer Recycling: Appliance Recycle | Recycling of a room air conditioner unit | 2 | InActive | 2016-01-01 |  | Operating Unit (10-27 cubic ft) | 1078 | UEC |  |  | The incremental cost for each appliance recycling measure is the actual cost associated with the removal and recycling of the retired unit. | per measure | Algorithm | Assumes complete removal of the base characteristic | [5 empty] | Algorithm | Ameren Missouri considered 3 measures for an Appliance Recycling program. All 3 measures were associated with different residential end uses: refrigeration, freezer, and miscellaneous. These measures are different than other measures in the TRM because the efficient characteristics assume a complete removal of the base characteristic |  | 84 |  | 8 |  |  |  |  | Appliance Recycle |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. where: UEC = average unit energy consumption. In-situ factor = factor considering appliances not plugged in year-round (also known as part-use) | per measure | 0.184 | 969.0
1060 | HVAC | Heat Pumps | Heat Pump, Geothermal | Geothermal HP Desuperheater: Efficient Products | Geothermal Heat Pump Desuperheater | 2 | Active | 2016-01-01 |  | No Desuperheater | [5 empty] | per measure | Algorithm | geothermal heat pump desuperheater |  |  | Electric Water Heater Thermostat set at 120°F |  |  | Algorithm | Savings, Cost, EUL values taken from Cadmus Potential Study measure list |  | 239 |  | 10 | 2016 - 18 |  |  |  | Efficient Products |  | The energy savings equation was taken from Morgan Measure Libraries. Morgan was appended to include information from Cadmus to include information for a geothermal heat pump desuperheater. | per measure | 0.065 | 730.5
932 | HVAC | Heat Pumps | Heat Pump, Geothermal | Geothermal HP Desuperheater: HVAC | Geothermal Heat Pump Desuperheater | 1 | InActive | 2013-01-02 | 2015-12-31 | No Desuperheater | [5 empty] | per measure | Algorithm | geothermal heat pump desuperheater |  |  | Electric Water Heater Thermostat set at 120°F |  |  | Algorithm | Savings, Cost, EUL values taken from Cadmus Potential Study measure list |  | 239 |  | 10 | 2013-15 |  |  |  | HVAC |  | The energy savings equation was taken from Morgan Measure Libraries. Morgan was appended to include information from Cadmus to include information for a geothermal heat pump desuperheater. | per measure | 0.170 | 1540.0
932 | HVAC | Heat Pumps | Heat Pump, Geothermal | Geothermal HP Desuperheater: HVAC | Geothermal Heat Pump Desuperheater | 2 | Active | 2016-01-01 |  | No Desuperheater | [5 empty] | per measure | Algorithm | geothermal heat pump desuperheater |  |  | Electric Water Heater Thermostat set at 120°F |  |  | Algorithm | Savings, Cost, EUL values taken from Cadmus Potential Study measure list |  | 239 |  | 10 | 2016-18 |  |  |  | HVAC |  | The energy savings equation was taken from Morgan Measure Libraries. Morgan was appended to include information from Cadmus to include information for a geothermal heat pump desuperheater. | per measure | 0.065 | 730.5
1060 | HVAC | Heat Pumps | Heat Pump, Geothermal | Geothermal HP Desuperheater: New Home Construction | Geothermal Heat Pump Desuperheater | 1 | InActive | 2013-01-02 | 2014-12-31 | No Desuperheater | [5 empty] | per measure | Algorithm | geothermal heat pump desuperheater |  |  | Electric Water Heater Thermostat set at 120°F |  |  | Algorithm | Savings, Cost, EUL values taken from Cadmus Potential Study measure list |  | 239 |  | 10 | 2013-15 |  |  |  | New Home Construction |  | The energy savings equation was taken from Morgan Measure Libraries. Morgan was appended to include information from Cadmus to include information for a geothermal heat pump desuperheater. | per measure | 0.170 | 1540.0
1248 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - 23 EER ER: HVAC | GSHP - 23 EER ER | 1 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per measure | [10 empty] | 4859 |  | 18 | 2016-18 |  |  |  | HVAC |  |  | per measure | 2.199 | 4717
1248 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - 23 EER ER: HVAC | GSHP - 23 EER ER | 2 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 4859 |  | 18 | 2016-18 |  |  |  | HVAC |  |  | per measure | 4.012 | 8607
1249 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - 23 EER Replace at Fail | GSHP - 23 EER Replace at Fail | 1 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per measure | [10 empty] | 3200 |  | 18 | 2016-18 |  |  |  | HVAC |  |  | per measure | 1.259 | 2702
1249 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - 23 EER Replace at Fail | GSHP - 23 EER Replace at Fail | 2 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 3200 |  | 18 | 2016-18 |  |  |  | HVAC |  |  | per measure | 1.681 | 3607
1218 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - EER 17_SF: HVAC | HVAC_GSHP - EER 17_SF | 1 | InActive | [8 empty] | per measure | [10 empty] | 539.37 |  | 12 |  |  |  |  | HVAC |  |  | per measure | 0.458 | 1771
1219 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - EER 19_SF: HVAC | HVAC_GSHP - EER 19_SF | 1 | InActive | [8 empty] | per measure | [10 empty] | 539.37 |  | 12 |  |  |  |  | HVAC |  |  | per measure | 0.641 | 2402.0
933 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - SEER 14+ ER ASHP with GSHP: HVAC | Ground Source Heat Pump SEER 14 Early Replacement | 1 | InActive | 2013-01-01 | 2015-12-31 | SEER 8 Air Source Heat Pump | 8 | SEER | 1.359 | 5125.8 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | Ground Source Heat Pump SEER 14 | SEER | 14 |  | 0.439 | 2081.8 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 4827 |  | 18 | 2013-15 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.359 | 5125.8 | Early Replacement
933 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - SEER 14+ ER ASHP with GSHP: HVAC | Ground Source Heat Pump SEER 14 Early Replacement | 2 | InActive |  |  | SEER 8 Air Source Heat Pump | 8 | SEER |  | 14848 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | Ground Source Heat Pump SEER 14 | SEER | 14 |  |  | 9146 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 4827 |  | 18 |  |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 2.220 | 14848.0 | Early Replacement
1061 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - SEER 14+ ER ASHP with GSHP: New Home Construction | Ground Source Heat Pump SEER 14 Early Replacement | 1 | InActive | 2013-01-02 | 2014-12-31 | SEER 8 Air Source Heat Pump | 8 | SEER | 1.359 | 5125.8 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | Ground Source Heat Pump SEER 14 | SEER | 14 |  | 0.439 | 2081.8 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 4827 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 1.359 | 5126.0 | Early Replacement
934 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - SEER 14+ ER Elec Resist Furnace: HVAC | Ground Source Heat Pump SEER 14 Early Replacement | 1 | InActive | 2013-01-02 | 2015-12-31 | SEER 8 Central Air Conditioner | 8 | SEER | 1.359 | 15841 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | Ground Source Heat Pump SEER 14 | SEER | 14 |  | .439 | 14349.8 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 5250 |  | 18 | 2013-15 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 0.000 | 15841.0 | Early Replacement
934 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - SEER 14+ ER Elec Resist Furnace: HVAC | Ground Source Heat Pump SEER 14 Early Replacement | 2 | InActive | 2016-01-01 | 2016-12-31 | SEER 8 Central Air Conditioner | 8 | SEER |  |  | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | Ground Source Heat Pump SEER 14 | SEER | 14 |  |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 5250 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 13.276 | 28485.3 | Early Replacement
934 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - SEER 14+ ER Elec Resist Furnace: HVAC | Ground Source Heat Pump SEER 14 Early Replacement | 3 | Active | 2017-01-01 |  | SEER 8 Central Air Conditioner | 8 | SEER |  |  | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | Ground Source Heat Pump SEER 14 | SEER | 14 |  |  |  | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 5250 |  | 18 | 2016-18 |  |  |  | HVAC |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 12.678 | 27201 | Early Replacement
1062 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - SEER 14+ ER Elec Resist Furnace: New Home Construction | Ground Source Heat Pump SEER 14 Early Replacement | 1 | InActive | 2013-01-02 | 2014-12-31 | SEER 8 Central Air Conditioner | 8 | SEER | 1.359 | 15841 | The determination of the incremental cost associated with the “early replacement” analysis is different than that used for a “replace on fail” analysis. In the “early replacement” analysis, the incremental cost is the difference between the Net Present Value (NPV) of the efficient equipment full install cost and the NPV of the Future Value (FV) of the base equipment full installation cost.; Savings and costs represent the entire unit. | per measure | Algorithm | Ground Source Heat Pump SEER 14 | SEER | 14 |  | .439 | 14349.8 | Algorithm | HVAC applications can either be applied as an "early replacement" or as a "replace on fail". The "early replacement" application is a more involved analysis. In this analysis, there are two timeframes that need to be analyzed. The first is the timeframe that the existing equipment would continue to operate before reaching the end of the equipment life, or the Remaining Useful Life (RUL). During the RUL of the existing equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the existing equipment. Following the RUL, the second timeframe for the operation of the existing equipment is entered where the efficient equipment will continue to operate for the remainder of the equipment life, or the Remaining Efficient Life (REL). The REL is the difference between the EUL of the efficient equipment and the RUL of the existing equipment. During the REL of the efficient equipment, the energy and demand savings gained through the use of the efficient equipment is the difference in energy and demand consumed by the efficient versus the base equipment that would have been installed if the existing equipment had failed. |  | 5250 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | To most accurately calculate HVAC savings, building simulation modeling should be conducted (see section Building Simulation Protocols). However, if the resources to conduct building simulation do not exist, the following values can be used.; Assume Unit size = 3 ton; Savings and costs represent the entire unit | per measure | 0.000 | 15841.0 | Early Replacement
935 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - SEER 14+ Replace Elec Resist Furnace: HVAC | Ground Source Heat Pump SEER 14 Replace on Fail | 1 | InActive | 2013-01-02 | 2015-12-31 | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Ground Source Heat Pump SEER 14 | SEER | 14 |  |  |  | Algorithm | Existing Unit RUL: 6 years ; New GSHP EUL: 18 years ; REL after RUL: 12 years |  | 4717 |  | 18 | 2013-15 |  |  |  | HVAC |  | Tons = 3.0 | per measure | 0.440 | 14350.0
935 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - SEER 14+ Replace Elec Resist Furnace: HVAC | Ground Source Heat Pump SEER 14 Replace on Fail | 2 | InActive | 2016-01-01 | 2016-12-31 | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Ground Source Heat Pump SEER 14 | SEER | 14 |  |  |  | Algorithm | Existing Unit RUL: 6 years ; New GSHP EUL: 18 years ; REL after RUL: 12 years |  | 4717 |  | 18 | 2016-18 |  |  |  | HVAC |  | Tons = 3.0 | per measure | 12.681 | 27207.5
935 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - SEER 14+ Replace Elec Resist Furnace: HVAC | Ground Source Heat Pump SEER 14 Replace on Fail | 3 | Active | 2017-01-01 |  | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Ground Source Heat Pump SEER 14 | SEER | 14 |  |  |  | Algorithm | Existing Unit RUL: 6 years ; New GSHP EUL: 18 years ; REL after RUL: 12 years |  | 4717 |  | 18 | 2016-18 |  |  |  | HVAC |  | Tons = 3.0 | per measure | 10.645 | 22840
1063 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - SEER 14+ Replace Elec Resist Furnace: New Home Construction | Ground Source Heat Pump SEER 14 Replace on Fail | 1 | InActive | 2013-01-02 | 2014-12-31 | Electric Resistance Furnace SEER 13 | 13 | SEER |  |  |  | per measure | Algorithm | Ground Source Heat Pump SEER 14 | SEER | 14 |  |  |  | Algorithm | Existing Unit RUL: 6 years ; New GSHP EUL: 18 years ; REL after RUL: 12 years |  | 4717 |  | 18 | 2013-15 |  |  |  | New Home Construction |  | Tons = 3.0 | per measure | 0.440 | 14350.0
1063 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP - SEER 14+ Replace Elec Resist Furnace: New Home Construction | Ground Source Heat Pump SEER 14 Replace on Fail | 2 | InActive |  |  | SEER 13 Electric Resistance Furnace | 13 | SEER |  |  |  | per measure | Algorithm | Ground Source Heat Pump SEER 14 | SEER | 14 |  |  |  | Algorithm | Existing Unit RUL: 6 years ; New GSHP EUL: 18 years ; REL after RUL: 12 years |  | 4717 |  | 18 |  |  |  |  | New Home Construction |  | Tons = 3.0 | per measure | 0.440 | 6771.0
1247 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP SEER 14+ ER ASHP with GSHP ER: HVAC | GSHP SEER 14+ ER ASHP with GSHP ERbegin | 1 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per measure | [10 empty] | 5250 |  | 18 | 2016-18 |  |  |  | HVAC |  |  | per measure | 2.946 | 6321.8
1247 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP SEER 14+ ER ASHP with GSHP ER: HVAC | GSHP SEER 14+ ER ASHP with GSHP ERbegin | 2 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 5250 |  | 18 | 2016-18 |  |  |  | HVAC |  |  | per measure | 5.904 | 12667
913 | HVAC | Heat Pumps | Heat Pump | Heat Pump Strip Installed: HVAC | Heat Pump Strip Heat Lock Out Installed | 1 | InActive | 2013-01-02 | 2015-12-31 | No heat pump control dial installed | [5 empty] | per measure | Algorithm | Heat pump strip control dial installed | [5 empty] | Algorithm |  |  | 154 |  | 15 | 2013-15 |  |  |  | HVAC |  | Assume 3 ton heat pump capacity | per measure | 0.470 | 1332.0
913 | HVAC | Heat Pumps | Heat Pump | Heat Pump Strip Installed: HVAC | Heat Pump Strip Heat Lock Out Installed | 2 | Active | 2016-01-01 |  | No heat pump control dial installed | [5 empty] | per measure | Algorithm | Heat pump strip control dial installed | [5 empty] | Algorithm |  |  | 154 |  | 15 | 2016-18 |  |  |  | HVAC |  | Assume 3 ton heat pump capacity | per measure | 0.621 | 1332.0
914 | HVAC | Heat Pumps | Heat Pump | Heat Pump Strip Reset: HVAC | Heat Pump Strip Heat Lock Out Reset | 1 | InActive | 2013-01-02 | 2015-12-31 | Heat pump control dial installed, but not set | [5 empty] | per measure | Algorithm | Heat pump strip lock out installed | [5 empty] | Algorithm |  |  | 154 |  | 15 | 2013-15 |  |  |  | HVAC |  | Assume 3 ton heat pump capacity | per measure | 0.470 | 1332.0
914 | HVAC | Heat Pumps | Heat Pump | Heat Pump Strip Reset: HVAC | Heat Pump Strip Heat Lock Out Reset | 2 | Active | 2016-01-01 |  | Heat pump control dial installed, but not set | [5 empty] | per measure | Algorithm | Heat pump strip dial reset | [5 empty] | Algorithm |  |  | 25 |  | 15 | 2016-18 |  |  |  | HVAC |  | Assume 3 ton heat pump capacity | per measure | 0.621 | 1332.0
1232 | Water Heating | Water Heaters | Heat Pump Water Heater | Heat Pump Water Heater: HVAC | Heat Pump Water Heater | 1 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per measure | [10 empty] | 1480 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.198 | 2229.5
1232 | Water Heating | Water Heaters | Heat Pump Water Heater | Heat Pump Water Heater: HVAC | Heat Pump Water Heater | 2 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 1480 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.254 | 2865.0
872 | Water Heating | Water Heaters | Heat Pump Water Heater | Heat Pump Water Heaters: Efficient Products | Residential Heat Pump Water Heaters | 1 | InActive | 2013-01-02 | 2015-12-31 | Heat pump water heater, 0.90 EF Standard water heater | 0.9 | EF |  |  |  | per measure | Algorithm | COP>2.0 |  |  | COP > 2.0 Heat Pump Water Heater |  |  | Algorithm | Water heater efficiency is rated according to its Energy Factor (EF). For residential storage tank electric water heaters, the current minimum standard requires an EF of 0.90 or greater. Heat Pump Water Heaters (HPWH) take heat from the surrounding air and transfer it to the water in the tank, unlike conventional water heaters, which use either gas (or sometimes other fuels) burners or electric resistance heating coils to heat the water. HPWH technology uses a standard heat pump thermodynamic cycle to remove energy from a low-temperature heat source (the ambient room air) and transfer it to a high-temperature heat sink (the water within the heater). Most HPWHs have back up heating elements to heat the water during very low temperature periods and come either self-contained with a storage tank or as an add-on unit using a conventional water heater for storage. |  | 1020 |  | 15 | 2013-15 |  |  |  | Efficient Products |  | The energy and demand savings for each residential water heater measure can be calculated using the following formula: Delta kWh =((1/(Base EF)-1/(Efficent EF))×(HWT-CWT) × 8.3 × GPD ×365)/3413 where EF = energy factor of water heater, Base EF= < 64.3, Efficient EF = >0.90, HWT = temperature in Fahrenheit of hot water (135°F according to standard DOE test procedure), CWT = temperature in Fahrenheit of cold water supply (58°F according to standard DOE test procedure), and GPD = hot water used in gallons per day | per measure | 0.325 | 1802.0
872 | Water Heating | Water Heaters | Heat Pump Water Heater | Heat Pump Water Heaters: Efficient Products | Residential Heat Pump Water Heaters | 2 | InActive | 2016-01-01 | 2016-12-31 | EF 0.95 Elec Water Heater (Energy Factor 0.95) | [5 empty] | per measure | Algorithm | Elec Heat pump water heater EF>=2.2 Energy Star 50 gallon HP Water Heater | [5 empty] | Algorithm |  |  | 1480 |  | 15 | 2016-18 |  |  |  | Efficient Products |  |  | per measure | 0.294 | 3315.04
872 | Water Heating | Water Heaters | Heat Pump Water Heater | Heat Pump Water Heaters: Efficient Products | Residential Heat Pump Water Heaters | 3 | Active | 2017-01-01 | [7 empty] | per measure | Algorithm | [6 empty] | Algorithm |  |  | 1480 |  | 15 | 2016-18 |  |  |  | Efficient Products |  |  | per measure | 0.254 | 2865.0
902 | Water Heating | Water Heaters | Heat Pump Water Heater | Heat Pump Water Heaters: Home Energy Performance | Residential Heat Pump Water Heaters | 1 | InActive | 2013-01-02 | 2015-12-31 | Heat pump water heater, 0.90 EF Standard water heater | 0.9 | EF |  |  |  | per measure | Algorithm | COP>2.0 |  |  | COP > 2.0 Heat Pump Water Heater |  |  | Algorithm | Water heater efficiency is rated according to its Energy Factor (EF). For residential storage tank electric water heaters, the current minimum standard requires an EF of 0.90 or greater. Heat Pump Water Heaters (HPWH) take heat from the surrounding air and transfer it to the water in the tank, unlike conventional water heaters, which use either gas (or sometimes other fuels) burners or electric resistance heating coils to heat the water. HPWH technology uses a standard heat pump thermodynamic cycle to remove energy from a low-temperature heat source (the ambient room air) and transfer it to a high-temperature heat sink (the water within the heater). Most HPWHs have back up heating elements to heat the water during very low temperature periods and come either self-contained with a storage tank or as an add-on unit using a conventional water heater for storage. |  | 1020 |  | 15 | 2013-15 |  |  |  | Home Energy Performance |  | The energy and demand savings for each residential water heater measure can be calculated using the following formula: Delta kWh =((1/(Base EF)-1/(Efficent EF))×(HWT-CWT) × 8.3 × GPD ×365)/3413 where EF = energy factor of water heater, Base EF= < 64.3, Efficient EF = >0.90, HWT = temperature in Fahrenheit of hot water (135°F according to standard DOE test procedure), CWT = temperature in Fahrenheit of cold water supply (58°F according to standard DOE test procedure), and GPD = hot water used in gallons per day | per measure | 0.325 | 1802.0
1092 | Water Heating | Water Heaters | Heat Pump Water Heater | Heat Pump Water Heaters: New Home Construction | Residential Heat Pump Water Heaters | 1 | InActive | 2013-01-02 | 2014-12-31 | Heat pump water heater, 0.90 EF Standard water heater | 0.9 | EF |  |  |  | per measure | Algorithm | COP>2.0 |  |  | COP > 2.0 Heat Pump Water Heater |  |  | Algorithm | Water heater efficiency is rated according to its Energy Factor (EF). For residential storage tank electric water heaters, the current minimum standard requires an EF of 0.90 or greater. Heat Pump Water Heaters (HPWH) take heat from the surrounding air and transfer it to the water in the tank, unlike conventional water heaters, which use either gas (or sometimes other fuels) burners or electric resistance heating coils to heat the water. HPWH technology uses a standard heat pump thermodynamic cycle to remove energy from a low-temperature heat source (the ambient room air) and transfer it to a high-temperature heat sink (the water within the heater). Most HPWHs have back up heating elements to heat the water during very low temperature periods and come either self-contained with a storage tank or as an add-on unit using a conventional water heater for storage. |  | 1020 |  | 15 | 2013-15 |  |  |  | New Home Construction |  | The energy and demand savings for each residential water heater measure can be calculated using the following formula: Delta kWh =((1/(Base EF)-1/(Efficent EF))×(HWT-CWT) × 8.3 × GPD ×365)/3413 where EF = energy factor of water heater, Base EF= < 64.3, Efficient EF = >0.90, HWT = temperature in Fahrenheit of hot water (135°F according to standard DOE test procedure), CWT = temperature in Fahrenheit of cold water supply (58°F according to standard DOE test procedure), GPD = hot water used in gallons per day | per measure | 0.325 | 1802.0
952 | Lighting | Exterior Lighting | HID | HID - Exterior: Lighting | HID Outdoor Bulb | 1 | InActive | 2013-01-02 | 2015-12-31 | Extended Service Lamp | 256.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | HID Outdoor Bulb | watts | 50 | HID Outdoor Bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 84.85 |  | 6 | 2013-15 |  |  |  | Lighting |  | Morgan was edited to include HID data from GEP. This demand came from the loadshape since it was not accounted for in Morgan. | per bulb | 0.0 | 603.0
1077 | Lighting | Exterior Lighting | HID | HID - Exterior: New Home Construction | HID Outdoor Bulb | 1 | InActive | 2013-01-02 | 2014-12-31 | Extended Service Lamp | 256.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | HID Outdoor Bulb | watts | 50 | HID Outdoor Bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 84.85 |  | 6 | 2013-15 |  |  |  | New Home Construction |  | Morgan was edited to include HID data from GEP. This demand came from the loadshape since it was not accounted for in Morgan. | per bulb | 0.018 | 603.0
1223 | Whole Home | Home Audit | Level 1 | Home Energy Report: Behavior | Home Energy Report | 1 | Active | 2016-01-01 | [7 empty] | per home | [10 empty] | 0 |  | 1 | 2016-18 |  |  |  | Behavior |  |  | per home | 0.0699 | 150
1245 | HVAC | HVAC O&M | HVAC Tune Up | HVAC Maintenance and Tune-up_MF: HVAC | HVAC Maintenance and Tune-up_MF | 1 | Active | 2016-01-01 | [7 empty] | per emasure | [10 empty] | 70 |  | 10 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.165 | 174
999 | HVAC | HVAC O&M | HVAC Tune Up | HVAC Maintenance and Tune-up_MF: Low Income | HVAC Maintenance and Tune-Up | 1 | InActive | 2013-01-01 | 2015-12-30 | 10% EER degradation; 5% furnace efficiency degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | HVAC maintenance and tune-up |  |  | HVAC maintenance and tune-up |  |  | Algorithm |  |  | 70 |  | 10 | 2013-15 |  |  |  | Low Income |  | Multifamily Tons = 1.5 | per measure | 0.090 | 75.0
999 | HVAC | HVAC O&M | HVAC Tune Up | HVAC Maintenance and Tune-up_MF: Low Income | HVAC Maintenance and Tune-Up | 2 | InActive | 2016-01-01 | 2016-12-31 | 10% EER degradation; 5% furnace efficiency degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | HVAC maintenance and tune-up |  |  | HVAC maintenance and tune-up |  |  | Algorithm |  |  | 90 |  | 10 | 2016-18 |  |  |  | Low Income |  | Multifamily Tons = 1.5 | per measure | 0.07 | 150
999 | HVAC | HVAC O&M | HVAC Tune Up | HVAC Maintenance and Tune-up_MF: Low Income | HVAC Maintenance and Tune-Up | 3 | Active | 2017-01-01 |  | 10% EER degradation; 5% furnace efficiency degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | HVAC maintenance and tune-up |  |  | HVAC maintenance and tune-up |  |  | Algorithm |  |  | 90 |  | 10 | 2016-18 |  |  |  | Low Income |  | Multifamily Tons = 1.5 | per measure | 0.067 | 143
943 | HVAC | HVAC O&M | HVAC Tune Up | HVAC Maintenance and Tune-up_SF: HVAC | HVAC Maintenance and Tune-Up | 1 | InActive | 2013-01-02 | 2015-12-31 | 10% EER degradation; 5% furnace efficiency degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | HVAC maintenance and tune-up |  |  | HVAC maintenance and tune-up |  |  | Algorithm |  |  | 130 |  | 10 | 2013-15 |  |  |  | HVAC |  | Single Family Tons = 2.7 | per measure | 0.210 | 174.0
943 | HVAC | HVAC O&M | HVAC Tune Up | HVAC Maintenance and Tune-up_SF: HVAC | HVAC Maintenance and Tune-Up | 2 | InActive | 2016-01-01 | 2016-12-31 | 10% EER degradation; 5% furnace efficiency degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | HVAC maintenance and tune-up |  |  | HVAC maintenance and tune-up |  |  | Algorithm |  |  | 70 |  | 10 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 2.7 | per measure | 0.001 | 2.84
943 | HVAC | HVAC O&M | HVAC Tune Up | HVAC Maintenance and Tune-up_SF: HVAC | HVAC Maintenance and Tune-Up | 3 | Active | 2017-01-01 |  | 10% EER degradation; 5% furnace efficiency degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | HVAC maintenance and tune-up |  |  | HVAC maintenance and tune-up |  |  | Algorithm |  |  | 70 |  | 10 | 2016-18 |  |  |  | HVAC |  | Single Family Tons = 2.7 | per measure | 0.081 | 174
1000 | HVAC | HVAC O&M | HVAC Tune Up | HVAC Maintenance and Tune-up_SF: Low Income | HVAC Maintenance and Tune-Up | 1 | InActive | 2013-01-01 | 2015-12-30 | 10% EER degradation; 5% furnace efficiency degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | HVAC maintenance and tune-up |  |  | HVAC maintenance and tune-up |  |  | Algorithm |  |  | 130 |  | 10 | 2013-15 |  |  |  | Low Income |  | Single Family Tons = 2.7 | per measure | 0.210 | 174.0
1000 | HVAC | HVAC O&M | HVAC Tune Up | HVAC Maintenance and Tune-up_SF: Low Income | HVAC Maintenance and Tune-Up | 2 | Active | 2016-01-01 |  | 10% EER degradation; 5% furnace efficiency degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | HVAC maintenance and tune-up |  |  | HVAC maintenance and tune-up |  |  | Algorithm |  |  | 100 |  | 10 | 2016-18 |  |  |  | Low Income |  | Single Family Tons = 2.7 | per measure | 0.081 | 174
941 | HVAC | HVAC O&M | Coil Cleaning | Indoor Coil Cleaning: HVAC | Indoor Coil Cleaning | 1 | InActive | 2013-01-02 | 2015-12-31 | Dirty coils | [5 empty] | per cleaning | Algorithm | Coil cleaning |  |  | Coil cleaning |  |  | Algorithm |  |  | 63 |  | 5 | 2013-15 |  |  |  | HVAC |  | Tons = 3.0 | per measure | 0.230 | 638.0
941 | HVAC | HVAC O&M | Coil Cleaning | Indoor Coil Cleaning: HVAC | Indoor Coil Cleaning | 2 | InActive | 2016-01-01 | 2016-12-31 | Dirty coils | [5 empty] | per cleaning | Algorithm | Coil cleaning |  |  | Coil cleaning |  |  | Algorithm |  |  | 63 |  | 5 | 2016-18 |  |  |  | HVAC |  | Tons = 3.0 | per measure | 0.104 | 223.94
941 | HVAC | HVAC O&M | Coil Cleaning | Indoor Coil Cleaning: HVAC | Indoor Coil Cleaning | 3 | Active | 2017-01-01 |  | Dirty coils | [5 empty] | per cleaning | Algorithm | Coil cleaning |  |  | Coil cleaning |  |  | Algorithm |  |  | 63 |  | 5 | 2016-18 |  |  |  | HVAC |  | Tons = 3.0 | per measure | 0.055 | 117
1230 | HVAC | HVAC Controls | Smart Thermostat | Learning Thermostat: Efficient Products | Learning Thermostat | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 224 |  | 10 | 2016-18 |  |  |  | Efficient Products |  |  | per unit | 0.438 | 462
1222 | HVAC | HVAC Controls | Smart Thermostat | Learning Thermostat: HVAC | Learning Thermostat | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 224 |  | 10 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.438 | 462
1018 | Lighting | Interior Lighting | LED, screw base | LED - 10.5W Downlight E26 Light Bulb_MF: Low Income | LED Downlight E26 Light Bulb Multi Family | 1 | InActive | 2013-01-01 | 2015-12-30 | Incandescent Downlight Bulb | 65.8 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Downlight E26 Light Bulb | watts | 10.5 | LED Downlight E26 Light Bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 32.97 |  | 25 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.000 | 21.3
1018 | Lighting | Interior Lighting | LED, screw base | LED - 10.5W Downlight E26 Light Bulb_MF: Low Income | LED Downlight E26 Light Bulb Multi Family | 2 | InActive | 2016-01-01 | 2016-12-31 | Incandescent Downlight Bulb | 65.8 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Downlight E26 Light Bulb | watts | 10.5 | LED Downlight E26 Light Bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 | 2016-18 |  |  |  | Low Income |  |  | per bulb | 0.004 | 28
1018 | Lighting | Interior Lighting | LED, screw base | LED - 10.5W Downlight E26 Light Bulb_MF: Low Income | LED Downlight E26 Light Bulb Multi Family | 3 | Active | 2017-01-01 |  | Incandescent Downlight Bulb | 65.8 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Downlight E26 Light Bulb | watts | 10.5 | LED Downlight E26 Light Bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 | 2016-18 |  |  |  | Low Income |  |  | per bulb | 0.003 | 21.3
1019 | Lighting | Interior Lighting | LED, screw base | LED - 10.5W Downlight E26 Light Bulb_SF: Low Income | LED Downlight E26 Light Bulb Single Family | 1 | InActive | 2013-01-01 | 2015-12-30 | Incandescent Downlight Bulb | 65.8 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Downlight E26 Light Bulb | watts | 10.5 | LED Downlight E26 Light Bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 32.97 |  | 25 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.000 | 55.0
1019 | Lighting | Interior Lighting | LED, screw base | LED - 10.5W Downlight E26 Light Bulb_SF: Low Income | LED Downlight E26 Light Bulb Single Family | 2 | Active | 2016-01-01 |  | Incandescent Downlight Bulb | 65.8 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Downlight E26 Light Bulb | watts | 10.5 | LED Downlight E26 Light Bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 | 2016-18 |  |  |  | Low Income |  |  | per bulb | 0.004 | 28
1019 | Lighting | Interior Lighting | LED, screw base | LED - 10.5W Downlight E26 Light Bulb_SF: Low Income | LED Downlight E26 Light Bulb Single Family | 3 | Proposed | 2017-01-01 |  | Incandescent Downlight Bulb | 65.8 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Downlight E26 Light Bulb | watts | 10.5 | LED Downlight E26 Light Bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 |  |  |  |  | Low Income |  |  | per bulb | 0.004 | 29.3
890 | Lighting | Interior Lighting | LED, screw base | LED - 10.5W Downlight E26 Light Bulb: Home Energy Performance | LED Downlight E26 Light Bulb | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Downlight Bulb | 65.8 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Downlight E26 Light Bulb | watts | 10.5 | LED Downlight E26 Light Bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 32.97 |  | 25 | 2013-15 |  |  |  | Home Energy Performance |  |  | per bulb | 0.000 | 54.5
890 | Lighting | Interior Lighting | LED, screw base | LED - 10.5W Downlight E26 Light Bulb: Home Energy Performance | LED Downlight E26 Light Bulb | 2 | InActive |  |  | Incandescent Downlight Bulb | 65.8 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Downlight E26 Light Bulb | watts | 10.5 | LED Downlight E26 Light Bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 32.97 |  | 25 |  |  |  |  | Home Energy Performance |  |  | per bulb | 0.000 | 49.0
962 | Lighting | Interior Lighting | LED, screw base | LED - 10.5W Downlight E26 Light Bulb: Lighting | LED Downlight E26 Light Bulb | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Downlight Bulb | 65.8 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Downlight E26 Light Bulb | watts | 10.5 | LED Downlight E26 Light Bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 32.97 |  | 25 | 2013-15 |  |  |  | Lighting |  |  | per bulb | 0.000 | 54.5
1085 | Lighting | Interior Lighting | LED, screw base | LED - 10.5W Downlight E26 Light Bulb: New Home Construction | LED Downlight E26 Light Bulb | 1 | InActive | 2013-01-02 | 2014-12-31 | Incandescent Downlight Bulb | 65.8 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Downlight E26 Light Bulb | watts | 10.5 | LED Downlight E26 Light Bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 32.97 |  | 25 | 2013-15 |  |  |  | New Home Construction |  |  | per bulb | 0.000 | 55.0
962 | Lighting | Interior Lighting | LED, screw base | LED - 10.5W Downlight E26: Lighting | LED Downlight E26 | 2 | InActive | 2016-01-01 | 2016-12-31 | 47W EISA Compliant light bulb |  |  |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | 10.5 W LED Downlight | [5 empty] | Algorithm |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.004 | 26.77
962 | Lighting | Interior Lighting | LED, screw base | LED - 10.5W Downlight E26: Lighting | LED Downlight E26 | 3 | Active | 2017-01-01 | [6 empty] | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | [6 empty] | Algorithm |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.006 | 40.8
1204 | Lighting | Interior Lighting | LED, screw base | LED - 10W: Lighting | 10W LED | 1 | InActive | 2016-01-01 | 2016-12-31 | 47W EISA Compliant Light Bulb |  |  | 0 | 27 |  | per bulb |  | 10 W LED |  |  |  | 0 | 6 |  |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.004 | 28
1204 | Lighting | Interior Lighting | LED, screw base | LED - 10W: Lighting | 10W LED | 2 | Active | 2017-01-01 |  |  |  |  | 0 | 27 |  | per bulb | [5 empty] | 0 | 6 |  |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.006 | 38.2
1263 | Lighting | Interior Lighting | LED, screw base | LED - 12 W_LI: Kits | LED - 12 W | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 0 |  | 25 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.004 | 25.8
1203 | Lighting | Interior Lighting | LED, screw base | LED - 12 W_MF: Kits | 12 W LED_MF | 1 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per bulb | [10 empty] | 0 |  | 25 | 2016-18 |  |  |  | Kits |  | Higher energy savings are for the first four years when they drop due to EISA standards. | per bulb | 0.004 | 25.8
1203 | Lighting | Interior Lighting | LED, screw base | LED - 12 W_MF: Kits | 12 W LED_MF | 2 | Active | 2017-01-01 | [7 empty] | per bulb | [10 empty] | 0 |  | 25 | 2016-18 |  |  |  | Kits |  | Higher energy savings are for the first four years when they drop due to EISA standards. | per bulb | 0.006 | 37.7
1202 | Lighting | Interior Lighting | LED, screw base | LED - 12 W_SF: Kits | 12 W LED | 1 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per bulb | [10 empty] | 0 |  | 25 | 2016-18 |  |  |  | Kits |  | Savings is higher for the first four years when it drops due to EISA standards | per bulb | 0.004 | 25.8
1202 | Lighting | Interior Lighting | LED, screw base | LED - 12 W_SF: Kits | 12 W LED | 2 | Active | 2017-01-01 | [7 empty] | per bulb | [10 empty] | 0 |  | 25 | 2016-18 |  |  |  | Kits |  | Savings is higher for the first four years when it drops due to EISA standards | per bulb | 0.004 | 23.9
1227 | Lighting | Interior Lighting | LED, screw base | LED - 12 W_SK: Kits | 12 W LED | 1 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per bulb | [10 empty] | 0 |  | 25 | 2016-18 |  |  |  | Kits |  | Savings is higher for the first four years when it drops due to EISA standards | per bulb | 0.004 | 25.8
1227 | Lighting | Interior Lighting | LED, screw base | LED - 12 W_SK: Kits | 12 W LED | 2 | Active | 2017-01-01 | [7 empty] | per bulb | [10 empty] | 0 |  | 25 | 2016-18 |  |  |  | Kits |  | Savings is higher for the first four years when it drops due to EISA standards | per bulb | 0.006 | 37.7
1227 | Lighting | Interior Lighting | LED, screw base | LED - 12 W_SK: Kits | 12 W LED | 3 | Proposed | 2018-01-01 | [7 empty] | per bulb | [10 empty] | 0 |  | 25 | 2016-18 |  |  |  | Kits |  | Savings is higher for the first four years when it drops due to EISA standards | per bulb | 0.004 | 30.0
1020 | Lighting | Interior Lighting | LED, screw base | LED - 12W Dimmable Light Bulb _SF: Low Income | LED 12W Dimmable Light Bulb Single Family | 1 | InActive | 2013-01-01 | 2015-12-30 | Incandescent Dimmable Bulb | 60.7 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Dimmable Light Bulb | watts | 12 | 12 watt LED Dimmable light bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 32.97 |  | 25 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.000 | 48.0
1020 | Lighting | Interior Lighting | LED, screw base | LED - 12W Dimmable Light Bulb _SF: Low Income | LED 12W Dimmable Light Bulb Single Family | 2 | Active | 2016-01-01 |  | Incandescent Dimmable Bulb | 60.7 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Dimmable Light Bulb | watts | 12 | 12 watt LED Dimmable light bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 | 2016-18 |  |  |  | Low Income |  |  | per bulb | 0.004 | 28
1020 | Lighting | Interior Lighting | LED, screw base | LED - 12W Dimmable Light Bulb _SF: Low Income | LED 12W Dimmable Light Bulb Single Family | 3 | Proposed | 2017-01-01 |  | Incandescent Dimmable Bulb | 60.7 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Dimmable Light Bulb | watts | 12 | 12 watt LED Dimmable light bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 |  |  |  |  | Low Income |  |  | per bulb | 0.004 | 24.9
891 | Lighting | Interior Lighting | LED, screw base | LED - 12W Dimmable Light Bulb : Home Energy Performance | LED 12W Dimmable Light Bulb | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Dimmable Bulb | 60.7 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Dimmable Light Bulb | watts | 12 | 12 watt LED Dimmable light bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 32.97 |  | 25 | 2013-15 |  |  |  | Home Energy Performance |  |  | per bulb | 0.000 | 48.0
891 | Lighting | Interior Lighting | LED, screw base | LED - 12W Dimmable Light Bulb : Home Energy Performance | LED 12W Dimmable Light Bulb | 2 | InActive |  |  | Incandescent Dimmable Bulb | 60.7 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Dimmable Light Bulb | watts | 12 | 12 watt LED Dimmable light bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 32.97 |  | 25 |  |  |  |  | Home Energy Performance |  |  | per bulb | 0.000 | 43.1
963 | Lighting | Interior Lighting | LED, screw base | LED - 12W Dimmable Light Bulb : Lighting | LED 12W Dimmable Light Bulb | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Dimmable Bulb | 60.7 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Dimmable Light Bulb | watts | 12 | 12 watt LED Dimmable light bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 32.97 |  | 25 | 2013-15 |  |  |  | Lighting |  |  | per bulb | 0.000 | 48.0
963 | Lighting | Interior Lighting | LED, screw base | LED - 12W Dimmable Light Bulb : Lighting | LED 12W Dimmable Light Bulb | 2 | InActive | 2016-01-01 | 2016-12-31 | 43 W EISA Compliant Light Bulb |  |  |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | 12W LED Dimmable Light Bulb | [5 empty] | Algorithm |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.004 | 28
963 | Lighting | Interior Lighting | LED, screw base | LED - 12W Dimmable Light Bulb : Lighting | LED 12W Dimmable Light Bulb | 3 | Active | 2017-01-01 | [6 empty] | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | [6 empty] | Algorithm |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.012 | 77.7
1086 | Lighting | Interior Lighting | LED, screw base | LED - 12W Dimmable Light Bulb : New Home Construction | LED 12W Dimmable Light Bulb | 1 | InActive | 2013-01-02 | 2014-12-31 | Incandescent Dimmable Bulb | 60.7 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Dimmable Light Bulb | watts | 12 | 12 watt LED Dimmable light bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 32.97 |  | 25 | 2013-15 |  |  |  | New Home Construction |  |  | per bulb | 0.000 | 48.0
1021 | Lighting | Interior Lighting | LED, screw base | LED - 12W Dimmable Light Bulb_MF: Low Income | LED 12W Dimmable Light Bulb Multi Family | 1 | InActive | 2013-01-01 | 2015-12-30 | Incandescent Dimmable Bulb | 60.7 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Dimmable Light Bulb | watts | 12 | 12 watt LED Dimmable light bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 32.97 |  | 25 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.000 | 48.0
1021 | Lighting | Interior Lighting | LED, screw base | LED - 12W Dimmable Light Bulb_MF: Low Income | LED 12W Dimmable Light Bulb Multi Family | 2 | InActive | 2016-01-01 | 2016-12-31 | Incandescent Dimmable Bulb | 60.7 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Dimmable Light Bulb | watts | 12 | 12 watt LED Dimmable light bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 | 2016-18 |  |  |  | Low Income |  |  | per bulb | 0.004 | 28
1021 | Lighting | Interior Lighting | LED, screw base | LED - 12W Dimmable Light Bulb_MF: Low Income | LED 12W Dimmable Light Bulb Multi Family | 3 | Active | 2017-01-01 |  | Incandescent Dimmable Bulb | 60.7 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Dimmable Light Bulb | watts | 12 | 12 watt LED Dimmable light bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 | 2016-18 |  |  |  | Low Income |  |  | per bulb | 0.003 | 22.8
1022 | Lighting | Interior Lighting | LED, screw base | LED - 15W Flood Light PAR30 Bulb (Post-EISA)_MF: Low Income | LED 15W Flood Light PAR30 Bulb POST-EISA Multi Family | 1 | InActive | 2013-01-01 | 2015-12-30 | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR30 Bulb POST-EISA | watts | 15 | 15 watt LED flood PAR30 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 5.97 |  | 25 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.000 | 35.0
1023 | Lighting | Interior Lighting | LED, screw base | LED - 15W Flood Light PAR30 Bulb (Post-EISA)_SF: Low Income | LED 15W Flood Light PAR30 Bulb POST-EISA Single Family | 1 | InActive | 2013-01-01 | 2015-12-30 | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR30 Bulb POST-EISA | watts | 15 | 15 watt LED flood PAR30 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 5.97 |  | 25 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.000 | 35.0
892 | Lighting | Interior Lighting | LED, screw base | LED - 15W Flood Light PAR30 Bulb (Post-EISA): Home Energy Performance | LED 15W Flood Light PAR30 Bulb POST-EISA | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR30 Bulb POST-EISA | watts | 15 | 15 watt LED flood PAR30 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 5.97 |  | 25 | 2013-15 |  |  |  | Home Energy Performance |  |  | per bulb | 0.000 | 35.0
892 | Lighting | Interior Lighting | LED, screw base | LED - 15W Flood Light PAR30 Bulb (Post-EISA): Home Energy Performance | LED 15W Flood Light PAR30 Bulb POST-EISA | 2 | InActive |  |  | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR30 Bulb POST-EISA | watts | 15 | 15 watt LED flood PAR30 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 5.97 |  | 25 |  |  |  |  | Home Energy Performance |  |  | per bulb | 0.000 | 31.5
964 | Lighting | Interior Lighting | LED, screw base | LED - 15W Flood Light PAR30 Bulb (POST-EISA): Lighting | LED 15W Flood Light PAR30 Bulb POST-EISA | 1 | InActive | 2013-01-01 | 2015-12-30 | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR30 Bulb POST-EISA | watts | 15 | 15 watt LED flood PAR30 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 5.97 |  | 25 | 2013-15 |  |  |  | Lighting |  |  | per bulb | 0.0 | 28.1
1087 | Lighting | Interior Lighting | LED, screw base | LED - 15W Flood Light PAR30 Bulb (Post-EISA): New Home Construction | LED 15W Flood Light PAR30 Bulb POST-EISA | 1 | InActive | 2013-01-02 | 2014-12-31 | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR30 Bulb POST-EISA | watts | 15 | 15 watt LED flood PAR30 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 5.97 |  | 25 | 2013-15 |  |  |  | New Home Construction |  |  | per bulb | 0.000 | 35.0
1022 | Lighting | Interior Lighting | LED, screw base | LED - 15W Flood Light PAR30 Bulb_MF: Low Income | LED 15W Flood Light PAR30 Bulb POST-EISA Multi Family | 2 | InActive | 2016-01-01 | 2016-12-31 | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR30 Bulb POST-EISA | watts | 15 | 15 watt LED flood PAR30 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 | 2016-18 |  |  |  | Low Income |  |  | per bulb | 0.005 | 33.5
1022 | Lighting | Interior Lighting | LED, screw base | LED - 15W Flood Light PAR30 Bulb_MF: Low Income | LED 15W Flood Light PAR30 Bulb POST-EISA Multi Family | 3 | Active | 2017-01-01 |  | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR30 Bulb POST-EISA | watts | 15 | 15 watt LED flood PAR30 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 | 2016-18 |  |  |  | Low Income |  |  | per bulb | 0.005 | 31.5
1023 | Lighting | Interior Lighting | LED, screw base | LED - 15W Flood Light PAR30 Bulb_SF: Low Income | LED 15W Flood Light PAR30 Bulb POST-EISA Single Family | 2 | Active | 2016-01-01 |  | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR30 Bulb POST-EISA | watts | 15 | 15 watt LED flood PAR30 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 | 2016-18 |  |  |  | Low Income |  |  | per bulb | 0.005 | 33.5
1023 | Lighting | Interior Lighting | LED, screw base | LED - 15W Flood Light PAR30 Bulb_SF: Low Income | LED 15W Flood Light PAR30 Bulb POST-EISA Single Family | 3 | Proposed | 2017-01-01 |  | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR30 Bulb POST-EISA | watts | 15 | 15 watt LED flood PAR30 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 |  |  |  |  | Low Income |  |  | per bulb | 0.004 | 28.1
964 | Lighting | Interior Lighting | LED, screw base | LED - 15W Flood Light PAR30 Bulb: Lighting | LED 15W Flood Light PAR30 Bulb | 2 | InActive | 2016-01-01 | 2016-12-31 | 50W Incandescent flood light bulb |  |  |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | 15W LED Flood Light Bulb | [5 empty] | Algorithm |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.005 | 33.5
964 | Lighting | Interior Lighting | LED, screw base | LED - 15W Flood Light PAR30 Bulb: Lighting | LED 15W Flood Light PAR30 Bulb | 3 | Active | 2017-01-01 | [6 empty] | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | [6 empty] | Algorithm |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.009 | 60.1
1205 | Lighting | Interior Lighting | LED, screw base | LED - 15W: Lighting | 15W LED | 1 | InActive | 2016-01-01 | 2016-12-31 | 53W EISA Compliant Bulb |  |  | 0 | 33 |  | per bulb |  | 15W LED Light |  |  |  | 0 | 9 |  |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.005 | 33.5
1205 | Lighting | Interior Lighting | LED, screw base | LED - 15W: Lighting | 15W LED | 2 | Active | 2017-01-01 |  |  |  |  | 0 | 33 |  | per bulb | [5 empty] | 0 | 9 |  |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.007 | 50.0
1024 | Lighting | Interior Lighting | LED, screw base | LED - 18W Flood Light PAR38 Bulb (Post-EISA)_MF: Low Income | LED 18W Flood PAR38 Bulb POST-EISA Multi Family | 1 | InActive | 2013-01-01 | 2015-12-30 | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR38 Bulb POST-EISA | watts | 18 | 18 watt LED flood PAR38 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 7.97 |  | 25 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.000 | 32.0
1025 | Lighting | Interior Lighting | LED, screw base | LED - 18W Flood Light PAR38 Bulb (Post-EISA)_SF: Low Income | LED 18W Flood PAR38 Bulb POST-EISA Single Family | 1 | InActive | 2013-01-01 | 2015-12-30 | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR38 Bulb POST-EISA | watts | 18 | 18 watt LED flood PAR38 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 7.97 |  | 25 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.000 | 32.0
893 | Lighting | Interior Lighting | LED, screw base | LED - 18W Flood Light PAR38 Bulb (Post-EISA): Home Energy Performance | LED 18W Flood PAR38 Bulb POST-EISA | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR38 Bulb POST-EISA | watts | 18 | 18 watt LED flood PAR38 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 7.97 |  | 25 | 2013-15 |  |  |  | Home Energy Performance |  |  | per bulb | 0.000 | 32.0
893 | Lighting | Interior Lighting | LED, screw base | LED - 18W Flood Light PAR38 Bulb (Post-EISA): Home Energy Performance | LED 18W Flood PAR38 Bulb POST-EISA | 2 | InActive |  |  | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR38 Bulb POST-EISA | watts | 18 | 18 watt LED flood PAR38 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 7.97 |  | 25 |  |  |  |  | Home Energy Performance |  |  | per bulb | 0.000 | 28.8
965 | Lighting | Interior Lighting | LED, screw base | LED - 18W Flood Light PAR38 Bulb (POST-EISA): Lighting | LED 18W Flood PAR38 Bulb POST-EISA | 1 | InActive | 2013-01-01 | 2015-12-30 | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR38 Bulb POST-EISA | watts | 18 | 18 watt LED flood PAR38 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 7.97 |  | 25 | 2013-15 |  |  |  | Lighting |  |  | per bulb | 0.0 | 32.0
1088 | Lighting | Interior Lighting | LED, screw base | LED - 18W Flood Light PAR38 Bulb (Post-EISA): New Home Construction | LED 18W Flood PAR38 Bulb POST-EISA | 1 | InActive | 2013-01-02 | 2014-12-31 | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR38 Bulb POST-EISA | watts | 18 | 18 watt LED flood PAR38 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 7.97 |  | 25 | 2013-15 |  |  |  | New Home Construction |  |  | per bulb | 0.000 | 32.0
1024 | Lighting | Interior Lighting | LED, screw base | LED - 18W Flood Light PAR38 Bulb_MF: Low Income | LED 18W Flood PAR38 Bulb POST-EISA Multi Family | 2 | InActive | 2016-01-01 | 2016-12-31 | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR38 Bulb POST-EISA | watts | 18 | 18 watt LED flood PAR38 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 | 2016-18 |  |  |  | Low Income |  |  | per bulb | 0.005 | 33.5
1024 | Lighting | Interior Lighting | LED, screw base | LED - 18W Flood Light PAR38 Bulb_MF: Low Income | LED 18W Flood PAR38 Bulb POST-EISA Multi Family | 3 | Active | 2017-01-01 |  | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR38 Bulb POST-EISA | watts | 18 | 18 watt LED flood PAR38 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 | 2016-18 |  |  |  | Low Income |  |  | per bulb | 0.004 | 29.8
1025 | Lighting | Interior Lighting | LED, screw base | LED - 18W Flood Light PAR38 Bulb_SF: Low Income | LED 18W Flood PAR38 Bulb POST-EISA Single Family | 2 | Active | 2016-01-01 |  | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR38 Bulb POST-EISA | watts | 18 | 18 watt LED flood PAR38 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 | 2016-18 |  |  |  | Low Income |  |  | per bulb | 0.005 | 33.5
1025 | Lighting | Interior Lighting | LED, screw base | LED - 18W Flood Light PAR38 Bulb_SF: Low Income | LED 18W Flood PAR38 Bulb POST-EISA Single Family | 3 | Proposed | 2017-01-01 |  | Incandescent Flood Light Bulb | 50.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Flood PAR38 Bulb POST-EISA | watts | 18 | 18 watt LED flood PAR38 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 |  |  |  |  | Low Income |  |  | per bulb | 0.004 | 25.7
965 | Lighting | Interior Lighting | LED, screw base | LED - 18W Flood Light PAR38 Bulb: Lighting | LED 18W Flood PAR38 Bulb | 2 | InActive | 2016-01-01 | 2016-12-31 | 50W Incandescent Flood Light Bulb |  |  |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | 18W LED Flood Light Bulb | [5 empty] | Algorithm |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.005 | 33.5
965 | Lighting | Interior Lighting | LED, screw base | LED - 18W Flood Light PAR38 Bulb: Lighting | LED 18W Flood PAR38 Bulb | 3 | Active | 2017-01-01 | [6 empty] | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | [6 empty] | Algorithm |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.013 | 88.2
1206 | Lighting | Interior Lighting | LED, screw base | LED - 20W: Lighting | 20W LED | 1 | InActive | 2016-01-01 | 2016-12-31 | 72W EISA Compliant Bulb |  |  | 0 | 49 |  | per bulb |  | 20W LED Light Bulb |  |  |  | 0 | 10 |  |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.008 | 51
1206 | Lighting | Interior Lighting | LED, screw base | LED - 20W: Lighting | 20W LED | 2 | Active | 2017-01-01 |  |  |  |  | 0 | 49 |  | per bulb | [5 empty] | 0 | 10 |  |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.0126 | 66.5
1231 | Lighting | Interior Lighting | LED, screw base | LED - 4W Candelabra: Lighting | 4W LED Candelabra | 1 | InActive | 2016-01-01 | 2016-12-31 | 40W Candelabra | [5 empty] | per bulb |  | 4W LED | [8 empty] | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.004 | 26.4
1231 | Lighting | Interior Lighting | LED, screw base | LED - 4W Candelabra: Lighting | 4W LED Candelabra | 2 | Active | 2017-01-01 | [7 empty] | per bulb | [10 empty] | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.006 | 42
1026 | Lighting | Interior Lighting | LED, screw base | LED - 8W Globe Light G25 Bulb_MF: Low Income | LED 8W Globe G25 Bulb Multi Family | 1 | InActive | 2013-01-01 | 2015-12-30 | Incandescent Globe Light Bulb | 40.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Globe G25 Bulb | watts | 8 | 8 watt LED Globe G25 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 22.97 |  | 25 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.000 | 32.0
1026 | Lighting | Interior Lighting | LED, screw base | LED - 8W Globe Light G25 Bulb_MF: Low Income | LED 8W Globe G25 Bulb Multi Family | 2 | InActive | 2016-01-01 | 2016-12-31 | Incandescent Globe Light Bulb | 40.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Globe G25 Bulb | watts | 8 | 8 watt LED Globe G25 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 | 2016-18 |  |  |  | Low Income |  |  | per bulb | 0.005 | 33.5
1026 | Lighting | Interior Lighting | LED, screw base | LED - 8W Globe Light G25 Bulb_MF: Low Income | LED 8W Globe G25 Bulb Multi Family | 3 | Active | 2017-01-01 |  | Incandescent Globe Light Bulb | 40.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Globe G25 Bulb | watts | 8 | 8 watt LED Globe G25 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 | 2016-18 |  |  |  | Low Income |  |  | per bulb | 0.002 | 12.8
1027 | Lighting | Interior Lighting | LED, screw base | LED - 8W Globe Light G25 Bulb_SF: Low Income | LED 8W Globe G25 Bulb Single Family | 1 | InActive | 2013-01-01 | 2015-12-30 | Incandescent Globe Light Bulb | 40.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Globe G25 Bulb | watts | 8 | 8 watt LED Globe G25 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 22.97 |  | 25 | 2013-15 |  |  |  | Low Income |  |  | per bulb | 0.000 | 32.0
1027 | Lighting | Interior Lighting | LED, screw base | LED - 8W Globe Light G25 Bulb_SF: Low Income | LED 8W Globe G25 Bulb Single Family | 2 | Active | 2016-01-01 |  | Incandescent Globe Light Bulb | 40.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Globe G25 Bulb | watts | 8 | 8 watt LED Globe G25 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 | 2016-18 |  |  |  | Low Income |  |  | per bulb | 0.005 | 33.5
1027 | Lighting | Interior Lighting | LED, screw base | LED - 8W Globe Light G25 Bulb_SF: Low Income | LED 8W Globe G25 Bulb Single Family | 3 | Proposed | 2017-01-01 |  | Incandescent Globe Light Bulb | 40.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Globe G25 Bulb | watts | 8 | 8 watt LED Globe G25 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 0 |  | 25 |  |  |  |  | Low Income |  |  | per bulb | 0.003 | 17.7
894 | Lighting | Interior Lighting | LED, screw base | LED - 8W Globe Light G25 Bulb: Home Energy Performance | LED 8W Globe G25 Bulb | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Globe Light Bulb | 40.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Globe G25 Bulb | watts | 8 | 8 watt LED Globe G25 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 22.97 |  | 25 | 2013-15 |  |  |  | Home Energy Performance |  |  | per bulb | 0.000 | 32.0
894 | Lighting | Interior Lighting | LED, screw base | LED - 8W Globe Light G25 Bulb: Home Energy Performance | LED 8W Globe G25 Bulb | 2 | InActive |  |  | Incandescent Globe Light Bulb | 40.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Globe G25 Bulb | watts | 8 | 8 watt LED Globe G25 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 22.97 |  | 25 |  |  |  |  | Home Energy Performance |  |  | per bulb | 0.000 | 29.0
966 | Lighting | Interior Lighting | LED, screw base | LED - 8W Globe Light G25 Bulb: Lighting | LED 8W Globe G25 Bulb | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Globe Light Bulb | 40.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Globe G25 Bulb | watts | 8 | 8 watt LED Globe G25 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 22.97 |  | 25 | 2013-15 |  |  |  | Lighting |  |  | per bulb | 0.000 | 32.0
966 | Lighting | Interior Lighting | LED, screw base | LED - 8W Globe Light G25 Bulb: Lighting | LED 8W Globe G25 Bulb | 2 | InActive | 2016-01-01 | 2016-12-31 | 72W EISA Compliant Bulb |  |  |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | 8W LED Globe Light | [5 empty] | Algorithm |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.005 | 33.5
966 | Lighting | Interior Lighting | LED, screw base | LED - 8W Globe Light G25 Bulb: Lighting | LED 8W Globe G25 Bulb | 3 | Active | 2017-01-01 | [6 empty] | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | [6 empty] | Algorithm |  |  | 0 |  | 25 | 2016-18 |  |  |  | Lighting |  | ISR increased from 94% in evaluation to 96% for LEDs vs CFLs and single packs vs multi packs | per bulb | 0.006 | 42.8
1089 | Lighting | Interior Lighting | LED, screw base | LED - 8W Globe Light G25 Bulb: New Home Construction | LED 8W Globe G25 Bulb | 1 | InActive | 2013-01-02 | 2014-12-31 | Incandescent Globe Light Bulb | 40.5 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per bulb | Algorithm | LED Globe G25 Bulb | watts | 8 | 8 watt LED Globe G25 bulb |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. |  | 22.97 |  | 25 | 2013-15 |  |  |  | New Home Construction |  |  | per bulb | 0.000 | 32.0
903 | Whole Home | Home Audit | Level 1 | Level 1 Home Audit: Home Energy Performance | Energy Audit | 1 | InActive | 2013-01-02 | 2015-12-31 | N/A | [5 empty] | per home | Algorithm | [6 empty] | Algorithm |  |  | 400 |  | 1 | 2013-15 |  |  |  | Home Energy Performance |  |  | per home | 0.000 | 0.0
904 | Whole Home | Home Audit | Level 2 | Level 2 Home Audit: Home Energy Performance | Energy Audit | 1 | InActive | 2013-01-02 | 2015-12-31 | N/A | [5 empty] | per home | Algorithm | [6 empty] | Algorithm |  |  | 400 |  | 1 | 2013-15 |  |  |  | Home Energy Performance |  |  | per home | 0.000 | 0.0
1033 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator _MF: Low Income | Low Flow Faucet Aerator for MultiFamily | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per home | Algorithm | Low Flow Faucet Aerator for Low Income Multifamily dwelling | GPM | 1.5 | Multifamily low income unit installation, minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 9.5 |  | 12 | 2013-15 |  |  |  | Low Income |  | The energy savings equation for low flow faucet aerator was taken from Ameren Missouri’s Multifamily PY2 Report. If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per home | 0.000 | 37.2
1033 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator _MF: Low Income | Low Flow Faucet Aerator for MultiFamily | 2 | InActive | 2016-01-01 | 2016-12-31 | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per measure | Algorithm | Low Flow Faucet Aerator for Low Income Multifamily dwelling | GPM | 1.5 | Multifamily low income unit installation, minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 14 |  | 12 | 2016-18 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.003 | 39
1033 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator _MF: Low Income | Low Flow Faucet Aerator for MultiFamily | 3 | Active | 2017-01-01 |  | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per measure | Algorithm | Low Flow Faucet Aerator for Low Income Multifamily dwelling | GPM | 1.5 | Multifamily low income unit installation, minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 14 |  | 12 | 2016-18 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.004 | 42
1034 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator _SF: Low Income | Low Flow Faucet Aerator for Single Family | 1 | InActive | 2013-01-01 | 2015-12-30 | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per measure | Algorithm | Low Flow Faucet Aerator for Single family dwelling | GPM | 1.5 | Single family dwelling installation, minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 9.5 |  | 12 | 2013-15 |  |  |  | Low Income |  | The energy savings equation for low flow faucet aerator was taken from Ameren Missouri’s Multifamily PY2 Report. If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.016 | 57.0
1034 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator _SF: Low Income | Low Flow Faucet Aerator for Single Family | 2 | Active | 2016-01-01 |  | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per measure | Algorithm | Low Flow Faucet Aerator for Single family dwelling | GPM | 1.5 | Single family dwelling installation, minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 16 |  | 12 | 2016-18 |  |  |  | Low Income |  | The energy savings equation for low flow faucet aerator was taken from Ameren Missouri’s Multifamily PY2 Report. If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.005 | 57
1034 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator _SF: Low Income | Low Flow Faucet Aerator for Single Family | 3 | Proposed | 2017-01-01 |  | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per measure | Algorithm | Low Flow Faucet Aerator for Single family dwelling | GPM | 1.5 | Single family dwelling installation, minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 14 |  | 12 |  |  |  |  | Low Income |  | The energy savings equation for low flow faucet aerator was taken from Ameren Missouri’s Multifamily PY2 Report. If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.003 | 36.6
865 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator - Bathroom_MF: Kits | Low Flow Faucet Aerator for MultiFamily Bathroom | 3 | Active | 2017-01-01 |  | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per measure | Algorithm | Low Flow Faucet Aerator for Multifamily dwelling | GPM | 1.5 | Multifamily unit installation, minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 2.5 |  | 12 | 2016-18 |  |  |  | Kits |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.003 | 38
1228 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator - Bathroom_SK: Kits | Low Flow Faucet Aerator | 2 | Active | 2017-01-01 |  | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per measure | Algorithm | Low Flow Faucet Aerator for Single family dwelling | GPM | 1.5 | Minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 2.5 |  | 12 | 2016-18 |  |  |  | Kits |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.002 | 22.1
1228 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator - Bathroom_SK: Kits | Low Flow Faucet Aerator | 3 | Proposed | 2018-01-01 |  | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per measure | Algorithm | Low Flow Faucet Aerator for Single family dwelling | GPM | 1.5 | Minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 2.5 |  | 12 | 2016-18 |  |  |  | Kits |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.002 | 23.1
865 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator - Electric water heater _MF: Efficient Products | Low Flow Faucet Aerator for MultiFamily | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per home | Algorithm | Low Flow Faucet Aerator for Multifamily dwelling | GPM | 1.5 | Multifamily unit installation, minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 9.5 |  | 12 | 2013-15 |  |  |  | Efficient Products |  | The energy savings equation for low flow faucet aerator was taken from Ameren Missouri’s Multifamily PY2 Report. If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per home | 0 | 37.2
865 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator - Electric water heater _MF: Kits | Low Flow Faucet Aerator for MultiFamily | 2 | InActive | 2016-01-01 | 2016-12-31 | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per measure | Algorithm | Low Flow Faucet Aerator for Multifamily dwelling | GPM | 1.5 | Multifamily unit installation, minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 2.5 |  | 12 | 2016-18 |  |  |  | Kits |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.003 | 39
1164 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator - Electric water heater_MF: Home Energy Performance | Low Flow Faucet Aerator | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per home | Algorithm | Low Flow Faucet Aerator for Single family dwelling | GPM | 1.5 | Minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 9.5 |  | 12 | 2013-15 |  |  |  | Home Energy Performance |  | The energy savings equation for low flow faucet aerator was taken from Ameren Missouri’s Multifamily PY2 Report. If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per home | 0.000 | 37.0
864 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator - Electric water heater_SF: Efficient Products | Low Flow Faucet Aerator | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per home | Algorithm | Low Flow Faucet Aerator for Single family dwelling | GPM | 1.5 | Minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 9.5 |  | 12 | 2013-15 |  |  |  | Efficient Products |  | The energy savings equation for low flow faucet aerator was taken from Ameren Missouri’s Multifamily PY2 Report. If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per home | 0.016 | 57.0
897 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator - Electric water heater_SF: Home Energy Performance | Low Flow Faucet Aerator | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per home | Algorithm | Low Flow Faucet Aerator for Single family dwelling | GPM | 1.5 | Minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 9.5 |  | 12 | 2013-15 |  |  |  | Home Energy Performance |  | The energy savings equation for low flow faucet aerator was taken from Ameren Missouri’s Multifamily PY2 Report. If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per home | 0.016 | 57.0
864 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator - Electric water heater_SF: Kits | Low Flow Faucet Aerator | 2 | InActive | 2016-01-01 | 2016-12-31 | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per measure | Algorithm | Low Flow Faucet Aerator for Single family dwelling | GPM | 1.5 | Minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 2.5 |  | 12 | 2016-18 |  |  |  | Kits |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.003 | 39
864 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator - Electric water heater_SF: Kits | Low Flow Faucet Aerator | 4 | Active | 2017-01-01 |  | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per measure | Algorithm | Low Flow Faucet Aerator for Single family dwelling | GPM | 1.5 | Minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 2.5 |  | 12 | 2016-18 |  |  |  | Kits |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.002 | 20.3
1228 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator - Electric water heater_SK: Kits | Low Flow Faucet Aerator | 1 | InActive | 2016-01-01 | 2016-12-31 | Standard faucet flow of 2.2 gpm | 2.2 | GPM |  |  |  | per measure | Algorithm | Low Flow Faucet Aerator for Single family dwelling | GPM | 1.5 | Minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 2.5 |  | 12 | 2016-18 |  |  |  | Kits |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.003 | 39
1273 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator - Kitchen_MF: Kits | Low Flow Faucet Aerator - Kitchen_MF: Kits | 1 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 2.5 |  | 12 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.007 | 78.3
1274 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator - Kitchen_SK: Kits | Low Flow Faucet Aerator - Kitchen_SK: Kits | 1 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 2.5 |  | 12 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.007 | 79.7
1274 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator - Kitchen_SK: Kits | Low Flow Faucet Aerator - Kitchen_SK: Kits | 2 | Proposed | 2018-01-01 | 2018-12-31 | [6 empty] | per measure | [10 empty] | 2.5 |  | 12 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.004 | 44.5
1262 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator_LI: Kits | Low Flow Faucet Aerator | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 3 |  | 12 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.003 | 39
1201 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Shower Aerator_MF: Kits | Low Flow Shower Aerator_MF | 1 | InActive | [8 empty] | per measure | [10 empty] | 4 |  | 12 |  |  |  |  | Kits |  |  | per measure | 0 | 25.6
1200 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Shower Aerator_SF: Kits | Low Flow Shower Aerator_SF | 1 | InActive | [8 empty] | per measure | [10 empty] | 4 |  | 12 |  |  |  |  | Kits |  |  | per measure | .016 | 28.5
1261 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead - Electric water heater_LI: Kits | Low Flow Showerhead - Electric water heater | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 9 |  | 12 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.019 | 218
867 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead - Electric water heater_MF: Efficient Products | Low Flow Showerhead for Multifamily | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard showerhead flow | [5 empty] | per measure | Algorithm | Low Flow showerhead for multifamily dwelling |  |  | Installad in multifamily unit |  |  | Algorithm |  |  | 31.6 |  | 12 | 2013-15 |  |  |  | Efficient Products |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per measure | 0.000 | 203.7
1166 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead - Electric water heater_MF: Home Energy Performance | Low flow showerhead with electric water heater | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard showerhead flow | [5 empty] | per unit | Algorithm | Low Flow showerhead |  |  | Must have electric water heater |  |  | Algorithm |  |  | 31.6 |  | 12 | 2013-15 |  |  |  | Home Energy Performance |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per measure | 0.000 | 204.0
867 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead - Electric water heater_MF: Kits | Low Flow Showerhead for Multifamily | 2 | InActive | 2016-01-01 | 2016-12-31 | Standard showerhead flow | [5 empty] | per measure | Algorithm | Low Flow showerhead for multifamily dwelling |  |  | Installad in multifamily unit |  |  | Algorithm |  |  | 9 |  | 12 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.019 | 218
867 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead - Electric water heater_MF: Kits | Low Flow Showerhead for Multifamily | 3 | Active | 2017-01-01 |  | Standard showerhead flow | [5 empty] | per measure | Algorithm | Low Flow showerhead for multifamily dwelling |  |  | Installad in multifamily unit |  |  | Algorithm |  |  | 9 |  | 12 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.018 | 206.2
866 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead - Electric water heater_SF: Efficient Products | Low flow showerhead with electric water heater | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard showerhead flow | [5 empty] | per unit | Algorithm | Low Flow showerhead |  |  | Must have electric water heater |  |  | Algorithm |  |  | 31.6 |  | 12 | 2013-15 |  |  |  | Efficient Products |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per measure | 0.048 | 361.0
898 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead - Electric water heater_SF: Home Energy Performance | Low flow showerhead with electric water heater | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard showerhead flow | [5 empty] | per unit | Algorithm | Low Flow showerhead |  |  | Must have electric water heater |  |  | Algorithm |  |  | 31.6 |  | 12 | 2013-15 |  |  |  | Home Energy Performance |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per measure | 0.048 | 361.0
866 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead - Electric water heater_SF: Kits | Low flow showerhead with electric water heater | 2 | InActive | 2016-01-01 | 2016-12-31 | Standard showerhead flow | [5 empty] | per measure | Algorithm | Low Flow showerhead |  |  | Must have electric water heater |  |  | Algorithm |  |  | 9 |  | 12 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.019 | 218
866 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead - Electric water heater_SF: Kits | Low flow showerhead with electric water heater | 3 | Active | 2017-01-01 |  | Standard showerhead flow | [5 empty] | per measure | Algorithm | Low Flow showerhead |  |  | Must have electric water heater |  |  | Algorithm |  |  | 9 |  | 12 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.009 | 104.3
1229 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead - Electric water heater_SK: Kits | Low flow showerhead with electric water heater | 1 | InActive | 2016-01-01 | 2016-12-31 | Standard showerhead flow | [5 empty] | per measure | Algorithm | Low Flow showerhead |  |  | Must have electric water heater |  |  | Algorithm |  |  | 9 |  | 12 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.019 | 218
1229 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead - Electric water heater_SK: Kits | Low flow showerhead with electric water heater | 2 | Active | 2017-01-01 |  | Standard showerhead flow | [5 empty] | per measure | Algorithm | Low Flow showerhead |  |  | Must have electric water heater |  |  | Algorithm |  |  | 9 |  | 12 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.016 | 181.6
1229 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead - Electric water heater_SK: Kits | Low flow showerhead with electric water heater | 3 | Proposed | 2018-01-01 |  | Standard showerhead flow | [5 empty] | per measure | Algorithm | Low Flow showerhead |  |  | Must have electric water heater |  |  | Algorithm |  |  | 9 |  | 12 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.006 | 72.4
1035 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead_MF: Low Income | Low Flow Showerhead for Multifamily | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard showerhead flow | [5 empty] | per measure | Algorithm | Low Flow showerhead for multifamily dwelling |  |  | Installad in multifamily unit |  |  | Algorithm |  |  | 31.6 |  | 12 | 2013-15 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per measure | 0.000 | 203.7
1035 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead_MF: Low Income | Low Flow Showerhead for Multifamily | 2 | InActive | 2016-01-01 | 2016-12-31 | Standard showerhead flow | [5 empty] | per measure | Algorithm | Low Flow showerhead for multifamily dwelling |  |  | Installad in multifamily unit |  |  | Algorithm |  |  | 42 |  | 12 | 2016-18 |  |  |  | Low Income |  |  | per measure | 0.019 | 218
1035 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead_MF: Low Income | Low Flow Showerhead for Multifamily | 3 | Active | 2017-01-01 |  | Standard showerhead flow | [5 empty] | per measure | Algorithm | Low Flow showerhead for multifamily dwelling |  |  | Installad in multifamily unit |  |  | Algorithm |  |  | 42 |  | 12 | 2016-18 |  |  |  | Low Income |  |  | per measure | 0.018 | 202.4
1036 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead_SF: Low Income | Low Flow Showerhead for Single Family | 1 | InActive | 2013-01-01 | 2015-12-30 | Standard showerhead flow | [5 empty] | per measure | Algorithm | Low Flow showerhead for single family dwelling |  |  | Installed in single family dwelling |  |  | Algorithm |  |  | 31.6 |  | 12 | 2013-15 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per measure | 0.048 | 361.0
1036 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead_SF: Low Income | Low Flow Showerhead for Single Family | 2 | Active | 2016-01-01 |  | Standard showerhead flow | [5 empty] | per measure | Algorithm | Low Flow showerhead for single family dwelling |  |  | Installed in single family dwelling |  |  | Algorithm |  |  | 42 |  | 12 | 2016-18 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per measure | 0.032 | 361
1036 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead_SF: Low Income | Low Flow Showerhead for Single Family | 3 | Proposed | 2017-01-01 |  | Standard showerhead flow | [5 empty] | per measure | Algorithm | Low Flow showerhead for single family dwelling |  |  | Installed in single family dwelling |  |  | Algorithm |  |  | 42 |  | 12 |  |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per measure | 0.028 | 318.4
953 | Lighting | Exterior Lighting | Metal Halide | Metal Halide Outdoor Lighting: Lighting | Metal Halide Outdoor Lighting | 1 | InActive | 2013-01-01 | 2015-12-30 | Incandescent Outdoor Lighting | 100 | watts |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per measure | Algorithm | Metal Halide Outdoor Lighting | watts | 35 | Metal Halide Outdoor Lighting |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. The following table summarizes individual measure level energy savings, demand savings, incremental cost, and effective useful life. |  | 112 |  | 15 | 2013-15 |  |  |  | Lighting |  |  | per measure | 0.000 | 190.0
967 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensor: Lighting | Occupancy Sensor | 1 | InActive | 2013-01-02 | 2015-12-31 | No Sensor | N/A |  |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per measure | Algorithm | Occupancy Sensor |  | N/A | Occupancy Sensor |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. The following table summarizes individual measure level energy savings, demand savings, incremental cost, and effective useful life. |  | 61 |  | 10 | 2013-15 |  |  |  | Lighting |  | Morgan was edited to include HID data from GEP. This demand came from the loadshape since it was not accounted for in Morgan. | per measure | 0.040 | 217.0
967 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensor: Lighting | Occupancy Sensor | 2 | InActive |  |  | No Sensor | N/A |  |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per measure | Algorithm | Occupancy Sensor |  | N/A | Occupancy Sensor |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. The following table summarizes individual measure level energy savings, demand savings, incremental cost, and effective useful life. |  | 61 |  | 10 |  |  |  |  | Lighting |  | Morgan was edited to include HID data from GEP. This demand came from the loadshape since it was not accounted for in Morgan. | per measure | 0.002 | 38.0
1090 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensor: New Home Construction | Occupancy Sensor | 1 | InActive | 2013-01-02 | 2014-12-31 | No Sensor | N/A |  |  |  | Incremental Cost is Negative when the Present Value of the Base and Efficient are compared | per measure | Algorithm | Occupancy Sensor |  | N/A | Occupancy Sensor |  |  | Algorithm | The baseline wattages reflect data gathered from evaluation contractors, which indicated customers replaced multiple baseline wattages with the efficient bulb. Example: in some instances, customers installing a 13 watt CFL would typically replace a 60 watt incandescent, but in certain cases, a 75 watt incandescent was replaced, or even a 40 watt incandescent was replaced. The EMV results are a blend of customer’s actual behavior. The following table summarizes individual measure level energy savings, demand savings, incremental cost, and effective useful life. |  | 61 |  | 10 | 2013-15 |  |  |  | New Home Construction |  | Morgan was edited to include HID data from GEP. This demand came from the loadshape since it was not accounted for in Morgan. | per measure | 0.040 | 217.0
942 | HVAC | HVAC O&M | Coil Cleaning | Outdoor Coil Cleaning: HVAC | Outdoor Coil Cleaning | 1 | InActive | 2013-01-02 | 2015-12-31 | Dirty coils | [5 empty] | per cleaning | Algorithm | Coil cleaning |  |  | Coil cleaning |  |  | Algorithm |  |  | 31 |  | 5 | 2013-15 |  |  |  | HVAC |  | Tons = 3.0 | per measure | 0.180 | 515.0
942 | HVAC | HVAC O&M | Coil Cleaning | Outdoor Coil Cleaning: HVAC | Outdoor Coil Cleaning | 2 | InActive | 2016-01-01 | 2016-12-31 | Dirty coils | [5 empty] | per cleaning | Algorithm | Coil cleaning |  |  | Coil cleaning |  |  | Algorithm |  |  | 31 |  | 5 | 2016-18 |  |  |  | HVAC |  | Tons = 3.0 | per measure | 0.066 | 140.6
942 | HVAC | HVAC O&M | Coil Cleaning | Outdoor Coil Cleaning: HVAC | Outdoor Coil Cleaning | 3 | Active | 2017-01-01 |  | Dirty coils | [5 empty] | per cleaning | Algorithm | Coil cleaning |  |  | Coil cleaning |  |  | Algorithm |  |  | 31 |  | 5 | 2016-18 |  |  |  | HVAC |  | Tons = 3.0 | per measure | 0.12 | 258
868 | Water Heating | Insulation | Pipe Insulation | Pipe Insulation_MF: Efficient Products | Pipe wrap/insulation for MF | 1 | InActive | 2013-01-02 | 2015-12-31 | Water Heater pipe wih no insulation | [5 empty] | per ft |  | Electric water heater pipe insulation for MF dwelling | [6 empty] | Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. |  | .67 |  | 6 | 2013-15 |  |  |  | Efficient Products |  | The energy savings equation for pipe wrap was taken from Ameren Missouri’s Multifamily PY2 Report. Delta kWh = Heat Loss ×Length of Pipe where: Heat Loss = heat loss of the baseline pipe per foot and Length of Pipe = length of pipe in feet. If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per ft | 0.029 | 28.0
1168 | Water Heating | Insulation | Pipe Insulation | Pipe Insulation_MF: Home Energy Performance | Pipe wrap/insulation for electric water heater | 1 | InActive | 2013-01-02 | 2015-12-31 | Water Heater pipe wih no insulation | [5 empty] | per measure | Algorithm | Electric Water Heater Pipe Insulation for Multifamily Dwelling |  |  | Electric water heater |  |  | Algorithm |  |  | 5 |  | 6 | 2013-15 |  |  |  | Home Energy Performance |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per measure | 0.000 | 28.0
868 | Water Heating | Insulation | Pipe Insulation | Pipe Insulation_MF: Kits | Pipe wrap/insulation for MF | 2 | InActive | 2016-01-01 | 2016-12-31 | Water Heater pipe wih no insulation | [5 empty] | per ft |  | Electric water heater pipe insulation for MF dwelling | [6 empty] | Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. |  | 0.42 |  | 6 | 2016-18 |  |  |  | Kits |  | Batchtool based on 12 feet | per ft | 0.002 | 21.4
868 | Water Heating | Insulation | Pipe Insulation | Pipe Insulation_MF: Kits | Pipe wrap/insulation for MF | 3 | Active | 2017-01-01 |  | Water Heater pipe wih no insulation | [5 empty] | per ft |  | Electric water heater pipe insulation for MF dwelling | [6 empty] | Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. |  | 0.67 |  | 6 | 2016-18 |  |  |  | Kits |  | Batchtool based on 12 feet | per ft | 0.002 | 22.7
1037 | Water Heating | Insulation | Pipe Insulation | Pipe Insulation_MF: Low Income | Pipe wrap/insulation for electric water heater in low income MF unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Water Heater pipe wih no insulation | [5 empty] | per measure | Algorithm | Electric water heater pipe insulation for MF dwelling |  |  | Electric water heater, low income MF unit |  |  | Algorithm |  |  | 5 |  | 6 | 2013-15 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per measure | 0.000 | 28.0
1037 | Water Heating | Insulation | Pipe Insulation | Pipe Insulation_MF: Low Income | Pipe wrap/insulation for electric water heater in low income MF unit | 2 | InActive | 2016-01-01 | 2016-12-31 | Water Heater pipe wih no insulation | [5 empty] | per ft | Algorithm | Electric water heater pipe insulation for MF dwelling |  |  | Electric water heater, low income MF unit |  |  | Algorithm |  |  | 1.5 |  | 6 | 2016-18 |  |  |  | Low Income |  |  | per ft | 0.002 | 23
1037 | Water Heating | Insulation | Pipe Insulation | Pipe Insulation_MF: Low Income | Pipe wrap/insulation for electric water heater in low income MF unit | 3 | Active | 2017-01-01 |  | Water Heater pipe wih no insulation | [5 empty] | per ft | Algorithm | Electric water heater pipe insulation for MF dwelling |  |  | Electric water heater, low income MF unit |  |  | Algorithm |  |  | 1.5 |  | 6 | 2016-18 |  |  |  | Low Income |  |  | per ft | 0.002 | 22.0
1167 | Water Heating | Insulation | Pipe Insulation | Pipe Insulation_SF: Efficient Products | Pipe wrap/insulation for electric water heater | 1 | InActive | 2013-01-02 | 2015-12-31 | Water Heater pipe wih no insulation | [5 empty] | per measure | Algorithm | Electric Water Heater Pipe Insulation for Multifamily Dwelling |  |  | Electric water heater |  |  | Algorithm |  |  | 5 |  | 6 | 2013-15 |  |  |  | Efficient Products |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per measure | 0.000 | 28.0
899 | Water Heating | Insulation | Pipe Insulation | Pipe Insulation_SF: Home Energy Performance | Pipe wrap/insulation for electric water heater in SF unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Water Heater pipe wih no insulation | [5 empty] | per measure | Algorithm | Electric Water Heater Tank Blanket Insulation, R-5 for Single Family Dwelling | r-value | 5 | Electric water heater, single family dwelling |  |  | Algorithm |  |  | 5 |  | 6 | 2013-15 |  |  |  | Home Energy Performance |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per measure | 0.029 | 257.0
1167 | Water Heating | Insulation | Pipe Insulation | Pipe Insulation_SF: Kits | Pipe wrap/insulation for electric water heater | 2 | InActive | 2016-01-01 | 2016-12-31 | Water Heater pipe wih no insulation | [5 empty] | per ft | Algorithm | Electric Water Heater Pipe Insulation for Multifamily Dwelling |  |  | Electric water heater |  |  | Algorithm |  |  | 0.42 |  | 6 | 2016-18 |  |  |  | Kits |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per ft | 0.002 | 21.4
1167 | Water Heating | Insulation | Pipe Insulation | Pipe Insulation_SF: Kits | Pipe wrap/insulation for electric water heater | 3 | Active | 2017-01-01 |  | Water Heater pipe wih no insulation | [5 empty] | per ft | Algorithm | Electric Water Heater Pipe Insulation for Multifamily Dwelling |  |  | Electric water heater |  |  | Algorithm |  |  | 0.42 |  | 6 | 2016-18 |  |  |  | Kits |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per ft | 0.001 | 10.7
1038 | Water Heating | Insulation | Pipe Insulation | Pipe Insulation_SF: Low Income | Pipe wrap/insulation for electric water heater in low income SF unit | 1 | InActive | 2013-01-01 | 2015-12-30 | Water Heater pipe wih no insulation | [5 empty] | per measure | Algorithm | Electric Water Heater Tank Blanket Insulation, R-5 for Single Family Dwelling | r-value | 5 | Electric water heater, low income single family dwelling |  |  | Algorithm |  |  | 5 |  | 6 | 2013-15 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per measure | 0.029 | 257.0
1038 | Water Heating | Insulation | Pipe Insulation | Pipe Insulation_SF: Low Income | Pipe wrap/insulation for electric water heater in low income SF unit | 2 | Active | 2016-01-01 |  | Water Heater pipe wih no insulation | [5 empty] | per ft | Algorithm | Electric Water Heater Tank Blanket Insulation, R-5 for Single Family Dwelling | r-value | 5 | Electric water heater, low income single family dwelling |  |  | Algorithm |  |  | 1.6 |  | 6 | 2016-18 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Note: the savings values have only been evaluated for multifamily units. It is likely there will be savings differences between multifamily and single family residences. | per ft | 0.002 | 25.7
1272 | Water Heating | Insulation | Pipe Insulation | Pipe Insulation_SK: Kits | Pipe Insulation_SK: Kits | 1 | Active | 2017-01-01 | [7 empty] | per ft | [10 empty] | .42 |  | 6 | 2016-18 |  |  |  | Kits |  |  | per ft | 0.002 | 26.0
1272 | Water Heating | Insulation | Pipe Insulation | Pipe Insulation_SK: Kits | Pipe Insulation_SK: Kits | 2 | Proposed | 2018-01-01 | [7 empty] | per ft | [10 empty] | .42 |  | 6 | 2016-18 |  |  |  | Kits |  |  | per ft | 0.002 | 26.0
860 | Motors | Pumps | Single Speed Pool Pump | Pool Pump and Motor Single Speed: Efficient Products | Pool Pump and Motor Single Speed | 1 | Active | 2013-01-02 |  | Standard Pool Pump and Motor Efficiency | [5 empty] | per measure | Algorithm | High efficiency pump and motor, speed control |  |  | Single Flow High Efficiency Pool Pump and Motor with Controls |  |  | Algorithm | The pool pump and motor measures are associated with the business motors end use. For each of the measures steady state operation was assumed. Morgan Measure libraries assumed a swimming season duration of May 1 through September 30. Morgan Measure libraries assumed the average pool volume is 25,000 gallons. |  | 85 |  | 10 | 2013-15, 2016-18 |  |  |  | Efficient Products |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. A base case and an improved case was calculated for each measure and the power reduction was taken as the average power reduction in the case of the single speed measure or the time weighted average power reduction in the case of the dual speed measure. A coincidence factor of 50% was used for peak savings. | per measure | 0.0957 | 694.0
859 | Motors | Pumps | Multi Speed Pool Pump | Pool Pump and motor w auto controls - multi speed: Efficient Products | Pool Pump and motor w/auto controls - multi speed | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Pool Pump and Motor Efficiency | [5 empty] | per measure | Algorithm | Two speed high efficiency pool pump and motor with controls |  |  | Two speed high efficiency pool pump and motor with controls |  |  | Algorithm | The pool pump and motor measures are associated with the business motors end use. For each of the measures steady state operation was assumed. Morgan Measure libraries assumed a swimming season duration of May 1 through September 30. Morgan Measure libraries assumed the average pool volume is 25,000 gallons. |  | 579 |  | 10 | 2013-15 |  |  |  | Efficient Products |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. A base case and an improved case was calculated for each measure and the power reduction was taken as the average power reduction in the case of the single speed measure or the time weighted average power reduction in the case of the dual speed measure. A coincidence factor of 50% was used for peak savings. | per measure | 0.796 | 1081.0
859 | Motors | Pumps | Multi Speed Pool Pump | Pool Pump and motor w auto controls - multi speed: Efficient Products | Pool Pump and motor w/auto controls - multi speed | 2 | Active | 2016-01-01 |  | Standard Pool Pump and Motor Efficiency | [5 empty] | per measure | Algorithm | Two speed high efficiency pool pump and motor with controls |  |  | Two speed high efficiency pool pump and motor with controls |  |  | Algorithm | The pool pump and motor measures are associated with the business motors end use. For each of the measures steady state operation was assumed. Morgan Measure libraries assumed a swimming season duration of May 1 through September 30. Morgan Measure libraries assumed the average pool volume is 25,000 gallons. |  | 579 |  | 10 | 2016-18 |  |  |  | Efficient Products |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. A base case and an improved case was calculated for each measure and the power reduction was taken as the average power reduction in the case of the single speed measure or the time weighted average power reduction in the case of the dual speed measure. A coincidence factor of 50% was used for peak savings. | per measure | 0.2483 | 1799.7
859 | Motors | Pumps | Multi Speed Pool Pump | Pool Pump and motor w auto controls - multi speed: Efficient Products | Pool Pump and motor w/auto controls - multi speed | 3 | InActive |  |  | Standard Pool Pump and Motor Efficiency | [5 empty] | per measure | Algorithm | Two speed high efficiency pool pump and motor with controls |  |  | Two speed high efficiency pool pump and motor with controls |  |  | Algorithm | The pool pump and motor measures are associated with the business motors end use. For each of the measures steady state operation was assumed. Morgan Measure libraries assumed a swimming season duration of May 1 through September 30. Morgan Measure libraries assumed the average pool volume is 25,000 gallons. |  | 579 |  | 10 | 2016-18 |  |  |  | Efficient Products |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. A base case and an improved case was calculated for each measure and the power reduction was taken as the average power reduction in the case of the single speed measure or the time weighted average power reduction in the case of the dual speed measure. A coincidence factor of 50% was used for peak savings. | per measure | 0.2497 | 1810.0
1233 | HVAC | Space Cooling | Package Terminal AC | PTAC 10 EER_MF: HVAC | PTAC 10 EER_MF | 1 | Active | 2016-01-01 |  | 8.7 EER | [5 empty] | per measure |  | 10.3 EER | [8 empty] | 124 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.126 | 133
1005 | HVAC | Space Cooling | Package Terminal AC | PTAC 10.3 EER_MF: Low Income | Packaged Terminal Air Conditioner EER 10.3 Replacing 8.7 EER unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Packaged Terminal Air Conditioner EER 8.7 | 8.7 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Air Conditioner EER 10.3 | EER | 10.3 | Packaged Terminal Air Conditioner EER 10.3 |  |  | Algorithm |  |  | 124 |  | 15 | 2013-15 |  |  |  | Low Income |  | Tons = 0.8 | per measure | 0.110 | 133.0
1005 | HVAC | Space Cooling | Package Terminal AC | PTAC 10.3 EER_MF: Low Income | Packaged Terminal Air Conditioner EER 10.3 Replacing 8.7 EER unit | 2 | Active | 2016-01-01 |  | Packaged Terminal Air Conditioner EER 8.7 | 8.7 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Air Conditioner EER 10.3 | EER | 10.3 | Packaged Terminal Air Conditioner EER 10.3 |  |  | Algorithm |  |  | 124 |  | 15 | 2016-18 |  |  |  | Low Income |  | Tons = 0.8 | per measure | 0.126 | 133.0
950 | HVAC | Space Cooling | Package Terminal AC | PTAC 10.3 EER_SF: HVAC | Packaged Terminal Air Conditioner EER 10.3 Replacing 8.7 EER unit | 1 | Active | 2013-01-02 |  | Packaged Terminal Air Conditioner EER 8.7 | 8.7 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Air Conditioner EER 10.3 | EER | 10.3 | Packaged Terminal Air Conditioner EER 10.3 |  |  | Algorithm |  |  | 124 |  | 15 | 2013-15, 2016-18 |  |  |  | HVAC |  | Tons = 0.8 | per measure | 0.126 | 133.0
1075 | HVAC | Space Cooling | Package Terminal AC | PTAC 10.3 EER_SF: New Home Construction | Packaged Terminal Air Conditioner EER 10.3 Replacing 8.7 EER unit | 1 | InActive | 2013-01-02 | 2014-12-31 | Packaged Terminal Air Conditioner EER 8.7 | 8.7 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Air Conditioner EER 10.3 | EER | 10.3 | Packaged Terminal Air Conditioner EER 10.3 |  |  | Algorithm |  |  | 124 |  | 15 | 2013-15 |  |  |  | New Home Construction |  | Tons = 0.8 | per measure | 0.110 | 133.0
1234 | HVAC | Space Cooling | Package Terminal AC | PTAC 9 EER_MF: HVAC | PTAC 9 EER_MF | 1 | Active | 2016-01-01 |  | 7.1 EER | [5 empty] | per measure |  | 9.3 EER | [8 empty] | 136 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.201 | 212.5
1006 | HVAC | Space Cooling | Package Terminal AC | PTAC 9.3 EER_MF: Low Income | Packaged Terminal Air Conditioner EER 9.3 Replacing 7.1 EER | 1 | InActive | 2013-01-02 | 2015-12-31 | Packaged Terminal Air Conditioner EER 7.1 | 7.1 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Air Conditioner EER 9.3 | EER | 9.3 | Packaged Terminal Air Conditioner EER 9.3 |  |  | Algorithm |  |  | 136 |  | 15 | 2013-15 |  |  |  | Low Income |  | Tons = 0.8 | per measure | 0.200 | 213.0
1006 | HVAC | Space Cooling | Package Terminal AC | PTAC 9.3 EER_MF: Low Income | Packaged Terminal Air Conditioner EER 9.3 Replacing 7.1 EER | 2 | Active | 2016-01-01 |  | Packaged Terminal Air Conditioner EER 7.1 | 7.1 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Air Conditioner EER 9.3 | EER | 9.3 | Packaged Terminal Air Conditioner EER 9.3 |  |  | Algorithm |  |  | 136 |  | 15 | 2016-18 |  |  |  | Low Income |  | Tons = 0.8 | per measure | 0.201 | 212.5
951 | HVAC | Space Cooling | Package Terminal AC | PTAC 9.3 EER_SF: HVAC | Packaged Terminal Air Conditioner EER 9.3 Replacing 7.1 EER | 1 | Active | 2013-01-02 |  | Packaged Terminal Air Conditioner EER 7.1 | 7.1 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Air Conditioner EER 9.3 | EER | 9.3 | Packaged Terminal Air Conditioner EER 9.3 |  |  | Algorithm |  |  | 136 |  | 15 | 2013-15, 2016-18 |  |  |  | HVAC |  | Tons = 0.8 | per measure | 0.201 | 212.5
1076 | HVAC | Space Cooling | Package Terminal AC | PTAC 9.3 EER_SF: New Home Construction | Packaged Terminal Air Conditioner EER 9.3 Replacing 7.1 EER | 1 | InActive | 2013-01-02 | 2014-12-31 | Packaged Terminal Air Conditioner EER 7.1 | 7.1 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Air Conditioner EER 9.3 | EER | 9.3 | Packaged Terminal Air Conditioner EER 9.3 |  |  | Algorithm |  |  | 136 |  | 15 | 2013-15 |  |  |  | New Home Construction |  | Tons = 0.8 | per measure | 0.200 | 213.0
1235 | HVAC | Heat Pumps | Package Terminal Heat Pump | PTHP 10 EER_MF: HVAC | PTHP 10 EER_MF | 1 | Active | 2016-01-01 |  | 8.5 SEER | [5 empty] | per measure |  | 10.9 SEER | [8 empty] | 155 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.114 | 244.3
991 | HVAC | Heat Pumps | Package Terminal Heat Pump | PTHP 10.9 EER_MF: Low Income | Packaged Terminal Heat Pump EER 10.9 Replacing 8.5 EER unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Packaged Terminal Heat Pump EER 8.5 | 8.5 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Heat Pump EER 10.9 | EER | 10.9 | Packaged Terminal Heat Pump EER 10.9 |  |  | Algorithm |  |  | 155 |  | 15 | 2013-15 |  |  |  | Low Income |  | Tons = 0.8 | per measure | 0.150 | 244.0
991 | HVAC | Heat Pumps | Package Terminal Heat Pump | PTHP 10.9 EER_MF: Low Income | Packaged Terminal Heat Pump EER 10.9 Replacing 8.5 EER unit | 2 | Active | 2016-01-01 |  | Packaged Terminal Heat Pump EER 8.5 | 8.5 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Heat Pump EER 10.9 | EER | 10.9 | Packaged Terminal Heat Pump EER 10.9 |  |  | Algorithm |  |  | 155 |  | 15 | 2016-18 |  |  |  | Low Income |  | Tons = 0.8 | per measure | 0.114 | 244.3
936 | HVAC | Heat Pumps | Package Terminal Heat Pump | PTHP 10.9 EER_SF: HVAC | Packaged Terminal Heat Pump EER 10.9 Replacing 8.5 EER unit | 1 | Active | 2013-01-02 |  | Packaged Terminal Heat Pump EER 8.5 | 8.5 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Heat Pump EER 10.9 | EER | 10.9 | Packaged Terminal Heat Pump EER 10.9 |  |  | Algorithm |  |  | 155 |  | 15 | 2013-15, 2016-18 |  |  |  | HVAC |  | Tons = 0.8 | per measure | 0.114 | 244.3
1064 | HVAC | Heat Pumps | Package Terminal Heat Pump | PTHP 10.9 EER_SF: New Home Construction | Packaged Terminal Heat Pump EER 10.9 Replacing 8.5 EER unit | 1 | InActive | 2013-01-02 | 2014-12-31 | Packaged Terminal Heat Pump EER 8.5 | 8.5 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Heat Pump EER 10.9 | EER | 10.9 | Packaged Terminal Heat Pump EER 10.9 |  |  | Algorithm |  |  | 155 |  | 15 | 2013-15 |  |  |  | New Home Construction |  | Tons = 0.8 | per measure | 0.150 | 244.0
1236 | HVAC | Heat Pumps | Package Terminal Heat Pump | PTHP 9 EER_MF: HVAC | PTHP 9 EER_MF | 1 | Active | 2016-01-01 |  | 7.0 EER | [5 empty] | per measure |  | 9.1 EER | [8 empty] | 169 |  | 15 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.157 | 336.2
992 | HVAC | Heat Pumps | Package Terminal Heat Pump | PTHP 9.1 EER_MF: Low Income | Packaged Terminal Heat Pump (PTHP) EER 9.1 replacing 7.0 EER unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Packaged Terminal Heat Pump EER 7.0 | 7 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Heat Pump EER 9.1 | EER | 9.1 | Packaged Terminal Heat Pump EER 9.1 |  |  | Algorithm |  |  | 169 |  | 15 | 2013-15 |  |  |  | Low Income |  | Tons = 0.8 | per measure | 0.200 | 336.0
992 | HVAC | Heat Pumps | Package Terminal Heat Pump | PTHP 9.1 EER_MF: Low Income | Packaged Terminal Heat Pump (PTHP) EER 9.1 replacing 7.0 EER unit | 2 | Active | 2016-01-01 |  | Packaged Terminal Heat Pump EER 7.0 | 7 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Heat Pump EER 9.1 | EER | 9.1 | Packaged Terminal Heat Pump EER 9.1 |  |  | Algorithm |  |  | 169 |  | 15 | 2016-18 |  |  |  | Low Income |  | Tons = 0.8 | per measure | 0.157 | 336.2
937 | HVAC | Heat Pumps | Package Terminal Heat Pump | PTHP 9.1 EER_SF: HVAC | Packaged Terminal Heat Pump (PTHP) EER 9.1 replacing 7.0 EER unit | 1 | Active | 2013-01-02 |  | Packaged Terminal Heat Pump EER 7.0 | 7 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Heat Pump EER 9.1 | EER | 9.1 | Packaged Terminal Heat Pump EER 9.1 |  |  | Algorithm |  |  | 169 |  | 15 | 2013-15, 2016-18 |  |  |  | HVAC |  | Tons = 0.8 | per measure | 0.157 | 336.2
1065 | HVAC | Heat Pumps | Package Terminal Heat Pump | PTHP 9.1 EER_SF: New Home Construction | Packaged Terminal Heat Pump (PTHP) EER 9.1 replacing 7.0 EER unit | 1 | InActive | 2013-01-02 | 2014-12-31 | Packaged Terminal Heat Pump EER 7.0 | 7 | EER |  |  |  | per measure | Algorithm | Packaged Terminal Heat Pump EER 9.1 | EER | 9.1 | Packaged Terminal Heat Pump EER 9.1 |  |  | Algorithm |  |  | 169 |  | 15 | 2013-15 |  |  |  | New Home Construction |  | Tons = 0.8 | per measure | 0.200 | 336.0
1246 | HVAC | HVAC O&M | RCA Improvement | RCA 10% improvement_MF: HVAC | RCA 10% improvement_MF | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 70 |  | 10 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.346 | 365
995 | HVAC | HVAC O&M | RCA Improvement | RCA 10% improvement_MF: Low Income | Refrigerant Charge Adjustment | 1 | InActive | 2013-01-02 | 2015-12-31 | 10% EER degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | Refrigerant Charge Adjustment 10% Improvement | % improvement | 0.1 | Correct Charge |  |  | Algorithm |  |  | 70 |  | 10 | 2013-15 |  |  |  | Low Income |  | Tons = 2.7 | per measure | 0.120 | 87.0
995 | HVAC | HVAC O&M | RCA Improvement | RCA 10% improvement_MF: Low Income | Refrigerant Charge Adjustment | 2 | InActive | 2016-01-01 | 2016-12-31 | 10% EER degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | Refrigerant Charge Adjustment 10% Improvement | % improvement | 0.1 | Correct Charge |  |  | Algorithm |  |  | 75 |  | 10 | 2016-18 |  |  |  | Low Income |  | Tons = 2.7 | per measure | 0.107 | 230
995 | HVAC | HVAC O&M | RCA Improvement | RCA 10% improvement_MF: Low Income | Refrigerant Charge Adjustment | 3 | Active | 2017-01-01 |  | 10% EER degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | Refrigerant Charge Adjustment 10% Improvement | % improvement | 0.1 | Correct Charge |  |  | Algorithm |  |  | 75 |  | 10 | 2016-18 |  |  |  | Low Income |  | Tons = 2.7 | per measure | 0.239 | 512
995 | HVAC | HVAC O&M | RCA Improvement | RCA 10% improvement_MF: Low Income | Refrigerant Charge Adjustment | 4 | Proposed | 2018-01-01 |  | 10% EER degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | Refrigerant Charge Adjustment 10% Improvement | % improvement | 0.1 | Correct Charge |  |  | Algorithm |  |  | 75 |  | 10 | 2016-18 |  |  |  | Low Income |  | Tons = 2.7 | per measure | 0.062 | 132
940 | HVAC | HVAC O&M | RCA Improvement | RCA 10% improvement_SF: HVAC | Refrigerant Charge Adjustment | 1 | InActive | 2013-01-02 | 2015-12-31 | 10% EER degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | Refrigerant Charge Adjustment 10% Improvement | % improvement | 0.1 | Correct Charge |  |  | Algorithm |  |  | 127 |  | 10 | 2013-15 |  |  |  | HVAC |  | Tons = 2.7 | per measure | 0.230 | 191.0
940 | HVAC | HVAC O&M | RCA Improvement | RCA 10% improvement_SF: HVAC | Refrigerant Charge Adjustment | 2 | InActive | 2016-01-01 | 2016-12-31 | 10% EER degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | Refrigerant Charge Adjustment 10% Improvement | % improvement | 0.1 | Correct Charge |  |  | Algorithm |  |  | 127 |  | 10 | 2016-18 |  |  |  | HVAC |  | Tons = 2.7 | per measure | 0.256 | 549.51
940 | HVAC | HVAC O&M | RCA Improvement | RCA 10% improvement_SF: HVAC | Refrigerant Charge Adjustment | 3 | Active | 2017-01-01 |  | 10% EER degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | Refrigerant Charge Adjustment 10% Improvement | % improvement | 0.1 | Correct Charge |  |  | Algorithm |  |  | 127 |  | 10 | 2016-18 |  |  |  | HVAC |  | Tons = 2.7 | per measure | 0.811 | 856
996 | HVAC | HVAC O&M | RCA Improvement | RCA 10% improvement_SF: Low Income | Refrigerant Charge Adjustment | 1 | InActive | 2013-01-01 | 2015-12-30 | 10% EER degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | Refrigerant Charge Adjustment 10% Improvement | % improvement | 0.1 | Correct Charge |  |  | Algorithm |  |  | 127 |  | 10 | 2013-15 |  |  |  | Low Income |  | Tons = 2.7 | per measure | 0.230 | 191.0
996 | HVAC | HVAC O&M | RCA Improvement | RCA 10% improvement_SF: Low Income | Refrigerant Charge Adjustment | 2 | Active | 2016-01-01 |  | 10% EER degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | Refrigerant Charge Adjustment 10% Improvement | % improvement | 0.1 | Correct Charge |  |  | Algorithm |  |  | 80 |  | 10 | 2016-18 |  |  |  | Low Income |  | Tons = 2.7 | per measure | 0.089 | 191
996 | HVAC | HVAC O&M | RCA Improvement | RCA 10% improvement_SF: Low Income | Refrigerant Charge Adjustment | 3 | Proposed | 2017-01-01 |  | 10% EER degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | Refrigerant Charge Adjustment 10% Improvement | % improvement | 0.1 | Correct Charge |  |  | Algorithm |  |  | 80 |  | 10 |  |  |  |  | Low Income |  | Tons = 2.7 | per measure | 0.373 | 801.2
1068 | HVAC | HVAC O&M | RCA Improvement | RCA 10% improvement_SF: New Home Construction | Refrigerant Charge Adjustment | 1 | InActive | 2013-01-02 | 2014-12-31 | 10% EER degradation | 0.1 | % EER degradation |  |  |  | per measure | Algorithm | Refrigerant Charge Adjustment 10% Improvement | % improvement | 0.1 | Correct Charge |  |  | Algorithm |  |  | 127 |  | 10 | 2013-15 |  |  |  | New Home Construction |  | Tons = 2.7 | per measure | 0.230 | 191.0
997 | HVAC | HVAC O&M | RCA Improvement | RCA 15% improvement_MF: Low Income | Refrigerant Charge Adjustment | 1 | InActive | 2013-01-02 | 2015-12-31 | 15% EER degradation | 0.15 | % EER degradation |  |  |  | per measure | Algorithm | Refrigerant Charge Adjustment 15% Improvement | % improvement | 0.15 | Correct Charge |  |  | Algorithm |  |  | 219 |  | 10 | 2013-15 |  |  |  | Low Income |  | Tons = 2.7 | per measure | 0.180 | 131.0
997 | HVAC | HVAC O&M | RCA Improvement | RCA 15% improvement_MF: Low Income | Refrigerant Charge Adjustment | 2 | InActive |  |  | 15% EER degradation | 0.15 | % EER degradation |  |  |  | per measure | Algorithm | Refrigerant Charge Adjustment 15% Improvement | % improvement | 0.15 | Correct Charge |  |  | Algorithm |  |  | 219 |  | 10 |  |  |  |  | Low Income |  | Tons = 2.7 | per measure | 0.177 | 130.6
1217 | HVAC | HVAC O&M | RCA Improvement | RCA 15% Improvement_SF: HVAC | 15% EER Degradation | 1 | InActive | [8 empty] | per unit | [10 empty] | 401.51 |  | 10 |  |  |  |  | HVAC |  |  | per measure | .358 | 1116.6
1213 | HVAC | HVAC O&M | RCA Improvement | RCA 15% Improvement_SF: Low Income | 15% EER Degradation | 1 | InActive | 2015-12-31 | [7 empty] | per measure | [10 empty] | 402 |  | 10 |  |  |  |  | Low Income |  |  | per measure | .358 | 289.3
998 | HVAC | HVAC O&M | RCA Improvement | RCA 5% improvement_MF: Low Income | Refrigerant Charge Adjustment | 1 | InActive | 2013-01-02 | 2015-12-31 | 5% EER degradation | 0.05 | % EER degradation |  |  |  | per measure | Algorithm | Refrigerant Charge Adjustment 5% Improvement | % improvement | 0.05 | Correct Charge |  |  | Algorithm |  |  | 58 |  | 10 | 2013-15 |  |  |  | Low Income |  | Tons = 2.7 | per measure | 0.060 | 44.0
998 | HVAC | HVAC O&M | RCA Improvement | RCA 5% improvement_MF: Low Income | Refrigerant Charge Adjustment | 2 | InActive |  |  | 5% EER degradation | 0.05 | % EER degradation |  |  |  | per measure | Algorithm | Refrigerant Charge Adjustment 5% Improvement | % improvement | 0.05 | Correct Charge |  |  | Algorithm |  |  | 58 |  | 10 |  |  |  |  | Low Income |  | Tons = 2.7 | per measure | 0.059 | 43.5
1216 | HVAC | HVAC O&M | RCA Improvement | RCA 5% Improvement_SF: HVAC | 5% EER Degradation | 1 | InActive | [8 empty] | per measure | [10 empty] | 105.29 |  | 10 |  |  |  |  | HVAC |  |  | per measure | .124 | 370.5
1214 | HVAC | HVAC O&M | RCA Improvement | RCA 5% Improvement_SF: Low Income | 5% EEr Degradation | 1 | InActive | 2015-12-31 | [7 empty] | per measure | [10 empty] | 105.29 |  | 10 |  |  |  |  | Low Income |  |  | per measure | .124 | 96
1265 | Appliances | Refrigerators | Refrigerator, residential | Refrigerator Coil Cleaning Brush_LI: Kits | Refrigerator Coil Cleaning Brush | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 3 |  | 2 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.002 | 16.5
1255 | Appliances | Refrigerators | Coil Cleaning | Refrigerator Coil Cleaning Brush_MF: Kits | Refrigerator Coil Cleaning Brush | 1 | Active | 2016-01-01 |  | No Brush | [5 empty] | per measure | Algorithm | Refrigerator Coil Cleaner Brush |  |  | Refrigerator Coil Cleaner Brush |  |  | Algorithm |  |  | 3 |  | 2 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.002 | 16.5
1256 | Appliances | Refrigerators | Coil Cleaning | Refrigerator Coil Cleaning Brush_SF: Kits | Refrigerator Coil Cleaning Brush | 1 | Active | 2016-01-01 |  | No Brush | [5 empty] | per measure | Algorithm | Refrigerator Coil Cleaner Brush |  |  | Refrigerator Coil Cleaner Brush |  |  | Algorithm |  |  | 3 |  | 2 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.002 | 16.5
1172 | Appliances | Refrigerators | Coil Cleaning | Refrigerator Coil Cleaning Brush_SF: Low Income | Refrigerator Coil Cleaning Brush | 1 | Active | 2013-01-02 |  | No Brush | [5 empty] | per measure | Algorithm | Refrigerator Coil Cleaner Brush |  |  | Refrigerator Coil Cleaner Brush |  |  | Algorithm |  |  | 8.5 |  | 2 | 2013-15, 2016-18 |  |  |  | Low Income |  |  | per measure | 0.002 | 16.5
1254 | Appliances | Refrigerators | Coil Cleaning | Refrigerator Coil Cleaning Brush_SK: Kits | Refrigerator Coil Cleaning Brush | 1 | Active | 2016-01-01 |  | No Brush | [5 empty] | per measure | Algorithm | Refrigerator Coil Cleaner Brush |  |  | Refrigerator Coil Cleaner Brush |  |  | Algorithm |  |  | 3 |  | 2 | 2016-18 |  |  |  | Kits |  |  | per measure | 0.002 | 16.5
3 | Appliances | Refrigerators | Recycling | Refrigerator Recycling: Appliance Recycle | Recycling of a freezer unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Operating Unit (10-27 cubic ft) | 1891 | UEC |  |  | The incremental cost for each appliance recycling measure is the actual cost associated with the removal and recycling of the retired unit. | per measure | Algorithm | Assumes complete removal of the base characteristic | [5 empty] | Algorithm | Ameren Missouri considered 3 measures for an Appliance Recycling program. All 3 measures were associated with different residential end uses: refrigeration, freezer, and miscellaneous. These measures are different than other measures in the TRM because the efficient characteristics assume a complete removal of the base characteristic |  | 84 |  | 10 | 2013-15 |  |  |  | Appliance Recycle |  | The energy and demand savings for the freezer and refrigerator recycling measures can be calculated using the following formula: Delta kWh=(Base UEC-Efficient UEC)× In-situ factor where UEC = average unit energy consumption In-situ factor = factor considering appliances not plugged in year-round (also known as part-use). If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.181 | 1440.0
3 | Appliances | Refrigerators | Recycling | Refrigerator Recycling: Appliance Recycle | Recycling of a freezer unit | 2 | InActive |  |  | Operating Unit (10-27 cubic ft) | 1178 | UEC |  |  | The incremental cost for each appliance recycling measure is the actual cost associated with the removal and recycling of the retired unit. | per measure | Algorithm | Assumes complete removal of the base characteristic | [5 empty] | Algorithm | Ameren Missouri considered 3 measures for an Appliance Recycling program. All 3 measures were associated with different residential end uses: refrigeration, freezer, and miscellaneous. These measures are different than other measures in the TRM because the efficient characteristics assume a complete removal of the base characteristic |  | 84 |  | 10 |  |  |  |  | Appliance Recycle |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. where: UEC = average unit energy consumption In-situ factor = factor considering appliances not plugged in year-round (also known as part-use) | per measure | 0.130 | 1013.3
4 | Appliances | Room AC | Recycling | Room AC recycling: Appliance Recycle | Recycling of a refrigerator unit | 1 | InActive | 2013-01-02 | 2015-12-31 | Old Operating Unit | N/A |  |  |  | The incremental cost for each appliance recycling measure is the actual cost associated with the removal and recycling of the retired unit. | per measure | Algorithm | Assumes complete removal of the base characteristic | [5 empty] | Algorithm | Ameren Missouri considered 3 measures for an Appliance Recycling program. All 3 measures were associated with different residential end uses: refrigeration, freezer, and miscellaneous. These measures are different than other measures in the TRM because the efficient characteristics assume a complete removal of the base characteristic |  | 49 |  | 8 | 2013-15 |  |  |  | Appliance Recycle |  |  | per measure | 0.107 | 113.0
4 | Appliances | Room AC | Recycling | Room AC recycling: Appliance Recycle | Recycling of a refrigerator unit | 2 | InActive |  |  | Old Operating Unit |  |  |  |  | The incremental cost for each appliance recycling measure is the actual cost associated with the removal and recycling of the retired unit. | per measure | Algorithm | Assumes complete removal of the base characteristic | [5 empty] | Algorithm | Ameren Missouri considered 3 measures for an Appliance Recycling program. All 3 measures were associated with different residential end uses: refrigeration, freezer, and miscellaneous. These measures are different than other measures in the TRM because the efficient characteristics assume a complete removal of the base characteristic |  | 49 |  | 8 |  |  |  |  | Appliance Recycle |  |  | per measure | 0.084 | 829.9
1275 | HVAC | Space Cooling | Central Air | SEER 14 MF ER: HVAC | SEER 14 MF ER | 1 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 445 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.773 | 815.5
1237 | HVAC | Space Cooling | Central Air | SEER 14 MF Replace on Fail: HVAC | SEER 14 MF | 2 | Active | 2017-01-01 |  | 13 SEER | [5 empty] | per measure |  | 14 SEER | [8 empty] | 178.5 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.155 | 163.8
1237 | HVAC | Space Cooling | Central Air | SEER 14 MF: HVAC | SEER 14 MF | 1 | InActive | 2016-01-01 | 2016-12-31 | 13 SEER | [5 empty] | per measure |  | 14 SEER | [8 empty] | 139 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.164 | 172.9
1276 | HVAC | Space Cooling | Central Air | SEER 15 MF ER: HVAC | SEER 15 MF ER | 1 | Active | 2017-01-01 | [7 empty] | per measure | [10 empty] | 623.5 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.903 | 953.5
1238 | HVAC | Space Cooling | Central Air | SEER 15 MF Replace on Fail: HVAC | SEER 15 MF | 2 | Active | 2017-01-01 |  | 13 SEER | [5 empty] | per measure |  | 15 SEER | [8 empty] | 357 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.18 | 190
1238 | HVAC | Space Cooling | Central Air | SEER 15 MF: HVAC | SEER 15 MF | 1 | InActive | 2016-01-01 | 2016-12-31 | 13 SEER | [5 empty] | per measure |  | 15 SEER | [8 empty] | 278 |  | 12 | 2016-18 |  |  |  | HVAC |  |  | per measure | 0.185 | 195.5
993 | HVAC | HVAC Controls | Thermostat Setback | Setback thermostat - full setback_MF: Low Income | Setback Thermostat: Full Setback | 1 | InActive | 2013-01-02 | 2015-12-31 | No setback | [5 empty] | per measure | Algorithm | Full Setback thermostat | [5 empty] | Algorithm |  |  | 63 |  | 9 | 2013-15 |  |  |  | Low Income |  | Assume 1,000 square ft dwelling area | per measure | -0.090 | 234.0
993 | HVAC | HVAC Controls | Thermostat Setback | Setback thermostat - full setback_MF: Low Income | Setback Thermostat: Full Setback | 2 | Active | 2016-01-01 |  | No setback | [5 empty] | per measure | Algorithm | Full Setback thermostat | [5 empty] | Algorithm |  |  | 75 |  | 9 | 2016-18 |  |  |  | Low Income |  | Assume 1,000 square ft dwelling area | per measure | 0.109 | 234
993 | HVAC | HVAC Controls | Thermostat Setback | Setback thermostat - full setback_MF: Low Income | Setback Thermostat: Full Setback | 3 | Proposed | 2017-01-01 | 2017-12-31 | No setback | [5 empty] | per measure | Algorithm | Full Setback thermostat | [5 empty] | Algorithm |  |  | 75 |  | 9 |  |  |  |  | Low Income |  | Assume 1,000 square ft dwelling area | per measure | 0.019 | 40
855 | HVAC | HVAC Controls | Thermostat Setback | Setback thermostat - full setback_SF: Efficient Products | Setback Thermostat: Full Setback | 1 | InActive | 2013-01-01 | 2015-12-30 | No setback | [5 empty] | per measure | Algorithm | Full Setback thermostat | [5 empty] | Algorithm |  |  | 63 |  | 9 | 2013-15 |  |  |  | Efficient Products |  | Assume 1,900 sq ft house | per measure | -0.020 | 753.0
938 | HVAC | HVAC Controls | Thermostat Setback | Setback thermostat - full setback_SF: HVAC | Setback Thermostat: Full Setback | 1 | InActive | 2013-01-01 | 2015-12-30 | No setback | [5 empty] | per measure | Algorithm | Full Setback thermostat | [5 empty] | Algorithm |  |  | 63 |  | 9 | 2013-15 |  |  |  | HVAC |  | Assume 1,900 sq ft house | per measure | -0.020 | 753.0
994 | HVAC | HVAC Controls | Thermostat Setback | Setback thermostat - full setback_SF: Low Income | Setback Thermostat: Full Setback | 1 | InActive | 2013-01-02 | 2015-12-31 | No setback | [5 empty] | per measure | Algorithm | Full Setback thermostat | [5 empty] | Algorithm |  |  | 63 |  | 9 | 2013-15 |  |  |  | Low Income |  | Assume 1,900 sq ft house | per measure | -0.020 | 753.0
994 | HVAC | HVAC Controls | Thermostat Setback | Setback thermostat - full setback_SF: Low Income | Setback Thermostat: Full Setback | 2 | Active | 2016-01-01 |  | No setback | [5 empty] | per measure | Algorithm | Full Setback thermostat | [5 empty] | Algorithm |  |  | 75 |  | 15 | 2016-18 |  |  |  | Low Income |  | Assume 1,900 sq ft house | per measure | 0.109 | 234
1066 | HVAC | HVAC Controls | Thermostat Setback | Setback thermostat - full setback_SF: New Home Construction | Setback Thermostat: Full Setback | 1 | InActive | 2013-01-02 | 2014-12-31 | No setback | [5 empty] | per measure | Algorithm | Full Setback thermostat | [5 empty] | Algorithm |  |  | 63 |  | 9 | 2013-15 |  |  |  | New Home Construction |  | Assume 1,900 sq ft house | per measure | -0.020 | 753.0
856 | HVAC | HVAC Controls | Thermostat Setback | Setback thermostat - moderate setback_SF: Efficient Products | Setback Thermostat: Moderate Setback | 1 | InActive | 2013-01-02 | 2015-12-31 | No setback | [5 empty] | per measure | Algorithm | Moderat setback thermostat | [5 empty] | Algorithm |  |  | 73 |  | 9 | 2013-15 |  |  |  | Efficient Products |  | Assumes a 1,900 square foot home | per measure | -0.200 | 543.0
856 | HVAC | HVAC Controls | Thermostat Setback | Setback thermostat - moderate setback_SF: Efficient Products | Setback Thermostat: Moderate Setback | 2 | InActive |  |  | No setback | [5 empty] | per measure | Algorithm | Moderat setback thermostat | [5 empty] | Algorithm |  |  | 73 |  | 9 |  |  |  |  | Efficient Products |  | Assumes a 1,900 square foot home | per measure | -0.011 | 105.0
939 | HVAC | HVAC Controls | Thermostat Setback | Setback thermostat - moderate setback_SF: HVAC | Setback Thermostat: Moderate Setback | 1 | InActive | 2013-01-02 | 2015-12-31 | No setback | [5 empty] | per measure | Algorithm | Moderat setback thermostat | [5 empty] | Algorithm |  |  | 73 |  | 9 | 2013-15 |  |  |  | HVAC |  | Assume 1,900 sq ft house | per measure | -0.020 | 543.0
939 | HVAC | HVAC Controls | Thermostat Setback | Setback thermostat - moderate setback_SF: HVAC | Setback Thermostat: Moderate Setback | 2 | InActive |  |  | No setback | [5 empty] | per measure | Algorithm | Moderat setback thermostat | [5 empty] | Algorithm |  |  | 73 |  | 9 |  |  |  |  | HVAC |  | Assume 1,900 sq ft house | per measure | 0.020 | 83.0
1067 | HVAC | HVAC Controls | Thermostat Setback | Setback thermostat - moderate setback_SF: New Home Construction | Setback Thermostat: Moderate Setback | 1 | InActive | 2013-01-02 | 2014-12-31 | No setback | [5 empty] | per measure | Algorithm | Moderat setback thermostat | [5 empty] | Algorithm |  |  | 73 |  | 9 | 2013-15 |  |  |  | New Home Construction |  | Assume 1,900 sq ft house | per measure | -0.020 | 543.0
1258 | Office Equipment | Smart Strips | Smart Strip | Smart Strip - Motion Sensing: Efficient Products | Smart Strip - Motion Sensing | 1 | InActive | 2016-01-01 | 2016-12-31 | Surge Strip | [5 empty] | per measure |  | Smart Strip | [8 empty] | 8.96 |  | 5 | 2016-18 |  |  |  | Efficient Products |  |  | per measure | 0.007 | 64.48
1258 | Office Equipment | Smart Strips | Smart Strip | Smart Strip - Motion Sensing: Efficient Products | Smart Strip - Motion Sensing | 2 | Active | 2017-01-01 |  | Surge Strip | [5 empty] | per measure |  | Smart Strip | [8 empty] | 8.96 |  | 5 | 2016-18 |  |  |  | Efficient Products |  |  | per measure | 0.007 | 64
1031 | Office Equipment | Smart Strips | Smart Strip | Smart Strip plug outlet_Load Sensing: Efficient Products | Smart Strip plug outlet_SF | 3 | Active | 2017-01-01 |  | Standard Plug +Outlet | [5 empty] | per measure | Algorithm | Smart Strip Plug Outlet |  |  | Smart Strip Plug Outlet |  |  | Algorithm | The smart strip plug outlet measure is associated with the residential miscellaneous end use. Morgan Measure Libraries considered the computer peripherals to include: speakers, ink-jet printer, internet terminal and phone/fax/copier. Morgan Measure Libraries considered the television peripherals to include: audio system/ speakers, DVD player, VCR, cable box, and video game console. |  | 4 |  | 5 | 2016-18 |  |  |  | Efficient Products |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Morgan Measure Libraries methodology for calculating the savings for smart strips considered idle wattages for computer and television peripherals and took an average of both peripheral systems. | per measure | 0.007 | 59.0
1030 | Office Equipment | Smart Strips | Smart Strip | Smart Strip plug outlet_MF: Low Income | Smart Strip plug outlet_MF | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Plug +Outlet | [5 empty] | per measure | Algorithm | Smart Strip Plug Outlet |  |  | Smart Strip Plug Outlet |  |  | Algorithm | The smart strip plug outlet measure is associated with the residential miscellaneous end use. Morgan Measure Libraries considered the computer peripherals to include: speakers, ink-jet printer, internet terminal and phone/fax/copier. Morgan Measure Libraries considered the television peripherals to include: audio system/ speakers, DVD player, VCR, cable box, and video game console. |  | 40 |  | 5 | 2013-15 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Morgan Measure Libraries methodology for calculating the savings for smart strips considered idle wattages for computer and television peripherals and took an average of both peripheral systems. | per measure | 0.026 | 184.0
1030 | Office Equipment | Smart Strips | Smart Strip | Smart Strip plug outlet_MF: Low Income | Smart Strip plug outlet_MF | 2 | InActive | 2016-01-01 | 2016-12-31 | Standard Plug +Outlet | [5 empty] | per measure | Algorithm | Smart Strip Plug Outlet |  |  | Smart Strip Plug Outlet |  |  | Algorithm | The smart strip plug outlet measure is associated with the residential miscellaneous end use. Morgan Measure Libraries considered the computer peripherals to include: speakers, ink-jet printer, internet terminal and phone/fax/copier. Morgan Measure Libraries considered the television peripherals to include: audio system/ speakers, DVD player, VCR, cable box, and video game console. |  | 40 |  | 5 | 2016-18 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Morgan Measure Libraries methodology for calculating the savings for smart strips considered idle wattages for computer and television peripherals and took an average of both peripheral systems. | per measure | 0.013 | 110
1030 | Office Equipment | Smart Strips | Smart Strip | Smart Strip plug outlet_MF: Low Income | Smart Strip plug outlet_MF | 3 | Active | 2017-01-01 |  | Standard Plug +Outlet | [5 empty] | per measure | Algorithm | Smart Strip Plug Outlet |  |  | Smart Strip Plug Outlet |  |  | Algorithm | The smart strip plug outlet measure is associated with the residential miscellaneous end use. Morgan Measure Libraries considered the computer peripherals to include: speakers, ink-jet printer, internet terminal and phone/fax/copier. Morgan Measure Libraries considered the television peripherals to include: audio system/ speakers, DVD player, VCR, cable box, and video game console. |  | 40 |  | 5 | 2016-18 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Morgan Measure Libraries methodology for calculating the savings for smart strips considered idle wattages for computer and television peripherals and took an average of both peripheral systems. | per measure | 0.011 | 70.0
1031 | Office Equipment | Smart Strips | Smart Strip | Smart Strip plug outlet_SF Kit Load Sensing: Efficient Products | Smart Strip plug outlet_SF | 2 | InActive | 2016-01-01 | 2016-12-31 | Surge Strip | [5 empty] | per measure | Algorithm | Smart Strip |  |  | Smart Strip Plug Outlet |  |  | Algorithm | The smart strip plug outlet measure is associated with the residential miscellaneous end use. Morgan Measure Libraries considered the computer peripherals to include: speakers, ink-jet printer, internet terminal and phone/fax/copier. Morgan Measure Libraries considered the television peripherals to include: audio system/ speakers, DVD player, VCR, cable box, and video game console. |  | 4 |  | 5 | 2016-18 |  |  |  | Efficient Products |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Morgan Measure Libraries methodology for calculating the savings for smart strips considered idle wattages for computer and television peripherals and took an average of both peripheral systems. | per measure | 0.006 | 53.9
1031 | Office Equipment | Smart Strips | Smart Strip | Smart Strip plug outlet_SF: Low Income | Smart Strip plug outlet_SF | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Plug +Outlet | [5 empty] | per measure | Algorithm | Smart Strip Plug Outlet |  |  | Smart Strip Plug Outlet |  |  | Algorithm | The smart strip plug outlet measure is associated with the residential miscellaneous end use. Morgan Measure Libraries considered the computer peripherals to include: speakers, ink-jet printer, internet terminal and phone/fax/copier. Morgan Measure Libraries considered the television peripherals to include: audio system/ speakers, DVD player, VCR, cable box, and video game console. |  | 40 |  | 5 | 2013-15 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Morgan Measure Libraries methodology for calculating the savings for smart strips considered idle wattages for computer and television peripherals and took an average of both peripheral systems. | per measure | 0.026 | 184.0
862 | Office Equipment | Smart Strips | Smart Strip | Smart Strip plug outlet: Efficient Products | Smart Strip plug outlet | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Plug +Outlet | [5 empty] | per measure | Algorithm | Smart Strip Plug Outlet |  |  | Smart Strip Plug Outlet |  |  | Algorithm | The smart strip plug outlet measure is associated with the residential miscellaneous end use. Morgan Measure Libraries considered the computer peripherals to include: speakers, ink-jet printer, internet terminal and phone/fax/copier. Morgan Measure Libraries considered the television peripherals to include: audio system/ speakers, DVD player, VCR, cable box, and video game console. |  | 40 |  | 5 | 2013-15 |  |  |  | Efficient Products |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Morgan Measure Libraries methodology for calculating the savings for smart strips considered idle wattages for computer and television peripherals and took an average of both peripheral systems. | per measure | 0.026 | 184.0
862 | Office Equipment | Smart Strips | Smart Strip | Smart Strip plug outlet: Efficient Products | Smart Strip plug outlet | 3 | InActive | 2016-01-01 | 2016-12-31 | Standard Plug +Outlet | [5 empty] | per measure | Algorithm | Smart Strip Plug Outlet |  |  | Smart Strip Plug Outlet |  |  | Algorithm | The smart strip plug outlet measure is associated with the residential miscellaneous end use. Morgan Measure Libraries considered the computer peripherals to include: speakers, ink-jet printer, internet terminal and phone/fax/copier. Morgan Measure Libraries considered the television peripherals to include: audio system/ speakers, DVD player, VCR, cable box, and video game console. |  | 4.01 |  | 5 | 2016-18 |  |  |  | Efficient Products |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Morgan Measure Libraries methodology for calculating the savings for smart strips considered idle wattages for computer and television peripherals and took an average of both peripheral systems. | per measure | 0.006 | 53.88
895 | Office Equipment | Smart Strips | Smart Strip | Smart Strip plug outlet: Home Energy Performance | Smart Strip plug outlet | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Plug +Outlet | [5 empty] | per measure | Algorithm | Smart Strip Plug Outlet |  |  | Smart Strip Plug Outlet |  |  | Algorithm | The smart strip plug outlet measure is associated with the residential miscellaneous end use. Morgan Measure Libraries considered the computer peripherals to include: speakers, ink-jet printer, internet terminal and phone/fax/copier. Morgan Measure Libraries considered the television peripherals to include: audio system/ speakers, DVD player, VCR, cable box, and video game console. |  | 40 |  | 5 | 2013-15 |  |  |  | Home Energy Performance |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Morgan Measure Libraries methodology for calculating the savings for smart strips considered idle wattages for computer and television peripherals and took an average of both peripheral systems. | per measure | 0.026 | 184.0
895 | Office Equipment | Smart Strips | Smart Strip | Smart Strip plug outlet: Home Energy Performance | Smart Strip plug outlet | 2 | InActive |  |  | Standard Plug +Outlet | 70.7 | watts |  |  |  | per measure | Algorithm | Smart Strip Plug Outlet | watts | 60.9 | Smart Strip Plug Outlet |  |  | Algorithm | The smart strip plug outlet measure is associated with the residential miscellaneous end use. Morgan Measure Libraries considered the computer peripherals to include: speakers, ink-jet printer, internet terminal and phone/fax/copier. Morgan Measure Libraries considered the television peripherals to include: audio system/ speakers, DVD player, VCR, cable box, and video game console. |  | 40 |  | 5 |  |  |  |  | Home Energy Performance |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. Morgan Measure Libraries methodology for calculating the savings for smart strips considered idle wattages for computer and television peripherals and took an average of both peripheral systems. | per measure | 0.026 | 73.0
861 | Motors | Pumps | VFD Pool Pump | VFDs on Residential Swimming Pool Pumps: Efficient Products | VFDs on Residential Swimming Pool Pumps | 1 | InActive | 2013-01-02 | 2015-12-31 | Pool Pump without speed control | [5 empty] | per measure | Algorithm | VFD on swimming pool |  |  | VFD on swimming pool |  |  | Algorithm | For each of the measures steady state operation was assumed. Morgan Measure libraries assumed a swimming season duration of May 1 through September 30. Morgan Measure libraries assumed the average pool volume is 25,000 gallons. The VFD on swimming pool pump measure is associated with the residential pool spa end use. |  | 425 |  | 10 | 2013-15 |  |  |  | Efficient Products |  | A base case and an improved case was calculated for each measure and the power reduction was taken as the average power reduction in the case of the single speed measure or the time weighted average power reduction in the case of the dual speed measure. A coincidence factor of 50% was used for peak savings. CF = control factor = Traditionally flow rates have been reduced by increasing the head and riding the pump curve back to a new flow rate (throttling control). Alternately some systems have bypasses that divert a portion of the flow back to the pump inlet to reduce system flow (bypass control). Some pumps may use no controls, and run at constant flow. | per measure | 0.528 | 1543.0
861 | Motors | Pumps | VFD Pool Pump | VFDs on Residential Swimming Pool Pumps: Efficient Products | VFDs on Residential Swimming Pool Pumps | 2 | InActive | 2016-01-01 | 2016-12-31 | Pool Pump without speed control | [5 empty] | per measure | Algorithm | Variable speed pump control |  |  | VFD on swimming pool |  |  | Algorithm | For each of the measures steady state operation was assumed. Morgan Measure libraries assumed a swimming season duration of May 1 through September 30. Morgan Measure libraries assumed the average pool volume is 25,000 gallons. The VFD on swimming pool pump measure is associated with the residential pool spa end use. |  | 425 |  | 10 | 2016-18 |  |  |  | Efficient Products |  | A base case and an improved case was calculated for each measure and the power reduction was taken as the average power reduction in the case of the single speed measure or the time weighted average power reduction in the case of the dual speed measure. A coincidence factor of 50% was used for peak savings. CF = control factor = Traditionally flow rates have been reduced by increasing the head and riding the pump curve back to a new flow rate (throttling control). Alternately some systems have bypasses that divert a portion of the flow back to the pump inlet to reduce system flow (bypass control). Some pumps may use no controls, and run at constant flow. | per measure | 0.363 | 1543
861 | Motors | Pumps | VFD Pool Pump | VFDs on Residential Swimming Pool Pumps: Efficient Products | VFDs on Residential Swimming Pool Pumps | 3 | Active | 2017-01-01 |  | Pool Pump without speed control | [5 empty] | per measure | Algorithm | VFD on swimming pool |  |  | VFD on swimming pool |  |  | Algorithm | For each of the measures steady state operation was assumed. Morgan Measure libraries assumed a swimming season duration of May 1 through September 30. Morgan Measure libraries assumed the average pool volume is 25,000 gallons. The VFD on swimming pool pump measure is associated with the residential pool spa end use. |  | 425 |  | 10 | 2016-18 |  |  |  | Efficient Products |  | A base case and an improved case was calculated for each measure and the power reduction was taken as the average power reduction in the case of the single speed measure or the time weighted average power reduction in the case of the dual speed measure. A coincidence factor of 50% was used for peak savings. CF = control factor = Traditionally flow rates have been reduced by increasing the head and riding the pump curve back to a new flow rate (throttling control). Alternately some systems have bypasses that divert a portion of the flow back to the pump inlet to reduce system flow (bypass control). Some pumps may use no controls, and run at constant flow. | per measure | 0.2832 | 2052.8
969 | Building Shell | Insulation | Wall Insulation | Wall Insulation_MF: Low Income | Add Wall Insulation: R-13 + R-7.5 (Code) | 1 | InActive | 2013-01-02 | 2015-12-31 | Varies by vintage | [5 empty] | per 1,000 square feet | Algorithm | varies by vintage | [5 empty] | Algorithm |  |  | 3041.11 |  | 20 | 2013-15 |  |  |  | Low Income |  |  | per 1,000 square feet | 0.012 | 139.0
871 | Water Heating | Water Heaters | Conventional Water Heater | Water Heater - Electric : Efficient Products | Electric tank water heater with at least 0.93 EF | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.90 EF Standard Tank Water Heater | 0.9 | Efficiency Factor |  |  |  | per unit | Algorithm | .93 EF Efficient Water Heater | Efficiency Factor | 0.93 | .93 EF Efficient tank Water Heater or better |  |  | Algorithm | Water heater efficiency is rated according to its Energy Factor (EF). For residential storage tank electric water heaters, the current minimum standard requires an EF of 0.90 or greater. |  | 49 |  | 15 | 2013-15 |  |  |  | Efficient Products |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure | per measure | 0.018 | 157.0
871 | Water Heating | Water Heaters | Conventional Water Heater | Water Heater - Electric : Efficient Products | Electric tank water heater with at least 0.93 EF | 2 | InActive |  |  | 0.90 EF Standard Tank Water Heater | 0.9 | Efficiency Factor |  |  |  | per measure | Algorithm | .93 EF Efficient Water Heater | Efficiency Factor | 0.93 | .93 EF Efficient tank Water Heater or better |  |  | Algorithm | Water heater efficiency is rated according to its Energy Factor (EF). For residential storage tank electric water heaters, the current minimum standard requires an EF of 0.90 or greater. |  | 49 |  | 15 |  |  |  |  | Efficient Products |  |  | per measure | 0.013 | 246.0
901 | Water Heating | Water Heaters | Conventional Water Heater | Water Heater - Electric : Home Energy Performance | Electric tank water heater with at least 0.93 EF | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.90 EF Standard Tank Water Heater | 0.9 | Efficiency Factor |  |  |  | per unit | Algorithm | .93 EF Efficient Water Heater | Efficiency Factor | 0.93 | .93 EF Efficient tank Water Heater or better |  |  | Algorithm | Water heater efficiency is rated according to its Energy Factor (EF). For residential storage tank electric water heaters, the current minimum standard requires an EF of 0.90 or greater. |  | 49 |  | 15 | 2013-15 |  |  |  | Home Energy Performance |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure | per measure | 0.018 | 157.0
1091 | Water Heating | Water Heaters | Conventional Water Heater | Water Heater - Electric : New Home Construction | Electric tank water heater with at least 0.93 EF | 1 | InActive | 2013-01-02 | 2014-12-31 | 0.90 EF Standard Tank Water Heater | 0.9 | Efficiency Factor |  |  |  | per unit | Algorithm | .93 EF Efficient Water Heater | Efficiency Factor | 0.93 | .93 EF Efficient tank Water Heater or better |  |  | Algorithm | Water heater efficiency is rated according to its Energy Factor (EF). For residential storage tank electric water heaters, the current minimum standard requires an EF of 0.90 or greater. |  | 49 |  | 15 | 2013-15 |  |  |  | New Home Construction |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure | per measure | 0.018 | 157.0
1039 | Water Heating | Insulation | Tank Blanket | Water Heater, Tank Blanket-Insulation - Electric_MF: Low Income | Water heater blankets having an R value of 11 when wrapped around electric water heaters | 1 | InActive | 2013-01-02 | 2015-12-31 | Water heater with no insulation | [5 empty] | per measure | Algorithm | Electric Water Heater Tank Blanket Insulation, R-5 for Multifamily Dwelling |  |  | Electric water heater, minimum R-5 insulation |  |  | Algorithm |  |  | 18 |  | 15 | 2013-15 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.000 | 33.0
1039 | Water Heating | Insulation | Tank Blanket | Water Heater, Tank Blanket-Insulation - Electric_MF: Low Income | Water heater blankets having an R value of 11 when wrapped around electric water heaters | 2 | Active | 2016-01-01 |  | Water heater with no insulation | [5 empty] | per measure | Algorithm | Electric Water Heater Tank Blanket Insulation, R-5 for Multifamily Dwelling |  |  | Electric water heater, minimum R-5 insulation |  |  | Algorithm |  |  | 18 |  | 15 | 2016-18 |  |  |  | Low Income |  |  | per measure | 0.004 | 41
1041 | Water Heating | Insulation | Tank Blanket | Water Heater, Tank Blanket-Insulation - Electric_SF: Low Income | Water heater blankets having an R value of 11 when wrapped around electric water heaters | 1 | InActive | 2013-01-02 | 2015-12-31 | Water heater with no insulation | [5 empty] | per measure | Algorithm | Electric Water Heater Tank Blanket Insulation, R-5 for Single Family Dwelling |  |  | Electric water heater, minimum R-5 insulation |  |  | Algorithm |  |  | 18 |  | 10 | 2013-15 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.016 | 180.0
1041 | Water Heating | Insulation | Tank Blanket | Water Heater, Tank Blanket-Insulation - Electric_SF: Low Income | Water heater blankets having an R value of 11 when wrapped around electric water heaters | 2 | Active | 2016-01-01 |  | Water heater with no insulation | [5 empty] | per measure | Algorithm | Electric Water Heater Tank Blanket Insulation, R-5 for Single Family Dwelling |  |  | Electric water heater, minimum R-5 insulation |  |  | Algorithm |  |  | 58.81 |  | 15 | 2016-18 |  |  |  | Low Income |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.016 | 180.0
870 | Water Heating | Insulation | Tank Blanket | Water Heater, Tank Blanket-Insulation - Electric: Efficient Products | Water heater blankets having an R value of 11 when wrapped around electric water heaters | 1 | InActive | 2013-01-01 | 2015-12-30 | Water heater with no insulation | [5 empty] | per measure | Algorithm | Electric Water Heater Tank Blanket Insulation, R-5 |  |  | Electric water heater, minimum R-5 insulation |  |  | Algorithm |  |  | 18 |  | 10 | 2013-15 |  |  |  | Efficient Products |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.020 | 180.0
900 | Water Heating | Insulation | Tank Blanket | Water Heater, Tank Blanket-Insulation - Electric: Home Energy Performance | Water heater blankets having an R value of 11 when wrapped around electric water heaters | 1 | InActive | 2013-01-02 | 2015-12-31 | Water heater with no insulation | [5 empty] | per measure | Algorithm | Electric Water Heater Tank Blanket Insulation, R-5 |  |  | Electric water heater, minimum R-5 insulation |  |  | Algorithm |  |  | 18 |  | 10 | 2013-15 |  |  |  | Home Energy Performance |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the following table are to be used for each measure. | per measure | 0.020 | 180.0
1032 | Water Heating | Controls | Thermostat Setback | Water Heater, Thermostat Setback - Electric_MF: Low Income | Residential Water Heater thermostat set-back | 1 | InActive | 2013-01-02 | 2015-12-31 | Electric Water Heater Thermostat set at 135°F | 135 | degrees farenheit |  |  | Derived from Cadmus Potential Study list | per measure | Algorithm | Electric Water Heater Thermostat set at 120°F | degrees farenheit | 120 | Electric Water Heater Thermostat set at 120°F |  |  | Algorithm | Derived from Cadmus Potential Study measure list |  | 8 |  | 4 | 2013-15 |  |  |  | Low Income |  | Assumes a 40 gallon residential tank; Savings values based on Cadmus Potential Study measure list | per measure | 0.020 | 163.0
1215 | Water Heating | Controls | Thermostat Setback | Water Heater, Thermostat Setback - Electric_SF: Low Income | Residential Water Heater thermostat set-back to 120°F | 1 | Proposed | 2015-12-31 22:00 | [7 empty] | per measure | Algorithm | [6 empty] | Algorithm |  |  | 8 |  | 4 |  |  |  |  | Low Income |  |  | per measure | .020 | 163
863 | Water Heating | Controls | Thermostat Setback | Water Heater, Thermostat Setback - Electric: Efficient Products | Residential Water Heater thermostat set-back to 120°F | 1 | InActive | 2013-01-02 | 2015-12-31 | Electric Water Heater Thermostat set at 135°F | 135 | degrees farenheit |  |  | Derived from Cadmus Potential Study list | per measure | Algorithm | Electric Water Heater Thermostat set at 120°F | degrees farenheit | 120 |  |  |  | Algorithm | Derived from Cadmus Potential Study measure list |  | 8 |  | 4 | 2013-15 |  |  |  | Efficient Products |  | Assumes a 40 gallon residential tank. Savings derived from Cadmus Potential Study list | per measure | 0.020 | 163.0
863 | Water Heating | Controls | Thermostat Setback | Water Heater, Thermostat Setback - Electric: Efficient Products | Residential Water Heater thermostat set-back to 120°F | 2 | Active | 2016-01-01 | [6 empty] | Derived from Cadmus Potential Study list | per measure | Algorithm | [6 empty] | Algorithm |  |  | 8 |  | 4 | 2016 - 18 |  |  |  | Efficient Products |  | Assumes a 40 gallon residential tank. Savings derived from Cadmus Potential Study list | per measure | 0.014 | 163.0
896 | Water Heating | Controls | Thermostat Setback | Water Heater, Thermostat Setback - Electric: Home Energy Performance | Residential Water Heater thermostat set-back | 1 | InActive | 2013-01-02 | 2015-12-31 | Electric Water Heater Thermostat set at 135°F | 135 | degrees farenheit |  |  |  | per measure | Algorithm | Electric Water Heater Thermostat set at 120°F | degrees farenheit | 120 | Electric Water Heater Thermostat set at 120°F |  |  | Algorithm |  |  | 8 |  | 4 | 2013-15 |  |  |  | Home Energy Performance |  | Assumes a 40 gallon residential tank; Savings values based on Cadmus Potential Study measure list | per measure | 0.020 | 163.0
896 | Water Heating | Controls | Thermostat Setback | Water Heater, Thermostat Setback - Electric: Home Energy Performance | Residential Water Heater thermostat set-back | 2 | InActive |  |  | Electric Water Heater Thermostat set at 135°F | 135 | degrees farenheit |  |  | rived from Cadmus Potential Study list | per measure | Algorithm | Electric Water Heater Thermostat set at 120°F | degrees farenheit | 120 | Electric Water Heater Thermostat set at 120°F |  |  | Algorithm | Derived from Cadmus Potential Study measure list | 6.4 therns | 8 |  | 4 |  |  |  |  | Home Energy Performance |  |  | per measure | 0.000 | -16.0
1212 | Building Shell | Windows | Window Film | Window Film_MF: Efficient Products | Residential MF Window Film, 2 pane clear; SHGC = .73; U=.72 | 1 | Proposed | 2016-01-01 | [7 empty] | per measure | Algorithm | [6 empty] | Algorithm |  |  | 1.54 |  | 10 |  |  |  |  | Efficient Products |  |  | per measure | 4.0E-4 | 0.9297
970 | Building Shell | Windows | Window Film | Window Film_MF: Low Income | Residential MF Window Film, 2 pane clear; SHGC = .73; U=.72 | 1 | InActive | 2013-01-02 | 2015-12-31 | Existing window with SHGC=.39, U=.72 | 0.39 | SHGC |  |  |  | per measure | Algorithm | Minimum threshold for credit: 2 pane clear; SHGC = .73; U=.72 | SHGC | 0.73 |  |  |  | Algorithm |  |  | 538 |  | 10 | 2013-15 |  |  |  | Low Income |  | The savings values represented below were developed using building simulations. See Building Simulation Protocols section for further details. | per measure | 0.626 | 325.0
970 | Building Shell | Windows | Window Film | Window Film_MF: Low Income | Residential MF Window Film, 2 pane clear; SHGC = .73; U=.72 | 2 | Active | 2016-01-01 |  | Existing window with SHGC=.39, U=.72 | 0.39 | SHGC |  |  |  | per measure | Algorithm | Minimum threshold for credit: 2 pane clear; SHGC = .73; U=.72 | SHGC | 0.73 |  |  |  | Algorithm |  |  | 538 |  | 10 | 2016-18 |  |  |  | Low Income |  | The savings values represented below were developed using building simulations. See Building Simulation Protocols section for further details. | per measure | 0.1515 | 325
971 | Building Shell | Windows | Window Replacement | Window Replacement_MF: Low Income | Residential MF Window Replacement, SHGC=0.4, U=0.35 | 1 | InActive | 2013-01-02 | 2015-12-31 | Varies by Vintage | [5 empty] | per home | Algorithm | Minimum threshold for credit: SHGC=0.4, U Factor=0.35 | [5 empty] | Algorithm |  |  | 1500 |  | 20 | 2013-15 |  |  |  | Low Income |  | The savings values represented below were developed using building simulations. | per home | 0.692 | 2140.0
882 | Building Shell | Windows | Window Replacement | Window Replacement_SF: Efficient Products | Residential SF Window Replacement, SHGC=0.4, U=0.35 | 2 | Active | 2016-01-01 |  | Varies By Vintage | [5 empty] | per sq ft | Algorithm | Minimum threshold for credit: SHGC=0.4, U Factor=0.35 | [5 empty] | Algorithm |  |  | 4.33 |  | 20 | 2016-18 |  |  |  | Efficient Products |  | Based on 110 sq ft of windows | per sq ft | 0.0021 | 4.41
882 | Building Shell | Windows | Window Replacement | Window Replacement_SF: Efficient Products | Residential SF Window Replacement, SHGC=0.4, U=0.35 | 4 | Proposed | 2017-01-01 |  | Varies By Vintage | [5 empty] | per sq ft | Algorithm | Minimum threshold for credit: SHGC=0.4, U Factor=0.35 | [5 empty] | Algorithm |  | 16.8 therms | 12.61 |  | 20 |  |  |  |  | Efficient Products |  |  | per sq ft | 0.0012 | 2.52
882 | Building Shell | Windows | Window Replacement | Window Replacement_SF: Home Energy Performance | Residential SF Window Replacement, SHGC=0.4, U=0.35 | 1 | InActive | 2013-01-02 | 2015-12-31 | Varies By Vintage | [5 empty] | per home | Algorithm | Minimum threshold for credit: SHGC=0.4, U Factor=0.35 | [5 empty] | Algorithm |  | 38 therms | 1500 |  | 20 | 2013-15 |  |  |  | Home Energy Performance |  | The savings values represented below were developed using building simulations. | per home | 0.517 | 1103.0
1211 | Building Shell | Windows | Window Replacement | Window Replacement_SF: Low Income | Residential SF Window Replacement, SHGC=0.4, U=0.35 | 1 | Active | 2016-01-01 | [7 empty] | per sq ft | Algorithm | [6 empty] | Algorithm |  |  | 14 |  | 20 | 2016-18 |  |  |  | Low Income |  |  | per sq ft | 0.0012 | 2.53
1045 | Building Shell | Windows | Window Replacement | Window Replacement_SF: New Home Construction | Residential SF Window Replacement, SHGC=0.4, U=0.35 | 1 | InActive | 2013-01-02 | 2014-12-31 | Varies By Vintage | [5 empty] | per home | Algorithm | Minimum threshold for credit: SHGC=0.4, U Factor=0.35 | [5 empty] | Algorithm |  | 38 therms | 1500 |  | 20 | 2013-15 |  |  |  | New Home Construction |  | The savings values represented below were developed using building simulations. | per home | 0.517 | 1103.0
1045 | Building Shell | Windows | Window Replacement | Window Replacement_SF: New Home Construction | Residential SF Window Replacement, SHGC=0.4, U=0.35 | 2 | InActive |  |  | Varies By Vintage | [5 empty] | per home | Algorithm | Minimum threshold for credit: SHGC=0.4, U Factor=0.35 | [5 empty] | Algorithm |  |  | 475.78 |  | 20 |  |  |  |  | New Home Construction |  | The savings values represented below were developed using building simulations. | per home | 0.517 | 486
726 | HVAC | Space Cooling | Packaged DX | AC 135,000 - 240,000: Biz Prescriptive | SEER 11 Unitary Air Conditioner <135,000 to <240,000 BTU/hr Replacing SEER 9.5 | 1 | Active | 2013-01-02 |  | 9.5 EER Unitary AC | 9.5 | EER |  |  |  | per ton | Algorithm | 11.0 EER Unitary AC | EER | 11 | 11.0 EER Unitary AC |  |  | Algorithm | To most accurately measure energy and demand savings attributable to heating, ventilation, and air conditioning measures, building simulation modeling should be conducted (see Section 05 below), however, if the resources required to complete building simulation analysis are not available, the following equations can be used to estimate savings. If a measure does not have a savings algorithm associated with it, the deemed values represented in the table should be used. |  | 110.89 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure | per ton | 0.1084 | 119.0 | Early Replacement
726-1 | HVAC | Space Cooling | Packaged DX | AC 240,000 - 760,000: Biz Prescriptive | SEER 11 Unitary Air Conditioner <135,000 to <240,000 BTU/hr Replacing SEER 9.5 | 1 | Active | 2016-01-02 |  | 9.5 EER Unitary AC | 9.5 | EER |  |  |  | per ton | Algorithm | 11.0 EER Unitary AC | EER | 11 | 11.0 EER Unitary AC |  |  | Algorithm | To most accurately measure energy and demand savings attributable to heating, ventilation, and air conditioning measures, building simulation modeling should be conducted (see Section 05 below), however, if the resources required to complete building simulation analysis are not available, the following equations can be used to estimate savings. If a measure does not have a savings algorithm associated with it, the deemed values represented in the table should be used. |  | 115.13 |  | 15 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure | per ton | 0.0568 | 62.4 | Early Replacement
727 | HVAC | Space Cooling | Packaged DX | AC greater than 760,000: Biz Prescriptive | 10 EER Unitary Air Conditioner >760,000 BTU/hr Replacing 9 ERR | 1 | Active | 2013-01-02 |  | 9 EER Air Conditioner | 9 | EER |  |  |  | per ton | Algorithm | 10 EER Air Conditioner | EER | 10 | 10 EER Air Conditioner |  |  | Algorithm | To most accurately measure energy and demand savings attributable to heating, ventilation, and air conditioning measures, building simulation modeling should be conducted (see Section 05 below), however, if the resources required to complete building simulation analysis are not available, the following equations can be used to estimate savings. If a measure does not have a savings algorithm associated with it, the deemed values represented in the table should be used. |  | 98.38 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.0839 | 92.1 | Early Replacement
728 | HVAC | Space Cooling | Packaged DX | AC less than 65,000 1 Ph: Biz Prescriptive | 14 SEER Unitary Air Conditioner <65,000 BTU/hr Replacing 13 SEER | 1 | Active | 2013-01-02 |  | SEER 13 Air Conditioner | 13 | SEER |  |  |  | per ton | Algorithm | SEER 14 Air Conditioner | SEER | 14 | SEER 14 Air Conditioner |  |  | Algorithm | To most accurately measure energy and demand savings attributable to heating, ventilation, and air conditioning measures, building simulation modeling should be conducted (see Section 05 below), however, if the resources required to complete building simulation analysis are not available, the following equations can be used to estimate savings. If a measure does not have a savings algorithm associated with it, the deemed values represented in the table should be used. |  | 55.57 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.0594 | 65.2 | Early Replacement
2800 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Recip Chiller COP = 2.8, IPLV = 3.41: Biz Prescriptive | Air-Cooled Recip Chiller (COP = 2.8, IPLV = 3.41) | 1 | Active | 2016-01-01 |  |  | 3.41 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 45.07 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.02 | 126.5 | Early Replacement
2801 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Recip Chiller COP = 2.8, IPLV = 3.89: Biz Prescriptive | Air-Cooled Recip Chiller (COP = 2.8, IPLV = 3.89) | 1 | Active | 2016-01-01 |  |  | 3.89 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 92.04 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.041 | 268.7 | Early Replacement
2802 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Recip Chiller COP = 2.8, IPLV = 4.24: Biz Prescriptive | Air-Cooled Recip Chiller (COP = 2.8, IPLV = 4.24) | 1 | Active | 2016-01-01 |  |  | 4.24 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 119.59 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.053 | 338.6 | Early Replacement
2803 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Recip Chiller COP = 3.08, IPLV = 3.36: Biz Prescriptive | Air-Cooled Recip Chiller (COP = 3.08, IPLV = 3.36) | 1 | Active | 2016-01-01 |  |  | 3.36 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 58.58 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.104 | 222.9 | Early Replacement
2804 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Recip Chiller COP = 3.08, IPLV = 3.76: Biz Prescriptive | Air-Cooled Recip Chiller (COP = 3.08, IPLV = 3.76) | 1 | Active | 2016-01-01 |  |  | 3.76 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 99.68 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.123 | 338 | Early Replacement
2805 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Recip Chiller COP = 3.08, IPLV = 4.28: Biz Prescriptive | Air-Cooled Recip Chiller (COP = 3.08, IPLV = 4.28) | 1 | Active | 2016-01-01 |  |  | 4.28 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 141.63 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.142 | 467.5 | Early Replacement
2806 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Recip Chiller COP = 3.08, IPLV = 4.67: Biz Prescriptive | Air-Cooled Recip Chiller (COP = 3.08, IPLV = 4.67) | 1 | Active | 2016-01-01 |  |  | 4.67 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 166.96 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.152 | 531.2 | Early Replacement
2807 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Recip Chiller COP = 3.36, IPLV = 3.66: Biz Prescriptive | Air-Cooled Recip Chiller (COP = 3.36, IPLV = 3.66) | 1 | Active | 2016-01-01 |  |  | 3.66 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 106.23 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.192 | 410.9 | Early Replacement
2808 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Recip Chiller COP = 3.36, IPLV = 4.10: Biz Prescriptive | Air-Cooled Recip Chiller (COP = 3.36, IPLV = 4.10) | 1 | Active | 2016-01-01 |  |  | 4.1 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 144.29 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.209 | 516.5 | Early Replacement
2809 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Recip Chiller COP = 3.36, IPLV = 4.67: Biz Prescriptive | Air-Cooled Recip Chiller (COP = 3.36, IPLV = 4.67) | 1 | Active | 2016-01-01 |  |  | 4.67 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 182.94 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.227 | 635.2 | Early Replacement
2810 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Recip Chiller COP = 3.36, IPLV = 5.09: Biz Prescriptive | Air-Cooled Recip Chiller (COP = 3.36, IPLV = 5.09) | 1 | Active | 2016-01-01 |  |  | 5.09 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 205.88 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.236 | 693.6 | Early Replacement
2811 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Screw Chiller COP = 2.8, IPLV = 3.46: Biz Prescriptive | Air-Cooled Screw Chiller (COP = 2.8, IPLV = 3.46) | 1 | Active | 2016-01-01 |  |  | 3.46 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 50.57 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.024 | 142.4 | Early Replacement
2812 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Screw Chiller COP = 2.8, IPLV = 3.64: Biz Prescriptive | Air-Cooled Screw Chiller (COP = 2.8, IPLV = 3.64) | 1 | Active | 2016-01-01 |  |  | 3.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 69.12 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.044 | 204.6 | Early Replacement
2813 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Screw Chiller COP = 2.8, IPLV = 4.75: Biz Prescriptive | Air-Cooled Screw Chiller (COP = 2.8, IPLV = 4.75) | 1 | Active | 2016-01-01 |  |  | 4.75 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 152.46 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.065 | 380.3 | Early Replacement
2814 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Screw Chiller COP = 3.08, IPLV = 3.36: Biz Prescriptive | Air-Cooled Screw Chiller (COP = 3.08, IPLV = 3.36) | 1 | Active | 2016-01-01 |  |  | 3.36 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 58.58 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.106 | 223.5 | Early Replacement
2815 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Screw Chiller COP = 3.08, IPLV = 3.80: Biz Prescriptive | Air-Cooled Screw Chiller (COP = 3.08, IPLV = 3.80) | 1 | Active | 2016-01-01 |  |  | 3.8 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 103.31 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.128 | 353.2 | Early Replacement
2816 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Screw Chiller COP = 3.08, IPLV = 4.00: Biz Prescriptive | Air-Cooled Screw Chiller (COP = 3.08, IPLV = 4.00) | 1 | Active | 2016-01-01 |  |  | 4 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 120.4 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.146 | 409.8 | Early Replacement
2817 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Screw Chiller COP = 3.08, IPLV = 5.22: Biz Prescriptive | Air-Cooled Screw Chiller (COP = 3.08, IPLV = 5.22) | 1 | Active | 2016-01-01 |  |  | 5.22 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 196.24 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.166 | 569.8 | Early Replacement
2818 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Screw Chiller COP = 3.36, IPLV = 3.66: Biz Prescriptive | Air-Cooled Screw Chiller (COP = 3.36, IPLV = 3.66) | 1 | Active | 2016-01-01 |  |  | 3.66 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 106.23 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.196 | 412.2 | Early Replacement
2819 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Screw Chiller COP = 3.36, IPLV = 4.15: Biz Prescriptive | Air-Cooled Screw Chiller (COP = 3.36, IPLV = 4.15) | 1 | Active | 2016-01-01 |  |  | 4.15 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 148.11 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.216 | 531 | Early Replacement
2820 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Screw Chiller COP = 3.36, IPLV = 4.42: Biz Prescriptive | Air-Cooled Screw Chiller (COP = 3.36, IPLV = 4.42) | 1 | Active | 2016-01-01 |  |  | 4.42 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 167.22 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.233 | 583 | Early Replacement
2821 | HVAC | Space Cooling | Chiller, Air-Cooled Recip | Air-Cooled Screw Chiller COP = 3.36, IPLV = 5.69: Biz Prescriptive | Air-Cooled Screw Chiller (COP = 3.36, IPLV = 5.69) | 1 | Active | 2016-01-01 |  |  | 5.69 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm |  | kW/Ton | 0.25 |  |  |  | Algorithm |  |  | 232.77 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.251 | 729.6 | Early Replacement
691 | HVAC | HVAC Controls | CHW Reset | CHW reset 10 deg: Biz Prescriptive | Chilled Water Reset Control by 10 degrees | 1 | InActive | 2013-01-02 | 2015-12-31 | 45 degree F fixed chilled-water temperature setpoint | 45 | degree setpoint |  |  |  | per ton | Algorithm | Reset water temperature to increase by 10 degrees | degree increase | 10 | Reset water temperature to increase by 10 degrees |  |  | Algorithm |  |  | 0.8 |  | 5 | 2013-15 |  |  |  | Biz Prescriptive |  | Assumption: 612.4 ton unit. Energy savings=54,362.9 kWh and Demand savings=3.928 kW | per ton | 0.0395 | 89.0 | Early Replacement
692 | HVAC | HVAC Controls | CHW Reset | CHW reset 5 deg: Biz Prescriptive | Chilled Water Reset Control by 5 degrees | 1 | InActive | 2013-01-02 | 2015-12-31 | 45 degree F fixed chilled-water temperature setpoint | 45 | degree setpoint |  |  |  | per ton | Algorithm | Reset water temperature to increase by 5 degrees | degree increase | 5 | Reset water temperature to increase by 5 degrees |  |  | Algorithm |  |  | 0.8 |  | 5 | 2013-15 |  |  |  | Biz Prescriptive |  | Assumption: 612.4 ton unit. Energy savings=45,821.1 kWh and Demand Savings=3.580 kW | per ton | 0.0329 | 74.0 | Early Replacement
674 | Compressed Air | O&M | System Optimization | Compressed Air Optimization: Biz Prescriptive | Compressed air optimization: 20% Improvement in air compressor energy consumption | 1 | InActive | 2013-01-02 | 2015-12-31 | N/A | [5 empty] | per measure | Algorithm | 20% improvement in air compressor energy consumption | improvement per unit | 0.2 | 20% Improvement in air compressor energy consumption |  |  | Algorithm |  |  | 16 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | Key Assumptions: Assumes 20% improvement over base case; see ICF Program Model | per measure | 0.0276 | 200.0 | Early Replacement
1169 | Custom | Custom | Custom | Custom Measure: Biz Custom | Measure protocols to be used to calculate energy and demand savings for any custom measure | 1 | Active | 2013-01-02 |  | n/a | [6 empty] | Algorithm | n/a |  |  | n/a |  |  | Algorithm |  |  | variable based on parameters |  |  | 2013-15, 2016-18 |  |  |  | Custom |  |  |  | variable based on parameters | variable based on parameters | Early Replacement
3027 | HVAC | Fans | Continuous Fan | ECM Motors on Furnaces (per furnace): Biz Prescriptive | ECM Motors on Furnaces | 1 | InActive | [19 empty] | 1250 |  | 10 |  |  |  |  | Biz Prescriptive |  | MEMD | per furnace | 0.3197 | 720
3027-1 | HVAC | Fans | Continuous Fan | ECM Motors on Furnaces (per HP): Biz Prescriptive | ECM Motors on Furnaces | 1 | InActive | [19 empty] | 1468 |  | 10 |  |  |  |  | Biz Prescriptive |  | MEMD | per HP | 0.5985 | 1348
693 | HVAC | HVAC Controls | EMS | EMS: Biz Prescriptive | Energy Management System | 1 | InActive | 2013-01-02 | 2015-12-31 | Constant chilled water temperature setpoint, loop pumps operating 24/7 | [5 empty] | per square foot | Algorithm | Chilled water temperature setback and on/off scheduling of loop pumps |  |  | Chilled water temperature setback and on/off scheduling of loop pumps |  |  | Algorithm |  |  | 0.32 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Tons = 612.4; Total kWh savings for 5 degree reset = 45,821.1 kWh; Total kW savings for 5 degree rest = 3.580 kW; Total kWh savings for 10 degree rest = 54,362.9 kWh; Total kW savings for 10 degree reset = 3.928 kW | per square foot | 4.0E-4 | 0.8 | Early Replacement
679 | Cooking | Holding Cabinets | Holding Cabinet, electric | ENERGY STAR Hot Holding Cabinets Full Size - Electric: Biz Prescriptive | ENERGY STAR Hot Holding Cabinets Full Size | 1 | InActive | 2013-01-02 | 2015-12-31 | Electric Hot Food Holding Cabinets (70 W/ft³) | 70 | W/ft3 |  |  |  | per measure | Algorithm | Energy Star Hot Food Holding Cabinet (< 40 W/ft³ internal volume) | W/ft3 | 40 | Energy Star Hot Food Holding Cabinet (< 40 W/ft³ internal volume) |  |  | Algorithm | The demand is assumed to be the average demand (per Food Service Technology Center). |  | 1783 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per measure | 1.055 | 5277.9 | Early Replacement
679 | Cooking | Holding Cabinets | Holding Cabinet, electric | ENERGY STAR Hot Holding Cabinets Full Size - Electric: Biz Prescriptive | ENERGY STAR Hot Holding Cabinets Full Size | 2 | Active | 2016-01-01 |  | Electric Hot Food Holding Cabinets (70 W/ft³) | 70 | W/ft3 |  |  |  | per measure | Algorithm | Energy Star Hot Food Holding Cabinet (< 40 W/ft³ internal volume) | W/ft3 | 40 | Energy Star Hot Food Holding Cabinet (< 40 W/ft³ internal volume) |  |  | Algorithm | The demand is assumed to be the average demand (per Food Service Technology Center). |  | 1783 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per measure | 1.3241 | 6624 | Early Replacement
679 | Cooking | Holding Cabinets | Holding Cabinet, electric | ENERGY STAR Hot Holding Cabinets Full Size - Electric: Biz Prescriptive | ENERGY STAR Hot Holding Cabinets Full Size | 3 | Proposed | 2017-01-01 |  | Electric Hot Food Holding Cabinets (70 W/ft³) | 70 | W/ft3 |  |  |  | per measure | Algorithm | Energy Star Hot Food Holding Cabinet (< 40 W/ft³ internal volume) | W/ft3 | 40 | Energy Star Hot Food Holding Cabinet (< 40 W/ft³ internal volume) |  |  | Algorithm | The demand is assumed to be the average demand (per Food Service Technology Center). |  | 1783 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per measure | 1.055 | 5277.9 | Early Replacement
1094 | Cooking | Holding Cabinets | Holding Cabinet, electric | ENERGY STAR Hot Holding Cabinets Half Size - Electric: Biz Prescriptive | ENERGY STAR Hot Holding Cabinets Full Size | 1 | InActive | 2013-01-02 | 2015-12-31 | Electric Hot Food Holding Cabinets (70 W/ft³) | 70 | W/ft3 |  |  |  | per measure | Algorithm | Energy Star Hot Food Holding Cabinet (< 40 W/ft³ internal volume) | W/ft3 | 40 | Energy Star Hot Food Holding Cabinet (< 40 W/ft³ internal volume) |  |  | Algorithm | The demand is assumed to be the average demand (per Food Service Technology Center). |  | 1783 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per measure | 0.3575 | 1788.4 | Early Replacement
1093 | Cooking | Holding Cabinets | Holding Cabinet, electric | ENERGY STAR Hot Holding Cabinets Three-Quarter Size - Electric: Biz Prescriptive | ENERGY STAR Hot Holding Cabinets Full Size | 1 | InActive | 2013-01-02 | 2015-12-31 | Electric Hot Food Holding Cabinets (70 W/ft³) | 70 | W/ft3 |  |  |  | per measure | Algorithm | Energy Star Hot Food Holding Cabinet (< 40 W/ft³ internal volume) | W/ft3 | 40 | Energy Star Hot Food Holding Cabinet (< 40 W/ft³ internal volume) |  |  | Algorithm | The demand is assumed to be the average demand (per Food Service Technology Center). |  | 1783 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per measure | 0.5662 | 2832.3 | Early Replacement
675 | Cooking | Cooking Equipment | Steamer | ENERGY STAR Steam Cookers 3 Pan - Electric: Biz Prescriptive | ENERGY STAR Steam Cookers 3 Pan (50% Efficient replacing 26% efficient unit) | 1 | Active | 2013-01-02 |  | Electric Steam Cooker 26% Heavy Load Cooking Energy Efficiency | 26 | Heavy Load Cooking Energy Efficiency (%) |  |  |  | per measure | Algorithm | Energy Star Steam Cooker 50% Heavy Load Cooking Energy Efficiency | Heavy Load Cooking Energy Efficiency (%) | 50 | Energy Star Steam Cooker (50% efficient) |  |  | Algorithm |  |  | 4150 |  | 12 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | One pre-heat daily, the preheat time is assumed to be 15 minutes, and the preheat energy 1.5 kWh/day; If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per measure | 2.2364 | 11188.0 | Early Replacement
676 | Cooking | Cooking Equipment | Steamer | ENERGY STAR Steam Cookers 4 Pan - Electric: Biz Prescriptive | ENERGY STAR Steam Cookers 4 Pan (50% Efficient replacing 26% efficient unit) | 1 | Active | 2013-01-02 |  | Electric Steam Cooker 26% Heavy Load Cooking Energy Efficiency | 26 | Heavy Load Cooking Energy Efficiency (%) |  |  |  | per measure | Algorithm | Energy Star Steam Cooker 50% Heavy Load Cooking Energy Efficiency | Heavy Load Cooking Energy Efficiency (%) | 50 | Energy Star Steam Cooker (50% efficient) |  |  | Algorithm |  |  | 4150 |  | 12 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | One pre-heat daily, the preheat time is assumed to be 15 minutes, and the preheat energy 1.5 kWh/day; If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per measure | 2.4306 | 12159.2 | Early Replacement
677 | Cooking | Cooking Equipment | Steamer | ENERGY STAR Steam Cookers 5 Pan - Electric: Biz Prescriptive | ENERGY STAR Steam Cookers 5 Pan (50% Efficient replacing 26% efficient unit) | 1 | Active | 2013-01-02 |  | Electric Steam Cooker 26% Heavy Load Cooking Energy Efficiency | 26 | Heavy Load Cooking Energy Efficiency (%) |  |  |  | per measure | Algorithm | Energy Star Steam Cooker 50% Heavy Load Cooking Energy Efficiency | Heavy Load Cooking Energy Efficiency (%) | 50 | Energy Star Steam Cooker (50% efficient) |  |  | Algorithm |  |  | 4150 |  | 12 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | One pre-heat daily, the preheat time is assumed to be 15 minutes, and the preheat energy 1.5 kWh/day; If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per measure | 2.6264 | 13138.9 | Early Replacement
678 | Cooking | Cooking Equipment | Steamer | ENERGY STAR Steam Cookers 6 Pan - Electric: Biz Prescriptive | ENERGY STAR Steam Cookers 6 Pan (50% Efficient replacing 26% efficient unit) | 1 | Active | 2013-01-02 |  | Electric Steam Cooker 26% Heavy Load Cooking Energy Efficiency | 26 | Heavy Load Cooking Energy Efficiency (%) |  |  |  | per measure | Algorithm | Energy Star Steam Cooker 50% Heavy Load Cooking Energy Efficiency | Heavy Load Cooking Energy Efficiency (%) | 50 | Energy Star Steam Cooker (50% efficient) |  |  | Algorithm |  |  | 4150 |  | 12 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | One pre-heat daily, the preheat time is assumed to be 15 minutes, and the preheat energy 1.5 kWh/day; If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per measure | 3.0323 | 15169.4 | Early Replacement
686 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP under 135,000 17EER: Biz Prescriptive | Ground Source Heat Pump <135,000 BTU/hr | 1 | Active | 2013-01-02 |  | 13.4 EER Ground Source Heat Pump | 13.4 | EER |  |  |  | per ton | Algorithm | 17 EER Ground Source Heat Pump | EER | 17 | 17 EER Ground Source Heat Pump |  |  | Algorithm |  |  | 180 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure | per ton | 0.1066 | 240.1 | Early Replacement
687 | HVAC | Heat Pumps | Heat Pump, Ground Source | GSHP under 135,000 19EER: Biz Prescriptive | Ground Source Heat Pump <135,000 BTU/hr | 1 | Active | 2013-01-02 |  | 13.4 EER Ground Source Heat Pump | 13.4 | EER |  |  |  | per ton | Algorithm | 19 EER Ground Source Heat Pump | EER | 19 | 19 EER Ground Source Heat Pump |  |  | Algorithm |  |  | 180 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.1356 | 305.4 | Early Replacement
695 | HVAC | HVAC Controls | Guest Room Control | Guest Room Energy Management, Electric Heating: Biz Prescriptive | Guest Room Energy Management System – Electric Heating (Hotel/Lodging) | 1 | InActive | 2013-01-02 | 2015-12-31 | Manual Controls | [5 empty] | per room | Algorithm | Keycard occupancy sensors and passive infrared occupancy sensors | [5 empty] | Algorithm | This measure only incorporates heating and cooling savings. To the extent any lighting is also controlled, those savings can be found in the Commercial Lighting Controls section of the TRM |  | 600 |  | 9 | 2013-15 |  |  |  | Biz Prescriptive |  | Assumes 30% energy savings over baseline; If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure | per room | 0.494 | 1112.6 | Early Replacement
683 | HVAC | Heat Pumps | Heat Pump | HP 135,000 - 240,000: Biz Prescriptive | 10 EER Heat Pump >135,000 to <240,000 BTU/hr replacing 9.1 EER unit | 1 | Active | 2013-01-02 |  | 9.1 EER Heat Pump | 9.1 | EER |  |  |  | per ton | Algorithm | 10 EER Heat Pump | EER | 10 | 10 EER Heat Pump |  |  | Algorithm | To most accurately measure energy and demand savings attributable to heating, ventilation, and air conditioning measures, building simulation modeling should be conducted (see Section 05 below), however, if the resources required to complete building simulation analysis are not available, the following equations can be used to estimate savings. If a measure does not have a savings algorithm associated with it, the deemed values represented in the table should be used. |  | 125 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure | per ton | 0.0635 | 143.0 | Early Replacement
684 | HVAC | Heat Pumps | Heat Pump | HP over 240,000: Biz Prescriptive | 10 EER Heat Pump >240,000 BTU/hr Replacing 8.8 EER unit | 1 | Active | 2013-01-02 |  | 8.8 EER Heat Pump | 8.8 | EER |  |  |  | per ton | Algorithm | 10 EER Heat Pump | EER | 10 | 10 EER Heat Pump |  |  | Algorithm | To most accurately measure energy and demand savings attributable to heating, ventilation, and air conditioning measures, building simulation modeling should be conducted (see Section 05 below), however, if the resources required to complete building simulation analysis are not available, the following equations can be used to estimate savings. If a measure does not have a savings algorithm associated with it, the deemed values represented in the table should be used. |  | 130 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure | per ton | 0.0777 | 175.1 | Early Replacement
685 | HVAC | Heat Pumps | Heat Pump | HP under 65,000 1 Ph: Biz Prescriptive | 14 SEER (7.97 HSPF) Heat Pump <65,000 BTU/hr Replacing 13 SEER (7.7 HSPF) unit | 1 | Active | 2013-01-02 |  | 13.0 SEER, 7.7 HSPF | 13 | SEER |  |  |  | per ton | Algorithm | 14 SEER; 7.97 HSPF Heat Pump | SEER | 14 | 14 SEER Heat Pump |  |  | Algorithm | To most accurately measure energy and demand savings attributable to heating, ventilation, and air conditioning measures, building simulation modeling should be conducted (see Section 05 below), however, if the resources required to complete building simulation analysis are not available, the following equations can be used to estimate savings. If a measure does not have a savings algorithm associated with it, the deemed values represented in the table should be used. |  | 73.5 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | Baseline: 7.7 HSPF; Retrofit: 7.97 HSPF; If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure | per ton | 0.0507 | 114.1 | Early Replacement
3058 | HVAC | HVAC Controls | Guest Room Control | HVAC - Occupancy Sensors: Biz Prescriptive | HVAC - Occupancy Sensors | 1 | Active | 2016-01-01 | [7 empty] | per building | [10 empty] | 6002 |  | 8 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per building | 5.7347 | 12916.48
3000 | Custom | New Construction | New Construction | New Construction: Biz New Construction | Measure protocols to be used to calculate energy and demand savings for any new construction measure | 1 | Active | 2013-01-02 |  | n/a | [6 empty] | Algorithm | n/a |  |  | n/a |  |  | Algorithm |  |  | variable based on parameters |  |  | 2013-15, 2016-18 |  |  |  | Biz New Construction |  |  |  | variable based on parameters | variable based on parameters | Early Replacement
1184 | Appliances | Refrigerators | Night Cover | Night Cover: Biz Prescriptive | Night cover on an open refrigerated case | 1 | InActive | 2013-01-02 | 2015-12-31 | No Covers | [5 empty] | per linear foot | Algorithm | Night covers installed |  |  | Night covers installed |  |  | Algorithm |  |  | 15 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | Applicant must install a night cover on an open refrigerated case at close of business each day. The savings estimate for this measure assumes that a night cover is placed on an open case that was previously left uncovered. Hours of operation = for a minimum of 6 hours per day, assumed 2,190 hours per year | per linear foot | 0.0059 | 43.8 | Early Replacement
1191 | Custom | RCx | RCx | Retrocommissioning: Biz RCx | Measure protocols to be used to calculate energy and demand savings for any retrocommissioning measure | 1 | Active | 2013-01-02 |  | n/a | [6 empty] | Algorithm | n/a |  |  | n/a |  |  | Algorithm |  |  | variable based on parameters |  |  | 2013-15, 2016-18 |  |  |  | Biz RCx |  |  |  | variable based on parameters | variable based on parameters | Early Replacement
697 | HVAC | HVAC Controls | Thermostat Setback | Setback-Setup Thermostat: Biz Prescriptive | Setback Thermostat: Restore unit to nameplate SEER | 1 | InActive | 2013-01-02 | 2015-12-31 | 10% EER degradation | 0.1 | percent EER degradation |  |  |  | per 1,000 square feet | Algorithm | Restore unit to nameplate SEER |  |  | Restore unit to nameplate SEER |  |  | Algorithm |  |  | 174 |  | 9 | 2013-15 |  |  |  | Biz Prescriptive |  |  | per 1,000 square feet | 0.4382 | 987.0 | Early Replacement
3085 | HVAC | HVAC Controls | Smart Thermostat | Smart Thermostat: Biz Prescriptive | Smart Thermostat | 1 | Active | 2017-06-01 | [7 empty] | per measure | [10 empty] | 224 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.1867 | 205
681 | Heating | Engine Block Heaters | Tractor Heater Timers | Tractor Heater Timers: Biz Prescriptive | Tractor Heater Timers | 1 | Active | 2013-01-02 |  | N/A | [5 empty] | per measure | Algorithm | N/A |  |  | Tractor Heater Timer |  |  | Algorithm |  |  | 35 |  | 10 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per measure | 0.0 | 576.0 | Early Replacement
3046 | HVAC | Pumps | VFD | VFD CHW Pump CV reheat econ: Biz Prescriptive | VFD CHW Pump CV reheat econ | 1 | Active | 2016-01-01 | [18 empty] | 198 |  | 15 | 2016-18 |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 2.4845 | 5596
3045 | HVAC | Pumps | VFD | VFD CHW Pump CV reheat no econ: Biz Prescriptive | VFD CHW Pump CV reheat no econ | 1 | InActive | [19 empty] | 198 |  | 15 |  |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 2.3962 | 5397
3047 | HVAC | Pumps | VFD | VFD CHW Pump VAV reheat econ: Biz Prescriptive | VFD CHW Pump VAV reheat econ | 1 | InActive | [19 empty] | 198 |  | 15 |  |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 2.4006 | 5407
3052 | HVAC | Pumps | VFD | VFD CW Pump CV reheat econ: Biz Prescriptive | VFD CW Pump CV reheat econ | 1 | InActive | [19 empty] | 198 |  | 15 |  |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 0.3867 | 871
3051 | HVAC | Pumps | VFD | VFD CW Pump CV reheat no econ: Biz Prescriptive | VFD CW Pump CV reheat no econ | 1 | InActive | [19 empty] | 198 |  | 15 |  |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 0.3632 | 818
3053 | HVAC | Pumps | VFD | VFD CW Pump VAV reheat econ: Biz Prescriptive | VFD CW Pump VAV reheat econ | 1 | InActive | [19 empty] | 198 |  | 15 |  |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 0.4276 | 963
3049 | HVAC | Pumps | VFD | VFD HW Pump CV reheat econ: Biz Prescriptive | VFD HW Pump CV reheat econ | 1 | InActive | [19 empty] | 198 |  | 15 |  |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 2.211 | 4980
3048 | HVAC | Pumps | VFD | VFD HW Pump CV reheat no econ: Biz Prescriptive | VFD HW Pump CV reheat no econ | 1 | InActive | [19 empty] | 198 |  | 15 |  |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 2.5298 | 5698
3050 | HVAC | Pumps | VFD | VFD HW Pump VAV reheat econ: Biz Prescriptive | VFD HW Pump VAV reheat econ | 1 | InActive | [19 empty] | 198 |  | 15 |  |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 2.4157 | 5441
3040 | HVAC | Pumps | VFD | VFD Return Fan VAV reheat econ: Biz Prescriptive | VFD Return Fan VAV reheat econ | 1 | InActive | [19 empty] | 198 |  | 15 |  |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 0.4617 | 1040
3041 | HVAC | Pumps | VFD | VFD Supply Fan VAV reheat econ: Biz Prescriptive | VFD Supply Fan VAV reheat econ | 1 | InActive | [19 empty] | 198 |  | 15 |  |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 0.5514 | 1242
3043 | HVAC | Pumps | VFD | VFD Tower Fan CV reheat econ: Biz Prescriptive | VFD Tower Fan CV reheat econ | 1 | InActive | [19 empty] | 198 |  | 15 |  |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 0.2824 | 636
3042 | HVAC | Pumps | VFD | VFD Tower Fan CV reheat no econ: Biz Prescriptive | VFD Tower Fan CV reheat no econ | 1 | InActive | [19 empty] | 198 |  | 15 |  |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 0.3285 | 740
3044 | HVAC | Pumps | VFD | VFD Tower Fan VAV reheat econ: Biz Prescriptive | VFD Tower Fan VAV reheat econ | 1 | InActive | [19 empty] | 198 |  | 15 |  |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 0.202 | 455
673 | Compressed Air | Equipment | Variable Speed Drive | VSD Air Compressors: Biz Prescriptive | VSD Air Compressor | 1 | InActive | 2013-01-02 | 2015-12-31 | Screw Air Compressor with Modulation Control | [5 empty] | per HP | Algorithm | Screw Air Compressor with Variable Speed Drive (VSD) Control | [5 empty] | Algorithm |  |  | 1 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  |  | per HP | 8.0E-4 | 5.8 | Early Replacement
4001 | Building Shell | Windows | Window Film | Window Film: Biz Prescriptive | Window Film | 1 | Active | 2016-01-01 | [7 empty] | per 100 sq ft | [10 empty] | 153.77 |  | 10 | 2016-18 | [6 empty] | 100 sq ft | 0.1849 | 416.48
671 | Building Shell | Windows | Window Replacement | Window replacement: Biz Prescriptive | Window replacement in commercial building above IECC 2009 minimum | 1 | Active | 2013-01-02 |  | Windows that meet International Energy Conservation Code (IECC) 2004 |  |  |  |  | Cost values derived from GEP Potential Study Measure list | per building | Algorithm | Windows that exceed IECC 2009 | [5 empty] | Algorithm |  |  | 7994.87 |  | 20 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | Key Assumptions: Savings are on a per building basis. Savings values derived from GEP Potential Study Measure list | per building | 12.5684 | 28308.24 | Early Replacement
2732 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.51 kWperTon with 0.3 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.51 kWperTon with 0.3 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.51 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.51 |  |  |  | Algorithm |  |  | 161.85 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.137 | 402.8 | Early Replacement
2733 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.51 kWperTon with 0.36 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.51 kWperTon with 0.36 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.51 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.51 |  |  |  | Algorithm |  |  | 149.24 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.131 | 359.1 | Early Replacement
705 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.51 kWperTon with 0.39 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.51 kWperTon with 0.39 kWperTon IPLV) | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.51 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.51 |  |  |  | Algorithm |  |  | 143 |  | 20 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.128 | 375.2 | Early Replacement
705 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.51 kWperTon with 0.39 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.51 kWperTon with 0.39 kWperTon IPLV) | 2 | Active | 2016-01-01 |  | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.51 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.51 |  |  |  | Algorithm |  |  | 143.51 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.128 | 336.6 | Early Replacement
2734 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.51 kWperTon with 0.41 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.51 kWperTon with 0.41 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.51 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.51 |  |  |  | Algorithm |  |  | 137.78 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.125 | 316.2 | Early Replacement
2735 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.51 kWperTon with 0.48 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.51 kWperTon with 0.48 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.51 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.51 |  |  |  | Algorithm |  |  | 122.87 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.116 | 256.4 | Early Replacement
2736 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.57 kWperTon with 0.34 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.57 kWperTon with 0.34 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.57 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.57 |  |  |  | Algorithm |  |  | 105.29 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.082 | 292.5 | Early Replacement
2737 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.57 kWperTon with 0.4 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.57 kWperTon with 0.4 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.57 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.57 |  |  |  | Algorithm |  |  | 91.1 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.075 | 243.4 | Early Replacement
706 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.57 kWperTon with 0.43 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.57 kWperTon with 0.43 kWperTon IPLV) | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.57 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.57 |  |  |  | Algorithm |  |  | 143 |  | 20 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.071 | 243.2 | Early Replacement
706 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.57 kWperTon with 0.43 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.57 kWperTon with 0.43 kWperTon IPLV) | 2 | Active | 2016-01-01 |  | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.57 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.57 |  |  |  | Algorithm |  |  | 84.65 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.071 | 218.2 | Early Replacement
2738 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.57 kWperTon with 0.46 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.57 kWperTon with 0.46 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.57 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.57 |  |  |  | Algorithm |  |  | 78.2 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.068 | 195.4 | Early Replacement
2739 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.57 kWperTon with 0.54 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.57 kWperTon with 0.54 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.57 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.57 |  |  |  | Algorithm |  |  | 61.44 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.058 | 128.2 | Early Replacement
2740 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.63 kWperTon with 0.38 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.63 kWperTon with 0.38 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.63 |  |  |  | Algorithm |  |  | 48.73 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.026 | 182.4 | Early Replacement
707 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.63 kWperTon with 0.45 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.63 kWperTon with 0.45 kWperTon IPLV) | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.63 |  |  |  | Algorithm |  |  | 143 |  | 20 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.018 | 142.6 | Early Replacement
707 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.63 kWperTon with 0.45 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.63 kWperTon with 0.45 kWperTon IPLV) | 2 | Active | 2016-01-01 |  | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.63 |  |  |  | Algorithm |  |  | 32.96 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.018 | 127.9 | Early Replacement
2741 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.63 kWperTon with 0.48 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.63 kWperTon with 0.48 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.63 |  |  |  | Algorithm |  |  | 25.8 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.014 | 100.0 | Early Replacement
2742 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller 150 - 300 ton 0.63 kWperTon with 0.51 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Centrifugal Chiller (0.63 kWperTon with 0.51 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.63 kW/ton full-load efficiency 0.60 kW/ton IPLV | 0.63 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.63 |  |  |  | Algorithm |  |  | 18.63 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.011 | 74.6 | Early Replacement
2721 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.46 kWperTon with 0.28 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.46 kWperTon with 0.28 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.46 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.46 |  |  |  | Algorithm |  |  | 130.19 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.125 | 371.0 | Early Replacement
2722 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.46 kWperTon with 0.33 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.46 kWperTon with 0.33 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.46 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.46 |  |  |  | Algorithm |  |  | 118.26 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.120 | 331.2 | Early Replacement
708 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.46 kWperTon with 0.35 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.46 kWperTon with 0.35 kWperTon IPLV) | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.46 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.46 |  |  |  | Algorithm |  |  | 112 |  | 20 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.117 | 346.4 | Early Replacement
708 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.46 kWperTon with 0.35 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.46 kWperTon with 0.35 kWperTon IPLV) | 2 | Active | 2016-01-01 |  | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.46 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.46 |  |  |  | Algorithm |  |  | 112.83 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.117 | 310.8 | Early Replacement
2723 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.46 kWperTon with 0.37 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.46 kWperTon with 0.37 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.46 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.46 |  |  |  | Algorithm |  |  | 107.41 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.114 | 292.2 | Early Replacement
2724 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.46 kWperTon with 0.44 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.46 kWperTon with 0.44 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.46 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.46 |  |  |  | Algorithm |  |  | 92.22 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.106 | 234.2 | Early Replacement
2725 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.52 kWperTon with 0.31 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.52 kWperTon with 0.31 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.52 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.52 |  |  |  | Algorithm |  |  | 88.82 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.075 | 270.8 | Early Replacement
2726 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.52 kWperTon with 0.37 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.52 kWperTon with 0.37 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.52 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.52 |  |  |  | Algorithm |  |  | 75.40 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.069 | 226.0 | Early Replacement
2727 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.52 kWperTon with 0.39 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.52 kWperTon with 0.39 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.52 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.52 |  |  |  | Algorithm |  |  | 69.30 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.065 | 203.1 | Early Replacement
2728 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.52 kWperTon with 0.42 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.52 kWperTon with 0.42 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.52 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.52 |  |  |  | Algorithm |  |  | 63.20 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.062 | 182.2 | Early Replacement
709 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.52 kWperTon with 0.49 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.52 kWperTon with 0.49 kWperTon IPLV) | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.52 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.52 |  |  |  | Algorithm |  |  | 112 |  | 20 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.053 | 130.5 | Early Replacement
709 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.52 kWperTon with 0.49 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.52 kWperTon with 0.49 kWperTon IPLV) | 2 | Active | 2016-01-01 |  | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.52 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.52 |  |  |  | Algorithm |  |  | 46.11 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.053 | 117.1 | Early Replacement
2729 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.58 kWperTon with 0.35 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.58 kWperTon with 0.35 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.58 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.58 |  |  |  | Algorithm |  |  | 47.46 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.025 | 170.5 | Early Replacement
710 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.58 kWperTon with 0.41 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.58 kWperTon with 0.41 kWperTon IPLV) | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.58 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.58 |  |  |  | Algorithm |  |  | 112 |  | 20 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.017 | 134.7 | Early Replacement
710 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.58 kWperTon with 0.41 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.58 kWperTon with 0.41 kWperTon IPLV) | 2 | Active | 2016-01-01 |  | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.58 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.58 |  |  |  | Algorithm |  |  | 32.54 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.017 | 120.8 | Early Replacement
2730 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.58 kWperTon with 0.44 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.58 kWperTon with 0.44 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.58 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.58 |  |  |  | Algorithm |  |  | 25.76 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.014 | 95.4 | Early Replacement
2731 | HVAC | Space Cooling | Chiller, Water-Cooled Central | Wtr-Cool cent Chiller over 300 ton 0.58 kWperTon with 0.47 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Centrifugal Chiller (0.58 kWperTon with 0.47 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.58 kW/ton full-load efficiency 0.55 kW/ton IPLV | 0.58 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.58 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.58 |  |  |  | Algorithm |  |  | 18.98 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.010 | 72.3 | Early Replacement
2709 | HVAC | Space Cooling | Chiller, Water-Cooled Centrifugal | Wtr-Cool Centrifugal Chiller under 150 ton 0.56 kWperTon with 0.34 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Centrifugal Chiller (0.56 kWperTon with 0.43 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.70 kW/ton full-load efficiency 0.67 kW/ton IPLV | 0.7 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.56 kW/ton full-load efficiency | kW/Ton full-load efficiency | 0.56 |  |  |  | Algorithm |  |  | 203.03 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.15305 | 452.09 | Early Replacement
2710 | HVAC | Space Cooling | Chiller, Water-Cooled Centrifugal | Wtr-Cool Centrifugal Chiller under 150 ton 0.56 kWperTon with 0.4 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Centrifugal Chiller (0.56 kWperTon with 0.43 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.70 kW/ton full-load efficiency 0.67 kW/ton IPLV | 0.7 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.56 kW/ton full-load efficiency | kW/Ton full-load efficiency | 0.56 |  |  |  | Algorithm |  |  | 191.42 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.14605 | 403.67 | Early Replacement
711 | HVAC | Space Cooling | Chiller, Water-Cooled Centrifugal | Wtr-Cool Centrifugal Chiller under 150 ton 0.56 kWperTon with 0.43 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Centrifugal Chiller (0.56 kWperTon with 0.43 kWperTon IPLV) | 1 | Active | 2013-01-02 |  | 0.70 kW/ton full-load efficiency 0.67 kW/ton IPLV | 0.7 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.56 kW/ton full-load efficiency | kW/Ton full-load efficiency | 0.56 |  |  |  | Algorithm |  |  | 186 |  | 20 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.142 | 422.3 | Early Replacement
2712 | HVAC | Space Cooling | Chiller, Water-Cooled Centrifugal | Wtr-Cool Centrifugal Chiller under 150 ton 0.56 kWperTon with 0.46 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Centrifugal Chiller (0.56 kWperTon with 0.43 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.70 kW/ton full-load efficiency 0.67 kW/ton IPLV | 0.7 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.56 kW/ton full-load efficiency | kW/Ton full-load efficiency | 0.56 |  |  |  | Algorithm |  |  | 180.87 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.13906 | 356.3 | Early Replacement
2713 | HVAC | Space Cooling | Chiller, Water-Cooled Centrifugal | Wtr-Cool Centrifugal Chiller under 150 ton 0.56 kWperTon with 0.53 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Centrifugal Chiller (0.56 kWperTon with 0.43 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.70 kW/ton full-load efficiency 0.67 kW/ton IPLV | 0.7 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.56 kW/ton full-load efficiency | kW/Ton full-load efficiency | 0.56 |  |  |  | Algorithm |  |  | 166.1 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.12909 | 285.73 | Early Replacement
2714 | HVAC | Space Cooling | Chiller, Water-Cooled Centrifugal | Wtr-Cool Centrifugal Chiller under 150 ton 0.63 kWperTon with 0.38 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Centrifugal Chiller (0.63 kWperTon with 0.48 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.70 kW/ton full-load efficiency 0.67 kW/ton IPLV | 0.7 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/Ton full-load efficiency | 0.63 |  |  |  | Algorithm |  |  | 124.6 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.09153 | 329.89 | Early Replacement
2715 | HVAC | Space Cooling | Chiller, Water-Cooled Centrifugal | Wtr-Cool Centrifugal Chiller under 150 ton 0.63 kWperTon with 0.45 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Centrifugal Chiller (0.63 kWperTon with 0.48 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.70 kW/ton full-load efficiency 0.67 kW/ton IPLV | 0.7 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/Ton full-load efficiency | 0.63 |  |  |  | Algorithm |  |  | 111.54 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.0836 | 275.5 | Early Replacement
712 | HVAC | Space Cooling | Chiller, Water-Cooled Centrifugal | Wtr-Cool Centrifugal Chiller under 150 ton 0.63 kWperTon with 0.48 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Centrifugal Chiller (0.63 kWperTon with 0.48 kWperTon IPLV) | 1 | Active | 2013-01-02 |  | 0.70 kW/ton full-load efficiency 0.67 kW/ton IPLV | 0.7 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/Ton full-load efficiency | 0.63 |  |  |  | Algorithm |  |  | 186 |  | 20 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.079 | 276.0 | Early Replacement
2716 | HVAC | Space Cooling | Chiller, Water-Cooled Centrifugal | Wtr-Cool Centrifugal Chiller under 150 ton 0.63 kWperTon with 0.51 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Centrifugal Chiller (0.63 kWperTon with 0.48 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.70 kW/ton full-load efficiency 0.67 kW/ton IPLV | 0.7 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/Ton full-load efficiency | 0.63 |  |  |  | Algorithm |  |  | 99.67 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.07579 | 222.22 | Early Replacement
2717 | HVAC | Space Cooling | Chiller, Water-Cooled Centrifugal | Wtr-Cool Centrifugal Chiller under 150 ton 0.63 kWperTon with 0.60 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Centrifugal Chiller (0.63 kWperTon with 0.48 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.70 kW/ton full-load efficiency 0.67 kW/ton IPLV | 0.7 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/Ton full-load efficiency | 0.63 |  |  |  | Algorithm |  |  | 83.05 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.06452 | 142.88 | Early Replacement
2718 | HVAC | Space Cooling | Chiller, Water-Cooled Centrifugal | Wtr-Cool Centrifugal Chiller under 150 ton 0.7 kWperTon with 0.44 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Centrifugal Chiller (0.7 kWperTon with 0.5 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.70 kW/ton full-load efficiency 0.67 kW/ton IPLV | 0.7 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.70 kW/ton full-load efficiency | kW/Ton full-load efficiency | 0.7 |  |  |  | Algorithm |  |  | 46.16 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.03001 | 207.39 | Early Replacement
713 | HVAC | Space Cooling | Chiller, Water-Cooled Centrifugal | Wtr-Cool Centrifugal Chiller under 150 ton 0.7 kWperTon with 0.5 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Centrifugal Chiller (0.7 kWperTon with 0.5 kWperTon IPLV) | 1 | Active | 2013-01-02 |  | 0.70 kW/ton full-load efficiency 0.67 kW/ton IPLV | 0.7 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.70 kW/ton full-load efficiency | kW/Ton full-load efficiency | 0.7 |  |  |  | Algorithm |  |  | 186 |  | 20 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.021 | 164.0 | Early Replacement
2719 | HVAC | Space Cooling | Chiller, Water-Cooled Centrifugal | Wtr-Cool Centrifugal Chiller under 150 ton 0.7 kWperTon with 0.53 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Centrifugal Chiller (0.7 kWperTon with 0.5 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.70 kW/ton full-load efficiency 0.67 kW/ton IPLV | 0.7 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.70 kW/ton full-load efficiency | kW/Ton full-load efficiency | 0.7 |  |  |  | Algorithm |  |  | 25.06 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.01668 | 116.17 | Early Replacement
2720 | HVAC | Space Cooling | Chiller, Water-Cooled Centrifugal | Wtr-Cool Centrifugal Chiller under 150 ton 0.7 kWperTon with 0.57 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Centrifugal Chiller (0.7 kWperTon with 0.5 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.70 kW/ton full-load efficiency 0.67 kW/ton IPLV | 0.7 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.70 kW/ton full-load efficiency | kW/Ton full-load efficiency | 0.7 |  |  |  | Algorithm |  |  | 18.46 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.01245 | 88.02 | Early Replacement
2771 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.57 kWperTon with 0.34 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.57 kWperTon with 0.34 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.57 kW/ton full-load efficiency | kW/Ton | 0.57 |  |  |  | Algorithm |  |  | 149.41 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.163 | 423.8 | Early Replacement
2772 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.57 kWperTon with 0.37 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.57 kWperTon with 0.37 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.57 kW/ton full-load efficiency | kW/Ton | 0.57 |  |  |  | Algorithm |  |  | 137.36 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.159 | 400.7 | Early Replacement
714 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.57 kWperTon with 0.4 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.57 kWperTon with 0.4 kWperTon IPLV) | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.57 kW/ton full-load efficiency | kW/Ton | 0.57 |  |  |  | Algorithm |  |  | 125 |  | 20 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.154 | 416.1 | Early Replacement
714 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.57 kWperTon with 0.4 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.57 kWperTon with 0.4 kWperTon IPLV) | 2 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.57 kW/ton full-load efficiency | kW/Ton | 0.57 |  |  |  | Algorithm |  |  | 125.31 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.154 | 373.3 | Early Replacement
2773 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.57 kWperTon with 0.43 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.57 kWperTon with 0.43 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.57 kW/ton full-load efficiency | kW/Ton | 0.57 |  |  |  | Algorithm |  |  | 113.26 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.148 | 343.7 | Early Replacement
2774 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.57 kWperTon with 0.45 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.57 kWperTon with 0.45 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.57 kW/ton full-load efficiency | kW/Ton | 0.57 |  |  |  | Algorithm |  |  | 103.62 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.144 | 322.3 | Early Replacement
2775 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.57 kWperTon with 0.51 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.57 kWperTon with 0.51 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.57 kW/ton full-load efficiency | kW/Ton | 0.57 |  |  |  | Algorithm |  |  | 79.52 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.134 | 266.3 | Early Replacement
2776 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.65 kWperTon with 0.39 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.65 kWperTon with 0.39 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.65 kW/ton full-load efficiency | kW/Ton | 0.65 |  |  |  | Algorithm |  |  | 118.38 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.1 | 310 | Early Replacement
2777 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.65 kWperTon with 0.42 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.65 kWperTon with 0.42 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.65 kW/ton full-load efficiency | kW/Ton | 0.65 |  |  |  | Algorithm |  |  | 104.83 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.095 | 283.7 | Early Replacement
715 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.65 kWperTon with 0.45 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.65 kWperTon with 0.45 kWperTon IPLV) | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.65 kW/ton full-load efficiency | kW/Ton | 0.65 |  |  |  | Algorithm |  |  | 125 |  | 20 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.089 | 281.8 | Early Replacement
715 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.65 kWperTon with 0.45 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.65 kWperTon with 0.45 kWperTon IPLV) | 2 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.65 kW/ton full-load efficiency | kW/Ton | 0.65 |  |  |  | Algorithm |  |  | 91.27 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.089 | 252.9 | Early Replacement
2778 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.65 kWperTon with 0.48 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.65 kWperTon with 0.48 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.65 kW/ton full-load efficiency | kW/Ton | 0.65 |  |  |  | Algorithm |  |  | 77.72 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.083 | 219.3 | Early Replacement
2779 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.65 kWperTon with 0.51 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.65 kWperTon with 0.51 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.65 kW/ton full-load efficiency | kW/Ton | 0.65 |  |  |  | Algorithm |  |  | 66.87 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.078 | 194.8 | Early Replacement
2780 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.65 kWperTon with 0.57 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.65 kWperTon with 0.57 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.65 kW/ton full-load efficiency | kW/Ton | 0.65 |  |  |  | Algorithm |  |  | 39.76 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.067 | 131.8 | Early Replacement
2781 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.72 kWperTon with 0.43 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.72 kWperTon with 0.43 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.72 kW/ton full-load efficiency | kW/Ton | 0.72 |  |  |  | Algorithm |  |  | 87.36 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.036 | 201.3 | Early Replacement
2782 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.72 kWperTon with 0.47 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.72 kWperTon with 0.47 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.72 kW/ton full-load efficiency | kW/Ton | 0.72 |  |  |  | Algorithm |  |  | 72.3 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.031 | 170.8 | Early Replacement
716 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.72 kWperTon with 0.5 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.72 kWperTon with 0.5 kWperTon IPLV) | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.72 kW/ton full-load efficiency | kW/Ton | 0.72 |  |  |  | Algorithm |  |  | 125 |  | 20 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.024 | 149.9 | Early Replacement
716 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.72 kWperTon with 0.5 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.72 kWperTon with 0.5 kWperTon IPLV) | 2 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.72 kW/ton full-load efficiency | kW/Ton | 0.72 |  |  |  | Algorithm |  |  | 57.24 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.024 | 134.5 | Early Replacement
2783 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.72 kWperTon with 0.54 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.72 kWperTon with 0.54 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.72 kW/ton full-load efficiency | kW/Ton | 0.72 |  |  |  | Algorithm |  |  | 42.17 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.017 | 95.4 | Early Replacement
2784 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller 150 - 300 ton 0.72 kWperTon with 0.57 kWperTon IPLV: Biz Prescriptive | >150 to <300 Ton Water Cooled Screw Chiller (0.72 kWperTon with 0.57 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.72 kW/ton full-load efficiency | kW/Ton | 0.72 |  |  |  | Algorithm |  |  | 30.12 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.012 | 67.3 | Early Replacement
2757 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.51 kWperTon with 0.31 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller (0.51 kWperTon with 0.31 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.51 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.51 |  |  |  | Algorithm |  |  | 114.05 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.145 | 380.168 | Early Replacement
2758 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.51 kWperTon with 0.33 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller (0.51 kWperTon with 0.33 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.51 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.51 |  |  |  | Algorithm |  |  | 104.02 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.141 | 359.569 | Early Replacement
717 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.51 kWperTon with 0.36 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller (0.51 kWperTon with 0.36 kWperTon IPLV) | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.51 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.51 |  |  |  | Algorithm |  |  | 93 |  | 20 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.137 | 373.4 | Early Replacement
717 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.51 kWperTon with 0.36 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller (0.51 kWperTon with 0.36 kWperTon IPLV) | 2 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.51 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.51 |  |  |  | Algorithm |  |  | 93.99 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.137 | 335.007 | Early Replacement
2759 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.51 kWperTon with 0.38 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller (0.51 kWperTon with 0.38 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.51 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.51 |  |  |  | Algorithm |  |  | 83.96 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.132 | 308.622 | Early Replacement
2760 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.51 kWperTon with 0.4 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller (0.51 kWperTon with 0.4 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.51 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.51 |  |  |  | Algorithm |  |  | 75.93 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.128 | 289.599 | Early Replacement
2761 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.51 kWperTon with 0.46 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller (0.51 kWperTon with 0.46 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.51 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.51 |  |  |  | Algorithm |  |  | 55.87 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.12 | 239.719 | Early Replacement
2762 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.58 kWperTon with 0.35 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller (0.58 kWperTon with 0.35 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.58 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.58 |  |  |  | Algorithm |  |  | 93.39 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.089 | 277.692 | Early Replacement
2763 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.58 kWperTon with 0.37 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller (0.58 kWperTon with 0.37 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.58 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.58 |  |  |  | Algorithm |  |  | 82.1 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.084 | 254.586 | Early Replacement
718 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.58 kWperTon with 0.4 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller (0.58 kWperTon with 0.4 kWperTon IPLV) | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.58 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.58 |  |  |  | Algorithm |  |  | 93 |  | 20 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.079 | 253.1 | Early Replacement
718 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.58 kWperTon with 0.4 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller (0.58 kWperTon with 0.4 kWperTon IPLV) | 2 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.58 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.58 |  |  |  | Algorithm |  |  | 70.82 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.079 | 227.053 | Early Replacement
2764 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.58 kWperTon with 0.43 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller (0.58 kWperTon with 0.43 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.58 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.58 |  |  |  | Algorithm |  |  | 59.53 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.074 | 197.441 | Early Replacement
2765 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.58 kWperTon with 0.45 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller (0.58 kWperTon with 0.45 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.58 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.58 |  |  |  | Algorithm |  |  | 50.51 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.07 | 175.985 | Early Replacement
2766 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.58 kWperTon with 0.51 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller (0.58 kWperTon with 0.51 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.58 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.58 |  |  |  | Algorithm |  |  | 27.94 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.06 | 119.836 | Early Replacement
2767 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.64 kWperTon with 0.38 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller 0.64 kWperTon with 0.38 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.64 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.64 |  |  |  | Algorithm |  |  | 72.72 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.032 | 176.176 | Early Replacement
2768 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.64 kWperTon with 0.42 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller 0.64 kWperTon with 0.42 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.64 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.64 |  |  |  | Algorithm |  |  | 60.18 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.027 | 150.281 | Early Replacement
719 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.64 kWperTon with 0.45 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller (0.58 kWperTon with 0.4 kWperTon IPLV) | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.64 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.64 |  |  |  | Algorithm |  |  | 93 |  | 20 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.021 | 133.3 | Early Replacement
719 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.64 kWperTon with 0.45 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller 0.64 kWperTon with 0.45 kWperTon IPLV) | 2 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.64 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.64 |  |  |  | Algorithm |  |  | 47.65 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.021 | 119.625 | Early Replacement
2769 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.64 kWperTon with 0.48 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller 0.64 kWperTon with 0.48 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.64 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.64 |  |  |  | Algorithm |  |  | 35.11 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.015 | 86.563 | Early Replacement
2770 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller over 300 ton 0.64 kWperTon with 0.51 kWperTon IPLV: Biz Prescriptive | >300 Ton Water Cooled Screw Chiller 0.64 kWperTon with 0.51 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.64 kW/ton full-load efficiency 0.57 kW/ton IPLV | 0.64 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.64 kW/ton full-load efficiency | kW/ton full-load efficiency | 0.64 |  |  |  | Algorithm |  |  | 25.08 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per ton | 0.011 | 62.36 | Early Replacement
2743 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.63 kWperTon with 0.38 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.63 kWperTon with 0.38 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/Ton | 0.63 |  |  |  | Algorithm |  |  | 193.99 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.4276 | 469.5 | Early Replacement
2744 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.63 kWperTon with 0.41 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.63 kWperTon with 0.41 kWperTon IPLV) | 1 | InActive |  |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/Ton | 0.63 |  |  |  | Algorithm |  |  | 179.73 |  | 20 |  |  |  |  | Biz Prescriptive |  |  | per ton | 0.4042 | 443.8 | Early Replacement
720 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.63 kWperTon with 0.44 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.63 kWperTon with 0.44 kWperTon IPLV) | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/Ton | 0.63 |  |  |  | Algorithm |  |  | 165 |  | 20 | 2013-15 |  |  |  | Biz Prescriptive |  |  | per ton | 0.169 | 460.9 | Early Replacement
720 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.63 kWperTon with 0.44 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.63 kWperTon with 0.44 kWperTon IPLV) | 2 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/Ton | 0.63 |  |  |  | Algorithm |  |  | 165.46 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.169 | 413.5 | Early Replacement
2745 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.63 kWperTon with 0.47 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.63 kWperTon with 0.47 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/Ton | 0.63 |  |  |  | Algorithm |  |  | 151.2 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.3467 | 380.7 | Early Replacement
2746 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.63 kWperTon with 0.5 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.63 kWperTon with 0.5 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/Ton | 0.63 |  |  |  | Algorithm |  |  | 139.78 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.3251 | 357.0 | Early Replacement
2747 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.63 kWperTon with 0.56 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.63 kWperTon with 0.56 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.63 kW/ton full-load efficiency | kW/Ton | 0.63 |  |  |  | Algorithm |  |  | 111.25 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.269 | 295.4 | Early Replacement
2748 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.71 kWperTon with 0.43 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.71 kWperTon with 0.43 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.71 kW/ton full-load efficiency | kW/Ton | 0.71 |  |  |  | Algorithm |  |  | 148.71 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.3182 | 349.4 | Early Replacement
2749 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.71 kWperTon with 0.46 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.71 kWperTon with 0.46 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.71 kW/ton full-load efficiency | kW/Ton | 0.71 |  |  |  | Algorithm |  |  | 132.66 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.2907 | 319.2 | Early Replacement
721 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.71 kWperTon with 0.5 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.71 kWperTon with 0.5 kWperTon IPLV) | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.71 kW/ton full-load efficiency | kW/Ton | 0.71 |  |  |  | Algorithm |  |  | 165 |  | 20 | 2013-15 |  |  |  | Biz Prescriptive |  |  | per ton | 0.097 | 315.7 | Early Replacement
721 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.71 kWperTon with 0.5 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.71 kWperTon with 0.5 kWperTon IPLV) | 2 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.71 kW/ton full-load efficiency | kW/Ton | 0.71 |  |  |  | Algorithm |  |  | 116.61 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.097 | 283.2 | Early Replacement
2750 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.71 kWperTon with 0.53 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.71 kWperTon with 0.53 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.71 kW/ton full-load efficiency | kW/Ton | 0.71 |  |  |  | Algorithm |  |  | 100.56 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.2226 | 244.4 | Early Replacement
2751 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.71 kWperTon with 0.56 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.71 kWperTon with 0.56 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.71 kW/ton full-load efficiency | kW/Ton | 0.71 |  |  |  | Algorithm |  |  | 87.72 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.1973 | 216.6 | Early Replacement
2752 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.71 kWperTon with 0.63 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.71 kWperTon with 0.63 kWperTon IPLV) | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.71 kW/ton full-load efficiency | kW/Ton | 0.71 |  |  |  | Algorithm |  |  | 55.63 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.1361 | 149.4 | Early Replacement
2753 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.79 kWperTon with 0.47 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.79 kWperTon with 0.47 kWperTon IPLV | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.79 kW/ton full-load efficiency | kW/Ton | 0.79 |  |  |  | Algorithm |  |  | 103.43 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.2044 | 224.4 | Early Replacement
2754 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.79 kWperTon with 0.51 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.79 kWperTon with 0.51 kWperTon IPLV | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.79 kW/ton full-load efficiency | kW/Ton | 0.79 |  |  |  | Algorithm |  |  | 85.59 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.1738 | 190.9 | Early Replacement
722 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.79 kWperTon with 0.55 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.79 kWperTon with 0.55 kWperTon IPLV | 1 | InActive | 2013-01-02 | 2015-12-31 | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.79 kW/ton full-load efficiency | kW/Ton | 0.79 |  |  |  | Algorithm |  |  | 165 |  | 20 | 2013-15 |  |  |  | Biz Prescriptive |  |  | per ton | 0.027 | 168.2 | Early Replacement
722 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.79 kWperTon with 0.55 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.79 kWperTon with 0.55 kWperTon IPLV | 2 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.79 kW/ton full-load efficiency | kW/Ton | 0.79 |  |  |  | Algorithm |  |  | 67.76 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.027 | 150.9 | Early Replacement
2755 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.79 kWperTon with 0.59 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.79 kWperTon with 0.59 kWperTon IPLV | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.79 kW/ton full-load efficiency | kW/Ton | 0.79 |  |  |  | Algorithm |  |  | 49.93 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.0983 | 107.9 | Early Replacement
2756 | HVAC | Space Cooling | Chiller, Water-Cooled Screw | Wtr-Cool screw chiller under 150 ton 0.79 kWperTon with 0.62 kWperTon IPLV: Biz Prescriptive | <150 Ton Water Cooled Screw Chiller (0.79 kWperTon with 0.62 kWperTon IPLV | 1 | Active | 2016-01-01 |  | 0.72 kW/ton full-load efficiency 0.63 kW/ton IPLV | 0.72 | kW/ton full-load efficiency |  |  |  | per ton | Algorithm | 0.79 kW/ton full-load efficiency | kW/Ton | 0.79 |  |  |  | Algorithm |  |  | 35.66 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ton | 0.0701 | 77.0 | Early Replacement
3059 | Lighting | Interior Lighting | LED, Linear | 4L T9: Biz Prescriptive | 4L T9 | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 219.50 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.2216 | 1166.29
3060 | Lighting | Interior Lighting | LED, Linear | 6L T8: Biz Prescriptive | 6L T8 | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 208 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.1579 | 830.97
3061 | Lighting | Interior Lighting | LED, fixture | Built-in to individual fixtures: Biz Prescriptive | Built-in to individual fixtures | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 1 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.0735 | 387
776-1 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: College/University: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.6517 | 19223.2 | Early Replacement
776-10 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Elementary School: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 1.4378 | 7568.8 | Early Replacement
776-15 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Exterior: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.6001 | 13687.5 | Early Replacement
776-19 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Garage, 24/7 lighting: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 5.2003 | 27375.0 | Early Replacement
776-4 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Garage: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.1015 | 11062.5 | Early Replacement
776-5 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Grocery: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.8611 | 20325.5 | Early Replacement
776-11 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Heavy Industry: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.6497 | 19212.4 | Early Replacement
776-12 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: High School/Middle School: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.5592 | 13471.9 | Early Replacement
776-6 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Hospital: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.1195 | 16421.4 | Early Replacement
776-7 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Hotel/Motel Common Areas: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 4.5893 | 24158.7 | Early Replacement
776-13 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Hotel/Motel Guest Rooms: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 0.4613 | 2428.1 | Early Replacement
776-9 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Light Industry: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.4421 | 18119.8 | Early Replacement
776-14 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Miscellaneous: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.2901 | 17319.9 | Early Replacement
776-16 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Multifamily Common Areas: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.5321 | 18593.8 | Early Replacement
776-8 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Office: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.764 | 14549.9 | Early Replacement
776-18 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Religious Worship/Church: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 0.9878 | 5200.0 | Early Replacement
776-3 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Restaurant: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.4119 | 17960.9 | Early Replacement
776-2 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Retail/Service: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.0003 | 15793.9 | Early Replacement
776-20 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Warehouse: Biz Prescriptive | Central lighting controls in commercial building | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.9961 | 15771.8 | Early Replacement
731-1 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: College/University: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.1414 | 744.3 | Early Replacement
731-10 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Elementary School: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.0557 | 293.1 | Early Replacement
731-15 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Exterior: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.1007 | 530.0 | Early Replacement
731-19 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Garage, 24/7 lighting: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.2014 | 1060.0 | Early Replacement
731-4 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Garage: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.0814 | 428.3 | Early Replacement
731-5 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Grocery: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.1495 | 787.0 | Early Replacement
731-11 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Heavy Industry: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.1413 | 743.9 | Early Replacement
731-12 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: High School/Middle School: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.0991 | 521.6 | Early Replacement
731-6 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Hospital: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.1208 | 635.8 | Early Replacement
731-7 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Hotel/Motel Common Areas: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.1777 | 935.4 | Early Replacement
731-13 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Hotel/Motel Guest Rooms: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.0179 | 94.0 | Early Replacement
731-9 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Light Industry: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.1333 | 701.6 | Early Replacement
731-14 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Miscellaneous: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.1274 | 670.6 | Early Replacement
731-16 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Multifamily Common Areas: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.1368 | 720.0 | Early Replacement
731-8 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Office: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.107 | 563.4 | Early Replacement
731-18 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Religious Worship/Church: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.0382 | 201.3 | Early Replacement
731-3 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Restaurant: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.1321 | 695.4 | Early Replacement
731-2 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Retail/Service: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.1162 | 611.5 | Early Replacement
731-20 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Warehouse: Biz Prescriptive | Ceramic Metal Halide 20-100W | 2 | Active | 2016-01-01 |  | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.116 | 610.7 | Early Replacement
3084 | Lighting | Interior Lighting | T8, Linear Fluorescent | Delamping: Biz Prescriptive | Delamping | 1 | Active | 2017-01-01 | [7 empty] | per ft | [10 empty] | 1.5 |  | 15 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per ft | 0.0058 | 30.4
738-1 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: College/University: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.003 | 525.9 | Early Replacement
738-10 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Elementary School: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0012 | 207.1 | Early Replacement
738-15 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Exterior: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0021 | 374.5 | Early Replacement
738-19 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Garage, 24/7 lighting: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0042 | 749.0 | Early Replacement
738-4 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Garage: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0017 | 302.7 | Early Replacement
738-5 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Grocery: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0031 | 556.1 | Early Replacement
738-11 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Heavy Industry: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.003 | 525.7 | Early Replacement
738-12 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: High School/Middle School: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0021 | 368.6 | Early Replacement
738-6 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Hospital: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0025 | 449.3 | Early Replacement
738-7 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Hotel/Motel Common Areas: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0037 | 661.0 | Early Replacement
738-13 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Hotel/Motel Guest Rooms: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 4.0E-4 | 66.4 | Early Replacement
738-9 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Light Industry: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0028 | 495.8 | Early Replacement
738-14 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Miscellaneous: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0027 | 473.9 | Early Replacement
738-16 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Multifamily Common Areas: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0029 | 508.7 | Early Replacement
738-8 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Office: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0022 | 398.1 | Early Replacement
738-18 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Religious Worship/Church: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 8.0E-4 | 142.3 | Early Replacement
738-3 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Restaurant: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0028 | 491.4 | Early Replacement
738-2 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Retail/Service: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0024 | 432.1 | Early Replacement
738-20 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Warehouse: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0024 | 431.5 | Early Replacement
739-1 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: College/University: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0031 | 550.6 | Early Replacement
739-10 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Elementary School: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0012 | 216.8 | Early Replacement
739-15 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Exterior: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0022 | 392.0 | Early Replacement
739-19 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Garage, 24/7 lighting: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0044 | 784.0 | Early Replacement
739-4 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Garage: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0018 | 316.8 | Early Replacement
739-5 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Grocery: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0033 | 582.1 | Early Replacement
739-11 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Heavy Industry: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0031 | 550.2 | Early Replacement
739-12 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: High School/Middle School: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0022 | 385.8 | Early Replacement
739-6 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Hospital: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0026 | 470.3 | Early Replacement
739-7 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Hotel/Motel Common Areas: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0039 | 691.9 | Early Replacement
739-13 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Hotel/Motel Guest Rooms: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 4.0E-4 | 69.5 | Early Replacement
739-9 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Light Industry: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0029 | 519.0 | Early Replacement
739-14 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Miscellaneous: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0028 | 496.0 | Early Replacement
739-16 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Multifamily Common Areas: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.003 | 532.5 | Early Replacement
739-8 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Office: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0023 | 416.7 | Early Replacement
739-18 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Religious Worship/Church: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 8.0E-4 | 148.9 | Early Replacement
739-3 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Restaurant: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0029 | 514.4 | Early Replacement
739-2 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Retail/Service: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0025 | 452.3 | Early Replacement
739-20 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Warehouse: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 3 | Active | 2017-01-01 |  | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0025 | 451.7 | Early Replacement
3075 | Lighting | Exterior Lighting | HID | Garage HID replacement to 175W HID retrofit: Biz Prescriptive | Garage HID replacement to 175W HID retrofit | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.1161 | 611
757-1 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: College/University: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1356 | 713.6 | Early Replacement
757-10 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Elementary School: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0534 | 281.0 | Early Replacement
757-15 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Exterior: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0965 | 508.1 | Early Replacement
757-19 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Garage, 24/7 lighting: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.193 | 1016.2 | Early Replacement
757-4 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Garage: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.078 | 410.6 | Early Replacement
757-5 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Grocery: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1433 | 754.5 | Early Replacement
757-11 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Heavy Industry: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1355 | 713.2 | Early Replacement
757-12 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: High School/Middle School: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.095 | 500.1 | Early Replacement
757-6 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Hospital: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1158 | 609.6 | Early Replacement
757-7 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Hotel/Motel Common Areas: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1704 | 896.8 | Early Replacement
757-13 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Hotel/Motel Guest Rooms: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0171 | 90.1 | Early Replacement
757-9 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Light Industry: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1278 | 672.6 | Early Replacement
757-14 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Miscellaneous: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1221 | 642.9 | Early Replacement
757-16 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Multifamily Common Areas: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1311 | 690.2 | Early Replacement
757-8 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Office: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1026 | 540.1 | Early Replacement
757-18 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Religious Worship/Church: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0367 | 193.0 | Early Replacement
757-3 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Restaurant: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1266 | 666.7 | Early Replacement
757-2 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Retail/Service: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1114 | 586.3 | Early Replacement
757-20 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Warehouse: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 295 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 179 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1112 | 585.4 | Early Replacement
758-1 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: College/University: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.409 | 2153.0 | Early Replacement
758-10 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Elementary School: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.161 | 847.7 | Early Replacement
758-15 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Exterior: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2912 | 1533.0 | Early Replacement
758-19 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Garage, 24/7 lighting: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.5824 | 3066.0 | Early Replacement
758-4 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Garage: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2354 | 1239.0 | Early Replacement
758-5 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Grocery: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.4325 | 2276.5 | Early Replacement
758-11 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Heavy Industry: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.4088 | 2151.8 | Early Replacement
758-12 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: High School/Middle School: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2866 | 1508.9 | Early Replacement
758-6 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Hospital: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.3494 | 1839.2 | Early Replacement
758-7 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Hotel/Motel Common Areas: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.514 | 2705.8 | Early Replacement
758-13 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Hotel/Motel Guest Rooms: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0517 | 272.0 | Early Replacement
758-9 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Light Industry: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.3855 | 2029.4 | Early Replacement
758-14 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Miscellaneous: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.3685 | 1939.8 | Early Replacement
758-16 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Multifamily Common Areas: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.3956 | 2082.5 | Early Replacement
758-8 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Office: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.3096 | 1629.6 | Early Replacement
758-18 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Religious Worship/Church: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1106 | 582.4 | Early Replacement
758-3 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Restaurant: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.3821 | 2011.6 | Early Replacement
758-2 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Retail/Service: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.336 | 1768.9 | Early Replacement
758-20 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Warehouse: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.3356 | 1766.4 | Early Replacement
759-1 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: College/University: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.2248 | 1183.5 | Early Replacement
759-10 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Elementary School: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.0885 | 466.0 | Early Replacement
759-15 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Exterior: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.1601 | 842.7 | Early Replacement
759-19 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Garage, 24/7 lighting: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.3201 | 1685.3 | Early Replacement
759-4 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Garage: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.1294 | 681.1 | Early Replacement
759-5 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Grocery: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.2377 | 1251.3 | Early Replacement
759-11 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Heavy Industry: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.2247 | 1182.8 | Early Replacement
759-12 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: High School/Middle School: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.1576 | 829.4 | Early Replacement
759-6 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Hospital: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.1921 | 1011.0 | Early Replacement
759-7 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Hotel/Motel Common Areas: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.2825 | 1487.3 | Early Replacement
759-13 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Hotel/Motel Guest Rooms: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.0284 | 149.5 | Early Replacement
759-9 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Light Industry: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.2119 | 1115.5 | Early Replacement
759-14 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Miscellaneous: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.2026 | 1066.3 | Early Replacement
759-16 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Multifamily Common Areas: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.2175 | 1144.7 | Early Replacement
759-8 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Office: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.1702 | 895.8 | Early Replacement
759-18 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Religious Worship/Church: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.0608 | 320.1 | Early Replacement
759-3 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Restaurant: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.2101 | 1105.8 | Early Replacement
759-2 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Retail/Service: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.1847 | 972.3 | Early Replacement
759-20 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Warehouse: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 250 W | 290.764706 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 98.376471 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.1845 | 971.0 | Early Replacement
760-1 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: College/University: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2884 | 1518.3 | Early Replacement
760-10 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Elementary School: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1136 | 597.8 | Early Replacement
760-15 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Exterior: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2054 | 1081.1 | Early Replacement
760-19 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Garage, 24/7 lighting: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.4107 | 2162.2 | Early Replacement
760-4 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Garage: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.166 | 873.8 | Early Replacement
760-5 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Grocery: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.305 | 1605.4 | Early Replacement
760-11 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Heavy Industry: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2883 | 1517.5 | Early Replacement
760-12 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: High School/Middle School: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2021 | 1064.1 | Early Replacement
760-6 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Hospital: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2464 | 1297.0 | Early Replacement
760-7 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Hotel/Motel Common Areas: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.3625 | 1908.1 | Early Replacement
760-13 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Hotel/Motel Guest Rooms: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0364 | 191.8 | Early Replacement
760-9 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Light Industry: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2719 | 1431.2 | Early Replacement
760-14 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Miscellaneous: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2599 | 1368.0 | Early Replacement
760-16 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Multifamily Common Areas: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.279 | 1468.6 | Early Replacement
760-8 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Office: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2183 | 1149.2 | Early Replacement
760-18 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Religious Worship/Church: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.078 | 410.7 | Early Replacement
760-3 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Restaurant: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2695 | 1418.6 | Early Replacement
760-2 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Retail/Service: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.237 | 1247.4 | Early Replacement
760-20 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Warehouse: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 400 W | 452.889375 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 206.067171 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2366 | 1245.7 | Early Replacement
761-1 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: College/University: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.5632 | 2965.0 | Early Replacement
761-10 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Elementary School: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2218 | 1167.4 | Early Replacement
761-15 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Exterior: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.4011 | 2111.2 | Early Replacement
761-19 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Garage, 24/7 lighting: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.8021 | 4222.3 | Early Replacement
761-4 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Garage: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.3241 | 1706.3 | Early Replacement
761-5 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Grocery: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.5955 | 3135.0 | Early Replacement
761-11 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Heavy Industry: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.5629 | 2963.3 | Early Replacement
761-12 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: High School/Middle School: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.3947 | 2077.9 | Early Replacement
761-6 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Hospital: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.4811 | 2532.8 | Early Replacement
761-7 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Hotel/Motel Common Areas: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.7078 | 3726.2 | Early Replacement
761-13 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Hotel/Motel Guest Rooms: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0711 | 374.5 | Early Replacement
761-9 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Light Industry: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.5309 | 2794.8 | Early Replacement
761-14 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Miscellaneous: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.5075 | 2671.4 | Early Replacement
761-16 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Multifamily Common Areas: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.5448 | 2867.9 | Early Replacement
761-8 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Office: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.4263 | 2244.2 | Early Replacement
761-18 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Religious Worship/Church: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1524 | 802.0 | Early Replacement
761-3 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Restaurant: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.5263 | 2770.3 | Early Replacement
761-2 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Retail/Service: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.4628 | 2436.0 | Early Replacement
761-20 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Warehouse: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 2 | Active | 2016-01-01 |  | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.4621 | 2432.6 | Early Replacement
762-1 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: College/University: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1871 | 984.9 | Early Replacement
762-10 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Elementary School: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0737 | 387.8 | Early Replacement
762-15 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Exterior: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1332 | 701.3 | Early Replacement
762-19 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Garage, 24/7 lighting: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2664 | 1402.5 | Early Replacement
762-4 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Garage: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1077 | 566.8 | Early Replacement
762-5 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Grocery: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1978 | 1041.4 | Early Replacement
762-11 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Heavy Industry: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.187 | 984.3 | Early Replacement
762-12 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: High School/Middle School: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1311 | 690.2 | Early Replacement
762-6 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Hospital: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1598 | 841.3 | Early Replacement
762-7 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Hotel/Motel Common Areas: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2351 | 1237.7 | Early Replacement
762-13 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Hotel/Motel Guest Rooms: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0236 | 124.4 | Early Replacement
762-9 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Light Industry: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1763 | 928.3 | Early Replacement
762-14 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Miscellaneous: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1686 | 887.4 | Early Replacement
762-16 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Multifamily Common Areas: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.181 | 952.6 | Early Replacement
762-8 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Office: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1416 | 745.4 | Early Replacement
762-18 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Religious Worship/Church: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0506 | 266.4 | Early Replacement
762-3 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Restaurant: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1748 | 920.2 | Early Replacement
762-2 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Retail/Service: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1537 | 809.2 | Early Replacement
762-20 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Warehouse: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 3 | Active | 2017-01-01 |  | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1535 | 808.0 | Early Replacement
3003 | Lighting | Exterior Lighting | Induction | Induction Street Lighting: Biz Prescriptive | Induction Street Lighting | 1 | Active | 2016-01-01 | [7 empty] | per fixture | [10 empty] | 0 |  | 20 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per fixture | 0.0011 | 192
3062 | Lighting | Lighting Controls | Lighting Control | Interior Ceiling (6 fixtures controlled): Biz Prescriptive | Interior Ceiling (6 fixtures controlled) | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 161 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.1804 | 949.8
3063 | Lighting | Lighting Controls | Lighting Control | Interior High-Bay T5 (3 fix. Controlled): Biz Prescriptive | Interior High-Bay T5 (3 fix. Controlled) | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 25 |  | 15 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.0361 | 190.2
779-1 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): College/University: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-10 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Elementary School: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Early Replacement
779-15 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Exterior: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-19 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Garage, 24/7 lighting: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-4 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Garage: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-5 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Grocery: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-11 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Heavy Industry: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-12 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): High School/Middle School: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-6 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Hospital: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-7 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Hotel/Motel Common Areas: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-13 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Hotel/Motel Guest Rooms: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-9 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Light Industry: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-14 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Miscellaneous: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-16 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Multifamily Common Areas: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-8 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Office: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-18 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Religious Worship/Church: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-3 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Restaurant: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-2 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Retail/Service: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Replace on Fail
779-20 | Lighting | Lighting Controls | Lighting Control | Interior Wall (3 fixtures controlled): Warehouse: Biz Prescriptive | Interior Wall Sensors (3 2-lamp T8 fixtures controlled) | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per 3 fixtures | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 91 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 3 fixtures | 0.060 | 620.9 | Early Replacement
3004-1 | Lighting | Exterior Lighting | LED | LED 100 Watt Lamp (12 hrs/day): Biz Prescriptive | LED 100 Watt Lamp (12 hrs/day) | 2 | Active | 2017-01-01 | [18 empty] | 233.64 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0052 | 924.2
3004-2 | Lighting | Exterior Lighting | LED | LED 100 Watt Lamp (24 hrs/day): Biz Prescriptive | LED 100 Watt Lamp (24 hrs/day) | 2 | Active | 2017-01-01 | [18 empty] | 233.64 |  | 9 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0104 | 1848.4
3005-1 | Lighting | Interior Lighting | LED, screw base | LED 120 Watt Lamp (12 hrs/day): Biz Prescriptive | LED ED 28 Lamp | 2 | Active | 2017-01-01 | [18 empty] | 361.64 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.2147 | 1130.0
3005-2 | Lighting | Exterior Lighting | LED | LED 120 Watt Lamp (24 hrs/day): Biz Prescriptive | LED ED 28 Lamp | 2 | Active | 2017-01-01 | [18 empty] | 361.64 |  | 9 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0127 | 2260.1
3006-1 | Lighting | Exterior Lighting | LED | LED 52 Watt Lamp (12 hrs/day): Biz Prescriptive | LED ED 28 Lamp | 1 | Active | 2016-01-01 | [18 empty] | 191.39 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.003 | 538.7
3006-2 | Lighting | Exterior Lighting | LED | LED 52 Watt Lamp (24 hrs/day): Biz Prescriptive | LED ED 28 Lamp | 1 | Active | 2016-01-01 | [18 empty] | 191.39 |  | 9 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0061 | 1077.5
3007 | Lighting | Interior Lighting | LED, fixture | LED (BAR/R) Reflector Lamp EISA Compliant: Biz Prescriptive | LED BR/ R 30,40 Lamp | 2 | Active | 2017-01-01 | [7 empty] | per lamp | [10 empty] | 48.27 |  | 9 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0344 | 181.3
3007-1 | Lighting | Interior Lighting | LED, screw base | LED (BR/R) Reflector Lamp EISA Exempt: Biz Prescriptive | LED (BR/R) Reflector Lamp EISA Exempt: Biz Prescriptive | 1 | Active | 2017-01-01 | [7 empty] | per lamp | [10 empty] | 48.27 |  | 9 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0467 | 246.0
3008 | Lighting | Interior Lighting | LED, fixture | LED (PAR) Reflector Lamp : Biz Prescriptive | LED PAR 38 Lamp | 2 | Active | 2017-01-01 | [18 empty] | 74.64 |  | 9 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0398 | 209.5
3010 | Lighting | Interior Lighting | LED, screw base | LED 1-8 Watt Decorative Lamp: Biz Prescriptive | LED Decorative C,T,B,G Lamp | 2 | Active | 2017-01-01 | [18 empty] | 22.64 |  | 5 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0454 | 239.1
3009 | Lighting | Interior Lighting | LED, screw base | LED 12-20 Watt A-Line Lamp: Biz Prescriptive | LED A-Line A15-24 Lamp | 1 | Active | 2016-01-01 | [18 empty] | 19.64 |  | 9 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0283 | 148.8
3011 | Lighting | Interior Lighting | LED, screw base | LED 5-11 Watt A-Line Lamp: Biz Prescriptive | LED A-Line A15-24 Lamp | 1 | Active | 2016-01-01 | [18 empty] | 15.64 |  | 9 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0161 | 85.0
8001 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_CF 18 base | LED Exit Sign - 3_0 W_CF 18 base | 1 | Active | 2016-01-01 |  | CF 18 Exit Sign | 18 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 91.68 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.8 | Early Replacement
8000 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_CF 9 base | LED Exit Sign - 3_0 W_CF 9 base | 1 | Active | 2016-01-01 |  | CF 9 Exit Sign | 9 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 45.45 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0462 | 243.1 | Replace on Fail
793-1 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: College/University: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-10 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Elementary School: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-15 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Exterior: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-19 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Garage, 24/7 lighting: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-4 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Garage: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-5 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Grocery: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-11 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Heavy Industry: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-12 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: High School/Middle School: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-6 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Hospital: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-7 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Hotel/Motel Common Areas: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-13 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Hotel/Motel Guest Rooms: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-9 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Light Industry: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-14 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Miscellaneous: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-16 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Multifamily Common Areas: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-8 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Office: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-18 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Religious Worship/Church: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-3 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Restaurant: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-2 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Retail/Service: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
793-20 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Warehouse: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 2 | Active | 2016-01-01 |  | Incandescent Exit Sign | 29.310069 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 2.911289 | LED Exit Sign |  |  | Algorithm |  |  | 63 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.0425 | 223.81 | Early Replacement
3012 | Lighting | Interior Lighting | LED, screw base | LED MR16 (12 Watt) Lamp: Biz Prescriptive | LED MR16 MR16 Lamp | 1 | Active | 2016-01-01 | [18 empty] | 39.64 |  | 9 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0329 | 173.1
3013 | Lighting | Interior Lighting | LED, screw base | LED MR16 (8 Watt) Lamp: Biz Prescriptive | LED MR16 MR16 Lamp | 2 | Active | 2017-01-01 | [18 empty] | 36.64 |  | 9 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.058 | 305.2
3023 | Lighting | Interior Lighting | LED, Linear | Linear Tube LED 4ft Efficient Lamp Upgrade - 25W T8 Base: Biz Prescriptive | LED (T) Tube Linear Lamp | 1 | Active | 2016-01-01 | [18 empty] | 29.64 |  | 17 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0063 | 33.4
3024 | Lighting | Interior Lighting | LED, Linear | Linear Tube LED 4ft Efficient Lamp Upgrade - 28W T8 Base | LED (T) Tube Linear Lamp | 1 | Active | 2016-01-01 | [18 empty] | 29.64 |  | 17 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0081 | 42.5
3025 | Lighting | Interior Lighting | LED, Linear | Linear Tube LED 4ft Efficient Lamp Upgrade - 32W T8 Base: Biz Prescriptive | LED (T) Tube Linear Lamp | 2 | Active | 2017-01-01 | [18 empty] | 29.64 |  | 17 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0104 | 54.7
3026 | Lighting | Interior Lighting | LED, Linear | Linear Tube LED 4ft Efficient Lamp Upgrade - T12 Base: Biz Prescriptive | LED (T) Tube Linear Lamp | 2 | Active | 2017-01-01 | [18 empty] | 29.64 |  | 17 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0104 | 54.7
3019 | Lighting | Interior Lighting | T8, Linear Fluorescent | Linear Tube T8 4ft Efficient Lamp Upgrade - T12 Base: Biz Prescriptive | T8 Lamp | 1 | Active | 2016-01-01 | [18 empty] | 10.49 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0035 | 18.2
3020 | Lighting | Interior Lighting | T8, Linear Fluorescent | Linear Tube T8 4ft Efficient Lamp Upgrade - T8 Base: Biz Prescriptive | T8 Lamp | 1 | Active | 2016-01-01 | [18 empty] | 10.49 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0035 | 18.2
3021 | Lighting | Interior Lighting | T8, Linear Fluorescent | Linear Tube T8 4ft High Efficient Lamp Upgrade - T12 Base: Biz Prescriptive | T8 Lamp | 1 | Active | 2016-01-01 | [18 empty] | 11.69 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0061 | 31.9
3022 | Lighting | Interior Lighting | T8, Linear Fluorescent | Linear Tube T8 4ft High Efficient Lamp Upgrade - T8 Base: Biz Prescriptive | T8 Lamp | 1 | Active | 2016-01-01 | [18 empty] | 11.69 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0061 | 31.9
3081 | Lighting | Interior Lighting | CFL Fixtures | LW HPT8 4ft 1 lamp, T12base: Biz Prescriptive | LW HPT8 4ft 1 lamp, T12base | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 25.29 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.0055 | 29
3082 | Lighting | Interior Lighting | CFL Fixtures | LW HPT8 4ft 2 lamp, T12base: Biz Prescriptive | LW HPT8 4ft 2 lamp, T12base | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 30.49 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.0091 | 48
3083 | Lighting | Interior Lighting | CFL Fixtures | LW HPT8 4ft 3 lamp, T12base: Biz Prescriptive | LW HPT8 4ft 3 lamp, T12base | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 31.56 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.0118 | 62
3076 | Lighting | Interior Lighting | CFL Fixtures | LW HPT8 4ft 4 lamp: Biz Prescriptive | LW HPT8 4ft 4 lamp | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 60 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.0175 | 92
3077 | Lighting | Lighting Controls | Occupany Sensor | Occ Sensor - Controlling Fixture GT 200 watts and LTEQ 500 watts: Biz Prescriptive | Occ Sensor - Controlling Fixture GT 200 watts and LTEQ 500 watts | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 116.33 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.057 | 300
3079 | Lighting | Lighting Controls | Occupany Sensor | Occ Sensor (Single Tech) - Controlling Lighting Circuit GT 120 watts: Biz Prescriptive | Occ Sensor (Single Tech) - Controlling Lighting Circuit GT 120 watts | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 119.56 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.0874 | 460
3080 | Lighting | Lighting Controls | Occupany Sensor | Occ Sensor (Single Tech) - Controlling Lighting Circuit GT 50 and LTEQ 120 watts: Biz Prescriptive | Occ Sensor (Single Tech) - Controlling Lighting Circuit GT 50 and LTEQ 120 watts | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 42.35 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.0237 | 125
3016 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensor (Dual Technology) - Controlling Lighting Circuit > 150 watts | Occupancy Sensor | 1 | Active | 2016-01-01 | [18 empty] | 128.08 |  | 8 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per sensor | 0.1463 | 770.4
786-1 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: College/University: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.3155 | 1660.9 | Early Replacement
786-10 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Elementary School: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.1242 | 653.9 | Early Replacement
786-15 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Exterior: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.2247 | 1182.6 | Early Replacement
786-19 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Garage, 24/7 lighting: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.4493 | 2365.2 | Early Replacement
786-4 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Garage: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.1816 | 955.8 | Early Replacement
786-5 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Grocery: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.3336 | 1756.1 | Early Replacement
786-11 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Heavy Industry: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.3153 | 1660.0 | Early Replacement
786-12 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: High School/Middle School: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.2211 | 1164.0 | Early Replacement
786-6 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Hospital: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.2695 | 1418.8 | Early Replacement
786-7 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Hotel/Motel Common Areas: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.3965 | 2087.3 | Early Replacement
786-13 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Hotel/Motel Guest Rooms: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.0399 | 209.8 | Early Replacement
786-9 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Light Industry: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.2974 | 1565.6 | Early Replacement
786-14 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Miscellaneous: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.2843 | 1496.4 | Early Replacement
786-16 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Multifamily Common Areas: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.3052 | 1606.5 | Early Replacement
786-8 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Office: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.2388 | 1257.1 | Early Replacement
786-18 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Religious Worship/Church: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.0854 | 449.3 | Early Replacement
786-3 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Restaurant: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.2948 | 1551.8 | Early Replacement
786-2 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Retail/Service: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.2592 | 1364.6 | Early Replacement
786-20 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Warehouse: Biz Prescriptive | Occupancy Sensors over 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.2589 | 1362.7 | Early Replacement
787-1 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: College/University: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.1262 | 664.4 | Early Replacement
787-10 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Elementary School: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.0497 | 261.6 | Early Replacement
787-15 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Exterior: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.0899 | 473.0 | Early Replacement
787-19 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Garage, 24/7 lighting: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.1797 | 946.1 | Early Replacement
787-4 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Garage: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.0726 | 382.3 | Early Replacement
787-5 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Grocery: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.1334 | 702.4 | Early Replacement
787-11 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Heavy Industry: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.1261 | 664.0 | Early Replacement
787-12 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: High School/Middle School: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.0884 | 465.6 | Early Replacement
787-6 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Hospital: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.1078 | 567.5 | Early Replacement
787-7 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Hotel/Motel Common Areas: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.1586 | 834.9 | Early Replacement
787-13 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Hotel/Motel Guest Rooms: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.0159 | 83.9 | Early Replacement
787-9 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Light Industry: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.119 | 626.2 | Early Replacement
787-14 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Miscellaneous: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.1137 | 598.6 | Early Replacement
787-16 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Multifamily Common Areas: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.1221 | 642.6 | Early Replacement
787-8 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Office: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.0955 | 502.8 | Early Replacement
787-18 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Religious Worship/Church: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.0341 | 179.7 | Early Replacement
787-3 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Restaurant: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.1179 | 620.7 | Early Replacement
787-2 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Retail/Service: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.1037 | 545.8 | Early Replacement
787-20 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Warehouse: Biz Prescriptive | Occupancy Sensors under 500 W | 2 | Active | 2016-01-01 |  | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.1035 | 545.1 | Early Replacement
781-1 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: College/University: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm | [6 empty] | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) |  | 0.023 | 616.3 | Replace on Fail
781-10 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Elementary School: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm | [6 empty] | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) |  | 0.023 | 616.3 | Early Replacement
781-15 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Exterior: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-19 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Garage, 24/7 lighting: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-4 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Garage: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-5 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Grocery: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-11 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Heavy Industry: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-12 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: High School/Middle School: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-6 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Hospital: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-7 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Hotel/Motel Common Areas: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-13 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Hotel/Motel Guest Rooms: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-9 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Light Industry: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-14 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Miscellaneous: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-16 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Multifamily Common Areas: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-8 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Office: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-18 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Religious Worship/Church: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-3 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Restaurant: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-2 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Retail/Service: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
781-20 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic_2: Warehouse: Biz Prescriptive | Passive Infrared or Ultrasonic_2 | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Early Replacement
780-1 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: College/University: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-10 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Elementary School: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Early Replacement
780-15 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Exterior: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-19 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Garage, 24/7 lighting: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-4 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Garage: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-5 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Grocery: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-11 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Heavy Industry: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-12 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: High School/Middle School: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-6 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Hospital: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-7 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Hotel/Motel Common Areas: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-13 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Hotel/Motel Guest Rooms: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-9 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Light Industry: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-14 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Miscellaneous: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-16 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Multifamily Common Areas: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-8 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Office: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-18 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Religious Worship/Church: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-3 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Restaurant: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-2 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Retail/Service: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Replace on Fail
780-20 | Lighting | Lighting Controls | Lighting Control | Passive Infrared or Ultrasonic: Warehouse: Biz Prescriptive | Passive Infrared or Ultrasonic | 1 | Active | 2013-01-02 |  | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.023 | 616.3 | Early Replacement
3035 | Lighting | Display Lighting | LED Case Light | Refrigerated Display Case Lighting 5ft T8 to 5ft LED - cooler: Biz Prescriptive | Refrigerated Display Case Lighting 5ft T8 to 5ft LED - cooler | 1 | Active | 2016-01-01 | [18 empty] | 250 |  | 8 | 2016-18 |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 0.0416 | 219
3036 | Lighting | Display Lighting | LED Case Light | Refrigerated Display Case Lighting 5ft T8 to 5ft LED - freezer: Biz Prescriptive | Refrigerated Display Case Lighting 5ft T8 to 5ft LED - freezer | 1 | Active | 2016-01-01 | [18 empty] | 250 |  | 8 | 2016-18 |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 0.0448 | 236
3037 | Lighting | Display Lighting | LED Case Light | Refrigerated Display Case Lighting 6ft T8 to 6ft LED - cooler: Biz Prescriptive | Refrigerated Display Case Lighting 6ft T8 to 6ft LED - cooler | 1 | Active | 2016-01-01 | [18 empty] | 250 |  | 8 | 2016-18 |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 0.0498 | 262
3038 | Lighting | Display Lighting | LED Case Light | Refrigerated Display Case Lighting 6ft T8 to 6ft LED - freezer: Biz Prescriptive | Refrigerated Display Case Lighting 6ft T8 to 6ft LED - freezer | 1 | Active | 2016-01-01 | [18 empty] | 250 |  | 8 | 2016-18 |  |  |  | Biz Prescriptive |  | IN TRM | per measure | 0.0538 | 283
3086 | Lighting | Interior Lighting | T5, Linear Fluorescent | T5 (Standard Output) Delamping: Biz Prescriptive | T5 (Standard Output) Delamping | 1 | Active | 2017-06-01 | [7 empty] | per measure | [10 empty] | 12 |  | 17 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.0171 | 89.9
3088 | Lighting | Interior Lighting | T5, Linear Fluorescent | T5 (Standard Output) to LED Retrofit: Biz Prescriptive | T5 (Standard Output) to LED Retrofit | 1 | Active | 2017-06-01 | [7 empty] | per measure | [10 empty] | 24 |  | 17 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.0098 | 51.36
1102-1 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: College/University: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: College/University | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2466 | 1298.0 | Early Replacement
1102-10 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Elementary School: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Elementary School | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0971 | 511.0 | Early Replacement
1102-15 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Exterior: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Exterior | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1756 | 924.2 | Early Replacement
1102-19 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Garage, 24/7 lighting: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Garage, 24/7 lighting | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.3511 | 1848.4 | Early Replacement
1102-4 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Garage: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Garage | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1419 | 746.9 | Early Replacement
1102-5 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Grocery: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Grocery | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2607 | 1372.4 | Early Replacement
1102-11 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Heavy Industry: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Heavy Industry | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2464 | 1297.2 | Early Replacement
1102-12 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: High School/Middle School: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: High School/Middle School | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1728 | 909.6 | Early Replacement
1102-6 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Hospital: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Hospital | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2106 | 1108.8 | Early Replacement
1102-7 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Hotel/Motel Common Areas: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Hotel/Motel Common Areas | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.3099 | 1631.2 | Early Replacement
1102-13 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Hotel/Motel Guest Rooms: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Hotel/Motel Guest Rooms | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0311 | 163.9 | Early Replacement
1102-9 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Light Industry: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Light Industry | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2324 | 1223.5 | Early Replacement
1102-14 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Miscellaneous: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Miscellaneous | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2221 | 1169.4 | Early Replacement
1102-16 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Multifamily Common Areas: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Multifamily Common Areas | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2385 | 1255.5 | Early Replacement
1102-8 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Office: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Office | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1866 | 982.4 | Early Replacement
1102-18 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Religious Worship/Church: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Religious Worship/Church | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0667 | 351.1 | Early Replacement
1102-3 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Restaurant: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Restaurant | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2304 | 1212.7 | Early Replacement
1102-2 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Retail/Service: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Retail/Service | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2026 | 1066.4 | Early Replacement
1102-20 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Warehouse: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Warehouse | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2023 | 1064.9 | Early Replacement
1106-1 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: College/University: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.104 | 547.5 | Early Replacement
1106-10 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Elementary School: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.041 | 215.6 | Early Replacement
1106-15 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Exterior: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.074 | 389.8 | Early Replacement
1106-19 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Garage, 24/7 lighting: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1481 | 779.6 | Early Replacement
1106-4 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Garage: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0599 | 315.1 | Early Replacement
1106-5 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Grocery: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.11 | 578.9 | Early Replacement
1106-11 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Heavy Industry: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1039 | 547.2 | Early Replacement
1106-12 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: High School/Middle School: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1597 | 840.6 | Early Replacement
1106-6 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Hospital: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0888 | 467.7 | Early Replacement
1106-7 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Hotel/Motel Common Areas: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1307 | 688.0 | Early Replacement
1106-13 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Hotel/Motel Guest Rooms: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0131 | 69.2 | Early Replacement
1106-9 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Light Industry: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.098 | 516.1 | Early Replacement
1106-14 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Miscellaneous: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0937 | 493.3 | Early Replacement
1106-16 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Multifamily Common Areas: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1006 | 529.6 | Early Replacement
1106-8 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Office: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0787 | 414.4 | Early Replacement
1106-18 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Religious Worship/Church: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0281 | 148.1 | Early Replacement
1106-3 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Restaurant: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0972 | 511.5 | Early Replacement
1106-2 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Retail/Service: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0854 | 449.8 | Early Replacement
1106-20 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Warehouse: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 3 | Active | 2017-01-01 |  | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0853 | 449.2 | Early Replacement
3087 | Lighting | Interior Lighting | T5, Linear Fluorescent | T5HO (High Output) Delamping: Biz Prescriptive | T5HO (High Output) Delamping | 1 | Active | 2017-06-01 | [7 empty] | per measure | [10 empty] | 25 |  | 17 | 2016-18 |  |  |  | Biz Prescriptive |  |  |  | 0.0439 | 231.12
3089 | Lighting | Interior Lighting | T5, Linear Fluorescent | T5HO (High Output) to LED Retrofit: Biz Prescriptive | T5HO (High Output) to LED Retrofit | 1 | Active | 2017-06-01 | [7 empty] | per measure | [10 empty] | 35 |  | 17 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.0236 | 124.12
776-1 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: College/University: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-10 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Elementary School: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Early Replacement
776-15 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Exterior: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-19 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Garage, 24/7 lighting: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-4 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Garage: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-5 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Grocery: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-11 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Heavy Industry: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-12 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: High School/Middle School: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-6 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Hospital: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-7 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Hotel/Motel Common Areas: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-13 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Hotel/Motel Guest Rooms: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-9 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Light Industry: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-14 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Miscellaneous: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-16 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Multifamily Common Areas: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-8 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Office: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-18 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Religious Worship/Church: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-3 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Restaurant: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-2 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Retail/Service: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Replace on Fail
776-20 | Lighting | Lighting Controls | Lighting Control | Central Lighting Control: Warehouse: Biz Prescriptive | Central lighting controls in commercial building | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm | Central lighting controls | [5 empty] | Algorithm |  |  | 3700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95); DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.808 | 11500.0 | Early Replacement
731-1 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: College/University: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-10 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Elementary School: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-15 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Exterior: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-19 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Garage, 24/7 lighting: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-4 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Garage: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-5 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Grocery: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-11 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Heavy Industry: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-12 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: High School/Middle School: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-6 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Hospital: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-7 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Hotel/Motel Common Areas: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-13 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Hotel/Motel Guest Rooms: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-9 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Light Industry: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-14 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Miscellaneous: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-16 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Multifamily Common Areas: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-8 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Office: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-18 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Religious Worship/Church: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-3 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Restaurant: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-2 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Retail/Service: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
731-20 | Lighting | Display Lighting | Ceramic Metal Halide Case Light | Ceramic Metal Halide 20-100W: Warehouse: Biz Prescriptive | Ceramic Metal Halide 20-100W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Display Lighting | 185 | watts |  |  |  | per measure | Algorithm | Ceramic Metal Halide | watts | 64 | Ceramic Metal Halide |  |  | Algorithm |  |  | 225 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95; Pulse-start MH 150 – 200 W | per measure | 0.115 | 445.0 | Early Replacement
3001 | Lighting | Interior Lighting | CFL | CFL (20-26) A-Line Lamp: Biz Prescriptive | CFL A-Line A15-24 Lamp | 1 | InActive | [19 empty] | 23.97 |  | 4 |  |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0231 | 121.5
3002 | Lighting | Exterior Lighting | CFL | CFL (9-14) A-Line Lamp: Biz Prescriptive | CFL (9-14) A-Line Lamp | 1 | InActive | [19 empty] | 10.49 |  | 4 |  |  |  |  | Biz Prescriptive |  |  | per lamp | 4.0E-4 | 75.9
746-1 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: College/University: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
746-1 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: College/University: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0643 | 338.3 | Early Replacement
745-10 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Elementary School: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-10 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Elementary School: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0253 | 133.2 | Early Replacement
745-15 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Exterior: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-15 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Exterior: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0458 | 240.9 | Early Replacement
745-19 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Garage, 24/7 lighting: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-19 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Garage, 24/7 lighting: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0915 | 481.8 | Early Replacement
745-4 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Garage: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-4 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Garage: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.037 | 194.7 | Early Replacement
745-5 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Grocery: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-5 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Grocery: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0679 | 357.7 | Early Replacement
745-11 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Heavy Industry: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-11 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Heavy Industry: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0642 | 338.1 | Early Replacement
745-12 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: High School/Middle School: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-12 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: High School/Middle School: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.045 | 237.1 | Early Replacement
745-6 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Hospital: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-6 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Hospital: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0549 | 289.0 | Early Replacement
745-7 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Hotel/Motel Common Areas: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-7 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Hotel/Motel Common Areas: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0808 | 425.2 | Early Replacement
745-13 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Hotel/Motel Guest Rooms: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-13 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Hotel/Motel Guest Rooms: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0081 | 42.7 | Early Replacement
745-9 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Light Industry: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-9 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Light Industry: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0606 | 318.9 | Early Replacement
745-14 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Miscellaneous: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-14 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Miscellaneous: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0579 | 304.8 | Early Replacement
745-16 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Multifamily Common Areas: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-16 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Multifamily Common Areas: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0622 | 327.3 | Early Replacement
745-8 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Office: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-8 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Office: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0486 | 256.1 | Early Replacement
745-18 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Religious Worship/Church: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-18 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Religious Worship/Church: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0174 | 91.5 | Early Replacement
745-3 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Restaurant: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-3 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Restaurant: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.06 | 316.1 | Early Replacement
745-2 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Retail/Service: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Replace on Fail
745-2 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Retail/Service: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0528 | 278.0 | Early Replacement
745-20 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Warehouse: Biz Prescriptive | CFL Reflector Flood | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.050 | 202.0 | Early Replacement
745-20 | Lighting | Interior Lighting | CFL, reflector | CFL Reflector Flood: Warehouse: Biz Prescriptive | CFL Reflector Flood | 2 | InActive |  |  | Incandescent lamps with reflectors | 74 | watts |  |  |  | per measure | Algorithm | Compact fluorescent lamps with reflectors | watts | 19 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 6 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0527 | 277.6 | Early Replacement
749-1 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: College/University: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-1 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: College/University: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1577 | 830.4 | Replace on Fail
749-10 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Elementary School: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Early Replacement
749-10 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Elementary School: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0621 | 327.0 | Early Replacement
749-15 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Exterior: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-15 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Exterior: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1123 | 591.3 | Replace on Fail
749-19 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Garage, 24/7 lighting: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-19 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Garage, 24/7 lighting: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.2247 | 1182.6 | Replace on Fail
749-4 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Garage: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-4 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Garage: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0908 | 477.9 | Replace on Fail
749-5 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Grocery: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-5 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Grocery: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1668 | 878.1 | Replace on Fail
749-11 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Heavy Industry: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-11 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Heavy Industry: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1577 | 830.0 | Replace on Fail
749-12 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: High School/Middle School: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-12 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: High School/Middle School: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1106 | 582.0 | Replace on Fail
749-6 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Hospital: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-6 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Hospital: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1348 | 709.4 | Replace on Fail
749-7 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Hotel/Motel Common Areas: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-7 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Hotel/Motel Common Areas: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1983 | 1043.7 | Replace on Fail
749-13 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Hotel/Motel Guest Rooms: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-13 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Hotel/Motel Guest Rooms: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0199 | 104.9 | Replace on Fail
749-9 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Light Industry: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-9 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Light Industry: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1487 | 782.8 | Replace on Fail
749-14 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Miscellaneous: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-14 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Miscellaneous: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1421 | 748.2 | Replace on Fail
749-16 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Multifamily Common Areas: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-16 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Multifamily Common Areas: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1526 | 803.3 | Replace on Fail
749-8 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Office: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-8 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Office: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1194 | 628.6 | Replace on Fail
749-18 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Religious Worship/Church: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-18 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Religious Worship/Church: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0427 | 224.6 | Replace on Fail
749-3 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Restaurant: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-3 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Restaurant: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1474 | 775.9 | Replace on Fail
749-2 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Retail/Service: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Replace on Fail
749-2 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Retail/Service: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1296 | 682.3 | Replace on Fail
749-20 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Warehouse: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.120 | 497.0 | Early Replacement
749-20 | Lighting | Interior Lighting | CFL, screw base | CFL Screw high wattage: Warehouse: Biz Prescriptive | Compact fluorescent lamp <= 30W X <= 115W | 2 | InActive |  |  | Incandescent lamp | 200 | watts |  |  |  | per measure | algorithm | Compact fluorescent lamp <= 30W X <= 115W1 | watts | 65 | Compact fluorescent lamp <= 30W X <= 115W1 |  |  | algorithm |  |  | 15 |  | 2 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1294 | 681.3 | Early Replacement
773-1 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: College/University: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-1 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: College/University: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 4.5573 | 23990.6 | Early Replacement
773-10 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Elementary School: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Early Replacement
773-10 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Elementary School: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 1.7944 | 9445.8 | Early Replacement
773-15 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Exterior: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-15 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Exterior: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.245 | 17082.0 | Early Replacement
773-19 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Garage, 24/7 lighting: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-19 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Garage, 24/7 lighting: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 6.4899 | 34164.0 | Early Replacement
773-4 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Garage: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-4 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Garage: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.6226 | 13806.0 | Early Replacement
773-5 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Grocery: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-5 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Grocery: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 4.8187 | 25366.2 | Early Replacement
773-11 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Heavy Industry: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-11 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Heavy Industry: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 4.5548 | 23977.1 | Early Replacement
773-12 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: High School/Middle School: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-12 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: High School/Middle School: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.1938 | 16812.9 | Early Replacement
773-6 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Hospital: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-6 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Hospital: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.8931 | 20493.8 | Early Replacement
773-7 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Hotel/Motel Common Areas: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-7 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Hotel/Motel Common Areas: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 5.7274 | 30150.1 | Early Replacement
773-13 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Hotel/Motel Guest Rooms: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-13 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Hotel/Motel Guest Rooms: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 0.5756 | 3030.3 | Early Replacement
773-9 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Light Industry: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-9 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Light Industry: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 4.2957 | 22613.5 | Early Replacement
773-14 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Miscellaneous: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-14 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Miscellaneous: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 4.1061 | 21615.2 | Early Replacement
773-16 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Multifamily Common Areas: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-16 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Multifamily Common Areas: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 4.4081 | 23205.0 | Early Replacement
773-8 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Office: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-8 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Office: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.4494 | 18158.3 | Early Replacement
773-18 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Religious Worship/Church: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-18 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Religious Worship/Church: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 1.2328 | 6489.6 | Early Replacement
773-3 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Restaurant: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-3 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Restaurant: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 4.2581 | 22415.3 | Early Replacement
773-2 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Retail/Service: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Replace on Fail
773-2 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Retail/Service: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.7443 | 19710.7 | Early Replacement
773-20 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Warehouse: Biz Prescriptive | Daylight Sensor controls | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.819 | 14800.0 | Early Replacement
773-20 | Lighting | Lighting Controls | Daylight Sensor | Daylight Sensor controls: Warehouse: Biz Prescriptive | Daylight Sensor controls | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.7391 | 19683.2 | Early Replacement
784-1 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): College/University: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-10 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Elementary School: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Early Replacement
784-15 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Exterior: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-19 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Garage, 24/7 lighting: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-4 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Garage: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-5 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Grocery: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-11 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Heavy Industry: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-12 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): High School/Middle School: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-6 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Hospital: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-7 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Hotel/Motel Common Areas: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-13 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Hotel/Motel Guest Rooms: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-9 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Light Industry: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-14 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Miscellaneous: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-16 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Multifamily Common Areas: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-8 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Office: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-18 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Religious Worship/Church: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-3 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Restaurant: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-2 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Retail/Service: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Replace on Fail
784-20 | Lighting | Lighting Controls | Occupany Sensor | Dual Technology Sensors (more than 150 Watts): Warehouse: Biz Prescriptive | Dual Technology Sensors (more than 150 Watts) | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per measure | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 128 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per measure | 0.034 | 770.4 | Early Replacement
738-1 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: College/University: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-1 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: College/University: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0037 | 658.2 | Early Replacement
738-10 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Elementary School: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-10 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Elementary School: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0015 | 259.2 | Early Replacement
738-15 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Exterior: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-15 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Exterior: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0026 | 468.7 | Early Replacement
738-19 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Garage, 24/7 lighting: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-19 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Garage, 24/7 lighting: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0053 | 937.3 | Early Replacement
738-4 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Garage: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-4 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Garage: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0021 | 378.8 | Early Replacement
738-5 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Grocery: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-5 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Grocery: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0039 | 695.9 | Early Replacement
738-11 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Heavy Industry: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-11 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Heavy Industry: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0037 | 657.8 | Early Replacement
738-12 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: High School/Middle School: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-12 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: High School/Middle School: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0026 | 461.3 | Early Replacement
738-6 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Hospital: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-6 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Hospital: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0032 | 562.3 | Early Replacement
738-7 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Hotel/Motel Common Areas: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-7 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Hotel/Motel Common Areas: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0046 | 827.2 | Early Replacement
738-13 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Hotel/Motel Guest Rooms: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-13 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Hotel/Motel Guest Rooms: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 5.0E-4 | 83.1 | Early Replacement
738-9 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Light Industry: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-9 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Light Industry: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0035 | 620.4 | Early Replacement
738-14 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Miscellaneous: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-14 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Miscellaneous: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0033 | 593.0 | Early Replacement
738-16 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Multifamily Common Areas: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-16 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Multifamily Common Areas: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0036 | 636.7 | Early Replacement
738-8 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Office: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-8 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Office: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0028 | 498.2 | Early Replacement
738-18 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Religious Worship/Church: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-18 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Religious Worship/Church: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.001 | 178.0 | Early Replacement
738-3 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Restaurant: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-3 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Restaurant: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0035 | 615.0 | Early Replacement
738-2 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Retail/Service: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-2 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Retail/Service: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.003 | 540.8 | Early Replacement
738-20 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Warehouse: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.102 | 936.0 | Early Replacement
738-20 | Lighting | Exterior Lighting | LED | Garage HID replacement above 175W to 250W HID retrofit: Warehouse: Biz Prescriptive | Garage HID replacement above 175W to 250W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 160 | LED/Induction |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.003 | 540.0 | Early Replacement
739-1 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: College/University: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Early Replacement
739-1 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: College/University: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0106 | 1895.2 | Early Replacement
739-10 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Elementary School: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Early Replacement
739-10 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Elementary School: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0042 | 746.2 | Early Replacement
739-15 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Exterior: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Early Replacement
739-15 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Exterior: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0076 | 1349.4 | Early Replacement
739-19 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Garage, 24/7 lighting: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Replace on Fail
739-19 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Garage, 24/7 lighting: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0152 | 2698.9 | Early Replacement
739-4 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Garage: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Replace on Fail
739-4 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Garage: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0061 | 1090.6 | Early Replacement
739-5 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Grocery: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Replace on Fail
739-5 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Grocery: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0113 | 2003.9 | Early Replacement
739-11 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Heavy Industry: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Early Replacement
739-11 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Heavy Industry: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0106 | 1894.1 | Early Replacement
739-12 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: High School/Middle School: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Early Replacement
739-12 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: High School/Middle School: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0075 | 1328.2 | Early Replacement
739-6 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Hospital: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Replace on Fail
739-6 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Hospital: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0091 | 1619.0 | Early Replacement
739-7 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Hotel/Motel Common Areas: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Replace on Fail
739-7 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Hotel/Motel Common Areas: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0134 | 2381.8 | Early Replacement
739-13 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Hotel/Motel Guest Rooms: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Early Replacement
739-13 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Hotel/Motel Guest Rooms: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0013 | 239.4 | Early Replacement
739-9 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Light Industry: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Replace on Fail
739-9 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Light Industry: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.01 | 1786.4 | Early Replacement
739-14 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Miscellaneous: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Early Replacement
739-14 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Miscellaneous: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0096 | 1707.6 | Early Replacement
739-16 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Multifamily Common Areas: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Replace on Fail
739-16 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Multifamily Common Areas: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0103 | 1833.2 | Early Replacement
739-8 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Office: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Replace on Fail
739-8 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Office: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0081 | 1434.5 | Early Replacement
739-18 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Religious Worship/Church: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Replace on Fail
739-18 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Religious Worship/Church: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0029 | 512.7 | Early Replacement
739-3 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Restaurant: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Replace on Fail
739-3 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Restaurant: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0099 | 1770.8 | Early Replacement
739-2 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Retail/Service: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Replace on Fail
739-2 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Retail/Service: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0087 | 1557.1 | Early Replacement
739-20 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Warehouse: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 1 | InActive | 2013-01-02 | 2015-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 279 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.175 | 1614.0 | Early Replacement
739-20 | Lighting | Exterior Lighting | LED | Garage HID replacement above 250W to 400W HID retrofit: Warehouse: Biz Prescriptive | Garage HID replacement above 250W to 400W HID retrofit | 2 | InActive | 2016-01-01 | 2016-12-31 | High Intensity Discharge Lamp | 461 | watts |  |  |  | per measure | Algorithm | LED/Induction | watts | 152.907407 | LED/Induction |  |  | Algorithm |  |  | 800 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0087 | 1554.9 | Early Replacement
742-1 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: College/University: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-1 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: College/University: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0923 | 486.0 | Early Replacement
742-10 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Elementary School: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Early Replacement
742-10 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Elementary School: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0363 | 191.3 | Early Replacement
742-15 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Exterior: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-15 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Exterior: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0657 | 346.0 | Early Replacement
742-19 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Garage, 24/7 lighting: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-19 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Garage, 24/7 lighting: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1315 | 692.0 | Early Replacement
742-4 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Garage: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-4 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Garage: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0531 | 279.7 | Early Replacement
742-5 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Grocery: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-5 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Grocery: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0976 | 513.8 | Early Replacement
742-11 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Heavy Industry: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-11 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Heavy Industry: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0923 | 485.7 | Early Replacement
742-12 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: High School/Middle School: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-12 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: High School/Middle School: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0647 | 340.6 | Early Replacement
742-6 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Hospital: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-6 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Hospital: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0789 | 415.1 | Early Replacement
742-7 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Hotel/Motel Common Areas: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-7 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Hotel/Motel Common Areas: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.116 | 610.7 | Early Replacement
742-13 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Hotel/Motel Guest Rooms: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-13 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Hotel/Motel Guest Rooms: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0117 | 61.4 | Early Replacement
742-9 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Light Industry: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-9 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Light Industry: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.087 | 458.1 | Early Replacement
742-14 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Miscellaneous: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-14 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Miscellaneous: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0832 | 437.8 | Early Replacement
742-16 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Multifamily Common Areas: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-16 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Multifamily Common Areas: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0893 | 470.1 | Early Replacement
742-8 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Office: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-8 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Office: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0699 | 367.8 | Early Replacement
742-18 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Religious Worship/Church: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-18 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Religious Worship/Church: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.025 | 131.5 | Early Replacement
742-3 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Restaurant: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-3 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Restaurant: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0863 | 454.1 | Early Replacement
742-2 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Retail/Service: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
742-2 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Retail/Service: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0759 | 399.3 | Early Replacement
742-20 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Warehouse: Biz Prescriptive | GU-24 pin based CFL_NCx | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Early Replacement
742-20 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin based CFL_NCx: Warehouse: Biz Prescriptive | GU-24 pin based CFL_NCx | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0757 | 398.7 | Early Replacement
743-1 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: College/University: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-1 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: College/University: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0923 | 486.0 | Early Replacement
743-10 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Elementary School: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Early Replacement
743-10 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Elementary School: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0363 | 191.3 | Early Replacement
743-15 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Exterior: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-15 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Exterior: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0657 | 346.0 | Early Replacement
743-19 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Garage, 24/7 lighting: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-19 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Garage, 24/7 lighting: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1315 | 692.0 | Early Replacement
743-4 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Garage: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-4 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Garage: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0531 | 279.7 | Early Replacement
743-5 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Grocery: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-5 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Grocery: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0976 | 513.8 | Early Replacement
743-11 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Heavy Industry: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-11 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Heavy Industry: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0923 | 485.7 | Early Replacement
743-12 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: High School/Middle School: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-12 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: High School/Middle School: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0647 | 340.6 | Early Replacement
743-6 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Hospital: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-6 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Hospital: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0789 | 415.1 | Early Replacement
743-7 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Hotel/Motel Common Areas: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-7 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Hotel/Motel Common Areas: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.116 | 610.7 | Early Replacement
743-13 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Hotel/Motel Guest Rooms: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-13 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Hotel/Motel Guest Rooms: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0117 | 61.4 | Early Replacement
743-9 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Light Industry: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-9 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Light Industry: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.087 | 458.1 | Early Replacement
743-14 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Miscellaneous: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-14 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Miscellaneous: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0832 | 437.8 | Early Replacement
743-16 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Multifamily Common Areas: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-16 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Multifamily Common Areas: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0893 | 470.1 | Early Replacement
743-8 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Office: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-8 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Office: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0699 | 367.8 | Early Replacement
743-18 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Religious Worship/Church: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-18 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Religious Worship/Church: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.025 | 131.5 | Early Replacement
743-3 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Restaurant: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-3 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Restaurant: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0863 | 454.1 | Early Replacement
743-2 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Retail/Service: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Replace on Fail
743-2 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Retail/Service: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0759 | 399.3 | Early Replacement
743-20 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Warehouse: Biz Prescriptive | GU-24 pin-based CFL - 30W | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.040 | 411.0 | Early Replacement
743-20 | Lighting | Interior Lighting | CFL, pin based | GU-24 pin-based CFL - 30W: Warehouse: Biz Prescriptive | GU-24 pin-based CFL - 30W | 2 | InActive |  |  | Incandescent <= 100W | 100 | watts |  |  |  | per measure | Algorithm | GU-24 pin-based CFL | watts | 21 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 11 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0757 | 398.7 | Early Replacement
757-1 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: College/University: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-10 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Elementary School: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Early Replacement
757-15 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Exterior: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-19 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Garage, 24/7 lighting: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-4 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Garage: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-5 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Grocery: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-11 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Heavy Industry: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-12 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: High School/Middle School: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-6 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Hospital: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-7 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Hotel/Motel Common Areas: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-13 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Hotel/Motel Guest Rooms: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-9 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Light Industry: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-14 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Miscellaneous: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-16 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Multifamily Common Areas: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-8 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Office: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-18 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Religious Worship/Church: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-3 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Restaurant: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-2 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Retail/Service: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Replace on Fail
757-20 | Lighting | Interior Lighting | T5, High Bay | High Bay 3L T5HO Replacing 250W HID: Warehouse: Biz Prescriptive | High Bay 3L T5HO Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay High Intensity Discharge (HID) – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 182 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 180 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.103 | 449.0 | Early Replacement
758-1 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: College/University: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-10 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Elementary School: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Early Replacement
758-15 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Exterior: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-19 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Garage, 24/7 lighting: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-4 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Garage: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-5 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Grocery: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-11 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Heavy Industry: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-12 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: High School/Middle School: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-6 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Hospital: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-7 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Hotel/Motel Common Areas: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-13 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Hotel/Motel Guest Rooms: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-9 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Light Industry: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-14 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Miscellaneous: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-16 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Multifamily Common Areas: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-8 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Office: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-18 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Religious Worship/Church: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-3 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Restaurant: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-2 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Retail/Service: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Replace on Fail
758-20 | Lighting | Interior Lighting | T5, High Bay | High Bay 6L T5HO Double fixture replace 1000W HID: Warehouse: Biz Prescriptive | High Bay 6L T5HO Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T5 High-output fluorescent lamps | watts | 730 | T5 High-output fluorescent lamps |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.333 | 1456.0 | Early Replacement
759-1 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: College/University: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-10 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Elementary School: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Early Replacement
759-15 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Exterior: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-19 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Garage, 24/7 lighting: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-4 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Garage: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-5 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Grocery: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-11 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Heavy Industry: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-12 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: High School/Middle School: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-6 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Hospital: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-7 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Hotel/Motel Common Areas: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-13 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Hotel/Motel Guest Rooms: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-9 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Light Industry: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-14 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Miscellaneous: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-16 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Multifamily Common Areas: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-8 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Office: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-18 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Religious Worship/Church: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-3 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Restaurant: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-2 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Retail/Service: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Replace on Fail
759-20 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 4LF32T8 Replacing 250W HID: Warehouse: Biz Prescriptive | High Bay Fluorescent 4LF32T8 Replacing 250W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 250 W | 290 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 142 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Coincidence Factor (CF) = 0.95 | per fixture | 0.141 | 616.0 | Early Replacement
760-1 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: College/University: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-10 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Elementary School: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Early Replacement
760-15 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Exterior: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-19 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Garage, 24/7 lighting: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-4 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Garage: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-5 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Grocery: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-11 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Heavy Industry: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-12 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: High School/Middle School: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-6 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Hospital: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-7 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Hotel/Motel Common Areas: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-13 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Hotel/Motel Guest Rooms: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-9 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Light Industry: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-14 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Miscellaneous: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-16 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Multifamily Common Areas: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-8 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Office: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-18 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Religious Worship/Church: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-3 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Restaurant: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-2 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Retail/Service: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Replace on Fail
760-20 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 6LF32T8 Replacing 400W HID: Warehouse: Biz Prescriptive | High Bay Fluorescent 6LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 455 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 224 | T8 Fluorescent |  |  | Algorithm |  |  | 160 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.219 | 961.0 | Early Replacement
761-1 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: College/University: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-10 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Elementary School: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Early Replacement
761-15 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Exterior: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-19 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Garage, 24/7 lighting: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-4 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Garage: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-5 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Grocery: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-11 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Heavy Industry: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-12 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: High School/Middle School: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-6 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Hospital: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-7 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Hotel/Motel Common Areas: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-13 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Hotel/Motel Guest Rooms: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-9 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Light Industry: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-14 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Miscellaneous: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-16 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Multifamily Common Areas: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-8 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Office: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-18 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Religious Worship/Church: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-3 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Restaurant: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-2 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Retail/Service: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Replace on Fail
761-20 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID: Warehouse: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Double fixture replace 1000W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 1,000 W | 1080 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 598 | T8 Fluorescent |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.458 | 2005.0 | Early Replacement
762-1 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: College/University: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-1 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: College/University: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1955 | 1028.9 | Early Replacement
762-10 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Elementary School: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Early Replacement
762-10 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Elementary School: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.077 | 405.1 | Early Replacement
762-15 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Exterior: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-15 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Exterior: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1392 | 732.6 | Early Replacement
762-19 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Garage, 24/7 lighting: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-19 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Garage, 24/7 lighting: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2783 | 1465.2 | Early Replacement
762-4 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Garage: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-4 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Garage: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1125 | 592.1 | Early Replacement
762-5 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Grocery: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-5 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Grocery: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2067 | 1087.9 | Early Replacement
762-11 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Heavy Industry: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-11 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Heavy Industry: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1953 | 1028.3 | Early Replacement
762-12 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: High School/Middle School: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-12 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: High School/Middle School: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.137 | 721.1 | Early Replacement
762-6 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Hospital: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-6 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Hospital: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.167 | 878.9 | Early Replacement
762-7 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Hotel/Motel Common Areas: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-7 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Hotel/Motel Common Areas: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2456 | 1293.1 | Early Replacement
762-13 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Hotel/Motel Guest Rooms: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-13 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Hotel/Motel Guest Rooms: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0247 | 130.0 | Early Replacement
762-9 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Light Industry: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-9 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Light Industry: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1842 | 969.8 | Early Replacement
762-14 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Miscellaneous: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-14 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Miscellaneous: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1761 | 927.0 | Early Replacement
762-16 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Multifamily Common Areas: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-16 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Multifamily Common Areas: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1891 | 995.2 | Early Replacement
762-8 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Office: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-8 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Office: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1479 | 778.8 | Early Replacement
762-18 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Religious Worship/Church: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-18 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Religious Worship/Church: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0529 | 278.3 | Early Replacement
762-3 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Restaurant: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-3 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Restaurant: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1826 | 961.3 | Early Replacement
762-2 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Retail/Service: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Replace on Fail
762-2 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Retail/Service: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1606 | 845.4 | Early Replacement
762-20 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Warehouse: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID – Metal Halide 400 W | 527 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 299 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.220 | 1184.0 | Early Replacement
762-20 | Lighting | Interior Lighting | T5, High Bay | High Bay Fluorescent 8LF32T8 Replacing 400W HID: Warehouse: Biz Prescriptive | High Bay Fluorescent 8LF32T8 Replacing 400W HID | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID – Metal Halide 400 W | 461.157895 | watts |  |  |  | per fixture | Algorithm | T8 Fluorescent | watts | 293.894737 | T8 Fluorescent |  |  | Algorithm |  |  | 414 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1604 | 844.2 | Early Replacement
740-1 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: College/University: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-1 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: College/University: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1671 | 879.7 | Early Replacement
740-10 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Elementary School: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Early Replacement
740-10 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Elementary School: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0658 | 346.3 | Early Replacement
740-15 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Exterior: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-15 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Exterior: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.119 | 626.3 | Early Replacement
740-19 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Garage, 24/7 lighting: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-19 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Garage, 24/7 lighting: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.238 | 1252.7 | Early Replacement
740-4 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Garage: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-4 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Garage: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0962 | 506.2 | Early Replacement
740-5 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Grocery: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-5 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Grocery: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1767 | 930.1 | Early Replacement
740-11 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Heavy Industry: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-11 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Heavy Industry: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.167 | 879.2 | Early Replacement
740-12 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: High School/Middle School: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-12 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: High School/Middle School: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1171 | 616.5 | Early Replacement
740-6 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Hospital: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-6 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Hospital: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1427 | 751.4 | Early Replacement
740-7 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Hotel/Motel Common Areas: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-7 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Hotel/Motel Common Areas: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.21 | 1105.5 | Early Replacement
740-13 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Hotel/Motel Guest Rooms: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-13 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Hotel/Motel Guest Rooms: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0211 | 111.1 | Early Replacement
740-9 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Light Industry: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-9 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Light Industry: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1575 | 829.2 | Early Replacement
740-14 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Miscellaneous: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-14 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Miscellaneous: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1506 | 792.6 | Early Replacement
740-16 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Multifamily Common Areas: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-16 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Multifamily Common Areas: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1616 | 850.9 | Early Replacement
740-8 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Office: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-8 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Office: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1265 | 665.8 | Early Replacement
740-18 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Religious Worship/Church: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-18 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Religious Worship/Church: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0452 | 238.0 | Early Replacement
740-3 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Restaurant: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-3 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Restaurant: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1561 | 821.9 | Early Replacement
740-2 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Retail/Service: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Replace on Fail
740-2 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Retail/Service: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1373 | 722.7 | Early Replacement
740-20 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Warehouse: Biz Prescriptive | Interior CF 1L 26W Quad | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 745.0 | Early Replacement
740-20 | Lighting | Interior Lighting | CFL | Interior CF 1L 26W Quad: Warehouse: Biz Prescriptive | Interior CF 1L 26W Quad | 2 | InActive |  |  | Incandescent | 169 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 26W Quad | watts | 26 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 92 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1371 | 721.7 | Early Replacement
741-1 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: College/University: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-1 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: College/University: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0386 | 203.0 | Early Replacement
741-10 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Elementary School: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Early Replacement
741-10 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Elementary School: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0152 | 79.9 | Early Replacement
741-15 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Exterior: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-15 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Exterior: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0274 | 144.5 | Early Replacement
741-19 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Garage, 24/7 lighting: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-19 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Garage, 24/7 lighting: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0549 | 289.1 | Early Replacement
741-4 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Garage: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-4 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Garage: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0222 | 116.8 | Early Replacement
741-5 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Grocery: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-5 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Grocery: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0408 | 214.6 | Early Replacement
741-11 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Heavy Industry: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-11 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Heavy Industry: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0385 | 202.9 | Early Replacement
741-12 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: High School/Middle School: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-12 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: High School/Middle School: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.027 | 142.3 | Early Replacement
741-6 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Hospital: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-6 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Hospital: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0329 | 173.4 | Early Replacement
741-7 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Hotel/Motel Common Areas: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-7 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Hotel/Motel Common Areas: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0485 | 255.1 | Early Replacement
741-13 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Hotel/Motel Guest Rooms: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-13 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Hotel/Motel Guest Rooms: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0049 | 25.6 | Early Replacement
741-9 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Light Industry: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-9 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Light Industry: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0363 | 191.3 | Early Replacement
741-14 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Miscellaneous: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-14 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Miscellaneous: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0347 | 182.9 | Early Replacement
741-16 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Multifamily Common Areas: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-16 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Multifamily Common Areas: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0373 | 196.4 | Early Replacement
741-8 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Office: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-8 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Office: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0292 | 153.6 | Early Replacement
741-18 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Religious Worship/Church: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-18 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Religious Worship/Church: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0104 | 54.9 | Early Replacement
741-3 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Restaurant: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-3 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Restaurant: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.036 | 189.7 | Early Replacement
741-2 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Retail/Service: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Replace on Fail
741-2 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Retail/Service: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0317 | 166.8 | Early Replacement
741-20 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Warehouse: Biz Prescriptive | Interior CF 1L 32W Triple | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.030 | 172.0 | Early Replacement
741-20 | Lighting | Interior Lighting | CFL | Interior CF 1L 32W Triple: Warehouse: Biz Prescriptive | Interior CF 1L 32W Triple | 2 | InActive |  |  | Incandescent | 65 | watts |  |  |  | per measure | Algorithm | Interior CF 1L 32W Triple | watts | 32 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 135 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0316 | 166.5 | Early Replacement
3004-1 | Lighting | Exterior Lighting | LED | LED 100 Watt Lamp (12 hrs/day): Biz Prescriptive | LED 100 Watt Lamp (12 hrs/day) | 1 | InActive | 2016-01-01 | 2016-12-31 | [17 empty] | 233.64 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0037 | 657.0
3004-2 | Lighting | Exterior Lighting | LED | LED 100 Watt Lamp (24 hrs/day): Biz Prescriptive | LED 100 Watt Lamp (24 hrs/day) | 1 | InActive | 2016-01-01 | 2016-12-31 | [17 empty] | 233.64 |  | 9 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0074 | 1314.0
3005-1 | Lighting | Interior Lighting | LED, screw base | LED 120 Watt Lamp (12 hrs/day): Biz Prescriptive | LED ED 28 Lamp | 1 | InActive | 2016-01-01 | 2016-12-31 | [17 empty] | 361.64 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.233 | 1226.4
3005-2 | Lighting | Exterior Lighting | LED | LED 120 Watt Lamp (24 hrs/day): Biz Prescriptive | LED ED 28 Lamp | 1 | InActive | 2016-01-01 | 2016-12-31 | [17 empty] | 361.64 |  | 9 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0138 | 2452.8
3007 | Lighting | Interior Lighting | LED, fixture | LED (BAR/R) Reflector Lamp: Biz Prescriptive | LED BR/ R 30,40 Lamp | 1 | InActive | 2016-01-01 | 2016-12-31 | [6 empty] | per lamp | [10 empty] | 48.27 |  | 9 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0372 | 195.9
3008 | Lighting | Interior Lighting | LED, fixture | LED (PAR) Reflector Lamp : Biz Prescriptive | LED PAR 38 Lamp | 1 | InActive | 2016-01-01 | 2016-12-31 | [17 empty] | 74.64 |  | 9 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0476 | 250.5
3010 | Lighting | Interior Lighting | LED, screw base | LED 1-8 Watt Decorative Lamp: Biz Prescriptive | LED Decorative C,T,B,G Lamp | 1 | InActive | 2016-01-01 | 2016-12-31 | [17 empty] | 22.64 |  | 5 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0389 | 205.0
734-1 | Lighting | Display Lighting | LED Case Light | LED Case lighting: College/University: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-1 | Lighting | Display Lighting | LED Case Light | LED Case lighting: College/University: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0362 | 190.7 | Early Replacement
734-10 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Elementary School: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-10 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Elementary School: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0143 | 75.1 | Early Replacement
734-15 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Exterior: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-15 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Exterior: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0258 | 135.8 | Early Replacement
734-19 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Garage, 24/7 lighting: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-19 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Garage, 24/7 lighting: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0516 | 271.6 | Early Replacement
734-4 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Garage: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-4 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Garage: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0208 | 109.7 | Early Replacement
734-5 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Grocery: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-5 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Grocery: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0383 | 201.6 | Early Replacement
734-11 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Heavy Industry: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-11 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Heavy Industry: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0362 | 190.6 | Early Replacement
734-12 | Lighting | Display Lighting | LED Case Light | LED Case lighting: High School/Middle School: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-12 | Lighting | Display Lighting | LED Case Light | LED Case lighting: High School/Middle School: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0254 | 133.6 | Early Replacement
734-6 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Hospital: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-6 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Hospital: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0309 | 162.9 | Early Replacement
734-7 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Hotel/Motel Common Areas: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-7 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Hotel/Motel Common Areas: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0455 | 239.7 | Early Replacement
734-13 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Hotel/Motel Guest Rooms: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-13 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Hotel/Motel Guest Rooms: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0046 | 24.1 | Early Replacement
734-9 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Light Industry: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-9 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Light Industry: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0341 | 179.7 | Early Replacement
734-14 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Miscellaneous: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-14 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Miscellaneous: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0326 | 171.8 | Early Replacement
734-16 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Multifamily Common Areas: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-16 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Multifamily Common Areas: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.035 | 184.5 | Early Replacement
734-8 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Office: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-8 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Office: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0274 | 144.3 | Early Replacement
734-18 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Religious Worship/Church: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-18 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Religious Worship/Church: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0098 | 51.6 | Early Replacement
734-3 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Restaurant: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-3 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Restaurant: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0339 | 178.2 | Early Replacement
734-2 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Retail/Service: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-2 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Retail/Service: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0298 | 156.7 | Early Replacement
734-20 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Warehouse: Biz Prescriptive | LED Case lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | T8 Fluorescent | 99 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 50 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.041 | 429.0 | Early Replacement
734-20 | Lighting | Display Lighting | LED Case Light | LED Case lighting: Warehouse: Biz Prescriptive | LED Case lighting | 2 | InActive |  |  | T8 Fluorescent | 85 | watts |  |  |  | per door | Algorithm | LED replacement | watts | 54 | LED replacement |  |  | Algorithm |  |  | 300 |  | 15 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: 25% of heat is lost through the case. Coincidence Factor (CF) = 0.95 | per door | 0.0297 | 156.5 | Early Replacement
793-1 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: College/University: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-10 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Elementary School: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Early Replacement
793-15 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Exterior: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-19 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Garage, 24/7 lighting: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-4 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Garage: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-5 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Grocery: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-11 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Heavy Industry: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-12 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: High School/Middle School: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-6 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Hospital: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-7 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Hotel/Motel Common Areas: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-13 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Hotel/Motel Guest Rooms: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-9 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Light Industry: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-14 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Miscellaneous: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-16 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Multifamily Common Areas: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-8 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Office: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-18 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Religious Worship/Church: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-3 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Restaurant: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-2 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Retail/Service: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Replace on Fail
793-20 | Lighting | Signage | LED, exit sign | LED Exit Sign - 3_0 W_Inc30 base: Warehouse: Biz Prescriptive | LED Exit Sign - 3_0 W_Inc30 base | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent Exit Sign | 30 | watts |  |  |  | per fixture |  | LED Exit Sign | watts | 3 | LED Exit Sign | [5 empty] | 63 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 1.0 | per fixture | 0.032 | 237.0 | Early Replacement
3013 | Lighting | Interior Lighting | LED, screw base | LED MR16 (8 Watt) Lamp: Biz Prescriptive | LED MR16 MR16 Lamp | 1 | InActive | 2016-01-01 | 2016-12-31 | [17 empty] | 36.64 |  | 9 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0234 | 123.0
3025 | Lighting | Interior Lighting | LED, Linear | Linear Tube LED 4ft Efficient Lamp Upgrade - 32W T8 Base: Biz Prescriptive | LED (T) Tube Linear Lamp | 1 | InActive | 2016-01-01 | 2016-12-31 | [17 empty] | 29.64 |  | 17 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.0092 | 48.6
3026 | Lighting | Interior Lighting | LED, Linear | Linear Tube LED 4ft Efficient Lamp Upgrade - T12 Base: Biz Prescriptive | LED (T) Tube Linear Lamp | 1 | InActive | 2016-01-01 | 2016-12-31 | [17 empty] | 29.64 |  | 17 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per lamp | 0.015 | 79.0
744-1 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): College/University: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-1 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): College/University: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.2092 | 1101.1 | Early Replacement
744-10 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Elementary School: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Early Replacement
744-10 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Elementary School: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0823 | 433.5 | Early Replacement
744-15 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Exterior: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-15 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Exterior: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1489 | 784.0 | Early Replacement
744-19 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Garage, 24/7 lighting: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-19 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Garage, 24/7 lighting: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.2979 | 1568.0 | Early Replacement
744-4 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Garage: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-4 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Garage: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1204 | 633.7 | Early Replacement
744-5 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Grocery: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-5 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Grocery: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.2212 | 1164.2 | Early Replacement
744-11 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Heavy Industry: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-11 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Heavy Industry: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.2091 | 1100.5 | Early Replacement
744-12 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): High School/Middle School: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-12 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): High School/Middle School: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1466 | 771.7 | Early Replacement
744-6 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Hospital: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-6 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Hospital: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1787 | 940.6 | Early Replacement
744-7 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Hotel/Motel Common Areas: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-7 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Hotel/Motel Common Areas: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.2629 | 1383.8 | Early Replacement
744-13 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Hotel/Motel Guest Rooms: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-13 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Hotel/Motel Guest Rooms: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0264 | 139.1 | Early Replacement
744-9 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Light Industry: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-9 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Light Industry: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1972 | 1037.9 | Early Replacement
744-14 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Miscellaneous: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-14 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Miscellaneous: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1885 | 992.1 | Early Replacement
744-16 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Multifamily Common Areas: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-16 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Multifamily Common Areas: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.2023 | 1065.1 | Early Replacement
744-8 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Office: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-8 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Office: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1583 | 833.4 | Early Replacement
744-18 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Religious Worship/Church: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-18 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Religious Worship/Church: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0566 | 297.9 | Early Replacement
744-3 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Restaurant: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-3 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Restaurant: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1954 | 1028.8 | Early Replacement
744-2 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Retail/Service: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Replace on Fail
744-2 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Retail/Service: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1719 | 904.7 | Early Replacement
744-20 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Warehouse: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 1 | InActive | 2013-01-02 | 2015-12-31 | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.140 | 1402.0 | Early Replacement
744-20 | Lighting | Interior Lighting | CFL, pin based | New pin-based CFL Fixture (_GT_45W): Warehouse: Biz Prescriptive | New pin-based CFL Fixture (_GT_45W) | 2 | InActive |  |  | Incandescent >100W | 224 | watts |  |  |  | per measure | Algorithm | New pin-based CFL Fixture (>45W) | watts | 45 | Compact Fluorescent Lights |  |  | Algorithm |  |  | 327 |  | 11 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1716 | 903.4 | Early Replacement
3015 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensor - Controlling Fixture > 200 watts and ≤ 500 watts: Biz Prescriptive | Occupancy Sensor | 1 | InActive | [19 empty] | 116.33 |  | 10 |  |  |  |  | Biz Prescriptive |  |  | per sensor | 0.057 | 300
3017 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensor (Single Technology) - Controlling Lighting Circuit > 120 watts: Biz Prescriptive | Occupancy Sensor | 1 | InActive | [19 empty] | 119.56 |  | 11 |  |  |  |  | Biz Prescriptive |  |  | per sensor | 0.0874 | 460
3018 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensor (Single Technology) - Controlling Lighting Circuit > 50 and ≤ 120 watts | Occupancy Sensor | 1 | InActive | [19 empty] | 42.35 |  | 11 |  |  |  |  | Biz Prescriptive |  |  | per sensor | 0.0237 | 125
786-1 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: College/University: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-10 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Elementary School: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Early Replacement
786-15 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Exterior: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-19 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Garage, 24/7 lighting: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-4 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Garage: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-5 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Grocery: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-11 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Heavy Industry: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-12 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: High School/Middle School: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-6 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Hospital: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-7 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Hotel/Motel Common Areas: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-13 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Hotel/Motel Guest Rooms: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-9 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Light Industry: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-14 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Miscellaneous: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-16 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Multifamily Common Areas: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-8 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Office: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-18 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Religious Worship/Church: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-3 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Restaurant: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-2 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Retail/Service: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Replace on Fail
786-20 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors over 500 W: Warehouse: Biz Prescriptive | Occupancy Sensors over 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 750 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 311 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 750 square feet | 0.243 | 994.0 | Early Replacement
787-1 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: College/University: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-10 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Elementary School: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Early Replacement
787-15 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Exterior: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-19 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Garage, 24/7 lighting: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-4 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Garage: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-5 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Grocery: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-11 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Heavy Industry: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-12 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: High School/Middle School: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-6 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Hospital: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-7 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Hotel/Motel Common Areas: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-13 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Hotel/Motel Guest Rooms: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-9 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Light Industry: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-14 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Miscellaneous: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-16 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Multifamily Common Areas: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-8 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Office: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-18 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Religious Worship/Church: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-3 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Restaurant: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-2 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Retail/Service: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Replace on Fail
787-20 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors under 500 W: Warehouse: Biz Prescriptive | Occupancy Sensors under 500 W | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 300 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 144 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 300 square feet | 0.099 | 397.0 | Early Replacement
754-1 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: College/University: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-1 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: College/University: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0666 | 350.6 | Early Replacement
754-10 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Elementary School: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Early Replacement
754-10 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Elementary School: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0262 | 138.1 | Early Replacement
754-15 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Exterior: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-15 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Exterior: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0474 | 249.7 | Early Replacement
754-19 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Garage, 24/7 lighting: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-19 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Garage, 24/7 lighting: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0948 | 499.3 | Early Replacement
754-4 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Garage: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-4 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Garage: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0383 | 201.8 | Early Replacement
754-5 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Grocery: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-5 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Grocery: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0704 | 370.7 | Early Replacement
754-11 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Heavy Industry: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-11 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Heavy Industry: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0666 | 350.4 | Early Replacement
754-12 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: High School/Middle School: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-12 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: High School/Middle School: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0467 | 245.7 | Early Replacement
754-6 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Hospital: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-6 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Hospital: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0569 | 299.5 | Early Replacement
754-7 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Hotel/Motel Common Areas: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-7 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Hotel/Motel Common Areas: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0837 | 440.7 | Early Replacement
754-13 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Hotel/Motel Guest Rooms: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-13 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Hotel/Motel Guest Rooms: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0084 | 44.3 | Early Replacement
754-9 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Light Industry: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-9 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Light Industry: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0628 | 330.5 | Early Replacement
754-14 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Miscellaneous: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-14 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Miscellaneous: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.06 | 315.9 | Early Replacement
754-16 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Multifamily Common Areas: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-16 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Multifamily Common Areas: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0644 | 339.2 | Early Replacement
754-8 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Office: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-8 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Office: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0504 | 265.4 | Early Replacement
754-18 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Religious Worship/Church: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-18 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Religious Worship/Church: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.018 | 94.8 | Early Replacement
754-3 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Restaurant: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-3 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Restaurant: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0622 | 327.6 | Early Replacement
754-2 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Retail/Service: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Replace on Fail
754-2 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Retail/Service: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0547 | 288.1 | Early Replacement
754-20 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Warehouse: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.054 | 237.0 | Early Replacement
754-20 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 150-200W retrofit only: Warehouse: Biz Prescriptive | Pulse Start Metal Halide 150-200W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | Avg 175 and 250 High Intensity Discharge Lamp | 267 | watts |  |  |  | per measure | Algorithm | Average 150, 175, 200 | watts | 210 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 135 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0547 | 287.7 | Early Replacement
755-1 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: College/University: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-1 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: College/University: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0993 | 522.9 | Early Replacement
755-10 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Elementary School: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Early Replacement
755-10 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Elementary School: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0391 | 205.9 | Early Replacement
755-15 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Exterior: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-15 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Exterior: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0707 | 372.3 | Early Replacement
755-19 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Garage, 24/7 lighting: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-19 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Garage, 24/7 lighting: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1414 | 744.6 | Early Replacement
755-4 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Garage: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-4 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Garage: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0572 | 300.9 | Early Replacement
755-5 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Grocery: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-5 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Grocery: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.105 | 552.9 | Early Replacement
755-11 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Heavy Industry: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-11 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Heavy Industry: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0993 | 522.6 | Early Replacement
755-12 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: High School/Middle School: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-12 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: High School/Middle School: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0696 | 366.4 | Early Replacement
755-6 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Hospital: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-6 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Hospital: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0849 | 446.7 | Early Replacement
755-7 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Hotel/Motel Common Areas: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-7 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Hotel/Motel Common Areas: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1248 | 657.1 | Early Replacement
755-13 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Hotel/Motel Guest Rooms: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-13 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Hotel/Motel Guest Rooms: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0125 | 66.0 | Early Replacement
755-9 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Light Industry: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-9 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Light Industry: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0936 | 492.9 | Early Replacement
755-14 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Miscellaneous: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-14 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Miscellaneous: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0895 | 471.1 | Early Replacement
755-16 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Multifamily Common Areas: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-16 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Multifamily Common Areas: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0961 | 505.8 | Early Replacement
755-8 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Office: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-8 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Office: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0752 | 395.8 | Early Replacement
755-18 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Religious Worship/Church: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-18 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Religious Worship/Church: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0269 | 141.4 | Early Replacement
755-3 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Restaurant: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-3 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Restaurant: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0928 | 488.5 | Early Replacement
755-2 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Retail/Service: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Replace on Fail
755-2 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Retail/Service: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0816 | 429.6 | Early Replacement
755-20 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Warehouse: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.081 | 354.0 | Early Replacement
755-20 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 320W retrofit only: Warehouse: Biz Prescriptive | Pulse Start Metal Halide 320W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 400 W High Intensity Discharge Lamp | 455 | watts |  |  |  | per measure | Algorithm | 320 Watt Metal Halide- Pulse Start | watts | 370 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 150 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0815 | 429.0 | Early Replacement
756-1 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: College/University: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-1 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: College/University: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.3062 | 1611.7 | Early Replacement
756-10 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Elementary School: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Early Replacement
756-10 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Elementary School: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1206 | 634.6 | Early Replacement
756-15 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Exterior: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-15 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Exterior: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.218 | 1147.6 | Early Replacement
756-19 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Garage, 24/7 lighting: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-19 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Garage, 24/7 lighting: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.436 | 2295.1 | Early Replacement
756-4 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Garage: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-4 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Garage: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.1762 | 927.5 | Early Replacement
756-5 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Grocery: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-5 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Grocery: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.3237 | 1704.1 | Early Replacement
756-11 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Heavy Industry: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-11 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Heavy Industry: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.306 | 1610.8 | Early Replacement
756-12 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: High School/Middle School: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-12 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: High School/Middle School: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.2146 | 1129.5 | Early Replacement
756-6 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Hospital: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-6 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Hospital: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.2615 | 1376.8 | Early Replacement
756-7 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Hotel/Motel Common Areas: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-7 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Hotel/Motel Common Areas: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.3848 | 2025.5 | Early Replacement
756-13 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Hotel/Motel Guest Rooms: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-13 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Hotel/Motel Guest Rooms: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0387 | 203.6 | Early Replacement
756-9 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Light Industry: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-9 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Light Industry: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.2886 | 1519.2 | Early Replacement
756-14 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Miscellaneous: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-14 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Miscellaneous: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.2758 | 1452.1 | Early Replacement
756-16 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Multifamily Common Areas: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-16 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Multifamily Common Areas: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.2961 | 1558.9 | Early Replacement
756-8 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Office: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-8 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Office: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.2317 | 1219.9 | Early Replacement
756-18 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Religious Worship/Church: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-18 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Religious Worship/Church: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.0828 | 436.0 | Early Replacement
756-3 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Restaurant: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-3 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Restaurant: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.286 | 1505.8 | Early Replacement
756-2 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Retail/Service: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Replace on Fail
756-2 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Retail/Service: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.2515 | 1324.2 | Early Replacement
756-20 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Warehouse: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 1 | InActive | 2013-01-02 | 2015-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.249 | 1090.0 | Early Replacement
756-20 | Lighting | Interior Lighting | Metal Halide, High Bay | Pulse Start Metal Halide 750W retrofit only: Warehouse: Biz Prescriptive | Pulse Start Metal Halide 750W retrofit only | 2 | InActive | 2016-01-01 | 2016-12-31 | 1000 W High Intensity Discharge Lamp | 1080 | watts |  |  |  | per measure | Algorithm | 750 Watt Metal Halide - Pulse Start | watts | 818 | Pulse Start Metal Halide |  |  | Algorithm |  |  | 200 |  | 16 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per measure | 0.2512 | 1322.3 | Early Replacement
782-1 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: College/University: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-1 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: College/University: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.6292 | 13840.7 | Early Replacement
782-10 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Elementary School: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Early Replacement
782-10 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Elementary School: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 1.0352 | 5449.5 | Early Replacement
782-15 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Exterior: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-15 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Exterior: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 1.8721 | 9855.0 | Early Replacement
782-19 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Garage, 24/7 lighting: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-19 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Garage, 24/7 lighting: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.7442 | 19710.0 | Early Replacement
782-4 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Garage: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-4 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Garage: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 1.5131 | 7965.0 | Early Replacement
782-5 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Grocery: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-5 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Grocery: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.78 | 14634.4 | Early Replacement
782-11 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Heavy Industry: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-11 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Heavy Industry: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.6278 | 13833.0 | Early Replacement
782-12 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: High School/Middle School: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-12 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: High School/Middle School: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 1.8426 | 9699.8 | Early Replacement
782-6 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Hospital: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-6 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Hospital: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.246 | 11823.4 | Early Replacement
782-7 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Hotel/Motel Common Areas: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-7 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Hotel/Motel Common Areas: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 3.3043 | 17394.3 | Early Replacement
782-13 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Hotel/Motel Guest Rooms: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-13 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Hotel/Motel Guest Rooms: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 0.3321 | 1748.3 | Early Replacement
782-9 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Light Industry: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-9 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Light Industry: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.4783 | 13046.3 | Early Replacement
782-14 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Miscellaneous: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-14 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Miscellaneous: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.3689 | 12470.3 | Early Replacement
782-16 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Multifamily Common Areas: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-16 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Multifamily Common Areas: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.5431 | 13387.5 | Early Replacement
782-8 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Office: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-8 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Office: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 1.99 | 10475.9 | Early Replacement
782-18 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Religious Worship/Church: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-18 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Religious Worship/Church: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 0.7112 | 3744.0 | Early Replacement
782-3 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Restaurant: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-3 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Restaurant: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.4566 | 12931.9 | Early Replacement
782-2 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Retail/Service: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Replace on Fail
782-2 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Retail/Service: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.1602 | 11371.6 | Early Replacement
782-20 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Warehouse: Biz Prescriptive | Switching Controls for Multilevel Lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.196 | 8000.0 | Early Replacement
782-20 | Lighting | Lighting Controls | Lighting Control | Switching Controls for Multilevel Lighting: Warehouse: Biz Prescriptive | Switching Controls for Multilevel Lighting | 2 | InActive |  |  | No Controls | [5 empty] | per 10,000 square feet | Algorithm |  |  |  | Automated or motion controls |  |  | Algorithm |  |  | 4000 |  | 12 |  |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.90 (Daylight Sensor Controls have CF = 0.95) DF = Diversity Factor (assumed at 0.9) | per 10,000 square feet | 2.1572 | 11355.7 | Early Replacement
1102-1 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: College/University: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: College/University | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-1 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: College/University: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: College/University | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2653 | 1396.4 | Early Replacement
1102-10 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Elementary School: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Elementary School | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-10 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Elementary School: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Elementary School | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1044 | 549.8 | Early Replacement
1102-15 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Exterior: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Exterior | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-15 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Exterior: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Exterior | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1889 | 994.3 | Early Replacement
1102-19 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Garage, 24/7 lighting: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Garage, 24/7 lighting | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-19 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Garage, 24/7 lighting: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Garage, 24/7 lighting | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.3777 | 1988.5 | Early Replacement
1102-4 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Garage: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Garage | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-4 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Garage: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Garage | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1527 | 803.6 | Early Replacement
1102-5 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Grocery: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Grocery | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-5 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Grocery: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Grocery | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2805 | 1476.4 | Early Replacement
1102-11 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Heavy Industry: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Heavy Industry | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-11 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Heavy Industry: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Heavy Industry | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2651 | 1395.6 | Early Replacement
1102-12 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: High School/Middle School: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: High School/Middle School | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-12 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: High School/Middle School: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: High School/Middle School | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1859 | 978.6 | Early Replacement
1102-6 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Hospital: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Hospital | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-6 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Hospital: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Hospital | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2266 | 1192.8 | Early Replacement
1102-7 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Hotel/Motel Common Areas: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Hotel/Motel Common Areas | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-7 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Hotel/Motel Common Areas: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Hotel/Motel Common Areas | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.3334 | 1754.9 | Early Replacement
1102-13 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Hotel/Motel Guest Rooms: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Hotel/Motel Guest Rooms | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-13 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Hotel/Motel Guest Rooms: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Hotel/Motel Guest Rooms | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0335 | 176.4 | Early Replacement
1102-9 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Light Industry: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Light Industry | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-9 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Light Industry: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Light Industry | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.25 | 1316.2 | Early Replacement
1102-14 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Miscellaneous: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Miscellaneous | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-14 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Miscellaneous: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Miscellaneous | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.239 | 1258.1 | Early Replacement
1102-16 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Multifamily Common Areas: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Multifamily Common Areas | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-16 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Multifamily Common Areas: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Multifamily Common Areas | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2566 | 1350.7 | Early Replacement
1102-8 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Office: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Office | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-8 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Office: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Office | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2008 | 1056.9 | Early Replacement
1102-18 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Religious Worship/Church: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Religious Worship/Church | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-18 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Religious Worship/Church: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Religious Worship/Church | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0717 | 377.7 | Early Replacement
1102-3 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Restaurant: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Restaurant | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-3 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Restaurant: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Restaurant | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2478 | 1304.7 | Early Replacement
1102-2 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Retail/Service: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Retail/Service | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-2 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Retail/Service: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Retail/Service | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2179 | 1147.3 | Early Replacement
1102-20 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Warehouse: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Warehouse | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.210 | 1180.8 | Early Replacement
1102-20 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 4L-F54HO: Warehouse: Biz Prescriptive | Commercial Lighting 4-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide: Warehouse | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 470 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 243 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 339 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2176 | 1145.7 | Early Replacement
1106-1 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: College/University: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-1 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: College/University: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2279 | 1199.5 | Early Replacement
1106-10 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Elementary School: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-10 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Elementary School: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0897 | 472.3 | Early Replacement
1106-15 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Exterior: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-15 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Exterior: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1622 | 854.1 | Early Replacement
1106-19 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Garage, 24/7 lighting: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-19 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Garage, 24/7 lighting: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.3245 | 1708.2 | Early Replacement
1106-4 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Garage: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-4 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Garage: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1311 | 690.3 | Early Replacement
1106-5 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Grocery: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-5 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Grocery: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2409 | 1268.3 | Early Replacement
1106-11 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Heavy Industry: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-11 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Heavy Industry: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2277 | 1198.9 | Early Replacement
1106-12 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: High School/Middle School: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-12 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: High School/Middle School: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0729 | 383.7 | Early Replacement
1106-6 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Hospital: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-6 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Hospital: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1947 | 1024.7 | Early Replacement
1106-7 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Hotel/Motel Common Areas: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-7 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Hotel/Motel Common Areas: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2864 | 1507.5 | Early Replacement
1106-13 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Hotel/Motel Guest Rooms: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-13 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Hotel/Motel Guest Rooms: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0288 | 151.5 | Early Replacement
1106-9 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Light Industry: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-9 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Light Industry: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2148 | 1130.7 | Early Replacement
1106-14 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Miscellaneous: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-14 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Miscellaneous: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2053 | 1080.8 | Early Replacement
1106-16 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Multifamily Common Areas: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-16 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Multifamily Common Areas: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2204 | 1160.3 | Early Replacement
1106-8 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Office: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-8 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Office: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1725 | 907.9 | Early Replacement
1106-18 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Religious Worship/Church: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-18 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Religious Worship/Church: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.0616 | 324.5 | Early Replacement
1106-3 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Restaurant: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-3 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Restaurant: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.2129 | 1120.8 | Early Replacement
1106-2 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Retail/Service: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-2 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Retail/Service: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.1872 | 985.5 | Early Replacement
1106-20 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Warehouse: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 1 | InActive | 2013-01-02 | 2015-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.165 | 1015.4 | Early Replacement
1106-20 | Lighting | Interior Lighting | T5, High Bay | T5 High-Bay 6L-F54HO: Warehouse: Biz Prescriptive | Commercial Lighting 6-Lamp T5 Fluorescent Lighting Fixture Replacing 400 watt Metal Halide | 2 | InActive | 2016-01-01 | 2016-12-31 | High Bay HID - Metal Halide 400 W | 560 | watts |  |  |  | per fixture | algorithm | T5 High-output fluorescent lamps | watts | 365 | T5 High-output fluorescent lamps |  |  | algorithm |  |  | 256 |  | 11 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Coincidence Factor (CF) = 0.95 | per fixture | 0.187 | 984.2 | Early Replacement
3003 | Lighting | Exterior Lighting | Induction | Induction Street Lighting: Biz Prescriptive | Induction Street Lighting | 2 | Proposed | 2017-01-01 | [18 empty] | 0 |  | 20 |  |  |  |  | Biz Prescriptive |  |  | per fixture | 4.0E-4 | 73.1
3057 | Lighting | Lighting Controls | Occupany Sensor | Occupancy Sensors for LED Refrigerator Lighting: Biz Prescriptive | Occupancy Sensors for LED Refrigerator Lighting | 1 | Proposed | 2016-01-01 | [18 empty] | 20 |  | 16 |  |  |  |  | Biz Prescriptive |  |  |  | .03 | 195
838 | Refrigeration | Refrigeration Controls | Anti-sweat heater control | Anti-Sweat Heater Controls -- Cooler: Biz Prescriptive | Anti-Sweat Heater Controls | 1 | Active | 2013-01-02 |  | Door with no control | [5 empty] | per measure | Algorithm | Automated Control | [5 empty] | Algorithm |  |  | 151 |  | 12 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per measure | 0.1855 | 1366.9 | Early Replacement
839 | Refrigeration | Refrigeration Controls | Vending Control | Beverage Vending Machine Control: Biz Prescriptive | Beverage vending machine automated/motion controls | 1 | InActive | 2013-01-02 | 2015-12-31 | Beverage Vending Machine with no controls | [5 empty] | per measure | Algorithm | Beverage vending machine automated/motion controls |  |  | Beverage vending machine automated/motion controls |  |  | Algorithm |  |  | 141 |  | 5 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Alternatively, if the variables listed in the above equation are not available, the following equation and parameters can be used to estimate savings: delta kWh= (Demand Novelty Cooler)*(0.45*hrs off/day*91 days)+(0.50*hrs off/day*274 days). Key Assumptions: Power Factor = 0.85 | per measure | 0.055 | 1646.0 | Early Replacement
839 | Refrigeration | Refrigeration Controls | Vending Control | Beverage Vending Machine Control: Biz Prescriptive | Beverage vending machine automated/motion controls | 2 | Active | 2016-01-01 |  | Beverage Vending Machine with no controls |  |  | 0.05541 | 1651.51 |  | per measure | Algorithm | Beverage vending machine automated/motion controls |  |  | Beverage vending machine automated/motion controls |  |  | Algorithm |  |  | 216 |  | 5 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Alternatively, if the variables listed in the above equation are not available, the following equation and parameters can be used to estimate savings: delta kWh= (Demand Novelty Cooler)*(0.45*hrs off/day*91 days)+(0.50*hrs off/day*274 days). Key Assumptions: Power Factor = 0.85 | per measure | 0.1086 | 800 | Early Replacement
816 | Motors | Refrigeration Motors | ECM Motor | ECM Cooler and Freezer Motors - Non Display Case: Biz Prescriptive | ECM replacing All Types | 1 | InActive |  |  | Shaded Pole or PSC on existing case | [5 empty] | per measure | Algorithm |  |  |  | ECM installed; Minimum qualifying ECM size is 1/20 hp |  |  | Algorithm |  |  | 269 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | Key Assumptions: 1. ECM savings are based on an average of typical sizes of ECM’s over PSC motors, as well as ECM’s over shaded-pole motors for all types, 2. User surveys from retailers were conducted to determine the single weighted-average of savings values among types of refrigeration cases. | per measure | 0.1883 | 1365 | Early Replacement
817 | Motors | Refrigeration Motors | ECM Motor | ECM Display Case Motors: Biz Prescriptive | ECM replacing all types | 1 | InActive | 2015-01-01 | 2015-12-31 | Shaded Pole or PSC on existing case | [5 empty] | per measure | Algorithm |  |  |  | ECM installed; Minimum qualifying ECM size is 1/20 hp |  |  | Algorithm |  |  | 140 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | Key Assumptions: 1. ECM savings are based on an average of typical sizes of ECM’s over PSC motors, as well as ECM’s over shaded-pole motors for all types of refrigeration cases, 2. User surveys from retailers were conducted to determine the single weighted-average of savings values among types of refrigeration cases. | per measure | 0.1137 | 824.0 | Early Replacement
825 | Refrigeration | Condenser | Efficient Condenser | Efficient Refrigeration Condenser : Biz Prescriptive | Efficient Refrigeration Condenser | 1 | InActive | 2013-01-02 | 2015-12-31 | Medium Temperature System = 15F design approach; Low Temperature System = 10F design approach | [5 empty] | per ton | Algorithm | Efficient Refrigeration Condenser |  |  | Condenser design temperature approach must be at or below the following parameters: Air-cooled condensers (exiting refrigerant vs. ambient dry bulb temperature): low temperature systems (8°F) and medium temperature systems (13°F). Evaporative-cooled condensers (exiting refrigerant vs. ambient wet bulb temperature): 18°F. |  |  | Algorithm |  |  | 35 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: System Capacity = Full Load = 2.3 kW/ton at 105°F saturated condensing temp. | per ton | 0.0163 | 119.8 | Early Replacement
3065 | Office Equipment | Desktop PC | Energy Star PC | Electronics - Monitor Power Management: Biz Prescriptive | Electronics - Monitor Power Management | 1 | Active | 2016-01-01 | [7 empty] | per building | [10 empty] | 6 |  | 5 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per building | 0.2438 | 1,767.47
826 | Refrigeration | Freezers | Glass Door Freezer, Commercial | ENERGY STAR Commercial Glass Door Freezers less than 15ft3: Biz Prescriptive | ENERGY STAR Commercial Glass Door Freezers less than 15ft3: Biz Standard | 1 | Active | 2013-01-02 |  | Standard Glass Door Freezers less than 15ft3 |  | Base kWh consumption |  |  |  | per measure | Algorithm | Energy Star Rated Glass Door |  |  | <= 0.607V + 0.893 |  |  | Algorithm |  |  | 220 |  | 12 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | Key Assumptions: 8760 operating hours per year; CF (coincident peak factor) | per measure | 0.2298 | 1693 | Early Replacement
827 | Refrigeration | Freezers | Glass Door Freezer, Commercial | ENERGY STAR Commercial Glass Door Freezers 15 to 30 ft3: Biz Prescriptive | ENERGY STAR Commercial Glass Door Freezers 15 to 30 ft3: Biz Standard | 1 | Active | 2013-01-02 |  | Standard Glass Door Freezers 15 to 30ft3 |  | Base kWh consumption |  |  |  | per measure | Algorithm | Energy Star Rated Glass Door |  |  | <= 0.733V – 1.000 |  |  | Algorithm |  |  | 950 |  | 12 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | Key Assumptions: 8760 operating hours per year; CF (coincident peak factor) | per measure | 0.272 | 2004.0 | Early Replacement
828 | Refrigeration | Freezers | Glass Door Freezer, Commercial | ENERGY STAR Commercial Glass Door Freezers 30 to 50ft3: Biz Prescriptive | ENERGY STAR Commercial Glass Door Freezers 30 to 50ft3: Biz Standard | 1 | Active | 2013-01-02 |  | Standard Glass Door Freezers 30 to 50ft3 |  | Base kWh consumption |  |  |  | per measure | Algorithm | Energy Star Rated Glass Door |  |  | <= 0.250V + 13.500 |  |  | Algorithm |  |  | 1307 |  | 12 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | Key Assumptions: 8760 operating hours per year; CF (coincident peak factor) | per measure | 0.5252 | 3869.0 | Early Replacement
829 | Refrigeration | Freezers | Glass Door Freezer, Commercial | ENERGY STAR Commercial Glass Door Freezers more than 50ft3: Biz Prescriptive | ENERGY STAR Commercial Glass Door Freezers more than 50ft3: Biz Standard | 1 | Active | 2013-01-02 |  | Standard Glass Door Freezers more than 50ft3 |  | Base kWh consumption |  |  |  | per measure | Algorithm | Energy Star Rated Glass Door |  |  | <= 0.450V + 3.500 |  |  | Algorithm |  |  | 2300 |  | 12 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | Key Assumptions: 8760 operating hours per year; CF (coincident peak factor) | per measure | 0.9662 | 7118.0 | Early Replacement
842 | Refrigeration | Refrigerators | Glass Door Refrig, Commercial | ENERGY STAR Commercial Glass Door Refrigerators less than 15ft3: Biz Prescriptive | ENERGY STAR Commercial Glass Door Refrigerators less than 15ft3: Biz Standard | 1 | InActive | 2013-01-02 | 2015-12-31 | Glass Door Refrigerators less than 15ft3 | 0.12*Volume+3.34 | Base kWh consumption |  |  |  | per measure | Algorithm | Energy Star Rated |  |  | <= 0.118V + 1.382 |  |  | Algorithm |  |  | 250 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | Key Assumptions: 8760 operating hours per year; CF (coincident peak factor) | per measure | 0.082 | 722.0 | Early Replacement
842 | Refrigeration | Refrigerators | Glass Door Refrig, Commercial | ENERGY STAR Commercial Glass Door Refrigerators less than 15ft3: Biz Prescriptive | ENERGY STAR Commercial Glass Door Refrigerators less than 15ft3: Biz Standard | 2 | Active | 2016-01-01 |  | Glass Door Refrigerators less than 15ft3 |  | Base kWh consumption |  |  |  | per measure | Algorithm | Energy Star Rated |  |  | <= 0.118V + 1.382 |  |  | Algorithm |  |  | 250 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | Key Assumptions: 8760 operating hours per year; CF (coincident peak factor) | per measure | 0.098 | 722 | Early Replacement
843 | Refrigeration | Refrigerators | Glass Door Refrig, Commercial | ENERGY STAR Commercial Glass Door Refrigerators 15 to 30 ft3: Biz Prescriptive | ENERGY STAR Commercial Glass Door Refrigerators 15 to 30 ft3: Biz Standard | 1 | InActive | 2013-01-02 | 2015-12-31 | Glass Door Refrigerators 15 to 30ft3 | 0.12*Volume+3.34 | Base kWh consumption |  |  |  | per measure | Algorithm | Energy Star Rated |  |  | <= 0.140V + 1.050 |  |  | Algorithm |  |  | 500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | Key Assumptions: 8760 operating hours per year; CF (coincident peak factor) | per measure | 0.164 | 1434.0 | Early Replacement
843 | Refrigeration | Refrigerators | Glass Door Refrig, Commercial | ENERGY STAR Commercial Glass Door Refrigerators 15 to 30 ft3: Biz Prescriptive | ENERGY STAR Commercial Glass Door Refrigerators 15 to 30 ft3: Biz Standard | 2 | Active | 2016-01-01 |  | Glass Door Refrigerators 15 to 30ft3 |  | Base kWh consumption |  |  |  | per measure | Algorithm | Energy Star Rated |  |  | <= 0.140V + 1.050 |  |  | Algorithm |  |  | 500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | Key Assumptions: 8760 operating hours per year; CF (coincident peak factor) | per measure | 0.0907 | 668 | Early Replacement
3028 | Refrigeration | Refrigerators | Glass Door Refrig, Commercial | ENERGY STAR Commercial Glass Door Refrigerators 30 to 50ft3: Biz Prescriptive | ENERGY STAR Commercial Glass Door Refrigerators 30 to 50ft3 | 1 | InActive | [19 empty] | 750 |  | 12 |  |  |  |  | Biz Prescriptive |  | MEMD | per measure | 0.0988 | 728
3029 | Refrigeration | Refrigerators | Glass Door Refrig, Commercial | ENERGY STAR Commercial Glass Door Refrigerators more than 50ft3: Biz Prescriptive | ENERGY STAR Commercial Glass Door Refrigerators more than 50ft3 | 1 | InActive | [19 empty] | 900 |  | 12 |  |  |  |  | Biz Prescriptive |  | MEMD | per measure | 0.1219 | 898
830 | Refrigeration | Freezers | Solid Door Freezer, Commercial | ENERGY STAR Commercial Solid Door Freezers less than 15ft3: Biz Prescriptive | ENERGY STAR Commercial Solid Door Freezers less than 15ft3: Biz Standard | 1 | Active | 2013-01-02 |  | Solid Door Freezers less than 15ft3 |  | Base kWh consumption |  |  |  | per measure | Algorithm | Energy Star Rated |  |  | <= 0.250V + 1.250 |  |  | Algorithm |  |  | 150 |  | 12 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | Key Assumptions: 8760 operating hours per year; CF (coincident peak factor) | per measure | 0.0808 | 595.0 | Early Replacement
831 | Refrigeration | Freezers | Solid Door Freezer, Commercial | ENERGY STAR Commercial Solid Door Freezers 15 to 30 ft3: Biz Prescriptive | ENERGY STAR Commercial Solid Door Freezers 15 to 30 ft3: Biz Standard | 1 | Active | 2013-01-02 |  | Solid Door Freezers 15 to 30ft3 |  | Base kWh consumption |  |  |  | per measure | Algorithm | Energy Star Rated |  |  | <= 0.400V – 1.000 |  |  | Algorithm |  |  | 400 |  | 12 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | Key Assumptions: 8760 operating hours per year; CF (coincident peak factor) | per measure | 0.118 | 869.0 | Early Replacement
832 | Refrigeration | Freezers | Solid Door Freezer, Commercial | ENERGY STAR Commercial Solid Door Freezers 30 to 50ft3: Biz Prescriptive | ENERGY STAR Commercial Solid Door Freezers 30 to 50ft3: Biz Standard | 1 | Active | 2013-01-02 |  | Solid Door Freezers 30 to 50ft3 |  | Base kWh consumption |  |  |  | per measure | Algorithm | Energy Star Rated |  |  | <= 0.163V + 6.125 |  |  | Algorithm |  |  | 550 |  | 12 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | Key Assumptions: 8760 operating hours per year; CF (coincident peak factor) | per measure | 0.2346 | 1728.0 | Early Replacement
833 | Refrigeration | Freezers | Solid Door Freezer, Commercial | ENERGY STAR Commercial Solid Door Freezers more than 50ft3: Biz Prescriptive | ENERGY STAR Commercial Solid Door Freezers more than 50ft3: Biz Standard | 1 | Active | 2013-01-02 |  | Solid Door Freezers more than 50ft3 |  | Base kWh consumption |  |  |  | per measure | Algorithm | Energy Star Rated |  |  | <= 0.158V + 6.333 |  |  | Algorithm |  |  | 700 |  | 12 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | Key Assumptions: 8760 operating hours per year; CF (coincident peak factor) | per measure | 0.51 | 3757.0 | Early Replacement
3030 | Refrigeration | Refrigerators | Glass Door Refrig, Commercial | ENERGY STAR Commercial Solid Door Refrigerators 15 to 30 ft3: Biz Prescriptive | ENERGY STAR Commercial Solid Door Refrigerators 15 to 30 ft3 | 1 | InActive | [19 empty] | 500 |  | 12 |  |  |  |  | Biz Prescriptive |  | MEMD | per measure | 0.0638 | 470
3031 | Refrigeration | Refrigerators | Glass Door Refrig, Commercial | ENERGY STAR Commercial Solid Door Refrigerators 30 to 50 ft3: Biz Prescriptive | ENERGY STAR Commercial Solid Door Refrigerators 15 to 30 ft3 | 1 | InActive | [19 empty] | 750 |  | 12 |  |  |  |  | Biz Prescriptive |  | MEMD | per measure | 0.1072 | 790
3032 | Refrigeration | Refrigerators | Glass Door Refrig, Commercial | ENERGY STAR Commercial Solid Door Refrigerators less than 15ft3: Biz Prescriptive | ENERGY STAR Commercial Solid Door Refrigerators 15 to 30 ft3 | 1 | InActive | [19 empty] | 250 |  | 12 |  |  |  |  | Biz Prescriptive |  | MEMD | per measure | 0.0366 | 270
3033 | Refrigeration | Refrigerators | Glass Door Refrig, Commercial | ENERGY STAR Commercial Solid Door Refrigerators more than 50 ft3: Biz Prescriptive | ENERGY STAR Commercial Solid Door Refrigerators 15 to 30 ft3 | 1 | Proposed | 2016-01-01 | [18 empty] | 900 |  | 12 |  |  |  |  | Biz Prescriptive |  | MEMD | per measure | 0.1538 | 1133
834 | Refrigeration | Ice Machines | Ice Machine | ENERGY STAR Ice Machines less than 500 lbs: Biz Prescriptive | Energy Star Ice Machines less than 500 lbs | 1 | InActive | 2013-01-02 | 2015-12-31 | N/A | [5 empty] | per measure | Algorithm | Energy Star Rated Ice Machine |  |  | Energy Star Certified Ice Machines |  |  | Algorithm |  |  | 600 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. 8760 operating hours per year. Coincidence Factor (CF) = 1.0 | per measure | 0.189 | 1652.0 | Early Replacement
834 | Refrigeration | Ice Machines | Ice Machine | ENERGY STAR Ice Machines less than 500 lbs: Biz Prescriptive | Energy Star Ice Machines less than 500 lbs | 2 | Active | 2016-01-01 |  | N/A | [5 empty] | per measure | Algorithm | Energy Star Rated Ice Machine |  |  | Energy Star Certified Ice Machines |  |  | Algorithm |  |  | 600 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. 8760 operating hours per year. Coincidence Factor (CF) = 1.0 | per measure | 0.0813 | 599 | Early Replacement
835 | Refrigeration | Ice Machines | Ice Machine | ENERGY STAR Ice Machines 500 to 1000 lbs: Biz Prescriptive | Energy Star Ice Machines 500 to 1000 lbs | 1 | InActive | 2013-01-02 | 2015-12-31 | N/A | [5 empty] | per measure | Algorithm | Energy Star Rated Ice Machine |  |  | Energy Star Certified Ice Machines |  |  | Algorithm |  |  | 1500 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. 8760 operating hours per year. Coincidence Factor (CF) = 1.0 | per measure | 0.308 | 2695.0 | Early Replacement
835 | Refrigeration | Ice Machines | Ice Machine | ENERGY STAR Ice Machines 500 to 1000 lbs: Biz Prescriptive | Energy Star Ice Machines 500 to 1000 lbs | 2 | Active | 2016-01-01 |  | N/A | [5 empty] | per measure | Algorithm | Energy Star Rated Ice Machine |  |  | Energy Star Certified Ice Machines |  |  | Algorithm |  |  | 1500 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. 8760 operating hours per year. Coincidence Factor (CF) = 1.0 | per measure | 0.1211 | 892 | Early Replacement
836 | Refrigeration | Ice Machines | Ice Machine | ENERGY STAR Ice Machines more than 1000 lbs: Biz Prescriptive | Energy Star Ice Machines more than 100 lbs | 1 | InActive | 2013-01-02 | 2015-12-31 | N/A | [5 empty] | per measure | Algorithm | Energy Star Rated Ice Machine |  |  | Energy Star Certified Ice Machines |  |  | Algorithm |  |  | 2000 |  | 12 | 2013-15 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. 8760 operating hours per year. Coincidence Factor (CF) = 1.0 | per measure | 0.690 | 6048.0 | Early Replacement
836 | Refrigeration | Ice Machines | Ice Machine | ENERGY STAR Ice Machines more than 1000 lbs: Biz Prescriptive | Energy Star Ice Machines more than 100 lbs | 2 | Active | 2016-01-01 |  | N/A | [5 empty] | per measure | Algorithm | Energy Star Rated Ice Machine |  |  | Energy Star Certified Ice Machines |  |  | Algorithm |  |  | 2000 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. 8760 operating hours per year. Coincidence Factor (CF) = 1.0 | per measure | 0.1746 | 1286 | Early Replacement
3066 | Office Equipment | Desktop PC | Energy Star PC | Energy Star Laptop: Biz Prescriptive | Energy Star Laptop | 1 | Active | 2016-01-01 | [7 empty] | per building | [10 empty] | .51 |  | 4 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per building | 0.1035 | 750.40
3067 | Office Equipment | Desktop PC | Energy Star PC | Energy Star POS Terminal: Biz Prescriptive | Energy Star POS Terminal | 1 | Active | 2016-01-01 | [7 empty] | per building | [10 empty] | 292.72 |  | 4 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per building | 0.3046 | 2,208.48
3068 | Office Equipment | Desktop PC | Energy Star PC | Energy Star Server: Biz Prescriptive | Energy Star Server | 1 | Active | 2016-01-01 | [7 empty] | per building | [10 empty] | .04 |  | 3 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per building | 0.3472 | 2,516.82
846 | Refrigeration | Vending Machines | Efficient Vending Machine | ENERGY STAR Vending Machine: Biz Prescriptive | Energy Star Vending Machine | 1 | InActive | 2013-01-02 | 2015-12-31 | Standard Vending Machine (non-Energy Star) | [5 empty] | per measure | Algorithm | Energy Star Rated |  |  | Energy Star Certified Vending Machines |  |  | Algorithm |  |  | 140 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  |  | per measure | 0.102 | 1000.0 | Early Replacement
846 | Refrigeration | Vending Machines | Efficient Vending Machine | ENERGY STAR Vending Machine: Biz Prescriptive | Energy Star Vending Machine | 2 | Active | 2016-01-01 |  | Standard Vending Machine (non-Energy Star) | [5 empty] | per measure | Algorithm | Energy Star Rated |  |  | Energy Star Certified Vending Machines |  |  | Algorithm |  |  | 140 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.1362 | 1003.35 | Early Replacement
3054 | Motors | Motors | AC Motor/Drive | Evaporator Fan Motor Controls on ECM Motors: Biz Prescriptive | Evaporator Fan Motor Controls on ECM Motors | 1 | InActive | [19 empty] | 621 |  | 5 |  |  |  |  | Biz Prescriptive |  |  | per measure | 0.0455 | 330
3055 | Motors | Motors | AC Motor/Drive | Evaporator Fan Motor Controls on PSC Motors: Biz Prescriptive | Evaporator Fan Motor Controls on PSC Motors | 1 | InActive | [19 empty] | 421 |  | 5 |  |  |  |  | Biz Prescriptive |  |  | per measure | 0.1098 | 796
3056 | Motors | Motors | AC Motor/Drive | Evaporator Fan Motor Controls on S-P Motors: Biz Prescriptive | Evaporator Fan Motor Controls on S-P Motors | 1 | InActive | [19 empty] | 421 |  | 5 |  |  |  |  | Biz Prescriptive |  |  | per measure | 0.1593 | 1155
850 | Water Heating | Water Heaters | Heat Pump Water Heater | HP Water Heater 10 to 50 MBH: Biz Prescriptive | Commercial Heat Pump Hot Water Heater with minimum COP of 3.0 | 1 | Active | 2013-01-02 |  | Electric commercial water heater with a efficiency value of 98% | 0.98 | Efficiency Factor |  |  | Cost estimates include installation | per measure | Algorithm | >= 3.0 Coefficient of Performance (COP) | COP | 3 | Heat Pump Water heater must have at least a 3.0 COP |  |  | Algorithm |  |  | 6000 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. / Heaters are generally located in unconditioned spaces | per measure | 3.8325 | 21156.0 | Early Replacement
851 | Water Heating | Water Heaters | Heat Pump Water Heater | HP Water Heater 100 to 300 MBH: Biz Prescriptive | Commercial Heat Pump Hot Water Heater with minimum COP of 3.0 | 1 | Active | 2013-01-02 |  | Electric commercial water heater with a efficiency value of 98% | 0.98 | Efficiency Factor |  |  | Cost estimates include installation | per measure | Algorithm | >= 3.0 Coefficient of Performance (COP) | COP | 3 | Heat Pump Water heater must have at least a 3.0 COP |  |  | Algorithm |  |  | 25000 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. / Heaters are generally located in unconditioned spaces | per measure | 25.5502 | 141041.0 | Early Replacement
852 | Water Heating | Water Heaters | Heat Pump Water Heater | HP Water Heater 300 to 500 MBH: Biz Prescriptive | Commercial Heat Pump Hot Water Heater with minimum COP of 3.0 | 1 | Active | 2013-01-02 |  | Electric commercial water heater with a efficiency value of 98% | 0.98 | Efficiency Factor |  |  | Cost estimates include installation | per measure | Algorithm | >= 3.0 Coefficient of Performance (COP) | COP | 3 | Heat Pump Water heater must have at least a 3.0 COP |  |  | Algorithm |  |  | 42000 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. / Heaters are generally located in unconditioned spaces | per measure | 51.1002 | 282081.0 | Early Replacement
853 | Water Heating | Water Heaters | Heat Pump Water Heater | HP Water Heater 50 to 100 MBH: Biz Prescriptive | Commercial Heat Pump Hot Water Heater with minimum COP of 3.0 | 1 | Active | 2013-01-02 |  | Electric commercial water heater with a efficiency value of 98% | 0.98 | Efficiency Factor |  |  | Cost estimates include installation | per measure | Algorithm | >= 3.0 Coefficient of Performance (COP) | COP | 3 | Heat Pump Water heater must have at least a 3.0 COP |  |  | Algorithm |  |  | 14000 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. / Heaters are generally located in unconditioned spaces | per measure | 9.5813 | 52890.0 | Early Replacement
854 | Water Heating | Water Heaters | Heat Pump Water Heater | HP Water Heater above 500 MBH: Biz Prescriptive | Commercial Heat Pump Hot Water Heater with minimum COP of 3.0 | 1 | Active | 2013-01-02 |  | Electric commercial water heater with a efficiency value of 98% | 0.98 | Efficiency Factor |  |  | Cost estimates include installation | per measure | Algorithm | >= 3.0 Coefficient of Performance (COP) | COP | 3 | Heat Pump Water heater must have at least a 3.0 COP |  |  | Algorithm |  |  | 63000 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. / Heaters are generally located in unconditioned spaces | per measure | 76.6505 | 423122.0 | Early Replacement
847 | Refrigeration | Vending Machines | Efficient Vending Machine | Lighted Snack Dispensing Machine: Biz Prescriptive | Lighted Snack Dispensing Machine | 1 | InActive | 2013-01-02 | 2015-12-31 | N/A | [5 empty] | per measure | Algorithm | N/A |  |  | N/A |  |  | Algorithm |  |  | 132 |  | 4 | 2013-15 |  |  |  | Biz Prescriptive |  |  | per measure | 0.000 | 368.0 | Early Replacement
847 | Refrigeration | Vending Machines | Efficient Vending Machine | Lighted Snack Dispensing Machine: Biz Prescriptive | Lighted Snack Dispensing Machine | 2 | Active | 2016-01-01 |  | N/A | [5 empty] | per measure | Algorithm | N/A |  |  | N/A |  |  | Algorithm |  |  | 47 |  | 4 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.0445 | 328 | Early Replacement
848 | Water Heating | Flow Control | Faucet Aerator | Low Flow Faucet Aerator - Electric water heater: Biz Prescriptive | Low Flow faucet aerator, Commercial Hot Water Measures | 1 | Active | 2013-01-02 |  | Standard faucet with a flow rate of at least 2.5 GPM | 2.5 | GPM |  |  |  | per building | Algorithm | Low Flow Faucet Aerator (1.5 GPM) | GPM | 1.5 | Minimum flow rate of 1.5 GPM |  |  | Algorithm |  |  | 31.10 |  | 9 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per building | 0.0315 | 173.9 | Early Replacement
3074 | Water Heating | Flow Control | Low Flow Showerhead | Low Flow Showerhead_MF: Biz Prescriptive | Low Flow Showerhead_MF | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 42.00 |  | 12 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.0380 | 210.00
3064 | Office Equipment | Desktop PC | Energy Star PC | Office Electronics - Monitor, Max Efficiency: Biz Prescriptive | Office Electronics - Monitor, Max Efficiency | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 137 |  | 4 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.1894 | 1,372.98
3069 | Office Equipment | Smart Strips | Smart Strip | Office Equipment - Plug Load Occupancy Sensors: Biz Presriptive | Office Equipment - Plug Load Occupancy Sensors | 1 | Active | 2016-01-01 | [7 empty] | per building | [10 empty] | 256.82 |  | 5 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per building | 0.9260 | 6,712.97
821 | Process | Process Cooling | System Optimization | Optimizing Process Cooling: Biz Prescriptive | Optimizing Process Cooling | 1 | InActive | 2013-01-02 | 2015-12-31 | Digital Control of Cooling Systems (Basic) |  |  |  |  | Cost values taken from Cadmus Potential Study Measure list | per project | Algorithm | Optimize to achieve 10% Improvement in building’s cooling load | [5 empty] | Algorithm |  |  | 1568 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Savings values taken from Cadmus Potential Study Measure List; Assumes 10% savings of building’s cooling energy consumption by optimizing the building’s existing Digital Control System | per project | 2.2519 | 16325.0 | Early Replacement
823 | Process | Process Heating | System Optimization | Optimizing Process Heating: Biz Prescriptive | Optimizing Process Heating | 1 | InActive | 2013-01-02 | 2015-12-31 | Digital Control of Heating Systems (Basic) |  |  |  |  | Cost values derived from Cadmus Potential Study Measure List | per project | Algorithm | Optimize to achieve 10% Improvement in building’s heating load | [5 empty] | Algorithm |  |  | 760 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Savings values based on Cadmus Potential Study Measure List; Assumes 10% savings of building’s heating energy consumption by optimizing the building’s existing Digital Control System | per project | 0.967 | 7053.0 | Early Replacement
1178 | Office Equipment | Desktop PC | Energy Star PC | PC Power Management Software: Biz Prescriptive | Centrally power managed desktop PC | 1 | Active | 2013-01-02 |  | Desktop PC, not centrally power managed | [5 empty] | per unit | Algorithm | Centrally power managed |  |  | Centrally power managed |  |  | Algorithm |  |  | 20 |  | 4 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | Key Assumptions: • Energy savings of typical PC usage in hospital, small office, large office and school setting was analyzed. • The term “PC”, “Computer”, or “end point” refers to a single-user computer as it is defined by EPA’s Program Requirements for Computers, Version 5.0 | per unit | 0.0276 | 200.0 | Early Replacement
3071 | Motors | Pumps | High Efficiency Pump | Pool Heater Heat Pump: Biz Prescriptive | Pool Heater Heat Pump | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 199.14 |  | 15 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.2497 | 1,810.39
3072 | Motors | Pumps | VFD Pool Pump | Pool Pump - Timer: Biz Prescriptive | Pool Pump - Timer | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 100 |  | 10 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.0830 | 601.89
849 | Water Heating | Flow Control | Pre-rinse sprayer | Pre Rinse Sprayers - Electric water heater: Biz Prescriptive | Commercial Pre-rinse Spray Valves with less than 0.64 gpm flow rate | 1 | Active | 2013-01-02 |  | Pre-rinse spray valve, greater then or equal to 1.6 GPM | 2.78 | GPM |  |  |  | per measure | Algorithm | Pre rinse spray valves, less than or equal to 0.64 GPM | GPM | 0.64 | Less than or equal to 0.64 GPM flow rate |  |  | Algorithm |  |  | 85.8 |  | 5 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per measure | 1.0201 | 5631.1 | Early Replacement
1114 | Motors | Pumps | High Efficiency Pump | Pumps HP 1.5 (Eff Increase: 5.66): Biz Prescriptive | Commercial Pumps for Process HP 1.5 (Eff Increase: 5.66) | 1 | InActive | 2013-01-02 | 2015-12-31 |  | See source document |  |  |  |  | per measure | Algorithm |  |  | See source document |  |  |  | Algorithm |  |  | 350 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.547 | 1991.0 | Early Replacement
795 | Motors | Pumps | High Efficiency Pump | Pumps HP 10 (Eff increase 2.96): Biz Prescriptive | Commercial Pumps for Process HP 10 (Eff Increase: 2.96) | 1 | InActive | 2013-01-02 | 2015-12-31 | [6 empty] | per measure | Algorithm | >= 75% Pump Efficiency Improvement (> 5 HP) | [5 empty] | Algorithm |  |  | 332 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.282 | 1026.0 | Early Replacement
1145 | Motors | Pumps | High Efficiency Pump | Pumps HP 10 (Eff Increase: 12.25): Biz Prescriptive | Commercial Pumps for Process HP 10 (Eff Increase: 12.25) | 1 | InActive | 2013-01-02 | 2015-12-31 | [6 empty] | per measure | Algorithm | >= 75% Pump Efficiency Improvement (> 5 HP) | [5 empty] | Algorithm |  |  | 332 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 1.111 | 4043.0 | Early Replacement
1141 | Motors | Pumps | High Efficiency Pump | Pumps HP 10 (Eff Increase: 4.6): Biz Prescriptive | Commercial Pumps for Process HP 10 (Eff Increase: 4.6) | 1 | InActive | 2013-01-02 | 2015-12-31 | [6 empty] | per measure | Algorithm | >= 75% Pump Efficiency Improvement (> 5 HP) | [5 empty] | Algorithm |  |  | 332 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.448 | 1629.0 | Early Replacement
2795 | Motors | Pumps | High Efficiency Pump | Pumps HP 10: Biz Prescriptive | Commercial Pumps for Process HP 10 | 1 | Active | 2016-01-01 | [7 empty] | per measure | Algorithm | [6 empty] | Algorithm |  |  | 332 |  | 15 | 2016-18 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.2778 | 2014 | Early Replacement
796 | Motors | Pumps | High Efficiency Pump | Pumps HP 15 (Eff increase 16.09): Biz Prescriptive | Commercial Pumps for Process HP 15 (Eff increase 16.09) | 1 | InActive | 2013-01-02 | 2015-12-31 | [6 empty] | per measure | Algorithm | >= 75% Pump Efficiency Improvement (> 5 HP) | [5 empty] | Algorithm |  |  | 585 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 2.014 | 7332.0 | Early Replacement
796 | Motors | Pumps | High Efficiency Pump | Pumps HP 15 (Eff increase 16.09): Biz Prescriptive | Commercial Pumps for Process HP 15 (Eff increase 16.09) | 2 | Active | 2016-01-01 | [7 empty] | per measure | Algorithm | [6 empty] | Algorithm |  |  | 585 |  | 15 | 2016-18 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.4167 | 3021 | Early Replacement
1118 | Motors | Pumps | High Efficiency Pump | Pumps HP 2 (Eff Increase: 7.48): Biz Prescriptive | Commercial Pumps for Process HP 2 (Eff Increase: 7.48) | 1 | InActive | 2013-01-02 | 2015-12-31 |  | See source document |  |  |  |  | per measure | Algorithm |  |  | See source document |  |  |  | Algorithm |  |  | 350 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.141 | 513.0 | Early Replacement
797 | Motors | Pumps | High Efficiency Pump | Pumps HP 20 (Eff Increase: 2.45): Biz Prescriptive | Commercial Pumps for Process HP 20 (Eff Increase: 2.45) | 1 | InActive | 2013-01-02 | 2015-12-31 | [6 empty] | per measure | Algorithm | >= 75% Pump Efficiency Improvement (> 5 HP) | [5 empty] | Algorithm |  |  | 850 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.348 | 1267.0 | Early Replacement
1153 | Motors | Pumps | High Efficiency Pump | Pumps HP 20 (Eff Increase: 4.0): Biz Prescriptive | Commercial Pumps for Process HP 20 (Eff Increase: 4) | 1 | InActive | 2013-01-02 | 2015-12-31 | [6 empty] | per measure | Algorithm | >= 75% Pump Efficiency Improvement (> 5 HP) | [5 empty] | Algorithm |  |  | 850 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.937 | 3409.0 | Early Replacement
1149 | Motors | Pumps | High Efficiency Pump | Pumps HP 20 (Eff Increase: 9.24): Biz Prescriptive | Commercial Pumps for Process HP 20 (Eff Increase: 9.24) | 1 | InActive | 2013-01-02 | 2015-12-31 | [6 empty] | per measure | Algorithm | >= 75% Pump Efficiency Improvement (> 5 HP) | [5 empty] | Algorithm |  |  | 850 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 1.467 | 5340.0 | Early Replacement
2797 | Motors | Pumps | High Efficiency Pump | Pumps HP 20: Biz Prescriptive | Commercial Pumps for Process HP 20 | 1 | Active | 2016-01-01 | [7 empty] | per measure | Algorithm | [6 empty] | Algorithm |  |  | 850 |  | 15 | 2016-18 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.5556 | 4028 | Early Replacement
798 | Motors | Pumps | High Efficiency Pump | Pumps HP 3 (Eff increase 7.19): Biz Prescriptive | Commercial Pumps for Process HP 3 (Eff increase 7.19) | 1 | InActive | 2013-01-01 | 2015-12-30 |  | See source document |  |  |  |  | per measure | Algorithm |  |  | See source document |  |  |  | Algorithm |  |  | 350 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.157 | 573 | Early Replacement
798 | Motors | Pumps | High Efficiency Pump | Pumps HP 3 (Eff increase 7.19): Biz Prescriptive | Commercial Pumps for Process HP 3 (Eff increase 7.19) | 2 | Active | 2016-01-01 | [7 empty] | per measure | Algorithm | [6 empty] | Algorithm |  |  | 350 |  | 15 | 2016-18 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.0833 | 604 | Early Replacement
1126 | Motors | Pumps | High Efficiency Pump | Pumps HP 5 (Eff Increase: 12.9): Biz Prescriptive | Commercial Pumps for Process HP 5 (Eff Increase: 12.9) | 1 | InActive | 2013-01-02 | 2015-12-31 |  | See source document |  |  |  |  | per measure | Algorithm |  |  | See source document |  |  |  | Algorithm |  |  | 341 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 1.210 | 4405.0 | Early Replacement
1130 | Motors | Pumps | High Efficiency Pump | Pumps HP 5 (Eff Increase: 13.75): Biz Prescriptive | Commercial Pumps for Process HP 5 (Eff Increase: 13.75) | 1 | InActive | 2013-01-02 | 2015-12-31 |  | See source document |  |  |  |  | per measure | Algorithm |  |  | See source document |  |  |  | Algorithm |  |  | 341 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.431 | 1569.0 | Early Replacement
799 | Motors | Pumps | High Efficiency Pump | Pumps HP 5 (Eff Increase: 2.86): Biz Prescriptive | Commercial Pumps for Process HP 5 (Eff Increase: 2.86) | 1 | InActive | 2013-01-02 | 2015-12-31 |  | See source document |  |  |  |  | per measure | Algorithm |  |  | See source document |  |  |  | Algorithm |  |  | 341 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.182 | 664.0 | Early Replacement
1122 | Motors | Pumps | High Efficiency Pump | Pumps HP 5 (Eff Increase: 21.3): Biz Prescriptive | Commercial Pumps for Process HP 5 (Eff Increase: 21.3) | 1 | InActive | 2013-01-02 | 2015-12-31 |  | See source document |  |  |  |  | per measure | Algorithm |  |  | See source document |  |  |  | Algorithm |  |  | 341 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 2.536 | 9232.0 | Early Replacement
1133 | Motors | Pumps | High Efficiency Pump | Pumps HP 5 (Eff Increase: 24.54): Biz Prescriptive | Commercial Pumps for Process HP 5 (Eff Increase: 24.54) | 1 | InActive | 2013-01-02 | 2015-12-31 |  | See source document |  |  |  |  | per measure | Algorithm |  |  | See source document |  |  |  | Algorithm |  |  | 341 |  | 15 | 2013-15 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 1.169 | 4254.0 | Early Replacement
2799 | Motors | Pumps | High Efficiency Pump | Pumps HP 5: Biz Prescriptive | Commercial Pumps for Process HP 5 | 1 | Active | 2016-01-01 | [7 empty] | per measure | Algorithm | [6 empty] | Algorithm |  |  | 341 |  | 15 | 2016-18 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.1389 | 1007 | Early Replacement
1137 | Motors | Pumps | High Efficiency Pump | Pumps HP 7.5 (Eff Increase: 6.05): Biz Prescriptive | Commercial Pumps for Process HP 7.5 (Eff Increase: 6.05) | 1 | Active | 2013-01-02 | [7 empty] | per measure | Algorithm | >= 75% Pump Efficiency Improvement (> 5 HP) | [5 empty] | Algorithm |  |  | 498 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.2372 | 1719.9 | Early Replacement
800 | Motors | Pumps | High Efficiency Pump | Pumps HP 7.5 (Eff Increase: 7.48): Biz Prescriptive | Commercial Pumps for Process HP 7.5 (Eff Increase: 7.48) | 1 | Active | 2013-01-02 | [7 empty] | per measure | Algorithm | >= 75% Pump Efficiency Improvement (> 5 HP) | [5 empty] | Algorithm |  |  | 498 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.2538 | 1840.2 | Early Replacement
2794 | Motors | Pumps | High Efficiency Pump | Pumps HP 7.5: Biz Prescriptive | Commercial Pumps for Process HP 7.5 | 1 | Active | 2016-01-01 | [7 empty] | per measure | Algorithm | [6 empty] | Algorithm |  |  | 498 |  | 15 | 2016-18 |  |  |  | Biz Prescriptive |  | Commercial pumps and drives can be deemed, but many of these measures will include sufficient variability in usage that the project would likely follow a custom analysis. It is important to identify the appropriate baseline efficiency when conducting pumps and drives savings calculations. *- If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: Load Factor (LF) = 76% | per measure | 0.2084 | 1511 | Early Replacement
837 | Refrigeration | Refrigerant Charging | Refrigerant Charging Improvement | Refrigerant charging correction: Biz Prescriptive | Refrigerant charging correction | 1 | InActive | 2013-01-02 | 2015-12-31 | Cooling capacity and EIR degraded by 10% to reflect “typical” refrigerant charge | [5 empty] | per square foot | Algorithm | 10% EER improvement |  |  | Standard cooling performance – proper refrigerant charge; 10% EER improvement |  |  | Algorithm |  |  | 38.35 |  | 10 | 2013-15 |  |  |  | Biz Prescriptive |  | Tons = 235.8; Total kWh savings for 10% EER improvement = 22,680.5kWh; Total kW savings for 10% EER improvement = 26.075 kW | per square foot | 0.0131 | 96.2 | Early Replacement
3039 | Refrigeration | Refrigerators | Display Case | Refrigeration Case Door Retrofits: Biz Prescriptive | Add Doors to Open Refrigeration Cases | 1 | InActive | [19 empty] | 686 |  | 12 |  |  |  |  | Biz Prescriptive |  | MEMD | per measure | 0.1974 | 1454
1110 | Refrigeration | Temp Maintain | Auto Door Closer | Refrigeration-Auto Door Closer: Biz Prescriptive | Auto Door Closer | 1 | InActive | 2013-01-02 | 2015-12-31 | Low or Medium Temperature walk in or reach in (-10 to 41F) | [5 empty] | per measure | algorithm | Auto Door closer installed |  |  | Auto Door closer installed |  |  | algorithm |  |  | 157 |  | 8 | 2013-15 |  |  |  | Biz Prescriptive |  | Key Assumptions: • Measures consist of installing an automatic door closer on an existing walk-in cooler or freezer door. • Using the door open time estimate, energy savings captured by the automatic door closer is calculated to be approximately 12% of cooling load for each case type. • Auto door closers should be applied to the main insulated door of a walk-in or reach-in cooler or freezer. • For both walk-in and reach-in cases, the minimum door perimeter is 16 feet. • One closer per case door. | per measure | 0.2206 | 1625 | Early Replacement
3073 | Refrigeration | Temp Maintain | Auto Door Closer | Refrigerator - Door Gasket Replacemen: Biz Prescriptivet | Refrigerator - Door Gasket Replacement | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 2,653.75 |  | 8 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 3.2747 | 24,124.99
3034 | Refrigeration | Temp Maintain | Strip Curtain | Strip Curtain - Walk In Freezer: Biz Prescriptive | Strip Curtain - Walk In Freezer | 1 | Active | 2016-01-01 | [18 empty] | 286.16 |  | 6 | 2016-18 |  |  |  | Biz Prescriptive |  | IL TRM | per measure | 4.0686 | 29974
845 | Refrigeration | Temp Maintain | Strip Curtain | Strip Curtain for Walk-in Cooler: Biz Prescriptive | Strip Curtain for Walk-in Cooler | 1 | InActive | 2013-01-02 | 2015-12-31 | No curtains | [5 empty] | per measure | Algorithm |  |  |  | Strip curtains installed |  |  | Algorithm |  |  | 132 |  | 4 | 2013-15 |  |  |  | Biz Prescriptive |  |  | per measure | 0.628 | 5058.0 | Early Replacement
845 | Refrigeration | Temp Maintain | Strip Curtain | Strip Curtain for Walk-in Cooler: Biz Prescriptive | Strip Curtain for Walk-in Cooler | 2 | Active | 2016-01-01 |  | No curtains | [5 empty] | per measure | Algorithm |  |  |  | Strip curtains installed |  |  | Algorithm |  |  | 286.16 |  | 4 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.0573 | 422 | Early Replacement
794 | Misc | Vending Controls | Vending Control | Vending Equipment Controller: Biz Prescriptive | Beverage Vending Machine automated/ motion Controls | 1 | Active | 2013-01-02 |  | Beverage Vending Machine with no controls | [5 empty] | per measure | Algorithm | Beverage vending machine automated/ motion control | [5 empty] | Algorithm |  |  | 141 |  | 5 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. | per measure | 0.2271 | 1646.0 | Early Replacement
801 | Motors | Pumps | VFD Control | VFD HP 10 Process Pumping: Biz Prescriptive | VFD HP 10 Process Pumping | 1 | Active | 2013-01-02 |  | N/A | [5 empty] | per measure | Algorithm | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | Algorithm |  |  | 2860 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: The average loading of the pumps analyzed was 86% pump capacity. Coincidence Factor (CF) = 0.78 | per measure | 1.4778 | 10713.4 | Early Replacement
802 | Motors | Pumps | VFD Control | VFD HP 15 Process Pumping: Biz Prescriptive | VFD HP 15 Process Pumping | 1 | Active | 2013-01-02 |  | N/A | [5 empty] | per measure | Algorithm | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | Algorithm |  |  | 3265 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: The average loading of the pumps analyzed was 86% pump capacity. Coincidence Factor (CF) = 0.78 | per measure | 2.2391 | 16232.3 | Early Replacement
803 | Motors | Pumps | VFD Control | VFD HP 20 Process Pumping: Biz Prescriptive | VFD HP 20 Process Pumping | 1 | Active | 2013-01-02 |  | N/A | [5 empty] | per measure | Algorithm | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | Algorithm |  |  | 4515 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: The average loading of the pumps analyzed was 86% pump capacity. Coincidence Factor (CF) = 0.78 | per measure | 2.9856 | 21643.7 | Early Replacement
804 | Motors | Pumps | VFD Control | VFD HP 25 Process Pumping: Biz Prescriptive | VFD HP 25 Process Pumping | 1 | Active | 2013-01-02 |  | N/A | [5 empty] | per measure | Algorithm | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | Algorithm |  |  | 5120 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: The average loading of the pumps analyzed was 86% pump capacity. Coincidence Factor (CF) = 0.78 | per measure | 3.7319 | 27054.1 | Early Replacement
805 | Motors | Pumps | VFD Control | VFD HP 3 Process Pumping: Biz Prescriptive | VFD HP 3 Process Pumping | 1 | Active | 2013-01-02 |  | N/A | [5 empty] | per measure | Algorithm | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | Algorithm |  |  | 1845 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: The average loading of the pumps analyzed was 86% pump capacity. Coincidence Factor (CF) = 0.78 | per measure | 0.4478 | 3246.3 | Early Replacement
806 | Motors | Pumps | VFD Control | VFD HP 30 Process Pumping: Biz Prescriptive | VFD HP 30 Process Pumping | 1 | Active | 2013-01-02 |  | N/A | [5 empty] | per measure | Algorithm | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | Algorithm |  |  | 5770 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: The average loading of the pumps analyzed was 86% pump capacity. Coincidence Factor (CF) = 0.78 | per measure | 4.4783 | 32464.6 | Early Replacement
807 | Motors | Pumps | VFD Control | VFD HP 40 Process Pumping: Biz Prescriptive | VFD HP 40 Process Pumping | 1 | Active | 2013-01-02 |  | N/A | [5 empty] | per measure | Algorithm | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | Algorithm |  |  | 8095 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: The average loading of the pumps analyzed was 86% pump capacity. Coincidence Factor (CF) = 0.78 | per measure | 5.971 | 43285.5 | Early Replacement
808 | Motors | Pumps | VFD Control | VFD HP 5 Process Pumping: Biz Prescriptive | VFD HP 5 Process Pumping | 1 | Active | 2013-01-02 |  | N/A | [5 empty] | per measure | Algorithm | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | Algorithm |  |  | 2070 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: The average loading of the pumps analyzed was 86% pump capacity. Coincidence Factor (CF) = 0.78 | per measure | 0.7389 | 5356.5 | Early Replacement
809 | Motors | Pumps | VFD Control | VFD HP 50 Process Pumping: Biz Prescriptive | VFD HP 50 Process Pumping | 1 | Active | 2013-01-02 |  | N/A | [5 empty] | per measure | Algorithm | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | Algorithm |  |  | 8950 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: The average loading of the pumps analyzed was 86% pump capacity. Coincidence Factor (CF) = 0.78 | per measure | 7.4639 | 54108.2 | Early Replacement
810 | Motors | Pumps | VFD Control | VFD HP 7.5 Process Pumping: Biz Prescriptive | VFD HP 7.5 Process Pumping | 1 | Active | 2013-01-02 |  | N/A | [5 empty] | per measure | Algorithm | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | VFD speed must be automatically controlled by differential pressure, flow, temperature, or other variable signal. |  |  | Algorithm |  |  | 2860 |  | 15 | 2013-15, 2016-18 |  |  |  | Biz Prescriptive |  | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure. Key Assumptions: The average loading of the pumps analyzed was 86% pump capacity. Coincidence Factor (CF) = 0.78 | per measure | 1.1196 | 8116.6 | Early Replacement
3070 | Motors | Pumps | VFD Control | VFDs on Commercial Swimming Pool Pumps: Biz Prescriptive | VFDs on Commercial Swimming Pool Pumps | 1 | Active | 2016-01-01 | [7 empty] | per measure | [10 empty] | 286 |  | 15 | 2016-18 |  |  |  | Biz Prescriptive |  |  | per measure | 0.3464 | 2,511.00
Note on I2: Please specify Date as value for this attribute.(In MM/DD/YYYY format )
Note on J2: Please specify Date as value for this attribute.(In MM/DD/YYYY format )
Note on AJ2: Please specify Date as value for this attribute.(In MM/DD/YYYY format )
Note on AM4: Formula Value.
Note on AM5: Formula Value.
Note on AM7: Formula Value.
Note on AM9: Formula Value.
Note on AM10: Formula Value.
Note on AM12: Formula Value.
Note on AM14: Formula Value.
Note on AM15: Formula Value.
Note on AM18: Formula Value.
Note on AM19: Formula Value.
Note on AM21: Formula Value.
Note on AM32: Formula Value.
Note on AM33: Formula Value.
Note on AM36: Formula Value.
Note on AM37: Formula Value.
Note on AM40: Formula Value.
Note on AM41: Formula Value.
Note on AM47: Formula Value.
Note on AM48: Formula Value.
Note on AM51: Formula Value.
Note on AM52: Formula Value.
Note on AM55: Formula Value.
Note on AM56: Formula Value.
Note on AM60: Formula Value.
Note on AM61: Formula Value.
Note on AM62: Formula Value.
Note on AM63: Formula Value.
Note on AM64: Formula Value.
Note on AM65: Formula Value.
Note on AM66: Formula Value.
Note on AM67: Formula Value.
Note on AM68: Formula Value.
Note on AM69: Formula Value.
Note on AM73: Formula Value.
Note on AM74: Formula Value.
Note on AM77: Formula Value.
Note on AM78: Formula Value.
Note on AM81: Formula Value.
Note on AM82: Formula Value.
Note on AM84: Formula Value.
Note on AM85: Formula Value.
Note on AM90: Formula Value.
Note on AM91: Formula Value.
Note on AM93: Formula Value.
Note on AM94: Formula Value.
Note on AM101: Formula Value.
Note on AM102: Formula Value.
Note on AM104: Formula Value.
Note on AM105: Formula Value.
Note on AM120: Formula Value.
Note on AM121: Formula Value.
Note on AM122: Formula Value.
Note on AM123: Formula Value.
Note on AM124: Formula Value.
Note on AM125: Formula Value.
Note on AM189: Formula Value.
Note on AM190: Formula Value.
Note on AM192: Formula Value.
Note on AM193: Formula Value.
Note on AM194: Formula Value.
Note on AM197: Formula Value.
Note on AM198: Formula Value.
Note on AM199: Formula Value.
Note on AM202: Formula Value.
Note on AM203: Formula Value.
Note on AM204: Formula Value.
Note on AM207: Formula Value.
Note on AM208: Formula Value.
Note on AM209: Formula Value.
Note on AM211: Formula Value.
Note on AM212: Formula Value.
Note on AM213: Formula Value.
Note on AM214: Formula Value.
Note on AM215: Formula Value.
Note on AM216: Formula Value.
Note on AM217: Formula Value.
Note on AM218: Formula Value.
Note on AM219: Formula Value.
Note on AM220: Formula Value.
Note on AM221: Formula Value.
Note on AM222: Formula Value.
Note on AM223: Formula Value.
Note on AM230: Formula Value.
Note on AM234: Formula Value.
Note on AM237: Formula Value.
Note on AM238: Formula Value.
Note on AM239: Formula Value.
Note on AM240: Formula Value.
Note on AM241: Formula Value.
Note on AM242: Formula Value.
Note on AM243: Formula Value.
Note on AM244: Formula Value.
Note on AM245: Formula Value.
Note on AM246: Formula Value.
Note on AM247: Formula Value.
Note on AM248: Formula Value.
Note on AM250: Formula Value.
Note on AM251: Formula Value.
Note on AM254: Formula Value.
Note on AM255: Formula Value.
Note on AM256: Formula Value.
Note on AM257: Formula Value.
Note on AM259: Formula Value.
Note on AM260: Formula Value.
Note on AM266: Formula Value.
Note on AM267: Formula Value.
Note on AM272: Formula Value.
Note on AM273: Formula Value.
Note on AM274: Formula Value.
Note on AM275: Formula Value.
Note on AM276: Formula Value.
Note on AM280: Formula Value.
Note on AM281: Formula Value.
Note on AM286: Formula Value.
Note on AM288: Formula Value.
Note on AM290: Formula Value.
Note on AM291: Formula Value.
Note on AM292: Formula Value.
Note on AM293: Formula Value.
Note on AM300: Formula Value.
Note on AM301: Formula Value.
Note on AM304: Formula Value.
Note on AM305: Formula Value.
Note on AM308: Formula Value.
Note on AM309: Formula Value.
Note on AM311: Formula Value.
Note on AM313: Formula Value.
Note on AM314: Formula Value.
Note on AM315: Formula Value.
Note on AM317: Formula Value.
Note on AM318: Formula Value.
Note on AM323: Formula Value.
Note on AM324: Formula Value.
Note on AM326: Formula Value.
Note on AM327: Formula Value.
Note on AM329: Formula Value.
Note on AM330: Formula Value.
Note on AM332: Formula Value.
Note on AM334: Formula Value.
Note on AM335: Formula Value.
Note on AM336: Formula Value.
Note on AM337: Formula Value.
Note on AM339: Formula Value.
Note on AM340: Formula Value.
Note on AM342: Formula Value.
Note on AM343: Formula Value.
Note on AM348: Formula Value.
Note on AM349: Formula Value.
Note on AM350: Formula Value.
Note on AM351: Formula Value.
Note on AM352: Formula Value.
Note on AM353: Formula Value.
Note on AM354: Formula Value.
Note on AM355: Formula Value.
Note on AM356: Formula Value.
Note on AM357: Formula Value.
Note on AM358: Formula Value.
Note on AM359: Formula Value.
Note on AM361: Formula Value.
Note on AM362: Formula Value.
Note on AM366: Formula Value.
Note on AM367: Formula Value.
Note on AM370: Formula Value.
Note on AM371: Formula Value.
Note on AM378: Formula Value.
Note on AM379: Formula Value.
Note on AM380: Formula Value.
Note on AM381: Formula Value.
Note on AM382: Formula Value.
Note on AM383: Formula Value.
Note on AM384: Formula Value.
Note on AM385: Formula Value.
Note on AM392: Formula Value.
Note on AM393: Formula Value.
Note on AM394: Formula Value.
Note on AM395: Formula Value.
Note on AM396: Formula Value.
Note on AM397: Formula Value.
Note on AM398: Formula Value.
Note on AM399: Formula Value.
Note on AM400: Formula Value.
Note on AM401: Formula Value.
Note on AM403: Formula Value.
Note on AM404: Formula Value.
Note on AM406: Formula Value.
Note on AM407: Formula Value.
Note on AM411: Formula Value.
Note on AM412: Formula Value.
Note on AM417: Formula Value.
Note on AM418: Formula Value.
Note on AM420: Formula Value.
Note on AM421: Formula Value.
Note on AM422: Formula Value.
Note on AM423: Formula Value.
Note on AM424: Formula Value.
Note on AM426: Formula Value.
Note on AM430: Formula Value.
Note on AM431: Formula Value.
Note on AM432: Formula Value.
Note on AM433: Formula Value.
Note on AM434: Formula Value.
Note on AM435: Formula Value.
Note on AM436: Formula Value.
Note on AM439: Formula Value.
Note on AM442: Formula Value.
Note on AM443: Formula Value.
Note on AM446: Formula Value.
Note on AM447: Formula Value.
Note on AM448: Formula Value.
Note on AM449: Formula Value.
Note on AM450: Formula Value.
Note on AM452: Formula Value.
Note on AM453: Formula Value.
Note on AM455: Formula Value.
Note on AM456: Formula Value.
Note on AM462: Formula Value.
Note on AM463: Formula Value.
Note on AM466: Formula Value.
Note on AM467: Formula Value.
Note on AM469: Formula Value.
Note on AM470: Formula Value.
Note on AM473: Formula Value.
Note on AM474: Formula Value.
Note on AM476: Formula Value.
Note on AM477: Formula Value.
Note on AM478: Formula Value.
Note on AM479: Formula Value.
Note on AM481: Formula Value.
Note on AM482: Formula Value.
Note on AM483: Formula Value.
Note on AM485: Formula Value.
Note on AM486: Formula Value.
Note on AM488: Formula Value.
Note on AM490: Formula Value.
Note on AM491: Formula Value.
Note on AM493: Formula Value.
Note on AM495: Formula Value.
Note on AM496: Formula Value.
Note on AM498: Formula Value.
Note on AM500: Formula Value.
Note on AM501: Formula Value.
Note on AM503: Formula Value.
Note on AM505: Formula Value.
Note on AM506: Formula Value.
Note on AM507: Formula Value.
Note on AM509: Formula Value.
Note on AM510: Formula Value.
Note on AM512: Formula Value.
Note on AM513: Formula Value.
Note on AM523: Formula Value.
Note on AM524: Formula Value.
Note on AM525: Formula Value.
Note on AM526: Formula Value.
Note on AM527: Formula Value.
Note on AM532: Formula Value.
Note on AM533: Formula Value.
Note on AM534: Formula Value.
Note on AM535: Formula Value.
Note on AM536: Formula Value.
Note on AM537: Formula Value.
Note on AM539: Formula Value.
Note on AM540: Formula Value.
Note on AM544: Formula Value.
Note on AM551: Formula Value.
Note on AM552: Formula Value.
Note on AM553: Formula Value.
Note on AM555: Formula Value.
Note on AM557: Formula Value.
Note on AM560: Formula Value.
Note on AM564: Formula Value.
Note on AM565: Formula Value.
Note on AM572: Formula Value.
Note on AM573: Formula Value.
Note on AM574: Formula Value.
Note on AM580: Formula Value.
Note on AM583: Formula Value.
Note on AM585: Formula Value.
Note on AM587: Formula Value.
Note on AM588: Formula Value.
Note on AM590: Formula Value.
Note on AM593: Formula Value.
Note on AM594: Formula Value.
Note on AM595: Formula Value.
Note on AM596: Formula Value.
Note on AM619: Formula Value.
Note on AM620: Formula Value.
Note on AM621: Formula Value.
Note on AM623: Formula Value.
Note on AM624: Formula Value.
Note on AM625: Formula Value.
Note on AM626: Formula Value.
Note on AM627: Formula Value.
Note on AM628: Formula Value.
Note on AM629: Formula Value.
Note on AM630: Formula Value.
Note on AM631: Formula Value.
Note on AM632: Formula Value.
Note on AM633: Formula Value.
Note on AM634: Formula Value.
Note on AM635: Formula Value.
Note on AM636: Formula Value.
Note on AM637: Formula Value.
Note on AM638: Formula Value.
Note on AM639: Formula Value.
Note on AM640: Formula Value.
Note on AM641: Formula Value.
Note on AM643: Formula Value.
Note on AM645: Formula Value.
Note on AM646: Formula Value.
Note on AM647: Formula Value.
Note on AM648: Formula Value.
Note on AM649: Formula Value.
Note on AM650: Formula Value.
Note on AM651: Formula Value.
Note on AM652: Formula Value.
Note on AM653: Formula Value.
Note on AM654: Formula Value.
Note on AM655: Formula Value.
Note on AM656: Formula Value.
Note on AM657: Formula Value.
Note on AM658: Formula Value.
Note on AM659: Formula Value.
Note on AM660: Formula Value.
Note on AM661: Formula Value.
Note on AM662: Formula Value.
Note on AM663: Formula Value.
Note on AM664: Formula Value.
Note on AM753: Formula Value.
Note on AM754: Formula Value.
Note on AM757: Formula Value.
Note on AM758: Formula Value.
Note on AM759: Formula Value.
Note on AM760: Formula Value.
Note on AM761: Formula Value.
Note on AM764: Formula Value.
Note on AM765: Formula Value.
Note on AM766: Formula Value.
Note on AM767: Formula Value.
Note on AM768: Formula Value.
Note on AM771: Formula Value.
Note on AM772: Formula Value.
Note on AM773: Formula Value.
Note on AM774: Formula Value.
Note on AM775: Formula Value.
Note on AM776: Formula Value.
Note on AM777: Formula Value.
Note on AM778: Formula Value.
Note on AM779: Formula Value.
Note on AM780: Formula Value.
Note on AM781: Formula Value.
Note on AM782: Formula Value.
Note on AM783: Formula Value.
Note on AM784: Formula Value.
Note on AM785: Formula Value.
Note on AM786: Formula Value.
Note on AM787: Formula Value.
Note on AM788: Formula Value.
Note on AM789: Formula Value.
Note on AM790: Formula Value.
Note on AM791: Formula Value.
Note on AM792: Formula Value.
Note on AM793: Formula Value.
Note on AM794: Formula Value.
Note on AM795: Formula Value.
Note on AM796: Formula Value.
Note on AM797: Formula Value.
Note on AM798: Formula Value.
Note on AM799: Formula Value.
Note on AM800: Formula Value.
Note on AM801: Formula Value.
Note on AM802: Formula Value.
Note on AM803: Formula Value.
Note on AM804: Formula Value.
Note on AM805: Formula Value.
Note on AM806: Formula Value.
Note on AM807: Formula Value.
Note on AM808: Formula Value.
Note on AM809: Formula Value.
Note on AM810: Formula Value.
Note on AM811: Formula Value.
Note on AM812: Formula Value.
Note on AM813: Formula Value.
Note on AM814: Formula Value.
Note on AM815: Formula Value.
Note on AM816: Formula Value.
Note on AM817: Formula Value.
Note on AM818: Formula Value.
Note on AM819: Formula Value.
Note on AM820: Formula Value.
Note on AM821: Formula Value.
Note on AM822: Formula Value.
Note on AM823: Formula Value.
Note on AM824: Formula Value.
Note on AM825: Formula Value.
Note on AM826: Formula Value.
Note on AM827: Formula Value.
Note on AM828: Formula Value.
Note on AM829: Formula Value.
Note on AM830: Formula Value.
Note on AM831: Formula Value.
Note on AM832: Formula Value.
Note on AM833: Formula Value.
Note on AM834: Formula Value.
Note on AM835: Formula Value.
Note on AM836: Formula Value.
Note on AM837: Formula Value.
Note on AM838: Formula Value.
Note on AM839: Formula Value.
Note on AM840: Formula Value.
Note on AM841: Formula Value.
Note on AM842: Formula Value.
Note on AM843: Formula Value.
Note on AM844: Formula Value.
Note on AM845: Formula Value.
Note on AM846: Formula Value.
Note on AM847: Formula Value.
Note on AM848: Formula Value.
Note on AM849: Formula Value.
Note on AM850: Formula Value.
Note on AM851: Formula Value.
Note on AM852: Formula Value.
Note on AM853: Formula Value.
Note on AM854: Formula Value.
Note on AM855: Formula Value.
Note on AM856: Formula Value.
Note on AM857: Formula Value.
Note on AM858: Formula Value.
Note on AM859: Formula Value.
Note on AM860: Formula Value.
Note on AM861: Formula Value.
Note on AM862: Formula Value.
Note on AM863: Formula Value.
Note on AM864: Formula Value.
Note on AM865: Formula Value.
Note on AM866: Formula Value.
Note on AM867: Formula Value.
Note on AM868: Formula Value.
Note on AM869: Formula Value.
Note on AM870: Formula Value.
Note on AM871: Formula Value.
Note on AM872: Formula Value.
Note on AM873: Formula Value.
Note on AM874: Formula Value.
Note on AM875: Formula Value.
Note on AM876: Formula Value.
Note on AM877: Formula Value.
Note on AM878: Formula Value.
Note on AM879: Formula Value.
Note on AM880: Formula Value.
Note on AM881: Formula Value.
Note on AM882: Formula Value.
Note on AM883: Formula Value.
Note on AM884: Formula Value.
Note on AM885: Formula Value.
Note on AM886: Formula Value.
Note on AM887: Formula Value.
Note on AM888: Formula Value.
Note on AM889: Formula Value.
Note on AM890: Formula Value.
Note on AM891: Formula Value.
Note on AM892: Formula Value.
Note on AM893: Formula Value.
Note on AM894: Formula Value.
Note on AM895: Formula Value.
Note on AM896: Formula Value.
Note on AM897: Formula Value.
Note on AM898: Formula Value.
Note on AM899: Formula Value.
Note on AM900: Formula Value.
Note on AM901: Formula Value.
Note on AM902: Formula Value.
Note on AM903: Formula Value.
Note on AM904: Formula Value.
Note on AM905: Formula Value.
Note on AM906: Formula Value.
Note on AM907: Formula Value.
Note on AM908: Formula Value.
Note on AM909: Formula Value.
Note on AM910: Formula Value.
Note on AM911: Formula Value.
Note on AM912: Formula Value.
Note on AM913: Formula Value.
Note on AM914: Formula Value.
Note on AM915: Formula Value.
Note on AM916: Formula Value.
Note on AM917: Formula Value.
Note on AM918: Formula Value.
Note on AM919: Formula Value.
Note on AM920: Formula Value.
Note on AM921: Formula Value.
Note on AM922: Formula Value.
Note on AM923: Formula Value.
Note on AM924: Formula Value.
Note on AM925: Formula Value.
Note on AM926: Formula Value.
Note on AM927: Formula Value.
Note on AM928: Formula Value.
Note on AM929: Formula Value.
Note on AM930: Formula Value.
Note on AM931: Formula Value.
Note on AM932: Formula Value.
Note on AM933: Formula Value.
Note on AM934: Formula Value.
Note on AM935: Formula Value.
Note on AM936: Formula Value.
Note on AM937: Formula Value.
Note on AM938: Formula Value.
Note on AM939: Formula Value.
Note on AM940: Formula Value.
Note on AM941: Formula Value.
Note on AM942: Formula Value.
Note on AM943: Formula Value.
Note on AM944: Formula Value.
Note on AM945: Formula Value.
Note on AM946: Formula Value.
Note on AM947: Formula Value.
Note on AM948: Formula Value.
Note on AM949: Formula Value.
Note on AM950: Formula Value.
Note on AM951: Formula Value.
Note on AM952: Formula Value.
Note on AM953: Formula Value.
Note on AM954: Formula Value.
Note on AM955: Formula Value.
Note on AM956: Formula Value.
Note on AM957: Formula Value.
Note on AM958: Formula Value.
Note on AM959: Formula Value.
Note on AM960: Formula Value.
Note on AM961: Formula Value.
Note on AM962: Formula Value.
Note on AM963: Formula Value.
Note on AM964: Formula Value.
Note on AM965: Formula Value.
Note on AM966: Formula Value.
Note on AM967: Formula Value.
Note on AM968: Formula Value.
Note on AM969: Formula Value.
Note on AM970: Formula Value.
Note on AM990: Formula Value.
Note on AM991: Formula Value.
Note on AM992: Formula Value.
Note on AM993: Formula Value.
Note on AM994: Formula Value.
Note on AM995: Formula Value.
Note on AM996: Formula Value.
Note on AM997: Formula Value.
Note on AM998: Formula Value.
Note on AM999: Formula Value.
Note on AM1000: Formula Value.
Note on AM1001: Formula Value.
Note on AM1002: Formula Value.
Note on AM1003: Formula Value.
Note on AM1004: Formula Value.
Note on AM1005: Formula Value.
Note on AM1006: Formula Value.
Note on AM1007: Formula Value.
Note on AM1008: Formula Value.
Note on AM1009: Formula Value.
Note on AM1010: Formula Value.
Note on AM1011: Formula Value.
Note on AM1012: Formula Value.
Note on AM1013: Formula Value.
Note on AM1014: Formula Value.
Note on AM1015: Formula Value.
Note on AM1016: Formula Value.
Note on AM1017: Formula Value.
Note on AM1018: Formula Value.
Note on AM1019: Formula Value.
Note on AM1020: Formula Value.
Note on AM1021: Formula Value.
Note on AM1022: Formula Value.
Note on AM1023: Formula Value.
Note on AM1024: Formula Value.
Note on AM1025: Formula Value.
Note on AM1026: Formula Value.
Note on AM1027: Formula Value.
Note on AM1028: Formula Value.
Note on AM1029: Formula Value.
Note on AM1030: Formula Value.
Note on AM1031: Formula Value.
Note on AM1032: Formula Value.
Note on AM1033: Formula Value.
Note on AM1034: Formula Value.
Note on AM1035: Formula Value.
Note on AM1036: Formula Value.
Note on AM1037: Formula Value.
Note on AM1038: Formula Value.
Note on AM1039: Formula Value.
Note on AM1040: Formula Value.
Note on AM1041: Formula Value.
Note on AM1042: Formula Value.
Note on AM1043: Formula Value.
Note on AM1044: Formula Value.
Note on AM1045: Formula Value.
Note on AM1046: Formula Value.
Note on AM1047: Formula Value.
Note on AM1048: Formula Value.
Note on AM1049: Formula Value.
Note on AM1050: Formula Value.
Note on AM1051: Formula Value.
Note on AM1052: Formula Value.
Note on AM1053: Formula Value.
Note on AM1054: Formula Value.
Note on AM1055: Formula Value.
Note on AM1056: Formula Value.
Note on AM1057: Formula Value.
Note on AM1058: Formula Value.
Note on AM1059: Formula Value.
Note on AM1060: Formula Value.
Note on AM1061: Formula Value.
Note on AM1062: Formula Value.
Note on AM1063: Formula Value.
Note on AM1064: Formula Value.
Note on AM1065: Formula Value.
Note on AM1066: Formula Value.
Note on AM1067: Formula Value.
Note on AM1068: Formula Value.
Note on AM1069: Formula Value.
Note on AM1070: Formula Value.
Note on AM1071: Formula Value.
Note on AM1072: Formula Value.
Note on AM1073: Formula Value.
Note on AM1074: Formula Value.
Note on AM1075: Formula Value.
Note on AM1076: Formula Value.
Note on AM1077: Formula Value.
Note on AM1078: Formula Value.
Note on AM1117: Formula Value.
Note on AM1118: Formula Value.
Note on AM1119: Formula Value.
Note on AM1120: Formula Value.
Note on AM1121: Formula Value.
Note on AM1122: Formula Value.
Note on AM1123: Formula Value.
Note on AM1124: Formula Value.
Note on AM1125: Formula Value.
Note on AM1126: Formula Value.
Note on AM1127: Formula Value.
Note on AM1128: Formula Value.
Note on AM1129: Formula Value.
Note on AM1130: Formula Value.
Note on AM1131: Formula Value.
Note on AM1132: Formula Value.
Note on AM1133: Formula Value.
Note on AM1134: Formula Value.
Note on AM1135: Formula Value.
Note on AM1136: Formula Value.
Note on AM1137: Formula Value.
Note on AM1138: Formula Value.
Note on AM1139: Formula Value.
Note on AM1140: Formula Value.
Note on AM1141: Formula Value.
Note on AM1142: Formula Value.
Note on AM1143: Formula Value.
Note on AM1144: Formula Value.
Note on AM1145: Formula Value.
Note on AM1146: Formula Value.
Note on AM1147: Formula Value.
Note on AM1148: Formula Value.
Note on AM1149: Formula Value.
Note on AM1150: Formula Value.
Note on AM1151: Formula Value.
Note on AM1152: Formula Value.
Note on AM1153: Formula Value.
Note on AM1154: Formula Value.
Note on AM1155: Formula Value.
Note on AM1156: Formula Value.
Note on AM1157: Formula Value.
Note on AM1158: Formula Value.
Note on AM1159: Formula Value.
Note on AM1160: Formula Value.
Note on AM1161: Formula Value.
Note on AM1162: Formula Value.
Note on AM1201: Formula Value.
Note on AM1202: Formula Value.
Note on AM1204: Formula Value.
Note on AM1206: Formula Value.
Note on AM1208: Formula Value.
Note on AM1210: Formula Value.
Note on AM1212: Formula Value.
Note on AM1214: Formula Value.
Note on AM1216: Formula Value.
Note on AM1218: Formula Value.
Note on AM1220: Formula Value.
Note on AM1222: Formula Value.
Note on AM1224: Formula Value.
Note on AM1226: Formula Value.
Note on AM1228: Formula Value.
Note on AM1230: Formula Value.
Note on AM1232: Formula Value.
Note on AM1234: Formula Value.
Note on AM1236: Formula Value.
Note on AM1238: Formula Value.
Note on AM1240: Formula Value.
Note on AM1242: Formula Value.
Note on AM1244: Formula Value.
Note on AM1246: Formula Value.
Note on AM1248: Formula Value.
Note on AM1250: Formula Value.
Note on AM1252: Formula Value.
Note on AM1254: Formula Value.
Note on AM1256: Formula Value.
Note on AM1258: Formula Value.
Note on AM1260: Formula Value.
Note on AM1262: Formula Value.
Note on AM1264: Formula Value.
Note on AM1266: Formula Value.
Note on AM1268: Formula Value.
Note on AM1270: Formula Value.
Note on AM1272: Formula Value.
Note on AM1274: Formula Value.
Note on AM1276: Formula Value.
Note on AM1278: Formula Value.
Note on AM1280: Formula Value.
Note on AM1282: Formula Value.
Note on AM1284: Formula Value.
Note on AM1286: Formula Value.
Note on AM1288: Formula Value.
Note on AM1290: Formula Value.
Note on AM1292: Formula Value.
Note on AM1294: Formula Value.
Note on AM1296: Formula Value.
Note on AM1298: Formula Value.
Note on AM1300: Formula Value.
Note on AM1302: Formula Value.
Note on AM1304: Formula Value.
Note on AM1306: Formula Value.
Note on AM1308: Formula Value.
Note on AM1310: Formula Value.
Note on AM1312: Formula Value.
Note on AM1314: Formula Value.
Note on AM1316: Formula Value.
Note on AM1337: Formula Value.
Note on AM1339: Formula Value.
Note on AM1341: Formula Value.
Note on AM1343: Formula Value.
Note on AM1345: Formula Value.
Note on AM1347: Formula Value.
Note on AM1349: Formula Value.
Note on AM1351: Formula Value.
Note on AM1353: Formula Value.
Note on AM1355: Formula Value.
Note on AM1357: Formula Value.
Note on AM1359: Formula Value.
Note on AM1361: Formula Value.
Note on AM1363: Formula Value.
Note on AM1365: Formula Value.
Note on AM1367: Formula Value.
Note on AM1369: Formula Value.
Note on AM1371: Formula Value.
Note on AM1373: Formula Value.
Note on AM1375: Formula Value.
Note on AM1377: Formula Value.
Note on AM1379: Formula Value.
Note on AM1381: Formula Value.
Note on AM1383: Formula Value.
Note on AM1385: Formula Value.
Note on AM1387: Formula Value.
Note on AM1389: Formula Value.
Note on AM1391: Formula Value.
Note on AM1393: Formula Value.
Note on AM1395: Formula Value.
Note on AM1397: Formula Value.
Note on AM1399: Formula Value.
Note on AM1401: Formula Value.
Note on AM1403: Formula Value.
Note on AM1405: Formula Value.
Note on AM1407: Formula Value.
Note on AM1409: Formula Value.
Note on AM1411: Formula Value.
Note on AM1413: Formula Value.
Note on AM1415: Formula Value.
Note on AM1417: Formula Value.
Note on AM1419: Formula Value.
Note on AM1421: Formula Value.
Note on AM1423: Formula Value.
Note on AM1425: Formula Value.
Note on AM1427: Formula Value.
Note on AM1429: Formula Value.
Note on AM1431: Formula Value.
Note on AM1433: Formula Value.
Note on AM1435: Formula Value.
Note on AM1437: Formula Value.
Note on AM1439: Formula Value.
Note on AM1441: Formula Value.
Note on AM1443: Formula Value.
Note on AM1445: Formula Value.
Note on AM1447: Formula Value.
Note on AM1449: Formula Value.
Note on AM1451: Formula Value.
Note on AM1453: Formula Value.
Note on AM1455: Formula Value.
Note on AM1457: Formula Value.
Note on AM1459: Formula Value.
Note on AM1461: Formula Value.
Note on AM1463: Formula Value.
Note on AM1465: Formula Value.
Note on AM1467: Formula Value.
Note on AM1469: Formula Value.
Note on AM1471: Formula Value.
Note on AM1473: Formula Value.
Note on AM1475: Formula Value.
Note on AM1477: Formula Value.
Note on AM1479: Formula Value.
Note on AM1481: Formula Value.
Note on AM1483: Formula Value.
Note on AM1485: Formula Value.
Note on AM1487: Formula Value.
Note on AM1584: Formula Value.
Note on AM1586: Formula Value.
Note on AM1588: Formula Value.
Note on AM1590: Formula Value.
Note on AM1592: Formula Value.
Note on AM1594: Formula Value.
Note on AM1596: Formula Value.
Note on AM1598: Formula Value.
Note on AM1600: Formula Value.
Note on AM1602: Formula Value.
Note on AM1604: Formula Value.
Note on AM1606: Formula Value.
Note on AM1608: Formula Value.
Note on AM1610: Formula Value.
Note on AM1612: Formula Value.
Note on AM1614: Formula Value.
Note on AM1616: Formula Value.
Note on AM1618: Formula Value.
Note on AM1620: Formula Value.
Note on AM1622: Formula Value.
Note on AM1624: Formula Value.
Note on AM1626: Formula Value.
Note on AM1628: Formula Value.
Note on AM1630: Formula Value.
Note on AM1632: Formula Value.
Note on AM1634: Formula Value.
Note on AM1636: Formula Value.
Note on AM1638: Formula Value.
Note on AM1640: Formula Value.
Note on AM1642: Formula Value.
Note on AM1644: Formula Value.
Note on AM1646: Formula Value.
Note on AM1648: Formula Value.
Note on AM1650: Formula Value.
Note on AM1652: Formula Value.
Note on AM1654: Formula Value.
Note on AM1656: Formula Value.
Note on AM1658: Formula Value.
Note on AM1660: Formula Value.
Note on AM1662: Formula Value.
Note on AM1664: Formula Value.
Note on AM1666: Formula Value.
Note on AM1668: Formula Value.
Note on AM1670: Formula Value.
Note on AM1672: Formula Value.
Note on AM1674: Formula Value.
Note on AM1676: Formula Value.
Note on AM1678: Formula Value.
Note on AM1680: Formula Value.
Note on AM1682: Formula Value.
Note on AM1684: Formula Value.
Note on AM1686: Formula Value.
Note on AM1688: Formula Value.
Note on AM1690: Formula Value.
Note on AM1692: Formula Value.
Note on AM1694: Formula Value.
Note on AM1696: Formula Value.
Note on AM1697: Formula Value.
Note on AM1698: Formula Value.
Note on AM1699: Formula Value.
Note on AM1700: Formula Value.
Note on AM1701: Formula Value.
Note on AM1702: Formula Value.
Note on AM1703: Formula Value.
Note on AM1705: Formula Value.
Note on AM1707: Formula Value.
Note on AM1709: Formula Value.
Note on AM1711: Formula Value.
Note on AM1713: Formula Value.
Note on AM1715: Formula Value.
Note on AM1717: Formula Value.
Note on AM1719: Formula Value.
Note on AM1721: Formula Value.
Note on AM1723: Formula Value.
Note on AM1725: Formula Value.
Note on AM1727: Formula Value.
Note on AM1729: Formula Value.
Note on AM1731: Formula Value.
Note on AM1733: Formula Value.
Note on AM1735: Formula Value.
Note on AM1737: Formula Value.
Note on AM1739: Formula Value.
Note on AM1741: Formula Value.
Note on AM1761: Formula Value.
Note on AM1762: Formula Value.
Note on AM1763: Formula Value.
Note on AM1765: Formula Value.
Note on AM1767: Formula Value.
Note on AM1769: Formula Value.
Note on AM1771: Formula Value.
Note on AM1773: Formula Value.
Note on AM1775: Formula Value.
Note on AM1777: Formula Value.
Note on AM1779: Formula Value.
Note on AM1781: Formula Value.
Note on AM1783: Formula Value.
Note on AM1785: Formula Value.
Note on AM1787: Formula Value.
Note on AM1789: Formula Value.
Note on AM1791: Formula Value.
Note on AM1793: Formula Value.
Note on AM1795: Formula Value.
Note on AM1797: Formula Value.
Note on AM1799: Formula Value.
Note on AM1801: Formula Value.
Note on AM1802: Formula Value.
Note on AM1803: Formula Value.
Note on AM1804: Formula Value.
Note on AM1844: Formula Value.
Note on AM1846: Formula Value.
Note on AM1848: Formula Value.
Note on AM1850: Formula Value.
Note on AM1852: Formula Value.
Note on AM1854: Formula Value.
Note on AM1856: Formula Value.
Note on AM1858: Formula Value.
Note on AM1860: Formula Value.
Note on AM1862: Formula Value.
Note on AM1864: Formula Value.
Note on AM1866: Formula Value.
Note on AM1868: Formula Value.
Note on AM1870: Formula Value.
Note on AM1872: Formula Value.
Note on AM1874: Formula Value.
Note on AM1876: Formula Value.
Note on AM1878: Formula Value.
Note on AM1880: Formula Value.
Note on AM1882: Formula Value.
Note on AM1884: Formula Value.
Note on AM1886: Formula Value.
Note on AM1888: Formula Value.
Note on AM1890: Formula Value.
Note on AM1892: Formula Value.
Note on AM1894: Formula Value.
Note on AM1896: Formula Value.
Note on AM1898: Formula Value.
Note on AM1900: Formula Value.
Note on AM1902: Formula Value.
Note on AM1904: Formula Value.
Note on AM1906: Formula Value.
Note on AM1908: Formula Value.
Note on AM1910: Formula Value.
Note on AM1912: Formula Value.
Note on AM1914: Formula Value.
Note on AM1916: Formula Value.
Note on AM1918: Formula Value.
Note on AM1920: Formula Value.
Note on AM1922: Formula Value.
Note on AM1924: Formula Value.
Note on AM1926: Formula Value.
Note on AM1928: Formula Value.
Note on AM1930: Formula Value.
Note on AM1932: Formula Value.
Note on AM1934: Formula Value.
Note on AM1936: Formula Value.
Note on AM1938: Formula Value.
Note on AM1940: Formula Value.
Note on AM1942: Formula Value.
Note on AM1944: Formula Value.
Note on AM1946: Formula Value.
Note on AM1948: Formula Value.
Note on AM1950: Formula Value.
Note on AM1952: Formula Value.
Note on AM1954: Formula Value.
Note on AM1956: Formula Value.
Note on AM1958: Formula Value.
Note on AM1960: Formula Value.
Note on AM1962: Formula Value.
Note on AM1964: Formula Value.
Note on AM1966: Formula Value.
Note on AM1968: Formula Value.
Note on AM1970: Formula Value.
Note on AM1972: Formula Value.
Note on AM1974: Formula Value.
Note on AM1976: Formula Value.
Note on AM1978: Formula Value.
Note on AM1980: Formula Value.
Note on AM1982: Formula Value.
Note on AM1984: Formula Value.
Note on AM1986: Formula Value.
Note on AM1988: Formula Value.
Note on AM1990: Formula Value.
Note on AM1992: Formula Value.
Note on AM1994: Formula Value.
Note on AM1996: Formula Value.
Note on AM1998: Formula Value.
Note on AM2000: Formula Value.
Note on AM2002: Formula Value.
Note on AM2004: Formula Value.
Note on AM2006: Formula Value.
Note on AM2008: Formula Value.
Note on AM2010: Formula Value.
Note on AM2012: Formula Value.
Note on AM2014: Formula Value.
Note on AM2016: Formula Value.
Note on AM2018: Formula Value.
Note on AM2020: Formula Value.
Note on AM2022: Formula Value.
Note on AM2024: Formula Value.
Note on AM2026: Formula Value.
Note on AM2028: Formula Value.
Note on AM2030: Formula Value.
Note on AM2032: Formula Value.
Note on AM2034: Formula Value.
Note on AM2036: Formula Value.
Note on AM2038: Formula Value.
Note on AM2040: Formula Value.
Note on AM2042: Formula Value.
Note on AM2044: Formula Value.
Note on AM2046: Formula Value.
Note on AM2048: Formula Value.
Note on AM2050: Formula Value.
Note on AM2052: Formula Value.
Note on AM2054: Formula Value.
Note on AM2056: Formula Value.
Note on AM2058: Formula Value.
Note on AM2060: Formula Value.
Note on AM2062: Formula Value.
Note on AM2064: Formula Value.
Note on AM2066: Formula Value.
Note on AM2068: Formula Value.
Note on AM2070: Formula Value.
Note on AM2071: Formula Value.
Note on AM2073: Formula Value.
Note on AM2075: Formula Value.
Note on AM2076: Formula Value.
Note on AM2077: Formula Value.
Note on AM2078: Formula Value.
Note on AM2080: Formula Value.
Note on AM2081: Formula Value.
Note on AM2082: Formula Value.
Note on AM2083: Formula Value.
Note on AM2085: Formula Value.
Note on AM2087: Formula Value.
Note on AM2088: Formula Value.
Note on AM2089: Formula Value.
Note on AM2090: Formula Value.
Note on AM2091: Formula Value.
Note on AM2092: Formula Value.
Note on AM2093: Formula Value.
Note on AM2094: Formula Value.
Note on AM2095: Formula Value.
Note on AM2096: Formula Value.
Note on AM2097: Formula Value.
Note on AM2099: Formula Value.
Note on AM2101: Formula Value.
Note on AM2103: Formula Value.
Note on AM2108: Formula Value.
Note on AM2109: Formula Value.
Note on AM2110: Formula Value.
Note on AM2111: Formula Value.
Note on AM2112: Formula Value.
Note on AM2113: Formula Value.
Note on AM2114: Formula Value.
Note on AM2115: Formula Value.
Note on AM2116: Formula Value.
Note on AM2118: Formula Value.
Note on AM2119: Formula Value.
Note on AM2123: Formula Value.
Note on AM2125: Formula Value.
Note on AM2128: Formula Value.
Note on AM2133: Formula Value.
Note on AM2135: Formula Value.
Note on AM2140: Formula Value.
Note on AM2142: Formula Value.
Note on AM2148: Formula Value.
Note on AM2149: Formula Value.
Note on AM2150: Formula Value.
Note on AM2151: Formula Value.
Note on AM2152: Formula Value.
Note on AM2153: Formula Value.
Note on AM2154: Formula Value.
Note on AM2156: Formula Value.
Note on AM2158: Formula Value.
Note on AM2159: Formula Value.
Note on AM2160: Formula Value.
Note on AM2161: Formula Value.
Note on AM2162: Formula Value.
Note on AM2163: Formula Value.
Note on AM2164: Formula Value.
Note on AM2165: Formula Value.
Note on AM2166: Formula Value.
Note on AM2167: Formula Value.
Note on AM2168: Formula Value.
Note on AM2169: Formula Value.
Note on AN5: Formula Value.
Note on AN10: Formula Value.
Note on AN14: Formula Value.
Note on AN15: Formula Value.
Note on AN120: Formula Value.
Note on AN121: Formula Value.
Note on AN122: Formula Value.
Note on AN123: Formula Value.
Note on AN124: Formula Value.
Note on AN125: Formula Value.
Note on AN126: Formula Value.
Note on AN164: Formula Value.
Note on AN169: Formula Value.
Note on AN184: Formula Value.
Note on AN223: Formula Value.
Note on AN254: Formula Value.
Note on AN259: Formula Value.
Note on AN267: Formula Value.
Note on AN273: Formula Value.
Note on AN275: Formula Value.
Note on AN276: Formula Value.
Note on AN281: Formula Value.
Note on AN285: Formula Value.
Note on AN300: Formula Value.
Note on AN304: Formula Value.
Note on AN315: Formula Value.
Note on AN318: Formula Value.
Note on AN321: Formula Value.
Note on AN338: Formula Value.
Note on AN340: Formula Value.
Note on AN343: Formula Value.
Note on AN354: Formula Value.
Note on AN356: Formula Value.
Note on AN358: Formula Value.
Note on AN359: Formula Value.
Note on AN362: Formula Value.
Note on AN371: Formula Value.
Note on AN376: Formula Value.
Note on AN379: Formula Value.
Note on AN381: Formula Value.
Note on AN393: Formula Value.
Note on AN395: Formula Value.
Note on AN404: Formula Value.
Note on AN407: Formula Value.
Note on AN421: Formula Value.
Note on AN423: Formula Value.
Note on AN424: Formula Value.
Note on AN431: Formula Value.
Note on AN433: Formula Value.
Note on AN434: Formula Value.
Note on AN435: Formula Value.
Note on AN443: Formula Value.
Note on AN447: Formula Value.
Note on AN449: Formula Value.
Note on AN450: Formula Value.
Note on AN456: Formula Value.
Note on AN467: Formula Value.
Note on AN470: Formula Value.
Note on AN474: Formula Value.
Note on AN477: Formula Value.
Note on AN478: Formula Value.
Note on AN481: Formula Value.
Note on AN482: Formula Value.
Note on AN529: Formula Value.
Note on AN531: Formula Value.
Note on AN553: Formula Value.
Note on AN556: Formula Value.
Note on AN557: Formula Value.
Note on AN565: Formula Value.
Note on AN587: Formula Value.
Note on AN588: Formula Value.
Note on AN590: Formula Value.
Note on AN593: Formula Value.
Note on AN594: Formula Value.
Note on AN595: Formula Value.
Note on AN596: Formula Value.
Note on AN626: Formula Value.
Note on AN628: Formula Value.
Note on AN629: Formula Value.
Note on AN630: Formula Value.
Note on AN631: Formula Value.
Note on AN632: Formula Value.
Note on AN633: Formula Value.
Note on AN634: Formula Value.
Note on AN635: Formula Value.
Note on AN636: Formula Value.
Note on AN637: Formula Value.
Note on AN638: Formula Value.
Note on AN639: Formula Value.
Note on AN640: Formula Value.
Note on AN643: Formula Value.
Note on AN647: Formula Value.
Note on AN776: Formula Value.
Note on AN777: Formula Value.
Note on AN778: Formula Value.
Note on AN779: Formula Value.
Note on AN780: Formula Value.
Note on AN781: Formula Value.
Note on AN782: Formula Value.
Note on AN783: Formula Value.
Note on AN784: Formula Value.
Note on AN785: Formula Value.
Note on AN786: Formula Value.
Note on AN787: Formula Value.
Note on AN788: Formula Value.
Note on AN789: Formula Value.
Note on AN790: Formula Value.
Note on AN791: Formula Value.
Note on AN792: Formula Value.
Note on AN793: Formula Value.
Note on AN794: Formula Value.
Note on AN795: Formula Value.
Note on AN796: Formula Value.
Note on AN797: Formula Value.
Note on AN798: Formula Value.
Note on AN799: Formula Value.
Note on AN800: Formula Value.
Note on AN801: Formula Value.
Note on AN802: Formula Value.
Note on AN803: Formula Value.
Note on AN804: Formula Value.
Note on AN805: Formula Value.
Note on AN806: Formula Value.
Note on AN807: Formula Value.
Note on AN808: Formula Value.
Note on AN809: Formula Value.
Note on AN810: Formula Value.
Note on AN811: Formula Value.
Note on AN812: Formula Value.
Note on AN813: Formula Value.
Note on AN815: Formula Value.
Note on AN816: Formula Value.
Note on AN817: Formula Value.
Note on AN818: Formula Value.
Note on AN819: Formula Value.
Note on AN820: Formula Value.
Note on AN821: Formula Value.
Note on AN822: Formula Value.
Note on AN823: Formula Value.
Note on AN824: Formula Value.
Note on AN825: Formula Value.
Note on AN826: Formula Value.
Note on AN827: Formula Value.
Note on AN828: Formula Value.
Note on AN829: Formula Value.
Note on AN830: Formula Value.
Note on AN831: Formula Value.
Note on AN832: Formula Value.
Note on AN833: Formula Value.
Note on AN834: Formula Value.
Note on AN835: Formula Value.
Note on AN836: Formula Value.
Note on AN837: Formula Value.
Note on AN838: Formula Value.
Note on AN839: Formula Value.
Note on AN840: Formula Value.
Note on AN841: Formula Value.
Note on AN842: Formula Value.
Note on AN843: Formula Value.
Note on AN844: Formula Value.
Note on AN845: Formula Value.
Note on AN846: Formula Value.
Note on AN847: Formula Value.
Note on AN848: Formula Value.
Note on AN849: Formula Value.
Note on AN850: Formula Value.
Note on AN851: Formula Value.
Note on AN852: Formula Value.
Note on AN854: Formula Value.
Note on AN855: Formula Value.
Note on AN856: Formula Value.
Note on AN857: Formula Value.
Note on AN858: Formula Value.
Note on AN859: Formula Value.
Note on AN860: Formula Value.
Note on AN861: Formula Value.
Note on AN862: Formula Value.
Note on AN863: Formula Value.
Note on AN864: Formula Value.
Note on AN865: Formula Value.
Note on AN866: Formula Value.
Note on AN867: Formula Value.
Note on AN868: Formula Value.
Note on AN869: Formula Value.
Note on AN870: Formula Value.
Note on AN871: Formula Value.
Note on AN872: Formula Value.
Note on AN873: Formula Value.
Note on AN874: Formula Value.
Note on AN875: Formula Value.
Note on AN876: Formula Value.
Note on AN877: Formula Value.
Note on AN878: Formula Value.
Note on AN879: Formula Value.
Note on AN880: Formula Value.
Note on AN881: Formula Value.
Note on AN882: Formula Value.
Note on AN883: Formula Value.
Note on AN884: Formula Value.
Note on AN885: Formula Value.
Note on AN886: Formula Value.
Note on AN887: Formula Value.
Note on AN888: Formula Value.
Note on AN889: Formula Value.
Note on AN890: Formula Value.
Note on AN891: Formula Value.
Note on AN892: Formula Value.
Note on AN893: Formula Value.
Note on AN894: Formula Value.
Note on AN895: Formula Value.
Note on AN896: Formula Value.
Note on AN897: Formula Value.
Note on AN898: Formula Value.
Note on AN899: Formula Value.
Note on AN900: Formula Value.
Note on AN901: Formula Value.
Note on AN902: Formula Value.
Note on AN903: Formula Value.
Note on AN904: Formula Value.
Note on AN905: Formula Value.
Note on AN906: Formula Value.
Note on AN907: Formula Value.
Note on AN908: Formula Value.
Note on AN909: Formula Value.
Note on AN910: Formula Value.
Note on AN911: Formula Value.
Note on AN912: Formula Value.
Note on AN913: Formula Value.
Note on AN914: Formula Value.
Note on AN915: Formula Value.
Note on AN916: Formula Value.
Note on AN917: Formula Value.
Note on AN918: Formula Value.
Note on AN919: Formula Value.
Note on AN920: Formula Value.
Note on AN921: Formula Value.
Note on AN922: Formula Value.
Note on AN923: Formula Value.
Note on AN924: Formula Value.
Note on AN925: Formula Value.
Note on AN926: Formula Value.
Note on AN927: Formula Value.
Note on AN928: Formula Value.
Note on AN929: Formula Value.
Note on AN930: Formula Value.
Note on AN931: Formula Value.
Note on AN932: Formula Value.
Note on AN933: Formula Value.
Note on AN934: Formula Value.
Note on AN935: Formula Value.
Note on AN936: Formula Value.
Note on AN937: Formula Value.
Note on AN938: Formula Value.
Note on AN939: Formula Value.
Note on AN940: Formula Value.
Note on AN941: Formula Value.
Note on AN942: Formula Value.
Note on AN943: Formula Value.
Note on AN944: Formula Value.
Note on AN945: Formula Value.
Note on AN946: Formula Value.
Note on AN947: Formula Value.
Note on AN948: Formula Value.
Note on AN949: Formula Value.
Note on AN950: Formula Value.
Note on AN951: Formula Value.
Note on AN952: Formula Value.
Note on AN953: Formula Value.
Note on AN954: Formula Value.
Note on AN955: Formula Value.
Note on AN956: Formula Value.
Note on AN957: Formula Value.
Note on AN958: Formula Value.
Note on AN959: Formula Value.
Note on AN960: Formula Value.
Note on AN961: Formula Value.
Note on AN962: Formula Value.
Note on AN963: Formula Value.
Note on AN964: Formula Value.
Note on AN965: Formula Value.
Note on AN966: Formula Value.
Note on AN967: Formula Value.
Note on AN990: Formula Value.
Note on AN991: Formula Value.
Note on AN992: Formula Value.
Note on AN993: Formula Value.
Note on AN994: Formula Value.
Note on AN995: Formula Value.
Note on AN996: Formula Value.
Note on AN997: Formula Value.
Note on AN998: Formula Value.
Note on AN999: Formula Value.
Note on AN1000: Formula Value.
Note on AN1001: Formula Value.
Note on AN1023: Formula Value.
Note on AN1024: Formula Value.
Note on AN1025: Formula Value.
Note on AN1026: Formula Value.
Note on AN1027: Formula Value.
Note on AN1028: Formula Value.
Note on AN1029: Formula Value.
Note on AN1030: Formula Value.
Note on AN1031: Formula Value.
Note on AN1032: Formula Value.
Note on AN1041: Formula Value.
Note on AN1042: Formula Value.
Note on AN1043: Formula Value.
Note on AN1044: Formula Value.
Note on AN1045: Formula Value.
Note on AN1046: Formula Value.
Note on AN1047: Formula Value.
Note on AN1048: Formula Value.
Note on AN1049: Formula Value.
Note on AN1050: Formula Value.
Note on AN1051: Formula Value.
Note on AN1052: Formula Value.
Note on AN1053: Formula Value.
Note on AN1054: Formula Value.
Note on AN1055: Formula Value.
Note on AN1056: Formula Value.
Note on AN1057: Formula Value.
Note on AN1058: Formula Value.
Note on AN1059: Formula Value.
Note on AN1060: Formula Value.
Note on AN1061: Formula Value.
Note on AN1062: Formula Value.
Note on AN1063: Formula Value.
Note on AN1064: Formula Value.
Note on AN1065: Formula Value.
Note on AN1066: Formula Value.
Note on AN1067: Formula Value.
Note on AN1068: Formula Value.
Note on AN1069: Formula Value.
Note on AN1070: Formula Value.
Note on AN1071: Formula Value.
Note on AN1072: Formula Value.
Note on AN1073: Formula Value.
Note on AN1074: Formula Value.
Note on AN1075: Formula Value.
Note on AN1076: Formula Value.
Note on AN1077: Formula Value.
Note on AN1078: Formula Value.
Note on AN1123: Formula Value.
Note on AN1124: Formula Value.
Note on AN1125: Formula Value.
Note on AN1126: Formula Value.
Note on AN1127: Formula Value.
Note on AN1128: Formula Value.
Note on AN1129: Formula Value.
Note on AN1130: Formula Value.
Note on AN1131: Formula Value.
Note on AN1132: Formula Value.
Note on AN1133: Formula Value.
Note on AN1134: Formula Value.
Note on AN1135: Formula Value.
Note on AN1136: Formula Value.
Note on AN1137: Formula Value.
Note on AN1138: Formula Value.
Note on AN1139: Formula Value.
Note on AN1140: Formula Value.
Note on AN1141: Formula Value.
Note on AN1142: Formula Value.
Note on AN1143: Formula Value.
Note on AN1144: Formula Value.
Note on AN1145: Formula Value.
Note on AN1146: Formula Value.
Note on AN1147: Formula Value.
Note on AN1148: Formula Value.
Note on AN1149: Formula Value.
Note on AN1150: Formula Value.
Note on AN1151: Formula Value.
Note on AN1152: Formula Value.
Note on AN1153: Formula Value.
Note on AN1154: Formula Value.
Note on AN1155: Formula Value.
Note on AN1156: Formula Value.
Note on AN1157: Formula Value.
Note on AN1158: Formula Value.
Note on AN1159: Formula Value.
Note on AN1160: Formula Value.
Note on AN1201: Formula Value.
Note on AN1202: Formula Value.
Note on AN1206: Formula Value.
Note on AN1208: Formula Value.
Note on AN1210: Formula Value.
Note on AN1212: Formula Value.
Note on AN1214: Formula Value.
Note on AN1216: Formula Value.
Note on AN1218: Formula Value.
Note on AN1220: Formula Value.
Note on AN1222: Formula Value.
Note on AN1224: Formula Value.
Note on AN1226: Formula Value.
Note on AN1228: Formula Value.
Note on AN1230: Formula Value.
Note on AN1232: Formula Value.
Note on AN1234: Formula Value.
Note on AN1236: Formula Value.
Note on AN1238: Formula Value.
Note on AN1240: Formula Value.
Note on AN1242: Formula Value.
Note on AN1244: Formula Value.
Note on AN1246: Formula Value.
Note on AN1248: Formula Value.
Note on AN1250: Formula Value.
Note on AN1252: Formula Value.
Note on AN1254: Formula Value.
Note on AN1256: Formula Value.
Note on AN1258: Formula Value.
Note on AN1260: Formula Value.
Note on AN1262: Formula Value.
Note on AN1264: Formula Value.
Note on AN1266: Formula Value.
Note on AN1268: Formula Value.
Note on AN1270: Formula Value.
Note on AN1272: Formula Value.
Note on AN1274: Formula Value.
Note on AN1276: Formula Value.
Note on AN1278: Formula Value.
Note on AN1280: Formula Value.
Note on AN1282: Formula Value.
Note on AN1284: Formula Value.
Note on AN1286: Formula Value.
Note on AN1288: Formula Value.
Note on AN1290: Formula Value.
Note on AN1292: Formula Value.
Note on AN1294: Formula Value.
Note on AN1296: Formula Value.
Note on AN1298: Formula Value.
Note on AN1300: Formula Value.
Note on AN1302: Formula Value.
Note on AN1304: Formula Value.
Note on AN1306: Formula Value.
Note on AN1308: Formula Value.
Note on AN1310: Formula Value.
Note on AN1312: Formula Value.
Note on AN1314: Formula Value.
Note on AN1316: Formula Value.
Note on AN1337: Formula Value.
Note on AN1339: Formula Value.
Note on AN1341: Formula Value.
Note on AN1343: Formula Value.
Note on AN1345: Formula Value.
Note on AN1347: Formula Value.
Note on AN1349: Formula Value.
Note on AN1351: Formula Value.
Note on AN1353: Formula Value.
Note on AN1355: Formula Value.
Note on AN1357: Formula Value.
Note on AN1359: Formula Value.
Note on AN1361: Formula Value.
Note on AN1363: Formula Value.
Note on AN1365: Formula Value.
Note on AN1367: Formula Value.
Note on AN1369: Formula Value.
Note on AN1371: Formula Value.
Note on AN1373: Formula Value.
Note on AN1375: Formula Value.
Note on AN1377: Formula Value.
Note on AN1379: Formula Value.
Note on AN1381: Formula Value.
Note on AN1383: Formula Value.
Note on AN1385: Formula Value.
Note on AN1387: Formula Value.
Note on AN1389: Formula Value.
Note on AN1391: Formula Value.
Note on AN1393: Formula Value.
Note on AN1395: Formula Value.
Note on AN1397: Formula Value.
Note on AN1399: Formula Value.
Note on AN1401: Formula Value.
Note on AN1403: Formula Value.
Note on AN1405: Formula Value.
Note on AN1407: Formula Value.
Note on AN1409: Formula Value.
Note on AN1411: Formula Value.
Note on AN1413: Formula Value.
Note on AN1415: Formula Value.
Note on AN1417: Formula Value.
Note on AN1419: Formula Value.
Note on AN1421: Formula Value.
Note on AN1423: Formula Value.
Note on AN1425: Formula Value.
Note on AN1427: Formula Value.
Note on AN1429: Formula Value.
Note on AN1431: Formula Value.
Note on AN1433: Formula Value.
Note on AN1435: Formula Value.
Note on AN1437: Formula Value.
Note on AN1439: Formula Value.
Note on AN1441: Formula Value.
Note on AN1443: Formula Value.
Note on AN1445: Formula Value.
Note on AN1447: Formula Value.
Note on AN1449: Formula Value.
Note on AN1451: Formula Value.
Note on AN1453: Formula Value.
Note on AN1455: Formula Value.
Note on AN1457: Formula Value.
Note on AN1459: Formula Value.
Note on AN1461: Formula Value.
Note on AN1463: Formula Value.
Note on AN1465: Formula Value.
Note on AN1467: Formula Value.
Note on AN1469: Formula Value.
Note on AN1471: Formula Value.
Note on AN1473: Formula Value.
Note on AN1475: Formula Value.
Note on AN1477: Formula Value.
Note on AN1479: Formula Value.
Note on AN1481: Formula Value.
Note on AN1483: Formula Value.
Note on AN1485: Formula Value.
Note on AN1487: Formula Value.
Note on AN1584: Formula Value.
Note on AN1586: Formula Value.
Note on AN1588: Formula Value.
Note on AN1590: Formula Value.
Note on AN1592: Formula Value.
Note on AN1594: Formula Value.
Note on AN1596: Formula Value.
Note on AN1598: Formula Value.
Note on AN1600: Formula Value.
Note on AN1602: Formula Value.
Note on AN1604: Formula Value.
Note on AN1606: Formula Value.
Note on AN1608: Formula Value.
Note on AN1610: Formula Value.
Note on AN1612: Formula Value.
Note on AN1614: Formula Value.
Note on AN1616: Formula Value.
Note on AN1618: Formula Value.
Note on AN1620: Formula Value.
Note on AN1622: Formula Value.
Note on AN1624: Formula Value.
Note on AN1626: Formula Value.
Note on AN1628: Formula Value.
Note on AN1630: Formula Value.
Note on AN1632: Formula Value.
Note on AN1634: Formula Value.
Note on AN1636: Formula Value.
Note on AN1638: Formula Value.
Note on AN1640: Formula Value.
Note on AN1642: Formula Value.
Note on AN1644: Formula Value.
Note on AN1646: Formula Value.
Note on AN1648: Formula Value.
Note on AN1650: Formula Value.
Note on AN1652: Formula Value.
Note on AN1654: Formula Value.
Note on AN1656: Formula Value.
Note on AN1658: Formula Value.
Note on AN1660: Formula Value.
Note on AN1662: Formula Value.
Note on AN1664: Formula Value.
Note on AN1666: Formula Value.
Note on AN1668: Formula Value.
Note on AN1670: Formula Value.
Note on AN1672: Formula Value.
Note on AN1674: Formula Value.
Note on AN1676: Formula Value.
Note on AN1678: Formula Value.
Note on AN1680: Formula Value.
Note on AN1682: Formula Value.
Note on AN1684: Formula Value.
Note on AN1686: Formula Value.
Note on AN1688: Formula Value.
Note on AN1690: Formula Value.
Note on AN1692: Formula Value.
Note on AN1694: Formula Value.
Note on AN1696: Formula Value.
Note on AN1697: Formula Value.
Note on AN1698: Formula Value.
Note on AN1699: Formula Value.
Note on AN1700: Formula Value.
Note on AN1701: Formula Value.
Note on AN1702: Formula Value.
Note on AN1703: Formula Value.
Note on AN1705: Formula Value.
Note on AN1707: Formula Value.
Note on AN1709: Formula Value.
Note on AN1711: Formula Value.
Note on AN1713: Formula Value.
Note on AN1715: Formula Value.
Note on AN1717: Formula Value.
Note on AN1719: Formula Value.
Note on AN1721: Formula Value.
Note on AN1723: Formula Value.
Note on AN1725: Formula Value.
Note on AN1727: Formula Value.
Note on AN1729: Formula Value.
Note on AN1731: Formula Value.
Note on AN1733: Formula Value.
Note on AN1735: Formula Value.
Note on AN1737: Formula Value.
Note on AN1739: Formula Value.
Note on AN1741: Formula Value.
Note on AN1761: Formula Value.
Note on AN1762: Formula Value.
Note on AN1763: Formula Value.
Note on AN1765: Formula Value.
Note on AN1767: Formula Value.
Note on AN1769: Formula Value.
Note on AN1771: Formula Value.
Note on AN1773: Formula Value.
Note on AN1775: Formula Value.
Note on AN1777: Formula Value.
Note on AN1779: Formula Value.
Note on AN1781: Formula Value.
Note on AN1783: Formula Value.
Note on AN1785: Formula Value.
Note on AN1787: Formula Value.
Note on AN1789: Formula Value.
Note on AN1791: Formula Value.
Note on AN1793: Formula Value.
Note on AN1795: Formula Value.
Note on AN1797: Formula Value.
Note on AN1799: Formula Value.
Note on AN1801: Formula Value.
Note on AN1844: Formula Value.
Note on AN1846: Formula Value.
Note on AN1848: Formula Value.
Note on AN1850: Formula Value.
Note on AN1852: Formula Value.
Note on AN1854: Formula Value.
Note on AN1856: Formula Value.
Note on AN1858: Formula Value.
Note on AN1860: Formula Value.
Note on AN1862: Formula Value.
Note on AN1864: Formula Value.
Note on AN1866: Formula Value.
Note on AN1868: Formula Value.
Note on AN1870: Formula Value.
Note on AN1872: Formula Value.
Note on AN1874: Formula Value.
Note on AN1876: Formula Value.
Note on AN1878: Formula Value.
Note on AN1880: Formula Value.
Note on AN1882: Formula Value.
Note on AN1884: Formula Value.
Note on AN1886: Formula Value.
Note on AN1888: Formula Value.
Note on AN1890: Formula Value.
Note on AN1892: Formula Value.
Note on AN1894: Formula Value.
Note on AN1896: Formula Value.
Note on AN1898: Formula Value.
Note on AN1900: Formula Value.
Note on AN1902: Formula Value.
Note on AN1904: Formula Value.
Note on AN1906: Formula Value.
Note on AN1908: Formula Value.
Note on AN1910: Formula Value.
Note on AN1912: Formula Value.
Note on AN1914: Formula Value.
Note on AN1916: Formula Value.
Note on AN1918: Formula Value.
Note on AN1920: Formula Value.
Note on AN1922: Formula Value.
Note on AN1924: Formula Value.
Note on AN1926: Formula Value.
Note on AN1928: Formula Value.
Note on AN1930: Formula Value.
Note on AN1932: Formula Value.
Note on AN1934: Formula Value.
Note on AN1936: Formula Value.
Note on AN1938: Formula Value.
Note on AN1940: Formula Value.
Note on AN1942: Formula Value.
Note on AN1944: Formula Value.
Note on AN1946: Formula Value.
Note on AN1948: Formula Value.
Note on AN1950: Formula Value.
Note on AN1952: Formula Value.
Note on AN1954: Formula Value.
Note on AN1956: Formula Value.
Note on AN1958: Formula Value.
Note on AN1960: Formula Value.
Note on AN1962: Formula Value.
Note on AN1964: Formula Value.
Note on AN1966: Formula Value.
Note on AN1968: Formula Value.
Note on AN1970: Formula Value.
Note on AN1972: Formula Value.
Note on AN1974: Formula Value.
Note on AN1976: Formula Value.
Note on AN1978: Formula Value.
Note on AN1980: Formula Value.
Note on AN1982: Formula Value.
Note on AN1984: Formula Value.
Note on AN1986: Formula Value.
Note on AN1988: Formula Value.
Note on AN1990: Formula Value.
Note on AN1992: Formula Value.
Note on AN1994: Formula Value.
Note on AN1996: Formula Value.
Note on AN1998: Formula Value.
Note on AN2000: Formula Value.
Note on AN2002: Formula Value.
Note on AN2004: Formula Value.
Note on AN2006: Formula Value.
Note on AN2008: Formula Value.
Note on AN2010: Formula Value.
Note on AN2012: Formula Value.
Note on AN2014: Formula Value.
Note on AN2016: Formula Value.
Note on AN2018: Formula Value.
Note on AN2020: Formula Value.
Note on AN2022: Formula Value.
Note on AN2024: Formula Value.
Note on AN2026: Formula Value.
Note on AN2028: Formula Value.
Note on AN2030: Formula Value.
Note on AN2032: Formula Value.
Note on AN2034: Formula Value.
Note on AN2036: Formula Value.
Note on AN2038: Formula Value.
Note on AN2040: Formula Value.
Note on AN2042: Formula Value.
Note on AN2044: Formula Value.
Note on AN2046: Formula Value.
Note on AN2048: Formula Value.
Note on AN2050: Formula Value.
Note on AN2052: Formula Value.
Note on AN2054: Formula Value.
Note on AN2056: Formula Value.
Note on AN2058: Formula Value.
Note on AN2060: Formula Value.
Note on AN2062: Formula Value.
Note on AN2064: Formula Value.
Note on AN2066: Formula Value.
Note on AN2068: Formula Value.
Note on AN2070: Formula Value.
Note on AN2071: Formula Value.
Note on AN2073: Formula Value.
Note on AN2078: Formula Value.
Note on AN2119: Formula Value.
Note on AN2128: Formula Value.
Note on AN2149: Formula Value.
Note on AN2150: Formula Value.
Note on AN2159: Formula Value.
Note on AN2160: Formula Value.
Note on AN2161: Formula Value.
Note on AN2162: Formula Value.
Note on AN2163: Formula Value.
Note on AN2164: Formula Value.
Note on AN2165: Formula Value.
Note on AN2166: Formula Value.
Note on AN2167: Formula Value.
Note on AN2168: Formula Value.
Note on AN2169: Formula Value.

## MeasureSectors
Measure Reference Number | Version Number | Sector | Sub Sector
972 | 1 | Residential
972 | 2 | Residential
972 | 3 | Residential
973 | 1 | Residential | Single Family
973 | 2 | Residential | Single Family
974 | 1 | Residential
974 | 2 | Residential
974 | 3 | Residential
975 | 1 | Residential | Single Family
975 | 2 | Residential | Single Family
857 | 1 | Residential
857 | 2 | Residential
857 | 3 | Residential
873 | 1 | Residential | Single Family
1042 | 1 | Residential | Single Family
1220 | 1 | Residential | Multi Family
874 | 2 | Residential | Single Family
874 | 1 | Residential | Single Family
1207 | 1 | Residential | Single Family
1043 | 1 | Residential | Single Family
1007 | 1 | Residential
915 | 1 | Residential
915 | 2 | Residential
916 | 1 | Residential
916 | 2 | Residential
918 | 1 | Residential
918 | 2 | Residential
981 | 1 | Residential
919 | 1 | Residential
919 | 2 | Residential
919 | 3 | Residential
1048 | 1 | Residential
920 | 1 | Residential
920 | 2 | Residential
920 | 3 | Residential
1049 | 1 | Residential
922 | 1 | Residential
922 | 2 | Residential
922 | 3 | Residential
1051 | 1 | Residential
1051 | 2 | Residential
982 | 1 | Residential
983 | 1 | Residential
923 | 1 | Residential
923 | 2 | Residential
923 | 3 | Residential
1052 | 1 | Residential
924 | 1 | Residential
924 | 2 | Residential
924 | 3 | Residential
1053 | 1 | Residential
926 | 1 | Residential
926 | 2 | Residential
926 | 3 | Residential
1055 | 1 | Residential
984 | 1 | Residential
985 | 1 | Residential
1239 | 2 | Residential
1266 | 1 | Residential | Multi Family
1268 | 1 | Residential | Multi Family
1239 | 1 | Residential
1240 | 2 | Residential
1270 | 1 | Residential | Multi Family
1271 | 1 | Residential | Multi Family
1269 | 1 | Residential | Multi Family
1240 | 1 | Residential
1267 | 1 | Residential | Multi Family
917 | 1 | Residential
917 | 2 | Residential
921 | 1 | Residential
921 | 2 | Residential
921 | 3 | Residential
1050 | 1 | Residential
925 | 1 | Residential
925 | 2 | Residential
925 | 3 | Residential
1054 | 1 | Residential
945 | 1 | Residential
945 | 2 | Residential
945 | 3 | Residential
944 | 1 | Residential
944 | 2 | Residential
944 | 3 | Residential
1069 | 1 | Residential
1069 | 2 | Residential
1001 | 1 | Residential
1070 | 1 | Residential
947 | 2 | Residential
947 | 3 | Residential
946 | 1 | Residential
946 | 2 | Residential
946 | 3 | Residential
1071 | 1 | Residential
1071 | 2 | Residential
1002 | 1 | Residential
947 | 1 | Residential
1072 | 1 | Residential
1003 | 1 | Residential
949 | 2 | Residential
949 | 3 | Residential
948 | 1 | Residential
948 | 2 | Residential
948 | 3 | Residential
1073 | 1 | Residential
1073 | 2 | Residential
949 | 1 | Residential
1074 | 1 | Residential
1004 | 1 | Residential
875 | 1 | Residential
876 | 1 | Residential
1044 | 1 | Residential
877 | 1 | Residential
877 | 2 | Residential
878 | 1 | Residential
879 | 1 | Residential
880 | 1 | Residential
880 | 2 | Residential
1209 | 1 | Residential | Multi Family
1208 | 1 | Residential | Single Family
1208 | 2 | Residential | Single Family
875 | 2 | Residential
876 | 2 | Residential
881 | 2 | Residential
1210 | 1 | Residential | Single Family
881 | 1 | Residential
858 | 1 | Residential
858 | 2 | Residential
883 | 1 | Residential
883 | 2 | Residential
954 | 1 | Residential
954 | 2 | Residential
1078 | 1 | Residential
1188 | 1 | Residential
1189 | 1 | Residential
1186 | 1 | Residential
1187 | 1 | Residential
1190 | 1 | Residential
1008 | 1 | Residential
1008 | 2 | Residential
1009 | 1 | Residential | Single Family
1009 | 2 | Residential | Single Family
1010 | 1 | Residential
1010 | 2 | Residential
1011 | 1 | Residential | Single Family
1011 | 2 | Residential | Single Family
884 | 1 | Residential
884 | 2 | Residential
955 | 1 | Residential
955 | 2 | Residential
1079 | 1 | Residential
1012 | 1 | Residential
1012 | 2 | Residential
1013 | 1 | Residential | Single Family
1013 | 2 | Residential | Single Family
885 | 1 | Residential
885 | 2 | Residential
956 | 1 | Residential
956 | 2 | Residential
1080 | 1 | Residential
1014 | 1 | Residential
886 | 1 | Residential
957 | 1 | Residential
1081 | 1 | Residential
887 | 1 | Residential
887 | 2 | Residential
958 | 1 | Residential
958 | 2 | Residential
1082 | 1 | Residential
1015 | 1 | Residential
1016 | 1 | Residential
888 | 1 | Residential
888 | 2 | Residential
959 | 1 | Residential
959 | 2 | Residential
1083 | 1 | Residential
1017 | 1 | Residential
889 | 1 | Residential
889 | 2 | Residential
960 | 1 | Residential
960 | 2 | Residential
1084 | 1 | Residential
961 | 1 | Residential
1 | 1 | Residential
1 | 2 | Residential
986 | 1 | Residential
927 | 1 | Residential | Single Family
927 | 2 | Residential | Single Family
927 | 3 | Residential | Single Family
987 | 1 | Residential
928 | 1 | Residential | Single Family
928 | 2 | Residential | Single Family
928 | 3 | Residential | Single Family
1056 | 1 | Residential | Single Family
988 | 1 | Residential
929 | 1 | Residential | Single Family
929 | 2 | Residential | Single Family
929 | 3 | Residential | Single Family
1057 | 1 | Residential | Single Family
989 | 1 | Residential
930 | 1 | Residential | Single Family
930 | 2 | Residential | Single Family
930 | 3 | Residential | Single Family
1058 | 1 | Residential | Single Family
990 | 1 | Residential
931 | 1 | Residential | Single Family
931 | 2 | Residential | Single Family
931 | 3 | Residential | Single Family
1059 | 1 | Residential | Single Family
1242 | 1 | Residential
1242 | 2 | Residential
1243 | 1 | Residential
1243 | 2 | Residential
1264 | 1 | Residential
1225 | 1 | Residential | Multi Family
1225 | 2 | Residential | Multi Family
1260 | 1 | Residential
1224 | 1 | Residential | Single Family
1259 | 1 | Residential
1226 | 1 | Residential
1226 | 2 | Residential
1226 | 3 | Residential
976 | 1 | Residential
977 | 1 | Residential
978 | 1 | Residential
979 | 1 | Residential
980 | 1 | Residential
905 | 1 | Residential
905 | 2 | Residential
1046 | 1 | Residential
1046 | 2 | Residential
906 | 1 | Residential
906 | 2 | Residential
1047 | 1 | Residential
1047 | 2 | Residential
1250 | 1 | Residential
1250 | 2 | Residential
1252 | 1 | Residential
1252 | 2 | Residential
1253 | 1 | Residential
1253 | 2 | Residential
1251 | 1 | Residential
1251 | 2 | Residential
908 | 2 | Residential
908 | 3 | Residential
1257 | 1 | Residential
1257 | 2 | Residential
907 | 1 | Residential
907 | 2 | Residential
907 | 3 | Residential
1028 | 1 | Residential
1029 | 1 | Residential
911 | 2 | Residential
911 | 3 | Residential
1244 | 1 | Residential
1244 | 2 | Residential
910 | 1 | Residential
910 | 2 | Residential
910 | 3 | Residential
908 | 1 | Residential
911 | 1 | Residential
1179 | 1 | Residential
1171 | 1 | Residential
1177 | 1 | Residential
1177 | 2 | Residential
1177 | 3 | Residential
1175 | 1 | Residential
1176 | 1 | Residential
1170 | 1 | Residential
968 | 1 | Residential
968 | 2 | Residential
968 | 3 | Residential
1221 | 1 | Residential | Single Family
1221 | 2 | Residential | Single Family
1180 | 1 | Residential
1182 | 1 | Residential
1173 | 1 | Residential
1181 | 1 | Residential
1181 | 2 | Residential
1181 | 3 | Residential
1183 | 1 | Residential
1174 | 1 | Residential
2 | 1 | Residential
2 | 2 | Residential
1060 | 2 | Residential
932 | 1 | Residential
932 | 2 | Residential
1060 | 1 | Residential
1248 | 1 | Residential
1248 | 2 | Residential
1249 | 1 | Residential
1249 | 2 | Residential
1218 | 1 | Residential | Single Family
1219 | 1 | Residential | Single Family
933 | 1 | Residential
933 | 2 | Residential
1061 | 1 | Residential
934 | 1 | Residential
934 | 2 | Residential
934 | 3 | Residential
1062 | 1 | Residential
935 | 1 | Residential
935 | 2 | Residential
935 | 3 | Residential
1063 | 1 | Residential
1063 | 2 | Residential
1247 | 1 | Residential
1247 | 2 | Residential
913 | 1 | Residential
913 | 2 | Residential
914 | 1 | Residential
914 | 2 | Residential
1232 | 1 | Residential
1232 | 2 | Residential
872 | 1 | Residential
872 | 2 | Residential
872 | 3 | Residential
902 | 1 | Residential
1092 | 1 | Residential
952 | 1 | Residential
1077 | 1 | Residential
1223 | 1 | Residential
1245 | 1 | Residential
999 | 1 | Residential
999 | 2 | Residential
999 | 3 | Residential
943 | 1 | Residential | Single Family
943 | 2 | Residential | Single Family
943 | 3 | Residential | Single Family
1000 | 1 | Residential | Single Family
1000 | 2 | Residential | Single Family
941 | 1 | Residential
941 | 2 | Residential
941 | 3 | Residential
1230 | 1 | Residential
1222 | 1 | Residential
1018 | 1 | Residential
1018 | 2 | Residential
1018 | 3 | Residential
1019 | 1 | Residential | Single Family
1019 | 2 | Residential | Single Family
1019 | 3 | Residential | Single Family
890 | 1 | Residential
890 | 2 | Residential
962 | 1 | Residential
1085 | 1 | Residential
962 | 2 | Residential
962 | 3 | Residential
1204 | 1 | Residential
1204 | 2 | Residential
1263 | 1 | Residential
1203 | 1 | Residential
1203 | 2 | Residential
1202 | 1 | Residential
1202 | 2 | Residential
1227 | 1 | Residential
1227 | 2 | Residential
1227 | 3 | Residential
1020 | 1 | Residential | Single Family
1020 | 2 | Residential | Single Family
1020 | 3 | Residential | Single Family
891 | 1 | Residential
891 | 2 | Residential
963 | 1 | Residential
963 | 2 | Residential
963 | 3 | Residential
1086 | 1 | Residential
1021 | 1 | Residential
1021 | 2 | Residential
1021 | 3 | Residential
1022 | 1 | Residential
1023 | 1 | Residential | Single Family
892 | 1 | Residential
892 | 2 | Residential
964 | 1 | Residential
1087 | 1 | Residential
1022 | 2 | Residential
1022 | 3 | Residential
1023 | 2 | Residential | Single Family
1023 | 3 | Residential | Single Family
964 | 2 | Residential
964 | 3 | Residential
1205 | 1 | Residential
1205 | 2 | Residential
1024 | 1 | Residential
1025 | 1 | Residential | Single Family
893 | 1 | Residential
893 | 2 | Residential
965 | 1 | Residential
1088 | 1 | Residential
1024 | 2 | Residential
1024 | 3 | Residential
1025 | 2 | Residential | Single Family
1025 | 3 | Residential | Single Family
965 | 2 | Residential
965 | 3 | Residential
1206 | 1 | Residential
1206 | 2 | Residential
1231 | 1 | Residential
1231 | 2 | Residential
1026 | 1 | Residential
1026 | 2 | Residential
1026 | 3 | Residential
1027 | 1 | Residential | Single Family
1027 | 2 | Residential | Single Family
1027 | 3 | Residential | Single Family
894 | 1 | Residential
894 | 2 | Residential
966 | 1 | Residential
966 | 2 | Residential
966 | 3 | Residential
1089 | 1 | Residential
903 | 1 | Residential
904 | 1 | Residential
1033 | 1 | Residential
1033 | 2 | Residential
1033 | 3 | Residential
1034 | 1 | Residential | Single Family
1034 | 2 | Residential | Single Family
1034 | 3 | Residential | Single Family
865 | 3 | Residential
1228 | 2 | Residential
1228 | 3 | Residential
865 | 1 | Residential
865 | 2 | Residential
1164 | 1 | Residential
864 | 1 | Residential | Single Family
897 | 1 | Residential | Single Family
864 | 2 | Residential | Single Family
864 | 4 | Residential | Single Family
1228 | 1 | Residential
1273 | 1 | Residential | Multi Family
1274 | 1 | Residential
1274 | 2 | Residential
1262 | 1 | Residential
1201 | 1 | Residential
1200 | 1 | Residential
1261 | 1 | Residential
867 | 1 | Residential
1166 | 1 | Residential
867 | 2 | Residential
867 | 3 | Residential
866 | 1 | Residential | Single Family
898 | 1 | Residential | Single Family
866 | 2 | Residential | Single Family
866 | 3 | Residential | Single Family
1229 | 1 | Residential
1229 | 2 | Residential
1229 | 3 | Residential
1035 | 1 | Residential
1035 | 2 | Residential
1035 | 3 | Residential
1036 | 1 | Residential | Single Family
1036 | 2 | Residential | Single Family
1036 | 3 | Residential | Single Family
953 | 1 | Residential
967 | 1 | Residential
967 | 2 | Residential
1090 | 1 | Residential
942 | 1 | Residential
942 | 2 | Residential
942 | 3 | Residential
868 | 1 | Residential
1168 | 1 | Residential
868 | 2 | Residential
868 | 3 | Residential
1037 | 1 | Residential
1037 | 2 | Residential
1037 | 3 | Residential
1167 | 1 | Residential
899 | 1 | Residential | Single Family
1167 | 2 | Residential
1167 | 3 | Residential
1038 | 1 | Residential | Single Family
1038 | 2 | Residential | Single Family
1272 | 1 | Residential
1272 | 2 | Residential
860 | 1 | Residential
859 | 1 | Residential
859 | 2 | Residential
859 | 3 | Residential
1233 | 1 | Residential
1005 | 1 | Residential
1005 | 2 | Residential
950 | 1 | Residential | Single Family
1075 | 1 | Residential | Single Family
1234 | 1 | Residential
1006 | 1 | Residential
1006 | 2 | Residential
951 | 1 | Residential | Single Family
1076 | 1 | Residential | Single Family
1235 | 1 | Residential
991 | 1 | Residential
991 | 2 | Residential
936 | 1 | Residential | Single Family
1064 | 1 | Residential | Single Family
1236 | 1 | Residential
992 | 1 | Residential
992 | 2 | Residential
937 | 1 | Residential | Single Family
1065 | 1 | Residential | Single Family
1246 | 1 | Residential
995 | 1 | Residential
995 | 2 | Residential
995 | 3 | Residential
995 | 4 | Residential
940 | 1 | Residential | Single Family
940 | 2 | Residential | Single Family
940 | 3 | Residential | Single Family
996 | 1 | Residential | Single Family
996 | 2 | Residential | Single Family
996 | 3 | Residential | Single Family
1068 | 1 | Residential | Single Family
997 | 1 | Residential
997 | 2 | Residential
1217 | 1 | Residential | Single Family
1213 | 1 | Residential | Single Family
998 | 1 | Residential
998 | 2 | Residential
1216 | 1 | Residential | Single Family
1214 | 1 | Residential | Single Family
1265 | 1 | Residential
1255 | 1 | Residential
1256 | 1 | Residential
1172 | 1 | Residential
1254 | 1 | Residential
3 | 1 | Residential
3 | 2 | Residential
4 | 1 | Residential
4 | 2 | Residential
1275 | 1 | Residential | Multi Family
1237 | 2 | Residential
1237 | 1 | Residential
1276 | 1 | Residential | Multi Family
1238 | 2 | Residential
1238 | 1 | Residential
993 | 1 | Residential
993 | 2 | Residential
993 | 3 | Residential
855 | 1 | Residential | Single Family
938 | 1 | Residential | Single Family
994 | 1 | Residential | Single Family
994 | 2 | Residential | Single Family
1066 | 1 | Residential | Single Family
856 | 1 | Residential | Single Family
856 | 2 | Residential | Single Family
939 | 1 | Residential | Single Family
939 | 2 | Residential | Single Family
1067 | 1 | Residential | Single Family
1258 | 1 | Residential
1258 | 2 | Residential
1031 | 3 | Residential | Single Family
1030 | 1 | Residential
1030 | 2 | Residential
1030 | 3 | Residential
1031 | 2 | Residential | Single Family
1031 | 1 | Residential | Single Family
862 | 1 | Residential
862 | 3 | Residential
895 | 1 | Residential
895 | 2 | Residential
861 | 1 | Residential
861 | 2 | Residential
861 | 3 | Residential
969 | 1 | Residential
871 | 1 | Residential
871 | 2 | Residential
901 | 1 | Residential
1091 | 1 | Residential
1039 | 1 | Residential
1039 | 2 | Residential
1041 | 1 | Residential | Single Family
1041 | 2 | Residential | Single Family
870 | 1 | Residential
900 | 1 | Residential
1032 | 1 | Residential
1215 | 1 | Residential | Single Family
863 | 1 | Residential
863 | 2 | Residential
896 | 1 | Residential
896 | 2 | Residential
1212 | 1 | Residential | Multi Family
970 | 1 | Residential
970 | 2 | Residential
971 | 1 | Residential
882 | 2 | Residential | Single Family
882 | 4 | Residential | Single Family
882 | 1 | Residential | Single Family
1211 | 1 | Residential | Single Family
1045 | 1 | Residential | Single Family
1045 | 2 | Residential | Single Family
726 | 1 | Business
726-1 | 1 | Business
727 | 1 | Business
728 | 1 | Business
2800 | 1 | Business
2801 | 1 | Business
2802 | 1 | Business
2803 | 1 | Business
2804 | 1 | Business
2805 | 1 | Business
2806 | 1 | Business
2807 | 1 | Business
2808 | 1 | Business
2809 | 1 | Business
2810 | 1 | Business
2811 | 1 | Business
2812 | 1 | Business
2813 | 1 | Business
2814 | 1 | Business
2815 | 1 | Business
2816 | 1 | Business
2817 | 1 | Business
2818 | 1 | Business
2819 | 1 | Business
2820 | 1 | Business
2821 | 1 | Business
691 | 1 | Business
692 | 1 | Business
674 | 1 | Business
1169 | 1 | Business
3027 | 1 | Business
3027-1 | 1 | Business
693 | 1 | Business
679 | 1 | Business
679 | 2 | Business
679 | 3 | Business
1094 | 1 | Business
1093 | 1 | Business
675 | 1 | Business
676 | 1 | Business
677 | 1 | Business
678 | 1 | Business
686 | 1 | Business
687 | 1 | Business
695 | 1 | Business
683 | 1 | Business
684 | 1 | Business
685 | 1 | Business
3058 | 1 | Business
3000 | 1 | Business
1184 | 1 | Business
1191 | 1 | Business
697 | 1 | Business
3085 | 1 | Business
681 | 1 | Business
3046 | 1 | Business
3045 | 1 | Business
3047 | 1 | Business
3052 | 1 | Business
3051 | 1 | Business
3053 | 1 | Business
3049 | 1 | Business
3048 | 1 | Business
3050 | 1 | Business
3040 | 1 | Business
3041 | 1 | Business
3043 | 1 | Business
3042 | 1 | Business
3044 | 1 | Business
673 | 1 | Business
4001 | 1 | Business
671 | 1 | Business
2732 | 1 | Business
2733 | 1 | Business
705 | 1 | Business
705 | 2 | Business
2734 | 1 | Business
2735 | 1 | Business
2736 | 1 | Business
2737 | 1 | Business
706 | 1 | Business
706 | 2 | Business
2738 | 1 | Business
2739 | 1 | Business
2740 | 1 | Business
707 | 1 | Business
707 | 2 | Business
2741 | 1 | Business
2742 | 1 | Business
2721 | 1 | Business
2722 | 1 | Business
708 | 1 | Business
708 | 2 | Business
2723 | 1 | Business
2724 | 1 | Business
2725 | 1 | Business
2726 | 1 | Business
2727 | 1 | Business
2728 | 1 | Business
709 | 1 | Business
709 | 2 | Business
2729 | 1 | Business
710 | 1 | Business
710 | 2 | Business
2730 | 1 | Business
2731 | 1 | Business
2709 | 1 | Business
2710 | 1 | Business
711 | 1 | Business
2712 | 1 | Business
2713 | 1 | Business
2714 | 1 | Business
2715 | 1 | Business
712 | 1 | Business
2716 | 1 | Business
2717 | 1 | Business
2718 | 1 | Business
713 | 1 | Business
2719 | 1 | Business
2720 | 1 | Business
2771 | 1 | Business
2772 | 1 | Business
714 | 1 | Business
714 | 2 | Business
2773 | 1 | Business
2774 | 1 | Business
2775 | 1 | Business
2776 | 1 | Business
2777 | 1 | Business
715 | 1 | Business
715 | 2 | Business
2778 | 1 | Business
2779 | 1 | Business
2780 | 1 | Business
2781 | 1 | Business
2782 | 1 | Business
716 | 1 | Business
716 | 2 | Business
2783 | 1 | Business
2784 | 1 | Business
2757 | 1 | Business
2758 | 1 | Business
717 | 1 | Business
717 | 2 | Business
2759 | 1 | Business
2760 | 1 | Business
2761 | 1 | Business
2762 | 1 | Business
2763 | 1 | Business
718 | 1 | Business
718 | 2 | Business
2764 | 1 | Business
2765 | 1 | Business
2766 | 1 | Business
2767 | 1 | Business
2768 | 1 | Business
719 | 1 | Business
719 | 2 | Business
2769 | 1 | Business
2770 | 1 | Business
2743 | 1 | Business
2744 | 1 | Business
720 | 1 | Business
720 | 2 | Business
2745 | 1 | Business
2746 | 1 | Business
2747 | 1 | Business
2748 | 1 | Business
2749 | 1 | Business
721 | 1 | Business
721 | 2 | Business
2750 | 1 | Business
2751 | 1 | Business
2752 | 1 | Business
2753 | 1 | Business
2754 | 1 | Business
722 | 1 | Business
722 | 2 | Business
2755 | 1 | Business
2756 | 1 | Business
3059 | 1 | Business
3060 | 1 | Business
3061 | 1 | Business
776-1 | 2 | Business | College/University
776-10 | 2 | Business | Elementary School
776-15 | 2 | Business | Exterior
776-19 | 2 | Business | Garage, 24/7
776-4 | 2 | Business | Garage
776-5 | 2 | Business | Grocery
776-11 | 2 | Business | Heavy Industry
776-12 | 2 | Business | High School/Middle School
776-6 | 2 | Business | Hospital
776-7 | 2 | Business | Hotel/Motel
776-13 | 2 | Business | Hotel/Motel
776-9 | 2 | Business | Light Industry
776-14 | 2 | Business | Miscellaneous
776-16 | 2 | Business | Multifamily Common Areas
776-8 | 2 | Business | Office
776-18 | 2 | Business | Religious Worship/Church
776-3 | 2 | Business | Restaurant
776-2 | 2 | Business | Retail/Service
776-20 | 2 | Business
731-1 | 2 | Business | College/University
731-10 | 2 | Business | Elementary School
731-15 | 2 | Business | Exterior
731-19 | 2 | Business | Garage, 24/7
731-4 | 2 | Business | Garage
731-5 | 2 | Business | Grocery
731-11 | 2 | Business | Heavy Industry
731-12 | 2 | Business | High School/Middle School
731-6 | 2 | Business | Hospital
731-7 | 2 | Business | Hotel/Motel
731-13 | 2 | Business | Hotel/Motel
731-9 | 2 | Business | Light Industry
731-14 | 2 | Business | Miscellaneous
731-16 | 2 | Business | Multifamily Common Areas
731-8 | 2 | Business | Office
731-18 | 2 | Business | Religious Worship/Church
731-3 | 2 | Business | Restaurant
731-2 | 2 | Business | Retail/Service
731-20 | 2 | Business
3084 | 1 | Business
738-1 | 3 | Business | College/University
738-10 | 3 | Business | Elementary School
738-15 | 3 | Business | Exterior
738-19 | 3 | Business | Garage, 24/7
738-4 | 3 | Business | Garage
738-5 | 3 | Business | Grocery
738-11 | 3 | Business | Heavy Industry
738-12 | 3 | Business | High School/Middle School
738-6 | 3 | Business | Hospital
738-7 | 3 | Business | Hotel/Motel
738-13 | 3 | Business | Hotel/Motel
738-9 | 3 | Business | Light Industry
738-14 | 3 | Business | Miscellaneous
738-16 | 3 | Business | Multifamily Common Areas
738-8 | 3 | Business | Office
738-18 | 3 | Business | Religious Worship/Church
738-3 | 3 | Business | Restaurant
738-2 | 3 | Business | Retail/Service
738-20 | 3 | Business
739-1 | 3 | Business | College/University
739-10 | 3 | Business | Elementary School
739-15 | 3 | Business | Exterior
739-19 | 3 | Business | Garage, 24/7
739-4 | 3 | Business | Garage
739-5 | 3 | Business | Grocery
739-11 | 3 | Business | Heavy Industry
739-12 | 3 | Business | High School/Middle School
739-6 | 3 | Business | Hospital
739-7 | 3 | Business | Hotel/Motel
739-13 | 3 | Business | Hotel/Motel
739-9 | 3 | Business | Light Industry
739-14 | 3 | Business | Miscellaneous
739-16 | 3 | Business | Multifamily Common Areas
739-8 | 3 | Business | Office
739-18 | 3 | Business | Religious Worship/Church
739-3 | 3 | Business | Restaurant
739-2 | 3 | Business | Retail/Service
739-20 | 3 | Business
3075 | 1 | Business
757-1 | 2 | Business | College/University
757-10 | 2 | Business | Elementary School
757-15 | 2 | Business | Exterior
757-19 | 2 | Business | Garage, 24/7
757-4 | 2 | Business | Garage
757-5 | 2 | Business | Grocery
757-11 | 2 | Business | Heavy Industry
757-12 | 2 | Business | High School/Middle School
757-6 | 2 | Business | Hospital
757-7 | 2 | Business | Hotel/Motel
757-13 | 2 | Business | Hotel/Motel
757-9 | 2 | Business | Light Industry
757-14 | 2 | Business | Miscellaneous
757-16 | 2 | Business | Multifamily Common Areas
757-8 | 2 | Business | Office
757-18 | 2 | Business | Religious Worship/Church
757-3 | 2 | Business | Restaurant
757-2 | 2 | Business | Retail/Service
757-20 | 2 | Business
758-1 | 2 | Business | College/University
758-10 | 2 | Business | Elementary School
758-15 | 2 | Business | Exterior
758-19 | 2 | Business | Garage, 24/7
758-4 | 2 | Business | Garage
758-5 | 2 | Business | Grocery
758-11 | 2 | Business | Heavy Industry
758-12 | 2 | Business | High School/Middle School
758-6 | 2 | Business | Hospital
758-7 | 2 | Business | Hotel/Motel
758-13 | 2 | Business | Hotel/Motel
758-9 | 2 | Business | Light Industry
758-14 | 2 | Business | Miscellaneous
758-16 | 2 | Business | Multifamily Common Areas
758-8 | 2 | Business | Office
758-18 | 2 | Business | Religious Worship/Church
758-3 | 2 | Business | Restaurant
758-2 | 2 | Business | Retail/Service
758-20 | 2 | Business
759-1 | 2 | Business | College/University
759-10 | 2 | Business | Elementary School
759-15 | 2 | Business | Exterior
759-19 | 2 | Business | Garage, 24/7
759-4 | 2 | Business | Garage
759-5 | 2 | Business | Grocery
759-11 | 2 | Business | Heavy Industry
759-12 | 2 | Business | High School/Middle School
759-6 | 2 | Business | Hospital
759-7 | 2 | Business | Hotel/Motel
759-13 | 2 | Business | Hotel/Motel
759-9 | 2 | Business | Light Industry
759-14 | 2 | Business | Miscellaneous
759-16 | 2 | Business | Multifamily Common Areas
759-8 | 2 | Business | Office
759-18 | 2 | Business | Religious Worship/Church
759-3 | 2 | Business | Restaurant
759-2 | 2 | Business | Retail/Service
759-20 | 2 | Business
760-1 | 2 | Business | College/University
760-10 | 2 | Business | Elementary School
760-15 | 2 | Business | Exterior
760-19 | 2 | Business | Garage, 24/7
760-4 | 2 | Business | Garage
760-5 | 2 | Business | Grocery
760-11 | 2 | Business | Heavy Industry
760-12 | 2 | Business | High School/Middle School
760-6 | 2 | Business | Hospital
760-7 | 2 | Business | Hotel/Motel
760-13 | 2 | Business | Hotel/Motel
760-9 | 2 | Business | Light Industry
760-14 | 2 | Business | Miscellaneous
760-16 | 2 | Business | Multifamily Common Areas
760-8 | 2 | Business | Office
760-18 | 2 | Business | Religious Worship/Church
760-3 | 2 | Business | Restaurant
760-2 | 2 | Business | Retail/Service
760-20 | 2 | Business
761-1 | 2 | Business | College/University
761-10 | 2 | Business | Elementary School
761-15 | 2 | Business | Exterior
761-19 | 2 | Business | Garage, 24/7
761-4 | 2 | Business | Garage
761-5 | 2 | Business | Grocery
761-11 | 2 | Business | Heavy Industry
761-12 | 2 | Business | High School/Middle School
761-6 | 2 | Business | Hospital
761-7 | 2 | Business | Hotel/Motel
761-13 | 2 | Business | Hotel/Motel
761-9 | 2 | Business | Light Industry
761-14 | 2 | Business | Miscellaneous
761-16 | 2 | Business | Multifamily Common Areas
761-8 | 2 | Business | Office
761-18 | 2 | Business | Religious Worship/Church
761-3 | 2 | Business | Restaurant
761-2 | 2 | Business | Retail/Service
761-20 | 2 | Business
762-1 | 3 | Business | College/University
762-10 | 3 | Business | Elementary School
762-15 | 3 | Business | Exterior
762-19 | 3 | Business | Garage, 24/7
762-4 | 3 | Business | Garage
762-5 | 3 | Business | Grocery
762-11 | 3 | Business | Heavy Industry
762-12 | 3 | Business | High School/Middle School
762-6 | 3 | Business | Hospital
762-7 | 3 | Business | Hotel/Motel
762-13 | 3 | Business | Hotel/Motel
762-9 | 3 | Business | Light Industry
762-14 | 3 | Business | Miscellaneous
762-16 | 3 | Business | Multifamily Common Areas
762-8 | 3 | Business | Office
762-18 | 3 | Business | Religious Worship/Church
762-3 | 3 | Business | Restaurant
762-2 | 3 | Business | Retail/Service
762-20 | 3 | Business
3003 | 1 | Business
3062 | 1 | Business
3063 | 1 | Business
779-1 | 1 | Business | College/University
779-10 | 1 | Business | Elementary School
779-15 | 1 | Business | Exterior
779-19 | 1 | Business | Garage, 24/7
779-4 | 1 | Business | Garage
779-5 | 1 | Business | Grocery
779-11 | 1 | Business | Heavy Industry
779-12 | 1 | Business | High School/Middle School
779-6 | 1 | Business | Hospital
779-7 | 1 | Business | Hotel/Motel
779-13 | 1 | Business | Hotel/Motel
779-9 | 1 | Business | Light Industry
779-14 | 1 | Business | Miscellaneous
779-16 | 1 | Business | Multifamily Common Areas
779-8 | 1 | Business | Office
779-18 | 1 | Business | Religious Worship/Church
779-3 | 1 | Business | Restaurant
779-2 | 1 | Business | Retail/Service
779-20 | 1 | Business
3004-1 | 2 | Business
3004-2 | 2 | Business
3005-1 | 2 | Business
3005-2 | 2 | Business
3006-1 | 1 | Business
3006-2 | 1 | Business
3007 | 2 | Business
3007-1 | 1 | Business
3008 | 2 | Business
3010 | 2 | Business
3009 | 1 | Business
3011 | 1 | Business
8001 | 1 | Business
8000 | 1 | Business
793-1 | 2 | Business | College/University
793-10 | 2 | Business | Elementary School
793-15 | 2 | Business | Exterior
793-19 | 2 | Business | Garage, 24/7
793-4 | 2 | Business | Garage
793-5 | 2 | Business | Grocery
793-11 | 2 | Business | Heavy Industry
793-12 | 2 | Business | High School/Middle School
793-6 | 2 | Business | Hospital
793-7 | 2 | Business | Hotel/Motel
793-13 | 2 | Business | Hotel/Motel
793-9 | 2 | Business | Light Industry
793-14 | 2 | Business | Miscellaneous
793-16 | 2 | Business | Multifamily Common Areas
793-8 | 2 | Business | Office
793-18 | 2 | Business | Religious Worship/Church
793-3 | 2 | Business | Restaurant
793-2 | 2 | Business | Retail/Service
793-20 | 2 | Business
3012 | 1 | Business
3013 | 2 | Business
3023 | 1 | Business
3024 | 1 | Business
3025 | 2 | Business
3026 | 2 | Business
3019 | 1 | Business
3020 | 1 | Business
3021 | 1 | Business
3022 | 1 | Business
3081 | 1 | Business
3082 | 1 | Business
3083 | 1 | Business
3076 | 1 | Business
3077 | 1 | Business
3079 | 1 | Business
3080 | 1 | Business
3016 | 1 | Business
786-1 | 2 | Business | College/University
786-10 | 2 | Business | Elementary School
786-15 | 2 | Business | Exterior
786-19 | 2 | Business | Garage, 24/7
786-4 | 2 | Business | Garage
786-5 | 2 | Business | Grocery
786-11 | 2 | Business | Heavy Industry
786-12 | 2 | Business | High School/Middle School
786-6 | 2 | Business | Hospital
786-7 | 2 | Business | Hotel/Motel
786-13 | 2 | Business | Hotel/Motel
786-9 | 2 | Business | Light Industry
786-14 | 2 | Business | Miscellaneous
786-16 | 2 | Business | Multifamily Common Areas
786-8 | 2 | Business | Office
786-18 | 2 | Business | Religious Worship/Church
786-3 | 2 | Business | Restaurant
786-2 | 2 | Business | Retail/Service
786-20 | 2 | Business
787-1 | 2 | Business | College/University
787-10 | 2 | Business | Elementary School
787-15 | 2 | Business | Exterior
787-19 | 2 | Business | Garage, 24/7
787-4 | 2 | Business | Garage
787-5 | 2 | Business | Grocery
787-11 | 2 | Business | Heavy Industry
787-12 | 2 | Business | High School/Middle School
787-6 | 2 | Business | Hospital
787-7 | 2 | Business | Hotel/Motel
787-13 | 2 | Business | Hotel/Motel
787-9 | 2 | Business | Light Industry
787-14 | 2 | Business | Miscellaneous
787-16 | 2 | Business | Multifamily Common Areas
787-8 | 2 | Business | Office
787-18 | 2 | Business | Religious Worship/Church
787-3 | 2 | Business | Restaurant
787-2 | 2 | Business | Retail/Service
787-20 | 2 | Business
781-1 | 1 | Business | College/University
781-10 | 1 | Business | Elementary School
781-15 | 1 | Business | Exterior
781-19 | 1 | Business | Garage, 24/7
781-4 | 1 | Business | Garage
781-5 | 1 | Business | Grocery
781-11 | 1 | Business | Heavy Industry
781-12 | 1 | Business | High School/Middle School
781-6 | 1 | Business | Hospital
781-7 | 1 | Business | Hotel/Motel
781-13 | 1 | Business | Hotel/Motel
781-9 | 1 | Business | Light Industry
781-14 | 1 | Business | Miscellaneous
781-16 | 1 | Business | Multifamily Common Areas
781-8 | 1 | Business | Office
781-18 | 1 | Business | Religious Worship/Church
781-3 | 1 | Business | Restaurant
781-2 | 1 | Business | Retail/Service
781-20 | 1 | Business
780-1 | 1 | Business | College/University
780-10 | 1 | Business | Elementary School
780-15 | 1 | Business | Exterior
780-19 | 1 | Business | Garage, 24/7
780-4 | 1 | Business | Garage
780-5 | 1 | Business | Grocery
780-11 | 1 | Business | Heavy Industry
780-12 | 1 | Business | High School/Middle School
780-6 | 1 | Business | Hospital
780-7 | 1 | Business | Hotel/Motel
780-13 | 1 | Business | Hotel/Motel
780-9 | 1 | Business | Light Industry
780-14 | 1 | Business | Miscellaneous
780-16 | 1 | Business | Multifamily Common Areas
780-8 | 1 | Business | Office
780-18 | 1 | Business | Religious Worship/Church
780-3 | 1 | Business | Restaurant
780-2 | 1 | Business | Retail/Service
780-20 | 1 | Business
3035 | 1 | Business
3036 | 1 | Business
3037 | 1 | Business
3038 | 1 | Business
3086 | 1 | Business
3088 | 1 | Business
1102-1 | 3 | Business
1102-10 | 3 | Business
1102-15 | 3 | Business
1102-19 | 3 | Business
1102-4 | 3 | Business
1102-5 | 3 | Business
1102-11 | 3 | Business
1102-12 | 3 | Business
1102-6 | 3 | Business
1102-7 | 3 | Business
1102-13 | 3 | Business
1102-9 | 3 | Business
1102-14 | 3 | Business
1102-16 | 3 | Business
1102-8 | 3 | Business
1102-18 | 3 | Business
1102-3 | 3 | Business
1102-2 | 3 | Business
1102-20 | 3 | Business
1106-1 | 3 | Business
1106-10 | 3 | Business
1106-15 | 3 | Business
1106-19 | 3 | Business
1106-4 | 3 | Business
1106-5 | 3 | Business
1106-11 | 3 | Business
1106-12 | 3 | Business
1106-6 | 3 | Business
1106-7 | 3 | Business
1106-13 | 3 | Business
1106-9 | 3 | Business
1106-14 | 3 | Business
1106-16 | 3 | Business
1106-8 | 3 | Business
1106-18 | 3 | Business
1106-3 | 3 | Business
1106-2 | 3 | Business
1106-20 | 3 | Business
3087 | 1 | Business
3089 | 1 | Business
776-1 | 1 | Business | College/University
776-10 | 1 | Business | Elementary School
776-15 | 1 | Business | Exterior
776-19 | 1 | Business | Garage, 24/7
776-4 | 1 | Business | Garage
776-5 | 1 | Business | Grocery
776-11 | 1 | Business | Heavy Industry
776-12 | 1 | Business | High School/Middle School
776-6 | 1 | Business | Hospital
776-7 | 1 | Business | Hotel/Motel
776-13 | 1 | Business | Hotel/Motel
776-9 | 1 | Business | Light Industry
776-14 | 1 | Business | Miscellaneous
776-16 | 1 | Business | Multifamily Common Areas
776-8 | 1 | Business | Office
776-18 | 1 | Business | Religious Worship/Church
776-3 | 1 | Business | Restaurant
776-2 | 1 | Business | Retail/Service
776-20 | 1 | Business
731-1 | 1 | Business | College/University
731-10 | 1 | Business | Elementary School
731-15 | 1 | Business | Exterior
731-19 | 1 | Business | Garage, 24/7
731-4 | 1 | Business | Garage
731-5 | 1 | Business | Grocery
731-11 | 1 | Business | Heavy Industry
731-12 | 1 | Business | High School/Middle School
731-6 | 1 | Business | Hospital
731-7 | 1 | Business | Hotel/Motel
731-13 | 1 | Business | Hotel/Motel
731-9 | 1 | Business | Light Industry
731-14 | 1 | Business | Miscellaneous
731-16 | 1 | Business | Multifamily Common Areas
731-8 | 1 | Business | Office
731-18 | 1 | Business | Religious Worship/Church
731-3 | 1 | Business | Restaurant
731-2 | 1 | Business | Retail/Service
731-20 | 1 | Business
3001 | 1 | Business
3002 | 1 | Business
746-1 | 1 | Business | College/University
746-1 | 2 | Business | College/University
745-10 | 1 | Business | Elementary School
745-10 | 2 | Business | Elementary School
745-15 | 1 | Business | Exterior
745-15 | 2 | Business | Exterior
745-19 | 1 | Business | Garage, 24/7
745-19 | 2 | Business | Garage, 24/7
745-4 | 1 | Business | Garage
745-4 | 2 | Business | Garage
745-5 | 1 | Business | Grocery
745-5 | 2 | Business | Grocery
745-11 | 1 | Business | Heavy Industry
745-11 | 2 | Business | Heavy Industry
745-12 | 1 | Business | High School/Middle School
745-12 | 2 | Business | High School/Middle School
745-6 | 1 | Business | Hospital
745-6 | 2 | Business | Hospital
745-7 | 1 | Business | Hotel/Motel
745-7 | 2 | Business | Hotel/Motel
745-13 | 1 | Business | Hotel/Motel
745-13 | 2 | Business | Hotel/Motel
745-9 | 1 | Business | Light Industry
745-9 | 2 | Business | Light Industry
745-14 | 1 | Business | Miscellaneous
745-14 | 2 | Business | Miscellaneous
745-16 | 1 | Business | Multifamily Common Areas
745-16 | 2 | Business | Multifamily Common Areas
745-8 | 1 | Business | Office
745-8 | 2 | Business | Office
745-18 | 1 | Business | Religious Worship/Church
745-18 | 2 | Business | Religious Worship/Church
745-3 | 1 | Business | Restaurant
745-3 | 2 | Business | Restaurant
745-2 | 1 | Business | Retail/Service
745-2 | 2 | Business | Retail/Service
745-20 | 1 | Business
745-20 | 2 | Business
749-1 | 1 | Business
749-1 | 2 | Business
749-10 | 1 | Business
749-10 | 2 | Business
749-15 | 1 | Business
749-15 | 2 | Business
749-19 | 1 | Business
749-19 | 2 | Business
749-4 | 1 | Business
749-4 | 2 | Business
749-5 | 1 | Business
749-5 | 2 | Business
749-11 | 1 | Business
749-11 | 2 | Business
749-12 | 1 | Business
749-12 | 2 | Business
749-6 | 1 | Business
749-6 | 2 | Business
749-7 | 1 | Business
749-7 | 2 | Business
749-13 | 1 | Business
749-13 | 2 | Business
749-9 | 1 | Business
749-9 | 2 | Business
749-14 | 1 | Business
749-14 | 2 | Business
749-16 | 1 | Business
749-16 | 2 | Business
749-8 | 1 | Business
749-8 | 2 | Business
749-18 | 1 | Business
749-18 | 2 | Business
749-3 | 1 | Business
749-3 | 2 | Business
749-2 | 1 | Business
749-2 | 2 | Business
749-20 | 1 | Business
749-20 | 2 | Business
773-1 | 1 | Business | College/University
773-1 | 2 | Business | College/University
773-10 | 1 | Business | Elementary School
773-10 | 2 | Business | Elementary School
773-15 | 1 | Business | Exterior
773-15 | 2 | Business | Exterior
773-19 | 1 | Business | Garage, 24/7
773-19 | 2 | Business | Garage, 24/7
773-4 | 1 | Business | Garage
773-4 | 2 | Business | Garage
773-5 | 1 | Business | Grocery
773-5 | 2 | Business | Grocery
773-11 | 1 | Business | Heavy Industry
773-11 | 2 | Business | Heavy Industry
773-12 | 1 | Business | High School/Middle School
773-12 | 2 | Business | High School/Middle School
773-6 | 1 | Business | Hospital
773-6 | 2 | Business | Hospital
773-7 | 1 | Business | Hotel/Motel
773-7 | 2 | Business | Hotel/Motel
773-13 | 1 | Business | Hotel/Motel
773-13 | 2 | Business | Hotel/Motel
773-9 | 1 | Business | Light Industry
773-9 | 2 | Business | Light Industry
773-14 | 1 | Business | Miscellaneous
773-14 | 2 | Business | Miscellaneous
773-16 | 1 | Business | Multifamily Common Areas
773-16 | 2 | Business | Multifamily Common Areas
773-8 | 1 | Business | Office
773-8 | 2 | Business | Office
773-18 | 1 | Business | Religious Worship/Church
773-18 | 2 | Business | Religious Worship/Church
773-3 | 1 | Business | Restaurant
773-3 | 2 | Business | Restaurant
773-2 | 1 | Business | Retail/Service
773-2 | 2 | Business | Retail/Service
773-20 | 1 | Business
773-20 | 2 | Business
784-1 | 1 | Business | College/University
784-10 | 1 | Business | Elementary School
784-15 | 1 | Business | Exterior
784-19 | 1 | Business | Garage, 24/7
784-4 | 1 | Business | Garage
784-5 | 1 | Business | Grocery
784-11 | 1 | Business | Heavy Industry
784-12 | 1 | Business | High School/Middle School
784-6 | 1 | Business | Hospital
784-7 | 1 | Business | Hotel/Motel
784-13 | 1 | Business | Hotel/Motel
784-9 | 1 | Business | Light Industry
784-14 | 1 | Business | Miscellaneous
784-16 | 1 | Business | Multifamily Common Areas
784-8 | 1 | Business | Office
784-18 | 1 | Business | Religious Worship/Church
784-3 | 1 | Business | Restaurant
784-2 | 1 | Business | Retail/Service
784-20 | 1 | Business
738-1 | 1 | Business | College/University
738-1 | 2 | Business | College/University
738-10 | 1 | Business | Elementary School
738-10 | 2 | Business | Elementary School
738-15 | 1 | Business | Exterior
738-15 | 2 | Business | Exterior
738-19 | 1 | Business | Garage, 24/7
738-19 | 2 | Business | Garage, 24/7
738-4 | 1 | Business | Garage
738-4 | 2 | Business | Garage
738-5 | 1 | Business | Grocery
738-5 | 2 | Business | Grocery
738-11 | 1 | Business | Heavy Industry
738-11 | 2 | Business | Heavy Industry
738-12 | 1 | Business | High School/Middle School
738-12 | 2 | Business | High School/Middle School
738-6 | 1 | Business | Hospital
738-6 | 2 | Business | Hospital
738-7 | 1 | Business | Hotel/Motel
738-7 | 2 | Business | Hotel/Motel
738-13 | 1 | Business | Hotel/Motel
738-13 | 2 | Business | Hotel/Motel
738-9 | 1 | Business | Light Industry
738-9 | 2 | Business | Light Industry
738-14 | 1 | Business | Miscellaneous
738-14 | 2 | Business | Miscellaneous
738-16 | 1 | Business | Multifamily Common Areas
738-16 | 2 | Business | Multifamily Common Areas
738-8 | 1 | Business | Office
738-8 | 2 | Business | Office
738-18 | 1 | Business | Religious Worship/Church
738-18 | 2 | Business | Religious Worship/Church
738-3 | 1 | Business | Restaurant
738-3 | 2 | Business | Restaurant
738-2 | 1 | Business | Retail/Service
738-2 | 2 | Business | Retail/Service
738-20 | 1 | Business
738-20 | 2 | Business
739-1 | 1 | Business | College/University
739-1 | 2 | Business | College/University
739-10 | 1 | Business | Elementary School
739-10 | 2 | Business | Elementary School
739-15 | 1 | Business | Exterior
739-15 | 2 | Business | Exterior
739-19 | 1 | Business | Garage, 24/7
739-19 | 2 | Business | Garage, 24/7
739-4 | 1 | Business | Garage
739-4 | 2 | Business | Garage
739-5 | 1 | Business | Grocery
739-5 | 2 | Business | Grocery
739-11 | 1 | Business | Heavy Industry
739-11 | 2 | Business | Heavy Industry
739-12 | 1 | Business | High School/Middle School
739-12 | 2 | Business | High School/Middle School
739-6 | 1 | Business | Hospital
739-6 | 2 | Business | Hospital
739-7 | 1 | Business | Hotel/Motel
739-7 | 2 | Business | Hotel/Motel
739-13 | 1 | Business | Hotel/Motel
739-13 | 2 | Business | Hotel/Motel
739-9 | 1 | Business | Light Industry
739-9 | 2 | Business | Light Industry
739-14 | 1 | Business | Miscellaneous
739-14 | 2 | Business | Miscellaneous
739-16 | 1 | Business | Multifamily Common Areas
739-16 | 2 | Business | Multifamily Common Areas
739-8 | 1 | Business | Office
739-8 | 2 | Business | Office
739-18 | 1 | Business | Religious Worship/Church
739-18 | 2 | Business | Religious Worship/Church
739-3 | 1 | Business | Restaurant
739-3 | 2 | Business | Restaurant
739-2 | 1 | Business | Retail/Service
739-2 | 2 | Business | Retail/Service
739-20 | 1 | Business
739-20 | 2 | Business
742-1 | 1 | Business | College/University
742-1 | 2 | Business | College/University
742-10 | 1 | Business | Elementary School
742-10 | 2 | Business | Elementary School
742-15 | 1 | Business | Exterior
742-15 | 2 | Business | Exterior
742-19 | 1 | Business | Garage, 24/7
742-19 | 2 | Business | Garage, 24/7
742-4 | 1 | Business | Garage
742-4 | 2 | Business | Garage
742-5 | 1 | Business | Grocery
742-5 | 2 | Business | Grocery
742-11 | 1 | Business | Heavy Industry
742-11 | 2 | Business | Heavy Industry
742-12 | 1 | Business | High School/Middle School
742-12 | 2 | Business | High School/Middle School
742-6 | 1 | Business | Hospital
742-6 | 2 | Business | Hospital
742-7 | 1 | Business | Hotel/Motel
742-7 | 2 | Business | Hotel/Motel
742-13 | 1 | Business | Hotel/Motel
742-13 | 2 | Business | Hotel/Motel
742-9 | 1 | Business | Light Industry
742-9 | 2 | Business | Light Industry
742-14 | 1 | Business | Miscellaneous
742-14 | 2 | Business | Miscellaneous
742-16 | 1 | Business | Multifamily Common Areas
742-16 | 2 | Business | Multifamily Common Areas
742-8 | 1 | Business | Office
742-8 | 2 | Business | Office
742-18 | 1 | Business | Religious Worship/Church
742-18 | 2 | Business | Religious Worship/Church
742-3 | 1 | Business | Restaurant
742-3 | 2 | Business | Restaurant
742-2 | 1 | Business | Retail/Service
742-2 | 2 | Business | Retail/Service
742-20 | 1 | Business
742-20 | 2 | Business
743-1 | 1 | Business | College/University
743-1 | 2 | Business | College/University
743-10 | 1 | Business | Elementary School
743-10 | 2 | Business | Elementary School
743-15 | 1 | Business | Exterior
743-15 | 2 | Business | Exterior
743-19 | 1 | Business | Garage, 24/7
743-19 | 2 | Business | Garage, 24/7
743-4 | 1 | Business | Garage
743-4 | 2 | Business | Garage
743-5 | 1 | Business | Grocery
743-5 | 2 | Business | Grocery
743-11 | 1 | Business | Heavy Industry
743-11 | 2 | Business | Heavy Industry
743-12 | 1 | Business | High School/Middle School
743-12 | 2 | Business | High School/Middle School
743-6 | 1 | Business | Hospital
743-6 | 2 | Business | Hospital
743-7 | 1 | Business | Hotel/Motel
743-7 | 2 | Business | Hotel/Motel
743-13 | 1 | Business | Hotel/Motel
743-13 | 2 | Business | Hotel/Motel
743-9 | 1 | Business | Light Industry
743-9 | 2 | Business | Light Industry
743-14 | 1 | Business | Miscellaneous
743-14 | 2 | Business | Miscellaneous
743-16 | 1 | Business | Multifamily Common Areas
743-16 | 2 | Business | Multifamily Common Areas
743-8 | 1 | Business | Office
743-8 | 2 | Business | Office
743-18 | 1 | Business | Religious Worship/Church
743-18 | 2 | Business | Religious Worship/Church
743-3 | 1 | Business | Restaurant
743-3 | 2 | Business | Restaurant
743-2 | 1 | Business | Retail/Service
743-2 | 2 | Business | Retail/Service
743-20 | 1 | Business
743-20 | 2 | Business
757-1 | 1 | Business | College/University
757-10 | 1 | Business | Elementary School
757-15 | 1 | Business | Exterior
757-19 | 1 | Business | Garage, 24/7
757-4 | 1 | Business | Garage
757-5 | 1 | Business | Grocery
757-11 | 1 | Business | Heavy Industry
757-12 | 1 | Business | High School/Middle School
757-6 | 1 | Business | Hospital
757-7 | 1 | Business | Hotel/Motel
757-13 | 1 | Business | Hotel/Motel
757-9 | 1 | Business | Light Industry
757-14 | 1 | Business | Miscellaneous
757-16 | 1 | Business | Multifamily Common Areas
757-8 | 1 | Business | Office
757-18 | 1 | Business | Religious Worship/Church
757-3 | 1 | Business | Restaurant
757-2 | 1 | Business | Retail/Service
757-20 | 1 | Business
758-1 | 1 | Business | College/University
758-10 | 1 | Business | Elementary School
758-15 | 1 | Business | Exterior
758-19 | 1 | Business | Garage, 24/7
758-4 | 1 | Business | Garage
758-5 | 1 | Business | Grocery
758-11 | 1 | Business | Heavy Industry
758-12 | 1 | Business | High School/Middle School
758-6 | 1 | Business | Hospital
758-7 | 1 | Business | Hotel/Motel
758-13 | 1 | Business | Hotel/Motel
758-9 | 1 | Business | Light Industry
758-14 | 1 | Business | Miscellaneous
758-16 | 1 | Business | Multifamily Common Areas
758-8 | 1 | Business | Office
758-18 | 1 | Business | Religious Worship/Church
758-3 | 1 | Business | Restaurant
758-2 | 1 | Business | Retail/Service
758-20 | 1 | Business
759-1 | 1 | Business | College/University
759-10 | 1 | Business | Elementary School
759-15 | 1 | Business | Exterior
759-19 | 1 | Business | Garage, 24/7
759-4 | 1 | Business | Garage
759-5 | 1 | Business | Grocery
759-11 | 1 | Business | Heavy Industry
759-12 | 1 | Business | High School/Middle School
759-6 | 1 | Business | Hospital
759-7 | 1 | Business | Hotel/Motel
759-13 | 1 | Business | Hotel/Motel
759-9 | 1 | Business | Light Industry
759-14 | 1 | Business | Miscellaneous
759-16 | 1 | Business | Multifamily Common Areas
759-8 | 1 | Business | Office
759-18 | 1 | Business | Religious Worship/Church
759-3 | 1 | Business | Restaurant
759-2 | 1 | Business | Retail/Service
759-20 | 1 | Business
760-1 | 1 | Business | College/University
760-10 | 1 | Business | Elementary School
760-15 | 1 | Business | Exterior
760-19 | 1 | Business | Garage, 24/7
760-4 | 1 | Business | Garage
760-5 | 1 | Business | Grocery
760-11 | 1 | Business | Heavy Industry
760-12 | 1 | Business | High School/Middle School
760-6 | 1 | Business | Hospital
760-7 | 1 | Business | Hotel/Motel
760-13 | 1 | Business | Hotel/Motel
760-9 | 1 | Business | Light Industry
760-14 | 1 | Business | Miscellaneous
760-16 | 1 | Business | Multifamily Common Areas
760-8 | 1 | Business | Office
760-18 | 1 | Business | Religious Worship/Church
760-3 | 1 | Business | Restaurant
760-2 | 1 | Business | Retail/Service
760-20 | 1 | Business
761-1 | 1 | Business | College/University
761-10 | 1 | Business | Elementary School
761-15 | 1 | Business | Exterior
761-19 | 1 | Business | Garage, 24/7
761-4 | 1 | Business | Garage
761-5 | 1 | Business | Grocery
761-11 | 1 | Business | Heavy Industry
761-12 | 1 | Business | High School/Middle School
761-6 | 1 | Business | Hospital
761-7 | 1 | Business | Hotel/Motel
761-13 | 1 | Business | Hotel/Motel
761-9 | 1 | Business | Light Industry
761-14 | 1 | Business | Miscellaneous
761-16 | 1 | Business | Multifamily Common Areas
761-8 | 1 | Business | Office
761-18 | 1 | Business | Religious Worship/Church
761-3 | 1 | Business | Restaurant
761-2 | 1 | Business | Retail/Service
761-20 | 1 | Business
762-1 | 1 | Business | College/University
762-1 | 2 | Business | College/University
762-10 | 1 | Business | Elementary School
762-10 | 2 | Business | Elementary School
762-15 | 1 | Business | Exterior
762-15 | 2 | Business | Exterior
762-19 | 1 | Business | Garage, 24/7
762-19 | 2 | Business | Garage, 24/7
762-4 | 1 | Business | Garage
762-4 | 2 | Business | Garage
762-5 | 1 | Business | Grocery
762-5 | 2 | Business | Grocery
762-11 | 1 | Business | Heavy Industry
762-11 | 2 | Business | Heavy Industry
762-12 | 1 | Business | High School/Middle School
762-12 | 2 | Business | High School/Middle School
762-6 | 1 | Business | Hospital
762-6 | 2 | Business | Hospital
762-7 | 1 | Business | Hotel/Motel
762-7 | 2 | Business | Hotel/Motel
762-13 | 1 | Business | Hotel/Motel
762-13 | 2 | Business | Hotel/Motel
762-9 | 1 | Business | Light Industry
762-9 | 2 | Business | Light Industry
762-14 | 1 | Business | Miscellaneous
762-14 | 2 | Business | Miscellaneous
762-16 | 1 | Business | Multifamily Common Areas
762-16 | 2 | Business | Multifamily Common Areas
762-8 | 1 | Business | Office
762-8 | 2 | Business | Office
762-18 | 1 | Business | Religious Worship/Church
762-18 | 2 | Business | Religious Worship/Church
762-3 | 1 | Business | Restaurant
762-3 | 2 | Business | Restaurant
762-2 | 1 | Business | Retail/Service
762-2 | 2 | Business | Retail/Service
762-20 | 1 | Business
762-20 | 2 | Business
740-1 | 1 | Business | College/University
740-1 | 2 | Business | College/University
740-10 | 1 | Business | Elementary School
740-10 | 2 | Business | Elementary School
740-15 | 1 | Business | Exterior
740-15 | 2 | Business | Exterior
740-19 | 1 | Business | Garage, 24/7
740-19 | 2 | Business | Garage, 24/7
740-4 | 1 | Business | Garage
740-4 | 2 | Business | Garage
740-5 | 1 | Business | Grocery
740-5 | 2 | Business | Grocery
740-11 | 1 | Business | Heavy Industry
740-11 | 2 | Business | Heavy Industry
740-12 | 1 | Business | High School/Middle School
740-12 | 2 | Business | High School/Middle School
740-6 | 1 | Business | Hospital
740-6 | 2 | Business | Hospital
740-7 | 1 | Business | Hotel/Motel
740-7 | 2 | Business | Hotel/Motel
740-13 | 1 | Business | Hotel/Motel
740-13 | 2 | Business | Hotel/Motel
740-9 | 1 | Business | Light Industry
740-9 | 2 | Business | Light Industry
740-14 | 1 | Business | Miscellaneous
740-14 | 2 | Business | Miscellaneous
740-16 | 1 | Business | Multifamily Common Areas
740-16 | 2 | Business | Multifamily Common Areas
740-8 | 1 | Business | Office
740-8 | 2 | Business | Office
740-18 | 1 | Business | Religious Worship/Church
740-18 | 2 | Business | Religious Worship/Church
740-3 | 1 | Business | Restaurant
740-3 | 2 | Business | Restaurant
740-2 | 1 | Business | Retail/Service
740-2 | 2 | Business | Retail/Service
740-20 | 1 | Business
740-20 | 2 | Business
741-1 | 1 | Business | College/University
741-1 | 2 | Business | College/University
741-10 | 1 | Business | Elementary School
741-10 | 2 | Business | Elementary School
741-15 | 1 | Business | Exterior
741-15 | 2 | Business | Exterior
741-19 | 1 | Business | Garage, 24/7
741-19 | 2 | Business | Garage, 24/7
741-4 | 1 | Business | Garage
741-4 | 2 | Business | Garage
741-5 | 1 | Business | Grocery
741-5 | 2 | Business | Grocery
741-11 | 1 | Business | Heavy Industry
741-11 | 2 | Business | Heavy Industry
741-12 | 1 | Business | High School/Middle School
741-12 | 2 | Business | High School/Middle School
741-6 | 1 | Business | Hospital
741-6 | 2 | Business | Hospital
741-7 | 1 | Business | Hotel/Motel
741-7 | 2 | Business | Hotel/Motel
741-13 | 1 | Business | Hotel/Motel
741-13 | 2 | Business | Hotel/Motel
741-9 | 1 | Business | Light Industry
741-9 | 2 | Business | Light Industry
741-14 | 1 | Business | Miscellaneous
741-14 | 2 | Business | Miscellaneous
741-16 | 1 | Business | Multifamily Common Areas
741-16 | 2 | Business | Multifamily Common Areas
741-8 | 1 | Business | Office
741-8 | 2 | Business | Office
741-18 | 1 | Business | Religious Worship/Church
741-18 | 2 | Business | Religious Worship/Church
741-3 | 1 | Business | Restaurant
741-3 | 2 | Business | Restaurant
741-2 | 1 | Business | Retail/Service
741-2 | 2 | Business | Retail/Service
741-20 | 1 | Business
741-20 | 2 | Business
3004-1 | 1 | Business
3004-2 | 1 | Business
3005-1 | 1 | Business
3005-2 | 1 | Business
3007 | 1 | Business
3008 | 1 | Business
3010 | 1 | Business
734-1 | 1 | Business | College/University
734-1 | 2 | Business | College/University
734-10 | 1 | Business | Elementary School
734-10 | 2 | Business | Elementary School
734-15 | 1 | Business | Exterior
734-15 | 2 | Business | Exterior
734-19 | 1 | Business | Garage, 24/7
734-19 | 2 | Business | Garage, 24/7
734-4 | 1 | Business | Garage
734-4 | 2 | Business | Garage
734-5 | 1 | Business | Grocery
734-5 | 2 | Business | Grocery
734-11 | 1 | Business | Heavy Industry
734-11 | 2 | Business | Heavy Industry
734-12 | 1 | Business | High School/Middle School
734-12 | 2 | Business | High School/Middle School
734-6 | 1 | Business | Hospital
734-6 | 2 | Business | Hospital
734-7 | 1 | Business | Hotel/Motel
734-7 | 2 | Business | Hotel/Motel
734-13 | 1 | Business | Hotel/Motel
734-13 | 2 | Business | Hotel/Motel
734-9 | 1 | Business | Light Industry
734-9 | 2 | Business | Light Industry
734-14 | 1 | Business | Miscellaneous
734-14 | 2 | Business | Miscellaneous
734-16 | 1 | Business | Multifamily Common Areas
734-16 | 2 | Business | Multifamily Common Areas
734-8 | 1 | Business | Office
734-8 | 2 | Business | Office
734-18 | 1 | Business | Religious Worship/Church
734-18 | 2 | Business | Religious Worship/Church
734-3 | 1 | Business | Restaurant
734-3 | 2 | Business | Restaurant
734-2 | 1 | Business | Retail/Service
734-2 | 2 | Business | Retail/Service
734-20 | 1 | Business
734-20 | 2 | Business
793-1 | 1 | Business | College/University
793-10 | 1 | Business | Elementary School
793-15 | 1 | Business | Exterior
793-19 | 1 | Business | Garage, 24/7
793-4 | 1 | Business | Garage
793-5 | 1 | Business | Grocery
793-11 | 1 | Business | Heavy Industry
793-12 | 1 | Business | High School/Middle School
793-6 | 1 | Business | Hospital
793-7 | 1 | Business | Hotel/Motel
793-13 | 1 | Business | Hotel/Motel
793-9 | 1 | Business | Light Industry
793-14 | 1 | Business | Miscellaneous
793-16 | 1 | Business | Multifamily Common Areas
793-8 | 1 | Business | Office
793-18 | 1 | Business | Religious Worship/Church
793-3 | 1 | Business | Restaurant
793-2 | 1 | Business | Retail/Service
793-20 | 1 | Business
3013 | 1 | Business
3025 | 1 | Business
3026 | 1 | Business
744-1 | 1 | Business | College/University
744-1 | 2 | Business | College/University
744-10 | 1 | Business | Elementary School
744-10 | 2 | Business | Elementary School
744-15 | 1 | Business | Exterior
744-15 | 2 | Business | Exterior
744-19 | 1 | Business | Garage, 24/7
744-19 | 2 | Business | Garage, 24/7
744-4 | 1 | Business | Garage
744-4 | 2 | Business | Garage
744-5 | 1 | Business | Grocery
744-5 | 2 | Business | Grocery
744-11 | 1 | Business | Heavy Industry
744-11 | 2 | Business | Heavy Industry
744-12 | 1 | Business | High School/Middle School
744-12 | 2 | Business | High School/Middle School
744-6 | 1 | Business | Hospital
744-6 | 2 | Business | Hospital
744-7 | 1 | Business | Hotel/Motel
744-7 | 2 | Business | Hotel/Motel
744-13 | 1 | Business | Hotel/Motel
744-13 | 2 | Business | Hotel/Motel
744-9 | 1 | Business | Light Industry
744-9 | 2 | Business | Light Industry
744-14 | 1 | Business | Miscellaneous
744-14 | 2 | Business | Miscellaneous
744-16 | 1 | Business | Multifamily Common Areas
744-16 | 2 | Business | Multifamily Common Areas
744-8 | 1 | Business | Office
744-8 | 2 | Business | Office
744-18 | 1 | Business | Religious Worship/Church
744-18 | 2 | Business | Religious Worship/Church
744-3 | 1 | Business | Restaurant
744-3 | 2 | Business | Restaurant
744-2 | 1 | Business | Retail/Service
744-2 | 2 | Business | Retail/Service
744-20 | 1 | Business
744-20 | 2 | Business
3015 | 1 | Business
3017 | 1 | Business
3018 | 1 | Business
786-1 | 1 | Business | College/University
786-10 | 1 | Business | Elementary School
786-15 | 1 | Business | Exterior
786-19 | 1 | Business | Garage, 24/7
786-4 | 1 | Business | Garage
786-5 | 1 | Business | Grocery
786-11 | 1 | Business | Heavy Industry
786-12 | 1 | Business | High School/Middle School
786-6 | 1 | Business | Hospital
786-7 | 1 | Business | Hotel/Motel
786-13 | 1 | Business | Hotel/Motel
786-9 | 1 | Business | Light Industry
786-14 | 1 | Business | Miscellaneous
786-16 | 1 | Business | Multifamily Common Areas
786-8 | 1 | Business | Office
786-18 | 1 | Business | Religious Worship/Church
786-3 | 1 | Business | Restaurant
786-2 | 1 | Business | Retail/Service
786-20 | 1 | Business
787-1 | 1 | Business | College/University
787-10 | 1 | Business | Elementary School
787-15 | 1 | Business | Exterior
787-19 | 1 | Business | Garage, 24/7
787-4 | 1 | Business | Garage
787-5 | 1 | Business | Grocery
787-11 | 1 | Business | Heavy Industry
787-12 | 1 | Business | High School/Middle School
787-6 | 1 | Business | Hospital
787-7 | 1 | Business | Hotel/Motel
787-13 | 1 | Business | Hotel/Motel
787-9 | 1 | Business | Light Industry
787-14 | 1 | Business | Miscellaneous
787-16 | 1 | Business | Multifamily Common Areas
787-8 | 1 | Business | Office
787-18 | 1 | Business | Religious Worship/Church
787-3 | 1 | Business | Restaurant
787-2 | 1 | Business | Retail/Service
787-20 | 1 | Business
754-1 | 1 | Business | College/University
754-1 | 2 | Business | College/University
754-10 | 1 | Business | Elementary School
754-10 | 2 | Business | Elementary School
754-15 | 1 | Business | Exterior
754-15 | 2 | Business | Exterior
754-19 | 1 | Business | Garage, 24/7
754-19 | 2 | Business | Garage, 24/7
754-4 | 1 | Business | Garage
754-4 | 2 | Business | Garage
754-5 | 1 | Business | Grocery
754-5 | 2 | Business | Grocery
754-11 | 1 | Business | Heavy Industry
754-11 | 2 | Business | Heavy Industry
754-12 | 1 | Business | High School/Middle School
754-12 | 2 | Business | High School/Middle School
754-6 | 1 | Business | Hospital
754-6 | 2 | Business | Hospital
754-7 | 1 | Business | Hotel/Motel
754-7 | 2 | Business | Hotel/Motel
754-13 | 1 | Business | Hotel/Motel
754-13 | 2 | Business | Hotel/Motel
754-9 | 1 | Business | Light Industry
754-9 | 2 | Business | Light Industry
754-14 | 1 | Business | Miscellaneous
754-14 | 2 | Business | Miscellaneous
754-16 | 1 | Business | Multifamily Common Areas
754-16 | 2 | Business | Multifamily Common Areas
754-8 | 1 | Business | Office
754-8 | 2 | Business | Office
754-18 | 1 | Business | Religious Worship/Church
754-18 | 2 | Business | Religious Worship/Church
754-3 | 1 | Business | Restaurant
754-3 | 2 | Business | Restaurant
754-2 | 1 | Business | Retail/Service
754-2 | 2 | Business | Retail/Service
754-20 | 1 | Business
754-20 | 2 | Business
755-1 | 1 | Business | College/University
755-1 | 2 | Business | College/University
755-10 | 1 | Business | Elementary School
755-10 | 2 | Business | Elementary School
755-15 | 1 | Business | Exterior
755-15 | 2 | Business | Exterior
755-19 | 1 | Business | Garage, 24/7
755-19 | 2 | Business | Garage, 24/7
755-4 | 1 | Business | Garage
755-4 | 2 | Business | Garage
755-5 | 1 | Business | Grocery
755-5 | 2 | Business | Grocery
755-11 | 1 | Business | Heavy Industry
755-11 | 2 | Business | Heavy Industry
755-12 | 1 | Business | High School/Middle School
755-12 | 2 | Business | High School/Middle School
755-6 | 1 | Business | Hospital
755-6 | 2 | Business | Hospital
755-7 | 1 | Business | Hotel/Motel
755-7 | 2 | Business | Hotel/Motel
755-13 | 1 | Business | Hotel/Motel
755-13 | 2 | Business | Hotel/Motel
755-9 | 1 | Business | Light Industry
755-9 | 2 | Business | Light Industry
755-14 | 1 | Business | Miscellaneous
755-14 | 2 | Business | Miscellaneous
755-16 | 1 | Business | Multifamily Common Areas
755-16 | 2 | Business | Multifamily Common Areas
755-8 | 1 | Business | Office
755-8 | 2 | Business | Office
755-18 | 1 | Business | Religious Worship/Church
755-18 | 2 | Business | Religious Worship/Church
755-3 | 1 | Business | Restaurant
755-3 | 2 | Business | Restaurant
755-2 | 1 | Business | Retail/Service
755-2 | 2 | Business | Retail/Service
755-20 | 1 | Business
755-20 | 2 | Business
756-1 | 1 | Business | College/University
756-1 | 2 | Business | College/University
756-10 | 1 | Business | Elementary School
756-10 | 2 | Business | Elementary School
756-15 | 1 | Business | Exterior
756-15 | 2 | Business | Exterior
756-19 | 1 | Business | Garage, 24/7
756-19 | 2 | Business | Garage, 24/7
756-4 | 1 | Business | Garage
756-4 | 2 | Business | Garage
756-5 | 1 | Business | Grocery
756-5 | 2 | Business | Grocery
756-11 | 1 | Business | Heavy Industry
756-11 | 2 | Business | Heavy Industry
756-12 | 1 | Business | High School/Middle School
756-12 | 2 | Business | High School/Middle School
756-6 | 1 | Business | Hospital
756-6 | 2 | Business | Hospital
756-7 | 1 | Business | Hotel/Motel
756-7 | 2 | Business | Hotel/Motel
756-13 | 1 | Business | Hotel/Motel
756-13 | 2 | Business | Hotel/Motel
756-9 | 1 | Business | Light Industry
756-9 | 2 | Business | Light Industry
756-14 | 1 | Business | Miscellaneous
756-14 | 2 | Business | Miscellaneous
756-16 | 1 | Business | Multifamily Common Areas
756-16 | 2 | Business | Multifamily Common Areas
756-8 | 1 | Business | Office
756-8 | 2 | Business | Office
756-18 | 1 | Business | Religious Worship/Church
756-18 | 2 | Business | Religious Worship/Church
756-3 | 1 | Business | Restaurant
756-3 | 2 | Business | Restaurant
756-2 | 1 | Business | Retail/Service
756-2 | 2 | Business | Retail/Service
756-20 | 1 | Business
756-20 | 2 | Business
782-1 | 1 | Business | College/University
782-1 | 2 | Business | College/University
782-10 | 1 | Business | Elementary School
782-10 | 2 | Business | Elementary School
782-15 | 1 | Business | Exterior
782-15 | 2 | Business | Exterior
782-19 | 1 | Business | Garage, 24/7
782-19 | 2 | Business | Garage, 24/7
782-4 | 1 | Business | Garage
782-4 | 2 | Business | Garage
782-5 | 1 | Business | Grocery
782-5 | 2 | Business | Grocery
782-11 | 1 | Business | Heavy Industry
782-11 | 2 | Business | Heavy Industry
782-12 | 1 | Business | High School/Middle School
782-12 | 2 | Business | High School/Middle School
782-6 | 1 | Business | Hospital
782-6 | 2 | Business | Hospital
782-7 | 1 | Business | Hotel/Motel
782-7 | 2 | Business | Hotel/Motel
782-13 | 1 | Business | Hotel/Motel
782-13 | 2 | Business | Hotel/Motel
782-9 | 1 | Business | Light Industry
782-9 | 2 | Business | Light Industry
782-14 | 1 | Business | Miscellaneous
782-14 | 2 | Business | Miscellaneous
782-16 | 1 | Business | Multifamily Common Areas
782-16 | 2 | Business | Multifamily Common Areas
782-8 | 1 | Business | Office
782-8 | 2 | Business | Office
782-18 | 1 | Business | Religious Worship/Church
782-18 | 2 | Business | Religious Worship/Church
782-3 | 1 | Business | Restaurant
782-3 | 2 | Business | Restaurant
782-2 | 1 | Business | Retail/Service
782-2 | 2 | Business | Retail/Service
782-20 | 1 | Business
782-20 | 2 | Business
1102-1 | 1 | Business
1102-1 | 2 | Business
1102-10 | 1 | Business
1102-10 | 2 | Business
1102-15 | 1 | Business
1102-15 | 2 | Business
1102-19 | 1 | Business
1102-19 | 2 | Business
1102-4 | 1 | Business
1102-4 | 2 | Business
1102-5 | 1 | Business
1102-5 | 2 | Business
1102-11 | 1 | Business
1102-11 | 2 | Business
1102-12 | 1 | Business
1102-12 | 2 | Business
1102-6 | 1 | Business
1102-6 | 2 | Business
1102-7 | 1 | Business
1102-7 | 2 | Business
1102-13 | 1 | Business
1102-13 | 2 | Business
1102-9 | 1 | Business
1102-9 | 2 | Business
1102-14 | 1 | Business
1102-14 | 2 | Business
1102-16 | 1 | Business
1102-16 | 2 | Business
1102-8 | 1 | Business
1102-8 | 2 | Business
1102-18 | 1 | Business
1102-18 | 2 | Business
1102-3 | 1 | Business
1102-3 | 2 | Business
1102-2 | 1 | Business
1102-2 | 2 | Business
1102-20 | 1 | Business
1102-20 | 2 | Business
1106-1 | 1 | Business
1106-1 | 2 | Business
1106-10 | 1 | Business
1106-10 | 2 | Business
1106-15 | 1 | Business
1106-15 | 2 | Business
1106-19 | 1 | Business
1106-19 | 2 | Business
1106-4 | 1 | Business
1106-4 | 2 | Business
1106-5 | 1 | Business
1106-5 | 2 | Business
1106-11 | 1 | Business
1106-11 | 2 | Business
1106-12 | 1 | Business
1106-12 | 2 | Business
1106-6 | 1 | Business
1106-6 | 2 | Business
1106-7 | 1 | Business
1106-7 | 2 | Business
1106-13 | 1 | Business
1106-13 | 2 | Business
1106-9 | 1 | Business
1106-9 | 2 | Business
1106-14 | 1 | Business
1106-14 | 2 | Business
1106-16 | 1 | Business
1106-16 | 2 | Business
1106-8 | 1 | Business
1106-8 | 2 | Business
1106-18 | 1 | Business
1106-18 | 2 | Business
1106-3 | 1 | Business
1106-3 | 2 | Business
1106-2 | 1 | Business
1106-2 | 2 | Business
1106-20 | 1 | Business
1106-20 | 2 | Business
3003 | 2 | Business
3057 | 1 | Business
838 | 1 | Business
839 | 1 | Business
839 | 2 | Business
816 | 1 | Business
817 | 1 | Business
825 | 1 | Business
3065 | 1 | Business
826 | 1 | Business
827 | 1 | Business
828 | 1 | Business
829 | 1 | Business
842 | 1 | Business
842 | 2 | Business
843 | 1 | Business
843 | 2 | Business
3028 | 1 | Business
3029 | 1 | Business
830 | 1 | Business
831 | 1 | Business
832 | 1 | Business
833 | 1 | Business
3030 | 1 | Business
3031 | 1 | Business
3032 | 1 | Business
3033 | 1 | Business
834 | 1 | Business
834 | 2 | Business
835 | 1 | Business
835 | 2 | Business
836 | 1 | Business
836 | 2 | Business
3066 | 1 | Business
3067 | 1 | Business
3068 | 1 | Business
846 | 1 | Business
846 | 2 | Business
3054 | 1 | Business
3055 | 1 | Business
3056 | 1 | Business
850 | 1 | Business
851 | 1 | Business
852 | 1 | Business
853 | 1 | Business
854 | 1 | Business
847 | 1 | Business
847 | 2 | Business
848 | 1 | Business
3074 | 1 | Business
3064 | 1 | Business
3069 | 1 | Business
821 | 1 | Business
823 | 1 | Business
1178 | 1 | Business
3071 | 1 | Business
3072 | 1 | Business
849 | 1 | Business
1114 | 1 | Business
795 | 1 | Business
1145 | 1 | Business
1141 | 1 | Business
2795 | 1 | Business
796 | 1 | Business
796 | 2 | Business
1118 | 1 | Business
797 | 1 | Business
1153 | 1 | Business
1149 | 1 | Business
2797 | 1 | Business
798 | 1 | Business
798 | 2 | Business
1126 | 1 | Business
1130 | 1 | Business
799 | 1 | Business
1122 | 1 | Business
1133 | 1 | Business
2799 | 1 | Business
1137 | 1 | Business
800 | 1 | Business
2794 | 1 | Business
837 | 1 | Business
3039 | 1 | Business
1110 | 1 | Business
3073 | 1 | Business
3034 | 1 | Business
845 | 1 | Business
845 | 2 | Business
794 | 1 | Business
801 | 1 | Business
802 | 1 | Business
803 | 1 | Business
804 | 1 | Business
805 | 1 | Business
806 | 1 | Business
807 | 1 | Business
808 | 1 | Business
809 | 1 | Business
810 | 1 | Business
3070 | 1 | Business

## MeasureWhereUsed
Measure Reference Number | Version Number | State | Utility
972 | 1 | MO
972 | 2 | MO | Ameren Missouri
972 | 3 | MO | Ameren Missouri
973 | 1 | MO
973 | 2 | MO
974 | 1 | MO
974 | 2 | MO
974 | 3 | MO
975 | 1 | MO
975 | 2 | MO
857 | 1 | MO
857 | 2 | MO
857 | 3 | MO
873 | 1 | MO
1042 | 1 | MO
1220 | 1 | MO | Ameren Missouri
874 | 2 | MO
874 | 1 | MO
1207 | 1 | MO | Ameren Missouri
1043 | 1 | MO
1007 | 1 | MO
915 | 1 | MO
915 | 2 | MO
916 | 1 | MO
916 | 2 | MO
918 | 1 | MO
918 | 2 | MO
981 | 1 | MO
919 | 1 | MO
919 | 2 | MO
919 | 3 | MO
1048 | 1 | MO
920 | 1 | MO
920 | 2 | MO
920 | 3 | MO
1049 | 1 | MO
922 | 1 | MO
922 | 2 | MO
922 | 3 | MO
1051 | 1 | MO
1051 | 2 | MO
982 | 1 | MO
983 | 1 | MO
923 | 1 | MO
923 | 2 | MO
923 | 3 | MO
1052 | 1 | MO
924 | 1 | MO
924 | 2 | MO
924 | 3 | MO
1053 | 1 | MO
926 | 1 | MO
926 | 2 | MO
926 | 3 | MO
1055 | 1 | MO
984 | 1 | MO
985 | 1 | MO
1239 | 2 | MO | Ameren Missouri
1266 | 1 | MO | Ameren Missouri
1268 | 1 | MO | Ameren Missouri
1239 | 1 | MO | Ameren Missouri
1240 | 2 | MO | Ameren Missouri
1270 | 1 | MO | Ameren Missouri
1271 | 1 | MO | Ameren Missouri
1269 | 1 | MO | Ameren Missouri
1240 | 1 | MO | Ameren Missouri
1267 | 1 | MO | Ameren Missouri
917 | 1 | MO
917 | 2 | MO
921 | 1 | MO
921 | 2 | MO
921 | 3 | MO
1050 | 1 | MO
925 | 1 | MO
925 | 2 | MO
925 | 3 | MO
1054 | 1 | MO
945 | 1 | MO
945 | 2 | MO
945 | 3 | MO
944 | 1 | MO
944 | 2 | MO
944 | 3 | MO
1069 | 1 | MO
1069 | 2 | MO
1001 | 1 | MO
1070 | 1 | MO
947 | 2 | MO
947 | 3 | MO
946 | 1 | MO
946 | 2 | MO
946 | 3 | MO
1071 | 1 | MO
1071 | 2 | MO
1002 | 1 | MO
947 | 1 | MO
1072 | 1 | MO
1003 | 1 | MO
949 | 2 | MO
949 | 3 | MO
948 | 1 | MO
948 | 2 | MO
948 | 3 | MO
1073 | 1 | MO
1073 | 2 | MO
949 | 1 | MO
1074 | 1 | MO
1004 | 1 | MO
875 | 1 | MO
876 | 1 | MO
1044 | 1 | MO
877 | 1 | MO
877 | 2 | MO
878 | 1 | MO
879 | 1 | MO
880 | 1 | MO
880 | 2 | MO
1209 | 1 | MO | Ameren Missouri
1208 | 1 | MO | Ameren Missouri
1208 | 2 | MO | Ameren Missouri
875 | 2 | MO
876 | 2 | MO
881 | 2 | MO
1210 | 1 | MO | Ameren Missouri
881 | 1 | MO
858 | 1 | MO
858 | 2 | MO
883 | 1 | MO
883 | 2 | MO
954 | 1 | MO
954 | 2 | MO
1078 | 1 | MO
1188 | 1 | MO
1189 | 1 | MO
1186 | 1 | MO
1187 | 1 | MO
1190 | 1 | MO
1008 | 1 | MO
1008 | 2 | MO
1009 | 1 | MO
1009 | 2 | MO
1010 | 1 | MO
1010 | 2 | MO
1011 | 1 | MO
1011 | 2 | MO
884 | 1 | MO
884 | 2 | MO
955 | 1 | MO
955 | 2 | MO
1079 | 1 | MO
1012 | 1 | MO
1012 | 2 | MO
1013 | 1 | MO
1013 | 2 | MO
885 | 1 | MO
885 | 2 | MO
956 | 1 | MO
956 | 2 | MO
1080 | 1 | MO
1014 | 1 | MO
886 | 1 | MO
957 | 1 | MO
1081 | 1 | MO
887 | 1 | MO
887 | 2 | MO
958 | 1 | MO
958 | 2 | MO
1082 | 1 | MO
1015 | 1 | MO
1016 | 1 | MO
888 | 1 | MO
888 | 2 | MO
959 | 1 | MO
959 | 2 | MO
1083 | 1 | MO
1017 | 1 | MO
889 | 1 | MO
889 | 2 | MO
960 | 1 | MO
960 | 2 | MO
1084 | 1 | MO
961 | 1 | MO
1 | 1 | MO
1 | 2 | MO
986 | 1 | MO
927 | 1 | MO
927 | 2 | MO
927 | 3 | MO
987 | 1 | MO
928 | 1 | MO
928 | 2 | MO
928 | 3 | MO
1056 | 1 | MO
988 | 1 | MO
929 | 1 | MO
929 | 2 | MO
929 | 3 | MO
1057 | 1 | MO
989 | 1 | MO
930 | 1 | MO
930 | 2 | MO
930 | 3 | MO
1058 | 1 | MO
990 | 1 | MO
931 | 1 | MO
931 | 2 | MO
931 | 3 | MO
1059 | 1 | MO
1242 | 1 | MO | Ameren Missouri
1242 | 2 | MO | Ameren Missouri
1243 | 1 | MO | Ameren Missouri
1243 | 2 | MO | Ameren Missouri
1264 | 1 | MO
1225 | 1 | MO | Ameren Missouri
1225 | 2 | MO | Ameren Missouri
1260 | 1 | MO
1224 | 1 | MO | Ameren Missouri
1259 | 1 | MO
1226 | 1 | MO
1226 | 2 | MO
1226 | 3 | MO
976 | 1 | MO
977 | 1 | MO
978 | 1 | MO
979 | 1 | MO
980 | 1 | MO
905 | 1 | MO
905 | 2 | MO
1046 | 1 | MO
1046 | 2 | MO
906 | 1 | MO
906 | 2 | MO
1047 | 1 | MO
1047 | 2 | MO
1250 | 1 | MO | Ameren Missouri
1250 | 2 | MO | Ameren Missouri
1252 | 1 | MO | Ameren Missouri
1252 | 2 | MO | Ameren Missouri
1253 | 1 | MO | Ameren Missouri
1253 | 2 | MO | Ameren Missouri
1251 | 1 | MO | Ameren Missouri
1251 | 2 | MO | Ameren Missouri
908 | 2 | MO
908 | 3 | MO
1257 | 1 | MO | Ameren Missouri
1257 | 2 | MO | Ameren Missouri
907 | 1 | MO
907 | 2 | MO
907 | 3 | MO
1028 | 1 | MO
1029 | 1 | MO
911 | 2 | MO
911 | 3 | MO
1244 | 1 | MO | Ameren Missouri
1244 | 2 | MO | Ameren Missouri
910 | 1 | MO
910 | 2 | MO
910 | 3 | MO
908 | 1 | MO
911 | 1 | MO
1179 | 1 | MO
1171 | 1 | MO
1177 | 1 | MO
1177 | 2 | MO
1177 | 3 | MO
1175 | 1 | MO
1176 | 1 | MO
1170 | 1 | MO
968 | 1 | MO
968 | 2 | MO
968 | 3 | MO
1221 | 1 | MO | Ameren Missouri
1221 | 2 | MO | Ameren Missouri
1180 | 1 | MO
1182 | 1 | MO
1173 | 1 | MO
1181 | 1 | MO
1181 | 2 | MO
1181 | 3 | MO
1183 | 1 | MO
1174 | 1 | MO
2 | 1 | MO
2 | 2 | MO
1060 | 2 | MO
932 | 1 | MO
932 | 2 | MO
1060 | 1 | MO
1248 | 1 | MO | Ameren Missouri
1248 | 2 | MO | Ameren Missouri
1249 | 1 | MO | Ameren Missouri
1249 | 2 | MO | Ameren Missouri
1218 | 1 | MO | Ameren Missouri
1219 | 1 | MO | Ameren Missouri
933 | 1 | MO
933 | 2 | MO
1061 | 1 | MO
934 | 1 | MO
934 | 2 | MO
934 | 3 | MO
1062 | 1 | MO
935 | 1 | MO
935 | 2 | MO
935 | 3 | MO
1063 | 1 | MO
1063 | 2 | MO
1247 | 1 | MO | Ameren Missouri
1247 | 2 | MO | Ameren Missouri
913 | 1 | MO
913 | 2 | MO
914 | 1 | MO
914 | 2 | MO
1232 | 1 | MO | Ameren Missouri
1232 | 2 | MO | Ameren Missouri
872 | 1 | MO
872 | 2 | MO
872 | 3 | MO
902 | 1 | MO
1092 | 1 | MO
952 | 1 | MO
1077 | 1 | MO
1223 | 1 | MO | Ameren Missouri
1245 | 1 | MO | Ameren Missouri
999 | 1 | MO
999 | 2 | MO
999 | 3 | MO
943 | 1 | MO
943 | 2 | MO
943 | 3 | MO
1000 | 1 | MO
1000 | 2 | MO
941 | 1 | MO
941 | 2 | MO
941 | 3 | MO
1230 | 1 | MO | Ameren Missouri
1222 | 1 | MO | Ameren Missouri
1018 | 1 | MO
1018 | 2 | MO
1018 | 3 | MO
1019 | 1 | MO
1019 | 2 | MO
1019 | 3 | MO
890 | 1 | MO
890 | 2 | MO
962 | 1 | MO
1085 | 1 | MO
962 | 2 | MO
962 | 3 | MO
1204 | 1 | MO | Ameren Missouri
1204 | 2 | MO | Ameren Missouri
1263 | 1 | MO
1203 | 1 | MO | Ameren Missouri
1203 | 2 | MO | Ameren Missouri
1202 | 1 | MO | Ameren Missouri
1202 | 2 | MO | Ameren Missouri
1227 | 1 | MO
1227 | 2 | MO
1227 | 3 | MO
1020 | 1 | MO
1020 | 2 | MO
1020 | 3 | MO
891 | 1 | MO
891 | 2 | MO
963 | 1 | MO
963 | 2 | MO
963 | 3 | MO
1086 | 1 | MO
1021 | 1 | MO
1021 | 2 | MO
1021 | 3 | MO
1022 | 1 | MO
1023 | 1 | MO
892 | 1 | MO
892 | 2 | MO
964 | 1 | MO
1087 | 1 | MO
1022 | 2 | MO
1022 | 3 | MO
1023 | 2 | MO
1023 | 3 | MO
964 | 2 | MO
964 | 3 | MO
1205 | 1 | MO | Ameren Missouri
1205 | 2 | MO | Ameren Missouri
1024 | 1 | MO
1025 | 1 | MO
893 | 1 | MO
893 | 2 | MO
965 | 1 | MO
1088 | 1 | MO
1024 | 2 | MO
1024 | 3 | MO
1025 | 2 | MO
1025 | 3 | MO
965 | 2 | MO
965 | 3 | MO
1206 | 1 | MO | Ameren Missouri
1206 | 2 | MO | Ameren Missouri
1231 | 1 | MO | Ameren Missouri
1231 | 2 | MO | Ameren Missouri
1026 | 1 | MO
1026 | 2 | MO
1026 | 3 | MO
1027 | 1 | MO
1027 | 2 | MO
1027 | 3 | MO
894 | 1 | MO
894 | 2 | MO
966 | 1 | MO
966 | 2 | MO
966 | 3 | MO
1089 | 1 | MO
903 | 1 | MO
904 | 1 | MO
1033 | 1 | MO
1033 | 2 | MO
1033 | 3 | MO
1034 | 1 | MO
1034 | 2 | MO
1034 | 3 | MO
865 | 3 | MO
1228 | 2 | MO
1228 | 3 | MO
865 | 1 | MO
865 | 2 | MO
1164 | 1 | MO
864 | 1 | MO
897 | 1 | MO
864 | 2 | MO
864 | 4 | MO
1228 | 1 | MO
1273 | 1 | MO | Ameren Missouri
1274 | 1 | MO | Ameren Missouri
1274 | 2 | MO | Ameren Missouri
1262 | 1 | MO
1201 | 1 | MO | Ameren Missouri
1200 | 1 | MO | Ameren Missouri
1261 | 1 | MO
867 | 1 | MO
1166 | 1 | MO
867 | 2 | MO
867 | 3 | MO
866 | 1 | MO
898 | 1 | MO
866 | 2 | MO
866 | 3 | MO
1229 | 1 | MO
1229 | 2 | MO
1229 | 3 | MO
1035 | 1 | MO
1035 | 2 | MO
1035 | 3 | MO
1036 | 1 | MO
1036 | 2 | MO
1036 | 3 | MO
953 | 1 | MO
967 | 1 | MO
967 | 2 | MO
1090 | 1 | MO
942 | 1 | MO
942 | 2 | MO
942 | 3 | MO
868 | 1 | MO
1168 | 1 | MO
868 | 2 | MO
868 | 3 | MO
1037 | 1 | MO
1037 | 2 | MO
1037 | 3 | MO
1167 | 1 | MO
899 | 1 | MO
1167 | 2 | MO
1167 | 3 | MO
1038 | 1 | MO
1038 | 2 | MO
1272 | 1 | MO | Ameren Missouri
1272 | 2 | MO | Ameren Missouri
860 | 1 | MO
859 | 1 | MO
859 | 2 | MO
859 | 3 | MO
1233 | 1 | MO | Ameren Missouri
1005 | 1 | MO
1005 | 2 | MO
950 | 1 | MO
1075 | 1 | MO
1234 | 1 | MO | Ameren Missouri
1006 | 1 | MO
1006 | 2 | MO
951 | 1 | MO
1076 | 1 | MO
1235 | 1 | MO | Ameren Missouri
991 | 1 | MO
991 | 2 | MO
936 | 1 | MO
1064 | 1 | MO
1236 | 1 | MO | Ameren Missouri
992 | 1 | MO
992 | 2 | MO
937 | 1 | MO
1065 | 1 | MO
1246 | 1 | MO
995 | 1 | MO
995 | 2 | MO
995 | 3 | MO
995 | 4 | MO
940 | 1 | MO
940 | 2 | MO
940 | 3 | MO
996 | 1 | MO
996 | 2 | MO
996 | 3 | MO
1068 | 1 | MO
997 | 1 | MO
997 | 2 | MO
1217 | 1 | MO | Ameren Missouri
1213 | 1 | MO | Ameren Missouri
998 | 1 | MO
998 | 2 | MO
1216 | 1 | MO | Ameren Missouri
1214 | 1 | MO | Ameren Missouri
1265 | 1 | MO
1255 | 1 | MO
1256 | 1 | MO
1172 | 1 | MO
1254 | 1 | MO
3 | 1 | MO
3 | 2 | MO
4 | 1 | MO
4 | 2 | MO
1275 | 1 | MO | Ameren Missouri
1237 | 2 | MO | Ameren Missouri
1237 | 1 | MO | Ameren Missouri
1276 | 1 | MO | Ameren Missouri
1238 | 2 | MO | Ameren Missouri
1238 | 1 | MO | Ameren Missouri
993 | 1 | MO
993 | 2 | MO
993 | 3 | MO
855 | 1 | MO
938 | 1 | MO
994 | 1 | MO
994 | 2 | MO
1066 | 1 | MO
856 | 1 | MO
856 | 2 | MO
939 | 1 | MO
939 | 2 | MO
1067 | 1 | MO
1258 | 1 | MO
1258 | 2 | MO
1031 | 3 | MO
1030 | 1 | MO
1030 | 2 | MO
1030 | 3 | MO
1031 | 2 | MO
1031 | 1 | MO
862 | 1 | MO
862 | 3 | MO
895 | 1 | MO
895 | 2 | MO
861 | 1 | MO
861 | 2 | MO
861 | 3 | MO
969 | 1 | MO
871 | 1 | MO
871 | 2 | MO
901 | 1 | MO
1091 | 1 | MO
1039 | 1 | MO
1039 | 2 | MO
1041 | 1 | MO
1041 | 2 | MO
870 | 1 | MO
900 | 1 | MO
1032 | 1 | MO
1215 | 1 | MO | Ameren Missouri
863 | 1 | MO
863 | 2 | MO
896 | 1 | MO
896 | 2 | MO
1212 | 1 | MO | Ameren Missouri
970 | 1 | MO
970 | 2 | MO
971 | 1 | MO
882 | 2 | MO
882 | 4 | MO
882 | 1 | MO
1211 | 1 | MO | Ameren Missouri
1045 | 1 | MO
1045 | 2 | MO
726 | 1 | MO
726-1 | 1 | MO | Ameren Missouri
727 | 1 | MO
728 | 1 | MO
2800 | 1 | MO
2801 | 1 | MO
2802 | 1 | MO
2803 | 1 | MO
2804 | 1 | MO
2805 | 1 | MO
2806 | 1 | MO
2807 | 1 | MO
2808 | 1 | MO
2809 | 1 | MO
2810 | 1 | MO
2811 | 1 | MO
2812 | 1 | MO
2813 | 1 | MO
2814 | 1 | MO
2815 | 1 | MO
2816 | 1 | MO
2817 | 1 | MO
2818 | 1 | MO
2819 | 1 | MO
2820 | 1 | MO
2821 | 1 | MO
691 | 1 | MO
692 | 1 | MO
674 | 1 | MO
1169 | 1 | MO
3027 | 1 | MO
3027-1 | 1 | MO
693 | 1 | MO
679 | 1 | MO
679 | 2 | MO
679 | 3 | MO
1094 | 1 | MO
1093 | 1 | MO
675 | 1 | MO
676 | 1 | MO
677 | 1 | MO
678 | 1 | MO
686 | 1 | MO
687 | 1 | MO
695 | 1 | MO
683 | 1 | MO
684 | 1 | MO
685 | 1 | MO
3058 | 1 | MO
3000 | 1 | MO
1184 | 1 | MO
1191 | 1 | MO
697 | 1 | MO
3085 | 1 | MO | Ameren Missouri
681 | 1 | MO
3046 | 1 | MO | Ameren Missouri
3045 | 1 | MO | Ameren Missouri
3047 | 1 | MO | Ameren Missouri
3052 | 1 | MO | Ameren Missouri
3051 | 1 | MO | Ameren Missouri
3053 | 1 | MO | Ameren Missouri
3049 | 1 | MO | Ameren Missouri
3048 | 1 | MO | Ameren Missouri
3050 | 1 | MO | Ameren Missouri
3040 | 1 | MO | Ameren Missouri
3041 | 1 | MO | Ameren Missouri
3042 | 1 | MO | Ameren Missouri
3044 | 1 | MO | Ameren Missouri
673 | 1 | MO
4001 | 1 | MO | Ameren Missouri
671 | 1 | MO
2732 | 1 | MO
2733 | 1 | MO
705 | 1 | MO
705 | 2 | MO
2734 | 1 | MO
2735 | 1 | MO
2736 | 1 | MO
2737 | 1 | MO
706 | 1 | MO
706 | 2 | MO
2738 | 1 | MO
2739 | 1 | MO
2740 | 1 | MO
707 | 1 | MO
707 | 2 | MO
2741 | 1 | MO
2742 | 1 | MO
2721 | 1 | MO
2722 | 1 | MO
708 | 1 | MO
708 | 2 | MO
2723 | 1 | MO
2724 | 1 | MO
2725 | 1 | MO
2726 | 1 | MO
2727 | 1 | MO
2728 | 1 | MO
709 | 1 | MO
709 | 2 | MO
2729 | 1 | MO
710 | 1 | MO
710 | 2 | MO
2730 | 1 | MO
2731 | 1 | MO
2709 | 1 | MO
2710 | 1 | MO
711 | 1 | MO
2712 | 1 | MO
2713 | 1 | MO
2714 | 1 | MO
2715 | 1 | MO
712 | 1 | MO
2716 | 1 | MO
2717 | 1 | MO
2718 | 1 | MO
713 | 1 | MO
2719 | 1 | MO
2720 | 1 | MO
2771 | 1 | MO
2772 | 1 | MO
714 | 1 | MO
714 | 2 | MO
2773 | 1 | MO
2774 | 1 | MO
2775 | 1 | MO
2776 | 1 | MO
2777 | 1 | MO
715 | 1 | MO
715 | 2 | MO
2778 | 1 | MO
2779 | 1 | MO
2780 | 1 | MO
2781 | 1 | MO
2782 | 1 | MO
716 | 1 | MO
716 | 2 | MO
2783 | 1 | MO
2784 | 1 | MO
2757 | 1 | MO
2758 | 1 | MO
717 | 1 | MO
717 | 2 | MO
2759 | 1 | MO
2760 | 1 | MO
2761 | 1 | MO
2762 | 1 | MO
2763 | 1 | MO
718 | 1 | MO
718 | 2 | MO
2764 | 1 | MO
2765 | 1 | MO
2766 | 1 | MO
2767 | 1 | MO
2768 | 1 | MO
719 | 1 | MO
719 | 2 | MO
2769 | 1 | MO
2770 | 1 | MO
2743 | 1 | MO
2744 | 1 | MO
720 | 1 | MO
720 | 2 | MO
2745 | 1 | MO
2746 | 1 | MO
2747 | 1 | MO
2748 | 1 | MO
2749 | 1 | MO
721 | 1 | MO
721 | 2 | MO
2750 | 1 | MO
2751 | 1 | MO
2752 | 1 | MO
2753 | 1 | MO
2754 | 1 | MO
722 | 1 | MO
722 | 2 | MO
2755 | 1 | MO
2756 | 1 | MO
3059 | 1 | MO
3060 | 1 | MO
3061 | 1 | MO
776-1 | 2 | MO
776-10 | 2 | MO
776-15 | 2 | MO
776-19 | 2 | MO
776-4 | 2 | MO
776-5 | 2 | MO
776-11 | 2 | MO
776-12 | 2 | MO
776-6 | 2 | MO
776-7 | 2 | MO
776-13 | 2 | MO
776-9 | 2 | MO
776-14 | 2 | MO
776-16 | 2 | MO
776-8 | 2 | MO
776-18 | 2 | MO
776-3 | 2 | MO
776-2 | 2 | MO
776-20 | 2 | MO
731-1 | 2 | MO
731-10 | 2 | MO
731-15 | 2 | MO
731-19 | 2 | MO
731-4 | 2 | MO
731-5 | 2 | MO
731-11 | 2 | MO
731-12 | 2 | MO
731-6 | 2 | MO
731-7 | 2 | MO
731-13 | 2 | MO
731-9 | 2 | MO
731-14 | 2 | MO
731-16 | 2 | MO
731-8 | 2 | MO
731-18 | 2 | MO
731-3 | 2 | MO
731-2 | 2 | MO
731-20 | 2 | MO
3084 | 1 | MO
738-1 | 3 | MO
738-10 | 3 | MO
738-15 | 3 | MO
738-19 | 3 | MO
738-4 | 3 | MO
738-5 | 3 | MO
738-11 | 3 | MO
738-12 | 3 | MO
738-6 | 3 | MO
738-7 | 3 | MO
738-13 | 3 | MO
738-9 | 3 | MO
738-14 | 3 | MO
738-16 | 3 | MO
738-8 | 3 | MO
738-18 | 3 | MO
738-3 | 3 | MO
738-2 | 3 | MO
738-20 | 3 | MO
739-1 | 3 | MO
739-10 | 3 | MO
739-15 | 3 | MO
739-19 | 3 | MO
739-4 | 3 | MO
739-5 | 3 | MO
739-11 | 3 | MO
739-12 | 3 | MO
739-6 | 3 | MO
739-7 | 3 | MO
739-13 | 3 | MO
739-9 | 3 | MO
739-14 | 3 | MO
739-16 | 3 | MO
739-8 | 3 | MO
739-18 | 3 | MO
739-3 | 3 | MO
739-2 | 3 | MO
739-20 | 3 | MO
3075 | 1 | MO
757-1 | 2 | MO
757-10 | 2 | MO
757-15 | 2 | MO
757-19 | 2 | MO
757-4 | 2 | MO
757-5 | 2 | MO
757-11 | 2 | MO
757-12 | 2 | MO
757-6 | 2 | MO
757-7 | 2 | MO
757-13 | 2 | MO
757-9 | 2 | MO
757-14 | 2 | MO
757-16 | 2 | MO
757-8 | 2 | MO
757-18 | 2 | MO
757-3 | 2 | MO
757-2 | 2 | MO
757-20 | 2 | MO
758-1 | 2 | MO
758-10 | 2 | MO
758-15 | 2 | MO
758-19 | 2 | MO
758-4 | 2 | MO
758-5 | 2 | MO
758-11 | 2 | MO
758-12 | 2 | MO
758-6 | 2 | MO
758-7 | 2 | MO
758-13 | 2 | MO
758-9 | 2 | MO
758-14 | 2 | MO
758-16 | 2 | MO
758-8 | 2 | MO
758-18 | 2 | MO
758-3 | 2 | MO
758-2 | 2 | MO
758-20 | 2 | MO
759-1 | 2 | MO
759-10 | 2 | MO
759-15 | 2 | MO
759-19 | 2 | MO
759-4 | 2 | MO
759-5 | 2 | MO
759-11 | 2 | MO
759-12 | 2 | MO
759-6 | 2 | MO
759-7 | 2 | MO
759-13 | 2 | MO
759-9 | 2 | MO
759-14 | 2 | MO
759-16 | 2 | MO
759-8 | 2 | MO
759-18 | 2 | MO
759-3 | 2 | MO
759-2 | 2 | MO
759-20 | 2 | MO
760-1 | 2 | MO
760-10 | 2 | MO
760-15 | 2 | MO
760-19 | 2 | MO
760-4 | 2 | MO
760-5 | 2 | MO
760-11 | 2 | MO
760-12 | 2 | MO
760-6 | 2 | MO
760-7 | 2 | MO
760-13 | 2 | MO
760-9 | 2 | MO
760-14 | 2 | MO
760-16 | 2 | MO
760-8 | 2 | MO
760-18 | 2 | MO
760-3 | 2 | MO
760-2 | 2 | MO
760-20 | 2 | MO
761-1 | 2 | MO
761-10 | 2 | MO
761-15 | 2 | MO
761-19 | 2 | MO
761-4 | 2 | MO
761-5 | 2 | MO
761-11 | 2 | MO
761-12 | 2 | MO
761-6 | 2 | MO
761-7 | 2 | MO
761-13 | 2 | MO
761-9 | 2 | MO
761-14 | 2 | MO
761-16 | 2 | MO
761-8 | 2 | MO
761-18 | 2 | MO
761-3 | 2 | MO
761-2 | 2 | MO
761-20 | 2 | MO
762-1 | 3 | MO
762-10 | 3 | MO
762-15 | 3 | MO
762-19 | 3 | MO
762-4 | 3 | MO
762-5 | 3 | MO
762-11 | 3 | MO
762-12 | 3 | MO
762-6 | 3 | MO
762-7 | 3 | MO
762-13 | 3 | MO
762-9 | 3 | MO
762-14 | 3 | MO
762-16 | 3 | MO
762-8 | 3 | MO
762-18 | 3 | MO
762-3 | 3 | MO
762-2 | 3 | MO
762-20 | 3 | MO
3003 | 1 | MO
3062 | 1 | MO
3063 | 1 | MO
779-1 | 1 | MO
779-10 | 1 | MO
779-15 | 1 | MO
779-19 | 1 | MO
779-4 | 1 | MO
779-5 | 1 | MO
779-11 | 1 | MO
779-12 | 1 | MO
779-6 | 1 | MO
779-7 | 1 | MO
779-13 | 1 | MO
779-9 | 1 | MO
779-14 | 1 | MO
779-16 | 1 | MO
779-8 | 1 | MO
779-18 | 1 | MO
779-3 | 1 | MO
779-2 | 1 | MO
779-20 | 1 | MO
3004-1 | 2 | MO
3004-2 | 2 | MO
3005-1 | 2 | MO
3005-2 | 2 | MO
3006-1 | 1 | MO
3006-2 | 1 | MO
3007 | 2 | MO
3007-1 | 1 | MO
3008 | 2 | MO
3010 | 2 | MO
3009 | 1 | MO
3011 | 1 | MO
8001 | 1 | MO
8000 | 1 | MO
793-1 | 2 | MO
793-10 | 2 | MO
793-15 | 2 | MO
793-19 | 2 | MO
793-4 | 2 | MO
793-5 | 2 | MO
793-11 | 2 | MO
793-12 | 2 | MO
793-6 | 2 | MO
793-7 | 2 | MO
793-13 | 2 | MO
793-9 | 2 | MO
793-14 | 2 | MO
793-16 | 2 | MO
793-8 | 2 | MO
793-18 | 2 | MO
793-3 | 2 | MO
793-2 | 2 | MO
793-20 | 2 | MO
3012 | 1 | MO
3012 | 1 | MO
3013 | 2 | MO
3023 | 1 | MO
3023 | 1 | MO
3024 | 1 | MO
3025 | 2 | MO
3026 | 2 | MO
3019 | 1 | MO
3020 | 1 | MO
3021 | 1 | MO
3022 | 1 | MO
3081 | 1 | MO
3082 | 1 | MO
3083 | 1 | MO
3076 | 1 | MO
3077 | 1 | MO
3079 | 1 | MO
3080 | 1 | MO
3016 | 1 | MO
786-1 | 2 | MO
786-10 | 2 | MO
786-15 | 2 | MO
786-19 | 2 | MO
786-4 | 2 | MO
786-5 | 2 | MO
786-11 | 2 | MO
786-12 | 2 | MO
786-6 | 2 | MO
786-7 | 2 | MO
786-13 | 2 | MO
786-9 | 2 | MO
786-14 | 2 | MO
786-16 | 2 | MO
786-8 | 2 | MO
786-18 | 2 | MO
786-3 | 2 | MO
786-2 | 2 | MO
786-20 | 2 | MO
787-1 | 2 | MO
787-10 | 2 | MO
787-15 | 2 | MO
787-19 | 2 | MO
787-4 | 2 | MO
787-5 | 2 | MO
787-11 | 2 | MO
787-12 | 2 | MO
787-6 | 2 | MO
787-7 | 2 | MO
787-13 | 2 | MO
787-9 | 2 | MO
787-14 | 2 | MO
787-16 | 2 | MO
787-8 | 2 | MO
787-18 | 2 | MO
787-3 | 2 | MO
787-2 | 2 | MO
787-20 | 2 | MO
781-1 | 1 | MO
781-10 | 1 | MO
781-15 | 1 | MO
781-19 | 1 | MO
781-4 | 1 | MO
781-5 | 1 | MO
781-11 | 1 | MO
781-12 | 1 | MO
781-6 | 1 | MO
781-7 | 1 | MO
781-13 | 1 | MO
781-9 | 1 | MO
781-14 | 1 | MO
781-16 | 1 | MO
781-8 | 1 | MO
781-18 | 1 | MO
781-3 | 1 | MO
781-2 | 1 | MO
781-20 | 1 | MO
780-1 | 1 | MO
780-10 | 1 | MO
780-15 | 1 | MO
780-19 | 1 | MO
780-4 | 1 | MO
780-5 | 1 | MO
780-11 | 1 | MO
780-12 | 1 | MO
780-6 | 1 | MO
780-7 | 1 | MO
780-13 | 1 | MO
780-9 | 1 | MO
780-14 | 1 | MO
780-16 | 1 | MO
780-8 | 1 | MO
780-18 | 1 | MO
780-3 | 1 | MO
780-2 | 1 | MO
780-20 | 1 | MO
3035 | 1 | MO
3036 | 1 | MO
3037 | 1 | MO
3038 | 1 | MO
3086 | 1 | MO
3088 | 1 | MO
1102-1 | 3 | MO
1102-10 | 3 | MO
1102-15 | 3 | MO
1102-19 | 3 | MO
1102-4 | 3 | MO
1102-5 | 3 | MO
1102-11 | 3 | MO
1102-12 | 3 | MO
1102-6 | 3 | MO
1102-7 | 3 | MO
1102-13 | 3 | MO
1102-9 | 3 | MO
1102-14 | 3 | MO
1102-16 | 3 | MO
1102-8 | 3 | MO
1102-18 | 3 | MO
1102-3 | 3 | MO
1102-2 | 3 | MO
1102-20 | 3 | MO
1106-1 | 3 | MO
1106-10 | 3 | MO
1106-15 | 3 | MO
1106-19 | 3 | MO
1106-4 | 3 | MO
1106-5 | 3 | MO
1106-11 | 3 | MO
1106-12 | 3 | MO
1106-6 | 3 | MO
1106-7 | 3 | MO
1106-13 | 3 | MO
1106-9 | 3 | MO
1106-14 | 3 | MO
1106-16 | 3 | MO
1106-8 | 3 | MO
1106-18 | 3 | MO
1106-3 | 3 | MO
1106-2 | 3 | MO
1106-20 | 3 | MO
3087 | 1 | MO
3089 | 1 | MO
776-1 | 1 | MO
776-10 | 1 | MO
776-15 | 1 | MO
776-19 | 1 | MO
776-4 | 1 | MO
776-5 | 1 | MO
776-11 | 1 | MO
776-12 | 1 | MO
776-6 | 1 | MO
776-7 | 1 | MO
776-13 | 1 | MO
776-9 | 1 | MO
776-14 | 1 | MO
776-16 | 1 | MO
776-8 | 1 | MO
776-18 | 1 | MO
776-3 | 1 | MO
776-2 | 1 | MO
776-20 | 1 | MO
731-1 | 1 | MO
731-10 | 1 | MO
731-15 | 1 | MO
731-19 | 1 | MO
731-4 | 1 | MO
731-5 | 1 | MO
731-11 | 1 | MO
731-12 | 1 | MO
731-6 | 1 | MO
731-7 | 1 | MO
731-13 | 1 | MO
731-9 | 1 | MO
731-14 | 1 | MO
731-16 | 1 | MO
731-8 | 1 | MO
731-18 | 1 | MO
731-3 | 1 | MO
731-2 | 1 | MO
731-20 | 1 | MO
3001 | 1 | MO | Ameren Missouri
3002 | 1 | MO | Ameren Missouri
746-1 | 1 | MO
746-1 | 2 | MO
745-10 | 1 | MO
745-10 | 2 | MO
745-15 | 1 | MO
745-15 | 2 | MO
745-19 | 1 | MO
745-19 | 2 | MO
745-4 | 1 | MO
745-4 | 2 | MO
745-5 | 1 | MO
745-5 | 2 | MO
745-11 | 1 | MO
745-11 | 2 | MO
745-12 | 1 | MO
745-12 | 2 | MO
745-6 | 1 | MO
745-6 | 2 | MO
745-7 | 1 | MO
745-7 | 2 | MO
745-13 | 1 | MO
745-13 | 2 | MO
745-9 | 1 | MO
745-9 | 2 | MO
745-14 | 1 | MO
745-14 | 2 | MO
745-16 | 1 | MO
745-16 | 2 | MO
745-8 | 1 | MO
745-8 | 2 | MO
745-18 | 1 | MO
745-18 | 2 | MO
745-3 | 1 | MO
745-3 | 2 | MO
745-2 | 1 | MO
745-2 | 2 | MO
745-20 | 1 | MO
745-20 | 2 | MO
749-1 | 1 | MO
749-1 | 2 | MO
749-10 | 1 | MO
749-10 | 2 | MO
749-15 | 1 | MO
749-15 | 2 | MO
749-19 | 1 | MO
749-19 | 2 | MO
749-4 | 1 | MO
749-4 | 2 | MO
749-5 | 1 | MO
749-5 | 2 | MO
749-11 | 1 | MO
749-11 | 2 | MO
749-12 | 1 | MO
749-12 | 2 | MO
749-6 | 1 | MO
749-6 | 2 | MO
749-7 | 1 | MO
749-7 | 2 | MO
749-13 | 1 | MO
749-13 | 2 | MO
749-9 | 1 | MO
749-9 | 2 | MO
749-14 | 1 | MO
749-14 | 2 | MO
749-16 | 1 | MO
749-16 | 2 | MO
749-8 | 1 | MO
749-8 | 2 | MO
749-18 | 1 | MO
749-18 | 2 | MO
749-3 | 1 | MO
749-3 | 2 | MO
749-2 | 1 | MO
749-2 | 2 | MO
749-20 | 1 | MO
749-20 | 2 | MO
773-1 | 1 | MO
773-1 | 2 | MO
773-10 | 1 | MO
773-10 | 2 | MO
773-15 | 1 | MO
773-15 | 2 | MO
773-19 | 1 | MO
773-19 | 2 | MO
773-4 | 1 | MO
773-4 | 2 | MO
773-5 | 1 | MO
773-5 | 2 | MO
773-11 | 1 | MO
773-11 | 2 | MO
773-12 | 1 | MO
773-12 | 2 | MO
773-6 | 1 | MO
773-6 | 2 | MO
773-7 | 1 | MO
773-7 | 2 | MO
773-13 | 1 | MO
773-13 | 2 | MO
773-9 | 1 | MO
773-9 | 2 | MO
773-14 | 1 | MO
773-14 | 2 | MO
773-16 | 1 | MO
773-16 | 2 | MO
773-8 | 1 | MO
773-8 | 2 | MO
773-18 | 1 | MO
773-18 | 2 | MO
773-3 | 1 | MO
773-3 | 2 | MO
773-2 | 1 | MO
773-2 | 2 | MO
773-20 | 1 | MO
773-20 | 2 | MO
784-1 | 1 | MO
784-10 | 1 | MO
784-15 | 1 | MO
784-19 | 1 | MO
784-4 | 1 | MO
784-5 | 1 | MO
784-11 | 1 | MO
784-12 | 1 | MO
784-6 | 1 | MO
784-7 | 1 | MO
784-13 | 1 | MO
784-9 | 1 | MO
784-14 | 1 | MO
784-16 | 1 | MO
784-8 | 1 | MO
784-18 | 1 | MO
784-3 | 1 | MO
784-2 | 1 | MO
784-20 | 1 | MO
738-1 | 1 | MO
738-1 | 2 | MO
738-10 | 1 | MO
738-10 | 2 | MO
738-15 | 1 | MO
738-15 | 2 | MO
738-19 | 1 | MO
738-19 | 2 | MO
738-4 | 1 | MO
738-4 | 2 | MO
738-5 | 1 | MO
738-5 | 2 | MO
738-11 | 1 | MO
738-11 | 2 | MO
738-12 | 1 | MO
738-12 | 2 | MO
738-6 | 1 | MO
738-6 | 2 | MO
738-7 | 1 | MO
738-7 | 2 | MO
738-13 | 1 | MO
738-13 | 2 | MO
738-9 | 1 | MO
738-9 | 2 | MO
738-14 | 1 | MO
738-14 | 2 | MO
738-16 | 1 | MO
738-16 | 2 | MO
738-8 | 1 | MO
738-8 | 2 | MO
738-18 | 1 | MO
738-18 | 2 | MO
738-3 | 1 | MO
738-3 | 2 | MO
738-2 | 1 | MO
738-2 | 2 | MO
738-20 | 1 | MO
738-20 | 2 | MO
739-1 | 1 | MO
739-1 | 2 | MO
739-10 | 1 | MO
739-10 | 2 | MO
739-15 | 1 | MO
739-15 | 2 | MO
739-19 | 1 | MO
739-19 | 2 | MO
739-4 | 1 | MO
739-4 | 2 | MO
739-5 | 1 | MO
739-5 | 2 | MO
739-11 | 1 | MO
739-11 | 2 | MO
739-12 | 1 | MO
739-12 | 2 | MO
739-6 | 1 | MO
739-6 | 2 | MO
739-7 | 1 | MO
739-7 | 2 | MO
739-13 | 1 | MO
739-13 | 2 | MO
739-9 | 1 | MO
739-9 | 2 | MO
739-14 | 1 | MO
739-14 | 2 | MO
739-16 | 1 | MO
739-16 | 2 | MO
739-8 | 1 | MO
739-8 | 2 | MO
739-18 | 1 | MO
739-18 | 2 | MO
739-3 | 1 | MO
739-3 | 2 | MO
739-2 | 1 | MO
739-2 | 2 | MO
739-20 | 1 | MO
739-20 | 2 | MO
742-1 | 1 | MO
742-1 | 2 | MO
742-10 | 1 | MO
742-10 | 2 | MO
742-15 | 1 | MO
742-15 | 2 | MO
742-19 | 1 | MO
742-19 | 2 | MO
742-4 | 1 | MO
742-4 | 2 | MO
742-5 | 1 | MO
742-5 | 2 | MO
742-11 | 1 | MO
742-11 | 2 | MO
742-12 | 1 | MO
742-12 | 2 | MO
742-6 | 1 | MO
742-6 | 2 | MO
742-7 | 1 | MO
742-7 | 2 | MO
742-13 | 1 | MO
742-13 | 2 | MO
742-9 | 1 | MO
742-9 | 2 | MO
742-14 | 1 | MO
742-14 | 2 | MO
742-16 | 1 | MO
742-16 | 2 | MO
742-8 | 1 | MO
742-8 | 2 | MO
742-18 | 1 | MO
742-18 | 2 | MO
742-3 | 1 | MO
742-3 | 2 | MO
742-2 | 1 | MO
742-2 | 2 | MO
742-20 | 1 | MO
742-20 | 2 | MO
743-1 | 1 | MO
743-1 | 2 | MO
743-10 | 1 | MO
743-10 | 2 | MO
743-15 | 1 | MO
743-15 | 2 | MO
743-19 | 1 | MO
743-19 | 2 | MO
743-4 | 1 | MO
743-4 | 2 | MO
743-5 | 1 | MO
743-5 | 2 | MO
743-11 | 1 | MO
743-11 | 2 | MO
743-12 | 1 | MO
743-12 | 2 | MO
743-6 | 1 | MO
743-6 | 2 | MO
743-7 | 1 | MO
743-7 | 2 | MO
743-13 | 1 | MO
743-13 | 2 | MO
743-9 | 1 | MO
743-9 | 2 | MO
743-14 | 1 | MO
743-14 | 2 | MO
743-16 | 1 | MO
743-16 | 2 | MO
743-8 | 1 | MO
743-8 | 2 | MO
743-18 | 1 | MO
743-18 | 2 | MO
743-3 | 1 | MO
743-3 | 2 | MO
743-2 | 1 | MO
743-2 | 2 | MO
743-20 | 1 | MO
743-20 | 2 | MO
757-1 | 1 | MO
757-10 | 1 | MO
757-15 | 1 | MO
757-19 | 1 | MO
757-4 | 1 | MO
757-5 | 1 | MO
757-11 | 1 | MO
757-12 | 1 | MO
757-6 | 1 | MO
757-7 | 1 | MO
757-13 | 1 | MO
757-9 | 1 | MO
757-14 | 1 | MO
757-16 | 1 | MO
757-8 | 1 | MO
757-18 | 1 | MO
757-3 | 1 | MO
757-2 | 1 | MO
757-20 | 1 | MO
758-1 | 1 | MO
758-10 | 1 | MO
758-15 | 1 | MO
758-19 | 1 | MO
758-4 | 1 | MO
758-5 | 1 | MO
758-11 | 1 | MO
758-12 | 1 | MO
758-6 | 1 | MO
758-7 | 1 | MO
758-13 | 1 | MO
758-9 | 1 | MO
758-14 | 1 | MO
758-16 | 1 | MO
758-8 | 1 | MO
758-18 | 1 | MO
758-3 | 1 | MO
758-2 | 1 | MO
758-20 | 1 | MO
759-1 | 1 | MO
759-10 | 1 | MO
759-15 | 1 | MO
759-19 | 1 | MO
759-4 | 1 | MO
759-5 | 1 | MO
759-11 | 1 | MO
759-12 | 1 | MO
759-6 | 1 | MO
759-7 | 1 | MO
759-13 | 1 | MO
759-9 | 1 | MO
759-14 | 1 | MO
759-16 | 1 | MO
759-8 | 1 | MO
759-18 | 1 | MO
759-3 | 1 | MO
759-2 | 1 | MO
759-20 | 1 | MO
760-1 | 1 | MO
760-10 | 1 | MO
760-15 | 1 | MO
760-19 | 1 | MO
760-4 | 1 | MO
760-5 | 1 | MO
760-11 | 1 | MO
760-12 | 1 | MO
760-6 | 1 | MO
760-7 | 1 | MO
760-13 | 1 | MO
760-9 | 1 | MO
760-14 | 1 | MO
760-16 | 1 | MO
760-8 | 1 | MO
760-18 | 1 | MO
760-3 | 1 | MO
760-2 | 1 | MO
760-20 | 1 | MO
761-1 | 1 | MO
761-10 | 1 | MO
761-15 | 1 | MO
761-19 | 1 | MO
761-4 | 1 | MO
761-5 | 1 | MO
761-11 | 1 | MO
761-12 | 1 | MO
761-6 | 1 | MO
761-7 | 1 | MO
761-13 | 1 | MO
761-9 | 1 | MO
761-14 | 1 | MO
761-16 | 1 | MO
761-8 | 1 | MO
761-18 | 1 | MO
761-3 | 1 | MO
761-2 | 1 | MO
761-20 | 1 | MO
762-1 | 1 | MO
762-1 | 2 | MO
762-10 | 1 | MO
762-10 | 2 | MO
762-15 | 1 | MO
762-15 | 2 | MO
762-19 | 1 | MO
762-19 | 2 | MO
762-4 | 1 | MO
762-4 | 2 | MO
762-5 | 1 | MO
762-5 | 2 | MO
762-11 | 1 | MO
762-11 | 2 | MO
762-12 | 1 | MO
762-12 | 2 | MO
762-6 | 1 | MO
762-6 | 2 | MO
762-7 | 1 | MO
762-7 | 2 | MO
762-13 | 1 | MO
762-13 | 2 | MO
762-9 | 1 | MO
762-9 | 2 | MO
762-14 | 1 | MO
762-14 | 2 | MO
762-16 | 1 | MO
762-16 | 2 | MO
762-8 | 1 | MO
762-8 | 2 | MO
762-18 | 1 | MO
762-18 | 2 | MO
762-3 | 1 | MO
762-3 | 2 | MO
762-2 | 1 | MO
762-2 | 2 | MO
762-20 | 1 | MO
762-20 | 2 | MO
740-1 | 1 | MO
740-1 | 2 | MO
740-10 | 1 | MO
740-10 | 2 | MO
740-15 | 1 | MO
740-15 | 2 | MO
740-19 | 1 | MO
740-19 | 2 | MO
740-4 | 1 | MO
740-4 | 2 | MO
740-5 | 1 | MO
740-5 | 2 | MO
740-11 | 1 | MO
740-11 | 2 | MO
740-12 | 1 | MO
740-12 | 2 | MO
740-6 | 1 | MO
740-6 | 2 | MO
740-7 | 1 | MO
740-7 | 2 | MO
740-13 | 1 | MO
740-13 | 2 | MO
740-9 | 1 | MO
740-9 | 2 | MO
740-14 | 1 | MO
740-14 | 2 | MO
740-16 | 1 | MO
740-16 | 2 | MO
740-8 | 1 | MO
740-8 | 2 | MO
740-18 | 1 | MO
740-18 | 2 | MO
740-3 | 1 | MO
740-3 | 2 | MO
740-2 | 1 | MO
740-2 | 2 | MO
740-20 | 1 | MO
740-20 | 2 | MO
741-1 | 1 | MO
741-1 | 2 | MO
741-10 | 1 | MO
741-10 | 2 | MO
741-15 | 1 | MO
741-15 | 2 | MO
741-19 | 1 | MO
741-19 | 2 | MO
741-4 | 1 | MO
741-4 | 2 | MO
741-5 | 1 | MO
741-5 | 2 | MO
741-11 | 1 | MO
741-11 | 2 | MO
741-12 | 1 | MO
741-12 | 2 | MO
741-6 | 1 | MO
741-6 | 2 | MO
741-7 | 1 | MO
741-7 | 2 | MO
741-13 | 1 | MO
741-13 | 2 | MO
741-9 | 1 | MO
741-9 | 2 | MO
741-14 | 1 | MO
741-14 | 2 | MO
741-16 | 1 | MO
741-16 | 2 | MO
741-8 | 1 | MO
741-8 | 2 | MO
741-18 | 1 | MO
741-18 | 2 | MO
741-3 | 1 | MO
741-3 | 2 | MO
741-2 | 1 | MO
741-2 | 2 | MO
741-20 | 1 | MO
741-20 | 2 | MO
3004-1 | 1 | MO | Ameren Missouri
3004-2 | 1 | MO | Ameren Missouri
3005-1 | 1 | MO | Ameren Missouri
3005-2 | 1 | MO | Ameren Missouri
3007 | 1 | MO | Ameren Missouri
3008 | 1 | MO | Ameren Missouri
3010 | 1 | MO | Ameren Missouri
734-1 | 1 | MO
734-1 | 2 | MO
734-10 | 1 | MO
734-10 | 2 | MO
734-15 | 1 | MO
734-15 | 2 | MO
734-19 | 1 | MO
734-19 | 2 | MO
734-4 | 1 | MO
734-4 | 2 | MO
734-5 | 1 | MO
734-5 | 2 | MO
734-11 | 1 | MO
734-11 | 2 | MO
734-12 | 1 | MO
734-12 | 2 | MO
734-6 | 1 | MO
734-6 | 2 | MO
734-7 | 1 | MO
734-7 | 2 | MO
734-13 | 1 | MO
734-13 | 2 | MO
734-9 | 1 | MO
734-9 | 2 | MO
734-14 | 1 | MO
734-14 | 2 | MO
734-16 | 1 | MO
734-16 | 2 | MO
734-8 | 1 | MO
734-8 | 2 | MO
734-18 | 1 | MO
734-18 | 2 | MO
734-3 | 1 | MO
734-3 | 2 | MO
734-2 | 1 | MO
734-2 | 2 | MO
734-20 | 1 | MO
734-20 | 2 | MO
793-1 | 1 | MO
793-10 | 1 | MO
793-15 | 1 | MO
793-19 | 1 | MO
793-4 | 1 | MO
793-5 | 1 | MO
793-11 | 1 | MO
793-12 | 1 | MO
793-6 | 1 | MO
793-7 | 1 | MO
793-13 | 1 | MO
793-9 | 1 | MO
793-14 | 1 | MO
793-16 | 1 | MO
793-8 | 1 | MO
793-18 | 1 | MO
793-3 | 1 | MO
793-2 | 1 | MO
793-20 | 1 | MO
3013 | 1 | MO | Ameren Missouri
3025 | 1 | MO | Ameren Missouri
3026 | 1 | MO | Ameren Missouri
744-1 | 1 | MO
744-1 | 2 | MO
744-10 | 1 | MO
744-10 | 2 | MO
744-15 | 1 | MO
744-15 | 2 | MO
744-19 | 1 | MO
744-19 | 2 | MO
744-4 | 1 | MO
744-4 | 2 | MO
744-5 | 1 | MO
744-5 | 2 | MO
744-11 | 1 | MO
744-11 | 2 | MO
744-12 | 1 | MO
744-12 | 2 | MO
744-6 | 1 | MO
744-6 | 2 | MO
744-7 | 1 | MO
744-7 | 2 | MO
744-13 | 1 | MO
744-13 | 2 | MO
744-9 | 1 | MO
744-9 | 2 | MO
744-14 | 1 | MO
744-14 | 2 | MO
744-16 | 1 | MO
744-16 | 2 | MO
744-8 | 1 | MO
744-8 | 2 | MO
744-18 | 1 | MO
744-18 | 2 | MO
744-3 | 1 | MO
744-3 | 2 | MO
744-2 | 1 | MO
744-2 | 2 | MO
744-20 | 1 | MO
744-20 | 2 | MO
3015 | 1 | MO | Ameren Missouri
3017 | 1 | MO | Ameren Missouri
3018 | 1 | MO | Ameren Missouri
786-1 | 1 | MO
786-10 | 1 | MO
786-15 | 1 | MO
786-19 | 1 | MO
786-4 | 1 | MO
786-5 | 1 | MO
786-11 | 1 | MO
786-12 | 1 | MO
786-6 | 1 | MO
786-7 | 1 | MO
786-13 | 1 | MO
786-9 | 1 | MO
786-14 | 1 | MO
786-16 | 1 | MO
786-8 | 1 | MO
786-18 | 1 | MO
786-3 | 1 | MO
786-2 | 1 | MO
786-20 | 1 | MO
787-1 | 1 | MO
787-10 | 1 | MO
787-15 | 1 | MO
787-19 | 1 | MO
787-4 | 1 | MO
787-5 | 1 | MO
787-11 | 1 | MO
787-12 | 1 | MO
787-6 | 1 | MO
787-7 | 1 | MO
787-13 | 1 | MO
787-9 | 1 | MO
787-14 | 1 | MO
787-16 | 1 | MO
787-8 | 1 | MO
787-18 | 1 | MO
787-3 | 1 | MO
787-2 | 1 | MO
787-20 | 1 | MO
754-1 | 1 | MO
754-1 | 2 | MO
754-10 | 1 | MO
754-10 | 2 | MO
754-15 | 1 | MO
754-15 | 2 | MO
754-19 | 1 | MO
754-19 | 2 | MO
754-4 | 1 | MO
754-4 | 2 | MO
754-5 | 1 | MO
754-5 | 2 | MO
754-11 | 1 | MO
754-11 | 2 | MO
754-12 | 1 | MO
754-12 | 2 | MO
754-6 | 1 | MO
754-6 | 2 | MO
754-7 | 1 | MO
754-7 | 2 | MO
754-13 | 1 | MO
754-13 | 2 | MO
754-9 | 1 | MO
754-9 | 2 | MO
754-14 | 1 | MO
754-14 | 2 | MO
754-16 | 1 | MO
754-16 | 2 | MO
754-8 | 1 | MO
754-8 | 2 | MO
754-18 | 1 | MO
754-18 | 2 | MO
754-3 | 1 | MO
754-3 | 2 | MO
754-2 | 1 | MO
754-2 | 2 | MO
754-20 | 1 | MO
754-20 | 2 | MO
755-1 | 1 | MO
755-1 | 2 | MO
755-10 | 1 | MO
755-10 | 2 | MO
755-15 | 1 | MO
755-15 | 2 | MO
755-19 | 1 | MO
755-19 | 2 | MO
755-4 | 1 | MO
755-4 | 2 | MO
755-5 | 1 | MO
755-5 | 2 | MO
755-11 | 1 | MO
755-11 | 2 | MO
755-12 | 1 | MO
755-12 | 2 | MO
755-6 | 1 | MO
755-6 | 2 | MO
755-7 | 1 | MO
755-7 | 2 | MO
755-13 | 1 | MO
755-13 | 2 | MO
755-9 | 1 | MO
755-9 | 2 | MO
755-14 | 1 | MO
755-14 | 2 | MO
755-16 | 1 | MO
755-16 | 2 | MO
755-8 | 1 | MO
755-8 | 2 | MO
755-18 | 1 | MO
755-18 | 2 | MO
755-3 | 1 | MO
755-3 | 2 | MO
755-2 | 1 | MO
755-2 | 2 | MO
755-20 | 1 | MO
755-20 | 2 | MO
756-1 | 1 | MO
756-1 | 2 | MO
756-10 | 1 | MO
756-10 | 2 | MO
756-15 | 1 | MO
756-15 | 2 | MO
756-19 | 1 | MO
756-19 | 2 | MO
756-4 | 1 | MO
756-4 | 2 | MO
756-5 | 1 | MO
756-5 | 2 | MO
756-11 | 1 | MO
756-11 | 2 | MO
756-12 | 1 | MO
756-12 | 2 | MO
756-6 | 1 | MO
756-6 | 2 | MO
756-7 | 1 | MO
756-7 | 2 | MO
756-13 | 1 | MO
756-13 | 2 | MO
756-9 | 1 | MO
756-9 | 2 | MO
756-14 | 1 | MO
756-14 | 2 | MO
756-16 | 1 | MO
756-16 | 2 | MO
756-8 | 1 | MO
756-8 | 2 | MO
756-18 | 1 | MO
756-18 | 2 | MO
756-3 | 1 | MO
756-3 | 2 | MO
756-2 | 1 | MO
756-2 | 2 | MO
756-20 | 1 | MO
756-20 | 2 | MO
782-1 | 1 | MO
782-1 | 2 | MO
782-10 | 1 | MO
782-10 | 2 | MO
782-15 | 1 | MO
782-15 | 2 | MO
782-19 | 1 | MO
782-19 | 2 | MO
782-4 | 1 | MO
782-4 | 2 | MO
782-5 | 1 | MO
782-5 | 2 | MO
782-11 | 1 | MO
782-11 | 2 | MO
782-12 | 1 | MO
782-12 | 2 | MO
782-6 | 1 | MO
782-6 | 2 | MO
782-7 | 1 | MO
782-7 | 2 | MO
782-13 | 1 | MO
782-13 | 2 | MO
782-9 | 1 | MO
782-9 | 2 | MO
782-14 | 1 | MO
782-14 | 2 | MO
782-16 | 1 | MO
782-16 | 2 | MO
782-8 | 1 | MO
782-8 | 2 | MO
782-18 | 1 | MO
782-18 | 2 | MO
782-3 | 1 | MO
782-3 | 2 | MO
782-2 | 1 | MO
782-2 | 2 | MO
782-20 | 1 | MO
782-20 | 2 | MO
1102-1 | 1 | MO
1102-1 | 2 | MO
1102-10 | 1 | MO
1102-10 | 2 | MO
1102-15 | 1 | MO
1102-15 | 2 | MO
1102-19 | 1 | MO
1102-19 | 2 | MO
1102-4 | 1 | MO
1102-4 | 2 | MO
1102-5 | 1 | MO
1102-5 | 2 | MO
1102-11 | 1 | MO
1102-11 | 2 | MO
1102-12 | 1 | MO
1102-12 | 2 | MO
1102-6 | 1 | MO
1102-6 | 2 | MO
1102-7 | 1 | MO
1102-7 | 2 | MO
1102-13 | 1 | MO
1102-13 | 2 | MO
1102-9 | 1 | MO
1102-9 | 2 | MO
1102-14 | 1 | MO
1102-14 | 2 | MO
1102-16 | 1 | MO
1102-16 | 2 | MO
1102-8 | 1 | MO
1102-8 | 2 | MO
1102-18 | 1 | MO
1102-18 | 2 | MO
1102-3 | 1 | MO
1102-3 | 2 | MO
1102-2 | 1 | MO
1102-2 | 2 | MO
1102-20 | 1 | MO
1102-20 | 2 | MO
1106-1 | 1 | MO
1106-1 | 2 | MO
1106-10 | 1 | MO
1106-10 | 2 | MO
1106-15 | 1 | MO
1106-15 | 2 | MO
1106-19 | 1 | MO
1106-19 | 2 | MO
1106-4 | 1 | MO
1106-4 | 2 | MO
1106-5 | 1 | MO
1106-5 | 2 | MO
1106-11 | 1 | MO
1106-11 | 2 | MO
1106-12 | 1 | MO
1106-12 | 2 | MO
1106-6 | 1 | MO
1106-6 | 2 | MO
1106-7 | 1 | MO
1106-7 | 2 | MO
1106-13 | 1 | MO
1106-13 | 2 | MO
1106-9 | 1 | MO
1106-9 | 2 | MO
1106-14 | 1 | MO
1106-14 | 2 | MO
1106-16 | 1 | MO
1106-16 | 2 | MO
1106-8 | 1 | MO
1106-8 | 2 | MO
1106-18 | 1 | MO
1106-18 | 2 | MO
1106-3 | 1 | MO
1106-3 | 2 | MO
1106-2 | 1 | MO
1106-2 | 2 | MO
1106-20 | 1 | MO
1106-20 | 2 | MO
3003 | 2 | MO | Ameren Missouri
3057 | 1 | MO | Ameren Missouri
838 | 1 | MO
839 | 1 | MO
839 | 2 | MO
816 | 1 | MO
817 | 1 | MO
825 | 1 | MO
3065 | 1 | MO
826 | 1 | MO
827 | 1 | MO
828 | 1 | MO
829 | 1 | MO
842 | 1 | MO
842 | 2 | MO
843 | 1 | MO
843 | 2 | MO
3028 | 1 | MO | Ameren Missouri
3029 | 1 | MO | Ameren Missouri
830 | 1 | MO
831 | 1 | MO
832 | 1 | MO
833 | 1 | MO
3030 | 1 | MO | Ameren Missouri
3031 | 1 | MO | Ameren Missouri
3032 | 1 | MO | Ameren Missouri
3033 | 1 | MO | Ameren Missouri
834 | 1 | MO
834 | 2 | MO
835 | 1 | MO
835 | 2 | MO
836 | 1 | MO
836 | 2 | MO
3066 | 1 | MO
3067 | 1 | MO
3068 | 1 | MO
846 | 1 | MO
846 | 2 | MO
3054 | 1 | MO | Ameren Missouri
3055 | 1 | MO | Ameren Missouri
3056 | 1 | MO | Ameren Missouri
850 | 1 | MO
851 | 1 | MO
852 | 1 | MO
853 | 1 | MO
854 | 1 | MO
847 | 1 | MO
847 | 2 | MO
848 | 1 | MO
3074 | 1 | MO
3064 | 1 | MO
3069 | 1 | MO
821 | 1 | MO
823 | 1 | MO
1178 | 1 | MO
3071 | 1 | MO
3072 | 1 | MO
849 | 1 | MO
1114 | 1 | MO
795 | 1 | MO
1145 | 1 | MO
1141 | 1 | MO
2795 | 1 | MO
796 | 1 | MO
796 | 2 | MO
1118 | 1 | MO
797 | 1 | MO
1153 | 1 | MO
1149 | 1 | MO
2797 | 1 | MO
798 | 1 | MO
798 | 2 | MO
1126 | 1 | MO
1130 | 1 | MO
799 | 1 | MO
1122 | 1 | MO
1133 | 1 | MO
2799 | 1 | MO
1137 | 1 | MO
800 | 1 | MO
2794 | 1 | MO
837 | 1 | MO
3039 | 1 | MO | Ameren Missouri
1110 | 1 | MO
3073 | 1 | MO
3034 | 1 | MO | Ameren Missouri
845 | 1 | MO
845 | 2 | MO
794 | 1 | MO
801 | 1 | MO
802 | 1 | MO
803 | 1 | MO
804 | 1 | MO
805 | 1 | MO
806 | 1 | MO
807 | 1 | MO
808 | 1 | MO
809 | 1 | MO
810 | 1 | MO
3070 | 1 | MO

## MeasureAttribValParams
Measure Reference Number | Version Number | Attribute Name | Parameter Name | Parameter Value | Parameter Source | Document
972 | 1 | Efficient Case Value | Source Documentation
972 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
972 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
972 | 1 | Baseline Value | Source Documentation
972 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = ((BTU/hr)*((1/EERbase)-(1/EEReff))*EFLHcool/1000)
972 | 2 | Total Gross Incremental Annual Electric Savings_kWh | BTU/hr | 12936
972 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLH secondary unit | 556
972 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %secondary | 0
972 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EEReff | 9.9
972 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLHcool | 860
972 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EERbase | 6.7
972 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
972 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %primary | 1
972 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
972 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLH primary unit | 863
972 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
972 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
972 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
972 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EEReff | 9.9016
972 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLHcool | 860
972 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
972 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
972 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %secondary | 0
972 | 3 | Total Gross Incremental Annual Electric Savings_kWh | BTU/hr | 12022
972 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %primary | 1
972 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
972 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
972 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH secondary unit | 556
972 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = ((BTU/hr)*((1/EERbase)-(1/EEReff))*EFLHcool/1000)
972 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EERbase | 6.7
972 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
972 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH primary unit | 860
973 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
973 | 1 | Efficient Case Value | Source Documentation
973 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
973 | 1 | Baseline Value | Source Documentation
973 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
973 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
973 | 2 | Baseline Value | Source Documentation
973 | 2 | Efficient Case Value | Source Documentation
974 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
974 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
974 | 1 | Baseline Value | Source Documentation
974 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
974 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons)
974 | 2 | Total Gross Incremental Annual Electric Savings_kWh | BTU/hr | 12936
974 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLHcool | 860
974 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLH primary unit | 863
974 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
974 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EEReff | 9.9
974 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
974 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EERbase | 6.7
974 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation E (Energy): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
974 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
974 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
974 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %secondary | 0
974 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLH secondary unit | 556
974 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %primary | 1
974 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = ((BTU/hr)*((1/EERbase)-(1/EEReff))*EFLHcool/1000)
974 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
974 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EEReff | 9.9016
974 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH primary unit | 860
974 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
974 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = ((BTU/hr)*((1/EERbase)-(1/EEReff))*EFLHcool/1000)
974 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EERbase | 6.7
974 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
974 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %primary | 1
974 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %secondary | 0
974 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH secondary unit | 556
974 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
974 | 3 | Total Gross Average Annual Demand Reduction_kW | Equation E (Energy): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
974 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
974 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
974 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLHcool | 860
974 | 3 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons)
974 | 3 | Total Gross Incremental Annual Electric Savings_kWh | BTU/hr | 12022
975 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
975 | 1 | Baseline Value | Source Documentation
975 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
975 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
975 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
975 | 2 | Baseline Value | Source Documentation
975 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
975 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
857 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBtuH (Cooling capacity in Btu/Hour )
857 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERBase
857 | 1 | Total Gross Incremental Annual Electric Savings_kWh | conversion factor between Wh and kWh (Wh/kWh) | 1000
857 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee
857 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
857 | 1 | Baseline Value | Source Documentation
857 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
857 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
857 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
857 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %primary | .16
857 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
857 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Algorithm | Energy Savings = BTU/hr *(1/EERbase-1/EEReff)*EFLH/1000
857 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EEReff | 10.7
857 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %secondary | .84
857 | 2 | Total Gross Incremental Annual Electric Savings_kWh | BTU/hr | 9558
857 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLH primary unit | 860
857 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
857 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
857 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLH secondary unit | 556
857 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
857 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EERbase | 9.8
857 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH secondary unit | 556
857 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %primary | .16
857 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %secondary | .84
857 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Algorithm | Energy Savings = BTU/hr *(1/EERbase-1/EEReff)*EFLH/1000
857 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
857 | 3 | Total Gross Incremental Annual Electric Savings_kWh | BTU/hr | 9640
857 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH primary unit | 860
857 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EERbase | 9.8
857 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
857 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
857 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EEReff | 10.7
857 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
873 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
873 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
873 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
873 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1042 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1042 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1042 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1042 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
874 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
874 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
874 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
874 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
874 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
874 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
874 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
874 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1207 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1207 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1043 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1043 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1043 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1043 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1007 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1007 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | N/A
1007 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1007 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1007 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1007 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1007 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1007 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1007 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | N/A
1007 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1007 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1007 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1007 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1007 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | N/A
1007 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1007 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
915 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 14 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
915 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
915 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
915 | 1 | Incremental Cost per Unit | Efficient Cost | 3246 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
915 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
915 | 1 | Incremental Cost per Unit | Base Cost | 2283 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
915 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
915 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 11748 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
915 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
915 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
915 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
915 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
915 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
915 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
915 | 1 | Total Gross Average Annual Demand Reduction_kW | Current installed ASHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
915 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
915 | 1 | Total Gross Average Annual Demand Reduction_kW | Efficient ASHP electric demand (kW) | 2.202 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
915 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
915 | 1 | Total Gross Incremental Annual Electric Savings_kWh | 1000: the conversion factor between Wh and kWh (Wh/kWh) | 1000
915 | 1 | Total Gross Average Annual Demand Reduction_kW | Baseline ASHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
915 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
915 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
915 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
915 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
915 | 2 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
915 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
915 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
915 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 2009 | This represents a measure of energy use by season during the on-peak and off peak periods. This value will be determined by existing measured data of kWh during the period divided by kW at design conditions
915 | 2 | Total Gross Average Annual Demand Reduction_kW | Efficient ASHP electric demand (kW) | 2.202 | Current installed ASHP annual energy usage
915 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5
915 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
915 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
915 | 2 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
915 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 2.8
915 | 2 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
915 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
915 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3
915 | 2 | Total Gross Average Annual Demand Reduction_kW | Baseline ASHP electric demand (kW) | 2.455 | Efficient ASHP annual energy usage
915 | 2 | Total Gross Average Annual Demand Reduction_kW | Current installed ASHP electric demand (kW) | 3.375 | Baseline ASHP annual energy usage
915 | 2 | Efficient Case Value | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
915 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor ) | 8.3
915 | 2 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
915 | 2 | Incremental Cost per Unit | Efficient Cost | 3246
915 | 2 | Baseline Value | Source Documentation |  |  | Ameren Missouri - CoolSavers PY13 Report_FINAL_10JUNE2014.pdf
915 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 3.4
915 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
915 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 11748
915 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
915 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
915 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
915 | 2 | Incremental Cost per Unit | Base Cost | 2283
915 | 2 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
916 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
916 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
916 | 1 | Incremental Cost per Unit | Efficient Cost | 3246 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
916 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
916 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
916 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
916 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
916 | 1 | Total Gross Incremental Annual Electric Savings_kWh | 1000: the conversion factor between Wh and kWh (Wh/kWh) | 1000
916 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 14 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
916 | 1 | Incremental Cost per Unit | Base Cost | 2835 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
916 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
916 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
916 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.767 | Proctor Engineering Group
916 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
916 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
916 | 2 | Incremental Cost per Unit | Efficient Cost | 3246
916 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
916 | 2 | Incremental Cost per Unit | Base Cost | 2835
916 | 2 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
916 | 2 | Efficient Case Value | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
916 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
916 | 2 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | IInc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
916 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 200900%
916 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
916 | 2 | Baseline Value | Source Documentation |  |  | Ameren Missouri - CoolSavers PY13 Report_FINAL_10JUNE2014.pdf
916 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 6.3
916 | 2 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.767
916 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
916 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
916 | 2 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
916 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3
916 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor ) | 8.4
918 | 1 | Efficient Case Value | Source Documentation
918 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
918 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
918 | 1 | Baseline Value | Source Documentation
918 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
918 | 2 | Efficient Case Value | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
918 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 7.7
918 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor ) | 8.1
918 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.8 | Capacity of unit (tons)
918 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73 | Cadmus used the metered coincidence factor (73.9%) observed during the peak period which occurred on August 30th during the hour from 4?5pm
918 | 2 | Incremental Cost per Unit | Source Documentation
918 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit. |  | Efficiency rating of the efficient unit
918 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 2009
918 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
918 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
918 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
918 | 2 | Measure Life | Source Documentation
918 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit |  | Efficiency rating of the efficient unit
981 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
981 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
981 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
981 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
919 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
919 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
919 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
919 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
919 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 11267 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
919 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
919 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 15 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
919 | 1 | Total Gross Average Annual Demand Reduction_kW | Current installed ASHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
919 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
919 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
919 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
919 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
919 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
919 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
919 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
919 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
919 | 1 | Incremental Cost per Unit | Base Cost | 2283 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
919 | 1 | Total Gross Average Annual Demand Reduction_kW | Baseline ASHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
919 | 1 | Incremental Cost per Unit | Efficient Cost | 3357 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
919 | 1 | Total Gross Incremental Annual Electric Savings_kWh | conversion factor between Wh and kWh (Wh/kWh) | 1000
919 | 1 | Total Gross Average Annual Demand Reduction_kW | Efficient ASHP electric demand (kW) | 2.105 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
919 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
919 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
919 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
919 | 2 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
919 | 2 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
919 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
919 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
919 | 2 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
919 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
919 | 2 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
919 | 2 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
919 | 2 | Incremental Cost per Unit | Base Cost | 2283
919 | 2 | Incremental Cost per Unit | Efficient Cost | 3357
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor ) | 8.3426
919 | 3 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEERee | 15.0333333333333
919 | 3 | Incremental Cost per Unit | Base Cost | 2283
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | rating of unit (tons) | 2.92307692307692
919 | 3 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
919 | 3 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
919 | 3 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 2.9
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
919 | 3 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
919 | 3 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 2009 | This represents a measure of energy use by season during the on-peak and off peak periods. This value will be determined by existing measured data of kWh during the period divided by kW at design conditions
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLHheating | 2009
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 1805
919 | 3 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
919 | 3 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.2
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | rating of unit (tons) ee | 2.92307692307692
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 15.276
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | meteredSEER | 15.2
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 11267
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
919 | 3 | Total Gross Average Annual Demand Reduction_kW | Efficient ASHP electric demand (kW) | 2.105
919 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 3.41
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 3.02
919 | 3 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | meteredsvgs | 1805
919 | 3 | Total Gross Average Annual Demand Reduction_kW | Baseline ASHP electric demand (kW) | 2.455
919 | 3 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
919 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
919 | 3 | Total Gross Average Annual Demand Reduction_kW | Current installed ASHP electric demand (kW) | 3.375
919 | 3 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
919 | 3 | Total Gross Incremental Annual Electric Savings_kWh | meteredtons | 3.1
919 | 3 | Incremental Cost per Unit | Efficient Cost | 3357
919 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1048 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
1048 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1048 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
1048 | 1 | Total Gross Average Annual Demand Reduction_kW | Current installed ASHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1048 | 1 | Incremental Cost per Unit | Base Cost | 2283 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1048 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
1048 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 11267 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1048 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 15 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1048 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1048 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1048 | 1 | Total Gross Average Annual Demand Reduction_kW | Baseline ASHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1048 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1048 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
1048 | 1 | Total Gross Incremental Annual Electric Savings_kWh | conversion factor between Wh and kWh (Wh/kWh) | 1000
1048 | 1 | Incremental Cost per Unit | Efficient Cost | 3357 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1048 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
1048 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
1048 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1048 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1048 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1048 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
1048 | 1 | Total Gross Average Annual Demand Reduction_kW | Efficient ASHP electric demand (kW) | 2.105 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1048 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
1048 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
920 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
920 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
920 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
920 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5
920 | 1 | Incremental Cost per Unit | Efficient Cost | 3357 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
920 | 1 | Total Gross Average Annual Demand Reduction_kW | Baseline ASHP electric demand (kW) | 2.455
920 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 15 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
920 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
920 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
920 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
920 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3
920 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
920 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
920 | 1 | Incremental Cost per Unit | Base Cost | 2835 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
920 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
920 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 11267
920 | 1 | Total Gross Average Annual Demand Reduction_kW | Efficient ASHP electric demand (kW) | 2.105
920 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
920 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
920 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
920 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
920 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
920 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
920 | 1 | Total Gross Average Annual Demand Reduction_kW | Current installed ASHP electric demand (kW) | 3.375
920 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
920 | 2 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
920 | 2 | Incremental Cost per Unit | Base Cost | 3246
920 | 2 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
920 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
920 | 2 | Total Gross Average Annual Demand Reduction_kW | Current installed ASHP electric demand (kW) | 3.375
920 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
920 | 2 | Incremental Cost per Unit | Efficient Cost | 3357
920 | 2 | Total Gross Average Annual Demand Reduction_kW | Efficient ASHP electric demand (kW) | 2.105
920 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
920 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
920 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.1
920 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
920 | 2 | Total Gross Average Annual Demand Reduction_kW | Baseline ASHP electric demand (kW) | 2.455
920 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
920 | 2 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
920 | 2 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
920 | 2 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
920 | 3 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.1
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EERbase: Efficiency rating of the baseline unit | 7.2
920 | 3 | Total Gross Average Annual Demand Reduction_kW | Baseline ASHP electric demand (kW) | 2.455
920 | 3 | Total Gross Average Annual Demand Reduction_kW | Efficient ASHP electric demand (kW) | 2.105
920 | 3 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
920 | 3 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | BtuH: Cooling capacity in Btu/Hour | 12000
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 15.2
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 11267
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 1805
920 | 3 | Incremental Cost per Unit | Efficient Cost | 3357
920 | 3 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.2
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 3.1
920 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
920 | 3 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EERq (Efficient): Efficiency rating of the High Efficiency unit | 15
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 6.3
920 | 3 | Incremental Cost per Unit | Base Cost | 3246
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 2009
920 | 3 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor ) | 8.5354
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5
920 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
920 | 3 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
920 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
920 | 3 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
920 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH (Full load hours) | 1215
920 | 3 | Total Gross Average Annual Demand Reduction_kW | Current installed ASHP electric demand (kW) | 3.375
920 | 3 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
920 | 3 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
1049 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
1049 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5
1049 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1049 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1049 | 1 | Total Gross Average Annual Demand Reduction_kW | Current installed ASHP electric demand (kW) | 3.375
1049 | 1 | Incremental Cost per Unit | Base Cost | 2835 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1049 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
1049 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
1049 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1049 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
1049 | 1 | Total Gross Average Annual Demand Reduction_kW | Baseline ASHP electric demand (kW) | 2.455
1049 | 1 | Incremental Cost per Unit | Efficient Cost | 3357 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1049 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
1049 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 11267
1049 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
1049 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 15 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1049 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
1049 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
1049 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3
1049 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1049 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
1049 | 1 | Total Gross Average Annual Demand Reduction_kW | Efficient ASHP electric demand (kW) | 2.105
1049 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
1049 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
922 | 1 | Baseline Value | Source Documentation
922 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
922 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
922 | 1 | Efficient Case Value | Source Documentation
922 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit |  | Efficiency rating of the efficient unit
922 | 2 | Measure Life | Source Documentation
922 | 2 | Incremental Cost per Unit | Source Documentation
922 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 2.9 | Capacity of unit (tons)
922 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
922 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit. |  | Efficiency rating of the efficient unit
922 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73 | Cadmus used the metered coincidence factor (73.9%) observed during the peak period which occurred on August 30th during the hour from 4?5pm
922 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
922 | 3 | Measure Life | Source Documentation
922 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEEReff | 15.1
922 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLHheat | 2009
922 | 3 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit |  | Efficiency rating of the efficient unit
922 | 3 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73 | Cadmus used the metered coincidence factor (73.9%) observed during the peak period which occurred on August 30th during the hour from 4?5pm
922 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase | 7.7
922 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
922 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLHcool | 869
922 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons | 3.02
922 | 3 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit. |  | Efficiency rating of the efficient unit
922 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
922 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff | 8.74842
922 | 3 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
922 | 3 | Incremental Cost per Unit | Source Documentation
922 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase | 13
922 | 3 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 2.9 | Capacity of unit (tons)
922 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1051 | 1 | Efficient Case Value | Source Documentation
1051 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
1051 | 1 | Baseline Value | Source Documentation
1051 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
982 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
982 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
982 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
982 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
983 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
983 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
983 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
983 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
923 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
923 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
923 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
923 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 16 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
923 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
923 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
923 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
923 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient ASHP electric demand (kW) | 2.016 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
923 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
923 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
923 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
923 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
923 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
923 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
923 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 10824 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
923 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
923 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
923 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
923 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Baseline ASHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
923 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
923 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current installed ASHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
923 | 1 | Incremental Cost per Unit | Base Cost | 2283 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
923 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
923 | 1 | Incremental Cost per Unit | Efficient Cost | 3768 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
923 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
923 | 2 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
923 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
923 | 2 | Incremental Cost per Unit | Efficient Cost | 3768
923 | 2 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
923 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
923 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
923 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.3
923 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
923 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
923 | 2 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
923 | 2 | Incremental Cost per Unit | Base Cost | 2283
923 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
923 | 2 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
923 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
923 | 2 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
923 | 3 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient ASHP electric demand (kW) | 2.016
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Baseline ASHP electric demand (kW) | 2.455
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Current installed ASHP electric demand (kW) | 3.375
923 | 3 | Incremental Cost per Unit | Efficient Cost | 3768
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor ) | 10.3097
923 | 3 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
923 | 3 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
923 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.1
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 2.8
923 | 3 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
923 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
923 | 3 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
923 | 3 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
923 | 3 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 1805
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 17.9
923 | 3 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
923 | 3 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
923 | 3 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.3
923 | 3 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
923 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
923 | 3 | Incremental Cost per Unit | Base Cost | 2283
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 10824
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 3.412
923 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 2009 | This represents a measure of energy use by season during the on-peak and off peak periods. This value will be determined by existing measured data of kWh during the period divided by kW at design conditions
1052 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
1052 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1052 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
1052 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1052 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
1052 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
1052 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
1052 | 1 | Incremental Cost per Unit | Efficient Cost | 3768 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1052 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1052 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1052 | 1 | Total Gross Average Annual Demand Reduction_kW | Baseline ASHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1052 | 1 | Total Gross Average Annual Demand Reduction_kW | Current installed ASHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1052 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
1052 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1052 | 1 | Total Gross Average Annual Demand Reduction_kW | Efficient ASHP electric demand (kW) | 2.016 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1052 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
1052 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1052 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
1052 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
1052 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 10824 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1052 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 16 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1052 | 1 | Incremental Cost per Unit | Base Cost | 2283 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1052 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1052 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
924 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 16 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
924 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 10824 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
924 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
924 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
924 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
924 | 1 | Total Gross Average Annual Demand Reduction_kW | Efficient ASHP electric demand (kW) | 2.016 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
924 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
924 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
924 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
924 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
924 | 1 | Total Gross Average Annual Demand Reduction_kW | Baseline ASHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
924 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
924 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
924 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
924 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
924 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
924 | 1 | Total Gross Average Annual Demand Reduction_kW | Current installed ASHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
924 | 1 | Incremental Cost per Unit | Efficient Cost | 3768 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
924 | 1 | Incremental Cost per Unit | Base Cost | 2835 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
924 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
924 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment
924 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
924 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
924 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
924 | 2 | Total Gross Average Annual Demand Reduction_kW | Efficient ASHP electric demand (kW) | 2.016
924 | 2 | Total Gross Average Annual Demand Reduction_kW | Current installed ASHP electric demand (kW) | 3.375
924 | 2 | Total Gross Average Annual Demand Reduction_kW | Baseline ASHP electric demand (kW) | 2.455
924 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
924 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
924 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
924 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
924 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
924 | 2 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
924 | 2 | Incremental Cost per Unit | Base Cost | 2835
924 | 2 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
924 | 2 | Incremental Cost per Unit | Efficient Cost | 3768
924 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
924 | 2 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
924 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
924 | 2 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
924 | 2 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
924 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.5
924 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3
924 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 1805
924 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.1
924 | 3 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
924 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
924 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
924 | 3 | Total Gross Average Annual Demand Reduction_kW | Baseline ASHP electric demand (kW) | 2.455
924 | 3 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
924 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 2.80
924 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 2009
924 | 3 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
924 | 3 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
924 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
924 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
924 | 3 | Incremental Cost per Unit | Efficient Cost | 3768
924 | 3 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
924 | 3 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
924 | 3 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
924 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5
924 | 3 | Total Gross Average Annual Demand Reduction_kW | Current installed ASHP electric demand (kW) | 3.375
924 | 3 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
924 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor ) | 10.6718
924 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
924 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 6.3
924 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 10824
924 | 3 | Total Gross Average Annual Demand Reduction_kW | Efficient ASHP electric demand (kW) | 2.016
924 | 3 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
924 | 3 | Incremental Cost per Unit | Base Cost | 2835
924 | 3 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.5
924 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
924 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 17.9
924 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
1053 | 1 | Total Gross Average Annual Demand Reduction_kW | Current installed ASHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1053 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1053 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1053 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
1053 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
1053 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1053 | 1 | Total Gross Average Annual Demand Reduction_kW | Efficient ASHP electric demand (kW) | 2.016 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1053 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
1053 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1053 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
1053 | 1 | Incremental Cost per Unit | Base Cost | 2835 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1053 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
1053 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1053 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 10824 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1053 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1053 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
1053 | 1 | Total Gross Average Annual Demand Reduction_kW | Baseline ASHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1053 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment
1053 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
1053 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1053 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
1053 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
1053 | 1 | Incremental Cost per Unit | Efficient Cost | 3768 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1053 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 16 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
926 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
926 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
926 | 1 | Efficient Case Value | Source Documentation
926 | 1 | Baseline Value | Source Documentation
926 | 2 | Measure Life | Source Documentation
926 | 2 | Incremental Cost per Unit | Source Documentation
926 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
926 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase | 7.7
926 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
926 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Heating Algorithm | Heating energy savings = unit rating in tons X 12 KBTU/ton *EFLH *(1/HSPFbase - 1/HSPFeff)
926 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 7.7
926 | 3 | Incremental Cost per Unit | Source Documentation
926 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
926 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Cooling Algorithm | Cooling energy savings = metered kWh x EEReff/EERbase - metered kWh
926 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 2009
926 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEEReff | 17.9
926 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor ) | 9.4
926 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLHheat | 2009
926 | 3 | Measure Life | Source Documentation
926 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons | 2.8
926 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase | 13
926 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff | 9.0083
926 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLHcool | 869
1055 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
1055 | 1 | Efficient Case Value | Source Documentation
1055 | 1 | Baseline Value | Source Documentation
1055 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
984 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
984 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
984 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
984 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
985 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
985 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
985 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
985 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
917 | 1 | Baseline Value | Source Documentation
917 | 1 | Efficient Case Value | Source Documentation
917 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
917 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
917 | 2 | Incremental Cost per Unit | Source Documentation
917 | 2 | Efficient Case Value | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
917 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit |  | Efficiency rating of the efficient unit
917 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
917 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 2009
917 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor ) | 8.1
917 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
917 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit. |  | Efficiency rating of the efficient unit
917 | 2 | Measure Life | Source Documentation
917 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 2.9 | Capacity of unit (tons)
917 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
917 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73 | Cadmus used the metered coincidence factor (73.9%) observed during the peak period which occurred on August 30th during the hour from 4?5pm
917 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
917 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 3.4
921 | 1 | Baseline Value | Source Documentation
921 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
921 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
921 | 1 | Efficient Case Value | Source Documentation
921 | 2 | Incremental Cost per Unit | Source Documentation
921 | 2 | Measure Life | Source Documentation
921 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
921 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3 | Capacity of unit (tons)
921 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit. |  | Efficiency rating of the efficient unit
921 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
921 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73 | Cadmus used the metered coincidence factor (73.9%) observed during the peak period which occurred on August 30th during the hour from 4?5pm
921 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit |  | Efficiency rating of the efficient unit
921 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
921 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 3.4
921 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 2009
921 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
921 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor ) | 8.8397
921 | 3 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73 | Cadmus used the metered coincidence factor (73.9%) observed during the peak period which occurred on August 30th during the hour from 4?5pm
921 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
921 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 3.02
921 | 3 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
921 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
921 | 3 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3 | Capacity of unit (tons)
921 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 15.1
921 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.1
921 | 3 | Incremental Cost per Unit | Source Documentation
921 | 3 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit |  | Efficiency rating of the efficient unit
921 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 360
921 | 3 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit. |  | Efficiency rating of the efficient unit
921 | 3 | Measure Life | Source Documentation
1050 | 1 | Baseline Value | Source Documentation
1050 | 1 | Efficient Case Value | Source Documentation
1050 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
1050 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
925 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
925 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
925 | 1 | Baseline Value | Source Documentation
925 | 1 | Efficient Case Value | Source Documentation
925 | 2 | Measure Life | Source Documentation
925 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit |  | Efficiency rating of the efficient unit
925 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit. |  | Efficiency rating of the efficient unit
925 | 2 | Incremental Cost per Unit | Source Documentation
925 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
925 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
925 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73 | Cadmus used the metered coincidence factor (73.9%) observed during the peak period which occurred on August 30th during the hour from 4?5pm
925 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.5 | Capacity of unit (tons)
925 | 3 | Incremental Cost per Unit | Source Documentation
925 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor ) | 9.4819
925 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 17.9
925 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
925 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
925 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 3.4
925 | 3 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit. |  | Efficiency rating of the efficient unit
925 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
925 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 2.8
925 | 3 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.5 | Capacity of unit (tons)
925 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 2009
925 | 3 | Measure Life | Source Documentation
925 | 3 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit |  | Efficiency rating of the efficient unit
925 | 3 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
925 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 360
925 | 3 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73 | Cadmus used the metered coincidence factor (73.9%) observed during the peak period which occurred on August 30th during the hour from 4?5pm
925 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.1
925 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1054 | 1 | Efficient Case Value | Source Documentation
1054 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
1054 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
1054 | 1 | Baseline Value | Source Documentation
945 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
945 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
945 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
945 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 14 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
945 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
945 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
945 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
945 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
945 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 3567.9 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
945 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Baseline GSHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
945 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
945 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
945 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
945 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 3976.4 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
945 | 1 | Incremental Cost per Unit | Efficient Cost | 2640 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
945 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
945 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
945 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current installed GSHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
945 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
945 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
945 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 5467.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
945 | 1 | Incremental Cost per Unit | Base Cost | 2283 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
945 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient GSHP electric demand (kW) | 2.202 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
945 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
945 | 2 | Incremental Cost per Unit | Efficient Cost | 2640
945 | 2 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
945 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
945 | 2 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
945 | 2 | Incremental Cost per Unit | Base Cost | 2283
945 | 2 | Measure Life | Source Documentation
945 | 2 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
945 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
945 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
945 | 2 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
945 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
945 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
945 | 2 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
945 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
945 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
945 | 3 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.1
945 | 3 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
945 | 3 | Incremental Cost per Unit | Efficient Cost | 2640
945 | 3 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EERbase: Efficiency rating of the baseline unit.
945 | 3 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
945 | 3 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
945 | 3 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 3567.9
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Current installed GSHP electric demand (kW) | 3.375
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 14.052
945 | 3 | Measure Life | Source Documentation
945 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = metered kWhi * (EEReff(T)/EERbase(T)) - metered kWhi
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Baseline GSHP electric demand (kW) | 2.455
945 | 3 | Incremental Cost per Unit | Base Cost | 2283
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 3976.4
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 1805
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EEReff: Efficiency rating of the efficient unit
945 | 3 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 3.01
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWhi
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient GSHP electric demand (kW) | 2.202
945 | 3 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3
945 | 3 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
945 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 5467.5
945 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
945 | 3 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
945 | 3 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
944 | 1 | Baseline Value | Source Documentation
944 | 1 | Efficient Case Value | Source Documentation
944 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
944 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
944 | 2 | Incremental Cost per Unit | Source Documentation
944 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
944 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit |  | Efficiency rating of the efficient unit
944 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit. |  | Efficiency rating of the efficient unit
944 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73 | Cadmus used the metered coincidence factor (73.9%) observed during the peak period which occurred on August 30th during the hour from 4?5pm
944 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.4 | Capacity of unit (tons)
944 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
944 | 2 | Measure Life | Source Documentation
944 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.1
944 | 3 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73 | Cadmus used the metered coincidence factor (73.9%) observed during the peak period which occurred on August 30th during the hour from 4?5pm
944 | 3 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
944 | 3 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit |  | Efficiency rating of the efficient unit
944 | 3 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.4 | Capacity of unit (tons)
944 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
944 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
944 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation | kWh saved = metered kWh x EEReff/EERbase - metered kWh
944 | 3 | Measure Life | Source Documentation
944 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 3.01
944 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
944 | 3 | Incremental Cost per Unit | Source Documentation
944 | 3 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit. |  | Efficiency rating of the efficient unit
944 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 360
944 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 14.15
1069 | 1 | Efficient Case Value | Source Documentation
1069 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
1069 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
1069 | 1 | Baseline Value | Source Documentation
1001 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1001 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1001 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1001 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1070 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 5467.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1070 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
1070 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
1070 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1070 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient GSHP electric demand (kW) | 2.202 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1070 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
1070 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current installed GSHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1070 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 3567.9 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1070 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
1070 | 1 | Incremental Cost per Unit | Base Cost | 2283 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1070 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 3976.4 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1070 | 1 | Incremental Cost per Unit | Efficient Cost | 2640 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1070 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
1070 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 14 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1070 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
1070 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1070 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
1070 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1070 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
1070 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
1070 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
1070 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1070 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1070 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Baseline GSHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1070 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
947 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
947 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
947 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.4
947 | 2 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
947 | 2 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
947 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
947 | 2 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
947 | 2 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
947 | 2 | Incremental Cost per Unit | RUL: Remaining Useful Life
947 | 2 | Incremental Cost per Unit | Efficient Cost | 2997
947 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
947 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
947 | 2 | Measure Life | Source Documentation
947 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
947 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
947 | 2 | Incremental Cost per Unit | Base Cost | 2283
947 | 3 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EERbase: Efficiency rating of the baseline unit.
947 | 3 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.4
947 | 3 | Measure Life | Source Documentation
947 | 3 | Incremental Cost per Unit | RUL: Remaining Useful Life
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
947 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Current installed GSHP electric demand (kW) | 3.375
947 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 1805
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 3976.4
947 | 3 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
947 | 3 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
947 | 3 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
947 | 3 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 3.2536
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = metered kWhi * (EEReff(T)/EERbase(T)) - metered kWhi
947 | 3 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
947 | 3 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Baseline GSHP electric demand (kW) | 2.455
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.1
947 | 3 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWhi
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 15.2
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient GSHP electric demand (kW) | 2.105
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 3410.2
947 | 3 | Incremental Cost per Unit | Base Cost | 2283
947 | 3 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EEReff: Efficiency rating of the efficient unit
947 | 3 | Incremental Cost per Unit | Efficient Cost | 2997
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 5467.5
947 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
946 | 1 | Baseline Value | Source Documentation
946 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
946 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
946 | 1 | Efficient Case Value | Source Documentation
946 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.2
946 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73 | Cadmus used the metered coincidence factor (73.9%) observed during the peak period which occurred on August 30th during the hour from 4?5pm
946 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
946 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 15.19
946 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit. |  | Efficiency rating of the efficient unit
946 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.4 | Capacity of unit (tons)
946 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
946 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
946 | 2 | Incremental Cost per Unit | Source Documentation
946 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation | kWh saved = metered kWh x EEReff/EERbase - metered kWh
946 | 2 | Measure Life | Source Documentation
946 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 3.368
946 | 2 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 360
946 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
946 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit |  | Efficiency rating of the efficient unit
946 | 3 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
946 | 3 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit |  | Efficiency rating of the efficient unit
946 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 3.251
946 | 3 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73 | Cadmus used the metered coincidence factor (73.9%) observed during the peak period which occurred on August 30th during the hour from 4?5pm
946 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
946 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 360
946 | 3 | Incremental Cost per Unit | Source Documentation
946 | 3 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit. |  | Efficiency rating of the efficient unit
946 | 3 | Measure Life | Source Documentation
946 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation | kWh saved = metered kWh x EEReff/EERbase - metered kWh
946 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
946 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
946 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.1
946 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 15.2
946 | 3 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.4 | Capacity of unit (tons)
1071 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
1071 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
1071 | 1 | Baseline Value | Source Documentation
1071 | 1 | Efficient Case Value | Source Documentation
1002 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1002 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1002 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1002 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
947 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
947 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
947 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 15 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
947 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 3410.2 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
947 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current installed GSHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
947 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
947 | 1 | Incremental Cost per Unit | Efficient Cost | 2997 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
947 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
947 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
947 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 3976.4 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
947 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
947 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Baseline GSHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
947 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
947 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
947 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient GSHP electric demand (kW) | 2.105 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
947 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 5467.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
947 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
947 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
947 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
947 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life
947 | 1 | Incremental Cost per Unit | Base Cost | 2283 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
947 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
947 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1072 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient GSHP electric demand (kW) | 2.105 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1072 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1072 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
1072 | 1 | Incremental Cost per Unit | Base Cost | 2283 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1072 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
1072 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
1072 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Baseline GSHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1072 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1072 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
1072 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
1072 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
1072 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1072 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
1072 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 3410.2 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1072 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current installed GSHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1072 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 15 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1072 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 5467.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1072 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 3976.4 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1072 | 1 | Incremental Cost per Unit | Efficient Cost | 2997 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1072 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
1072 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life
1072 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
1072 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
1003 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1003 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1003 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1003 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 3266
949 | 2 | Incremental Cost per Unit | Efficient Cost | 3054
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EEReff: Efficiency rating of the efficient unit
949 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.1
949 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
949 | 2 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 3976.4
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Current installed GSHP electric demand (kW) | 3.375
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | metered kWhi
949 | 2 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
949 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
949 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 3.07
949 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
949 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
949 | 2 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = metered kWhi * (EEReff(T)/EERbase(T)) - metered kWhi
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
949 | 2 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
949 | 2 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
949 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
949 | 2 | Incremental Cost per Unit | Base Cost | 2283
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Baseline GSHP electric demand (kW) | 2.455
949 | 2 | Measure Life | Source Documentation
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EERbase: Efficiency rating of the baseline unit.
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.2
949 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 16.262
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 1805
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 5467.5
949 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient GSHP electric demand (kW) | 2.016
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 16.3
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 3.0702
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
949 | 3 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 1805
949 | 3 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
949 | 3 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
949 | 3 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.1
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EEReff: Efficiency rating of the efficient unit
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 3266
949 | 3 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EERbase: Efficiency rating of the baseline unit.
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Baseline GSHP electric demand (kW) | 2.455
949 | 3 | Incremental Cost per Unit | Base Cost | 2283
949 | 3 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = metered kWhi * (EEReff(T)/EERbase(T)) - metered kWhi
949 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Current installed GSHP electric demand (kW) | 3.375
949 | 3 | Measure Life | Source Documentation
949 | 3 | Incremental Cost per Unit | Efficient Cost | 3054
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWhi
949 | 3 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
949 | 3 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.2
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient GSHP electric demand (kW) | 2.016
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 3976.4
949 | 3 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 5467.5
949 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
949 | 3 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
949 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
949 | 3 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
948 | 1 | Efficient Case Value | Source Documentation
948 | 1 | Baseline Value | Source Documentation
948 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
948 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
948 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73 | Cadmus used the metered coincidence factor (73.9%) observed during the peak period which occurred on August 30th during the hour from 4?5pm
948 | 2 | Incremental Cost per Unit | Source Documentation
948 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
948 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
948 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 16.26
948 | 2 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 360
948 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
948 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 3.07
948 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
948 | 2 | Measure Life | Source Documentation
948 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation | Energy savings = Metered kWh x EEReff/EERbase - metered kWh
948 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.2
948 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit |  | Efficiency rating of the efficient unit
948 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.1 | Capacity of unit (tons)
948 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit. |  | Efficiency rating of the efficient unit
948 | 3 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit |  | Efficiency rating of the efficient unit
948 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
948 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
948 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 3.075
948 | 3 | Measure Life | Source Documentation
948 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.2
948 | 3 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 3.1 | Capacity of unit (tons)
948 | 3 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73 | Cadmus used the metered coincidence factor (73.9%) observed during the peak period which occurred on August 30th during the hour from 4?5pm
948 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation | Energy savings = Metered kWh x EEReff/EERbase - metered kWh
948 | 3 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
948 | 3 | Incremental Cost per Unit | Source Documentation
948 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 360
948 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 16.26
948 | 3 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit. |  | Efficiency rating of the efficient unit
948 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1073 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
1073 | 1 | Baseline Value | Source Documentation
1073 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
1073 | 1 | Efficient Case Value | Source Documentation
949 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
949 | 1 | Incremental Cost per Unit | Base Cost | 2283 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
949 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
949 | 1 | Incremental Cost per Unit | Efficient Cost | 3054 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
949 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
949 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current installed GSHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
949 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
949 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 3266 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
949 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 3976.4 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
949 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
949 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 5467.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
949 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 16 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
949 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
949 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
949 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
949 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
949 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient GSHP electric demand (kW) | 2.016 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
949 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
949 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
949 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Baseline GSHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
949 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
949 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
949 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1074 | 1 | Incremental Cost per Unit | Efficient Cost | 3054 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1074 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current installed GSHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1074 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
1074 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1074 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
1074 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
1074 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
1074 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 3266 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1074 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 3976.4 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1074 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
1074 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient GSHP electric demand (kW) | 2.016 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1074 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1074 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
1074 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
1074 | 1 | Incremental Cost per Unit | Base Cost | 2283 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1074 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1074 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
1074 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 16 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1074 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 5467.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1074 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
1074 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Baseline GSHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1074 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
1074 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1004 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1004 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1004 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1004 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
875 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
875 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
875 | 1 | Measure Life | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
875 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
875 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (After 2006)" Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 13 | Illinois TRM 2012
875 | 1 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 950
875 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts Btu to kBtu | 1000
875 | 1 | Gross Incremental Annual Gas Savings_MMBTU | n-Heat: Efficiency of heating system | 70% | Illinois TRM 2012
875 | 1 | Gross Incremental Annual Gas Savings_MMBTU | A_attic: Total area of insulated ceiling/attic (ft2) | 950
875 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
875 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts hours to days | 24
875 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1646 | National Climatic Data Center
875 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
875 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
875 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
875 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Savings Algorithm | Gas savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * HDD] / (100,067 * nHeat)
875 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
875 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
875 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
875 | 1 | Gross Incremental Annual Gas Savings_MMBTU | HDD: Cooling Degree Days | 4535 | National Climatic Data Center
875 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (Before 2006): Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 10 | Illinois TRM 2012
875 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | kWh Savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * CDD] / (1000 * n-Cool) E80
875 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
876 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts hours to days | 24
876 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
876 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
876 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
876 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | kWh Savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * CDD] / (1000 * n-Cool) E80
876 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
876 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
876 | 1 | Gross Incremental Annual Gas Savings_MMBTU | HDD: Cooling Degree Days | 4535 | National Climatic Data Center
876 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
876 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (After 2006)" Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 13 | Illinois TRM 2012
876 | 1 | Measure Life | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
876 | 1 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 950
876 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
876 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (Before 2006): Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 10 | Illinois TRM 2012
876 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1646 | National Climatic Data Center
876 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
876 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
876 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
876 | 1 | Gross Incremental Annual Gas Savings_MMBTU | n-Heat: Efficiency of heating system | 70% | Illinois TRM 2012
876 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
876 | 1 | Gross Incremental Annual Gas Savings_MMBTU | A_attic: Total area of insulated ceiling/attic (ft2) | 950
876 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Savings Algorithm | Gas savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * HDD] / (100,067 * nHeat)
876 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts Btu to kBtu | 1000
1044 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | kWh Savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * CDD] / (1000 * n-Cool) E80
1044 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts hours to days | 24
1044 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
1044 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
1044 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
1044 | 1 | Gross Incremental Annual Gas Savings_MMBTU | n-Heat: Efficiency of heating system | 70% | Illinois TRM 2012
1044 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
1044 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
1044 | 1 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 950
1044 | 1 | Gross Incremental Annual Gas Savings_MMBTU | A_attic: Total area of insulated ceiling/attic (ft2) | 950
1044 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
1044 | 1 | Measure Life | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
1044 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
1044 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
1044 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
1044 | 1 | Gross Incremental Annual Gas Savings_MMBTU | HDD: Cooling Degree Days | 4535 | National Climatic Data Center
1044 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
1044 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (After 2006)" Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 13 | Illinois TRM 2012
1044 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (Before 2006): Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 10 | Illinois TRM 2012
1044 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
1044 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1646 | National Climatic Data Center
1044 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Savings Algorithm | Gas savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * HDD] / (100,067 * nHeat)
1044 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts Btu to kBtu | 1000
877 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | kWh Savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * CDD] / (1000 * n-Cool) E80
877 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1646 | National Climatic Data Center
877 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (Before 2006): Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 10 | Illinois TRM 2012
877 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
877 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
877 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
877 | 1 | Gross Incremental Annual Gas Savings_MMBTU | A_attic: Total area of insulated ceiling/attic (ft2) | 950
877 | 1 | Measure Life | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
877 | 1 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 950
877 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
877 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
877 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (After 2006)" Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 13 | Illinois TRM 2012
877 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
877 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
877 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts Btu to kBtu | 1000
877 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Savings Algorithm | Gas savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * HDD] / (100,067 * nHeat)
877 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts hours to days | 24
877 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
877 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
877 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
877 | 1 | Gross Incremental Annual Gas Savings_MMBTU | n-Heat: Efficiency of heating system | 70% | Illinois TRM 2012
877 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
877 | 1 | Gross Incremental Annual Gas Savings_MMBTU | HDD: Cooling Degree Days | 4535 | National Climatic Data Center
877 | 2 | Gross Incremental Annual Gas Savings_MMBTU | HDD: Heating Degree Days | 4535 | NOAA @65 degrees @ Lambert. National Climatic Data Center, Cooling Degree Days are based on a base temp of 65°F. There is a county mapping table in the Appendix providing the appropriate city to use for each county of Illinois.
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 49
877 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Converts hours to days | 24
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 11
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm2 | kWh Heat Savings = [ (1/R old - 1/R attic) * A attic * (1-Framing factor/2)) * 24 * HDD) / (COP * 3413) ]
877 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Btu/therm | 100067
877 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Framing_factor: Adjustment to account for area of framing | 0.15 | Factor is used directly for walls, but reduced by 1/2 for attics, assuming that the average joist is 5.5" and R-38 requires 11" of cellulose, therefore at each joist, 1/2 the thickness of insulation has been added as between the joists.
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 1000-1784
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1646
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Discretionary Use Adjustment | 0.75
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Factor is used directly for walls, but reduced by 1/2 for attics, assuming that the average joist is 5.5" and R-38 requires 11" of cellulose, therefore at each joist, 1/2 the thickness of insulation has been added as between the joists.
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | COP | 65% - 100% | Use actual values if known
877 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Savings Algorithm3 | delta therms = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * HDD] / (100,067 * nHeat)
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 15% | Factor is used directly for walls, but reduced by 1/2 for attics, assuming that the average joist is 5.5" and R-38 requires 11" of cellulose, therefore at each joist, 1/2 the thickness of insulation has been added as between the joists.
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 49
877 | 2 | Gross Incremental Annual Gas Savings_MMBTU | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 49
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm1 | kWh Cool Savings = [ (1/R old - 1/R attic) * A attic * (1-Framing factor/2)) * 24 * CDD * DUA] / (1000 * SEER) ]
877 | 2 | Gross Incremental Annual Gas Savings_MMBTU | A_attic: Total area of insulated ceiling/attic (ft2) | 1000-1784
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000 | These default system efficiencies are based on the applicable minimum Federal Standards. In 2006 the Federal Standard for Central AC was adjusted. While one would expect the average system efficiency to be higher than this minimum, the likely degradation of efficiencies over time mean that using the minimum standard is appropriate.
877 | 2 | Gross Incremental Annual Gas Savings_MMBTU | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11 | An estimate based on review of Madison Gas and Electric, Exterior Wall Insulation, R-value for no insulation in walls, and NREL's Building Energy Simulation Test for Existing Homes (BESTEST-EX).
877 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SEER | 10.2-14.5 | These default system efficiencies are based on the applicable minimum Federal Standards. In 2006 the Federal Standard for Central AC was adjusted. While one would expect the average system efficiency to be higher than this minimum, the likely degradation of efficiencies over time mean that using the minimum standard is appropriate.
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HDD: Heating Degree Days | 4535 | NOAA @65 degrees @ Lambert. National Climatic Data Center, Cooling Degree Days are based on a base temp of 65°F. There is a county mapping table in the Appendix providing the appropriate city to use for each county of Illinois.
877 | 2 | Gross Incremental Annual Gas Savings_MMBTU | n-Heat | 84% | Use actual values if known
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Btu/kWh | 3413
877 | 2 | Measure Life | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
877 | 2 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 1000-1784
877 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Insulation Cost Table_Residential.docx
878 | 1 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 950
878 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts hours to days | 24
878 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (Before 2006): Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 10 | Illinois TRM 2012
878 | 1 | Measure Life | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
878 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
878 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
878 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1646 | National Climatic Data Center
878 | 1 | Gross Incremental Annual Gas Savings_MMBTU | HDD: Cooling Degree Days | 4535 | National Climatic Data Center
878 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
878 | 1 | Gross Incremental Annual Gas Savings_MMBTU | n-Heat: Efficiency of heating system | 70% | Illinois TRM 2012
878 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | kWh Savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * CDD] / (1000 * n-Cool) E80
878 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Savings Algorithm | Gas savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * HDD] / (100,067 * nHeat)
878 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
878 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (After 2006)" Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 13 | Illinois TRM 2012
878 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
878 | 1 | Gross Incremental Annual Gas Savings_MMBTU | A_attic: Total area of insulated ceiling/attic (ft2) | 950
878 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
878 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
878 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts Btu to kBtu | 1000
878 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
878 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
878 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
878 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
879 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (Before 2006): Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 10 | Illinois TRM 2012
879 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
879 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts Btu to kBtu | 1000
879 | 1 | Measure Life | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
879 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1646 | National Climatic Data Center
879 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Savings Algorithm | Gas savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * HDD] / (100,067 * nHeat)
879 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
879 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | kWh Savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * CDD] / (1000 * n-Cool) E80
879 | 1 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 950
879 | 1 | Gross Incremental Annual Gas Savings_MMBTU | A_attic: Total area of insulated ceiling/attic (ft2) | 950
879 | 1 | Gross Incremental Annual Gas Savings_MMBTU | n-Heat: Efficiency of heating system | 70% | Illinois TRM 2012
879 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
879 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
879 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (After 2006)" Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 13 | Illinois TRM 2012
879 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
879 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts hours to days | 24
879 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
879 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
879 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
879 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
879 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
879 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
879 | 1 | Gross Incremental Annual Gas Savings_MMBTU | HDD: Cooling Degree Days | 4535 | National Climatic Data Center
880 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Savings Algorithm | Gas savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * HDD] / (100,067 * nHeat)
880 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts Btu to kBtu | 1000
880 | 1 | Measure Life | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
880 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts hours to days | 24
880 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
880 | 1 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 950
880 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
880 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
880 | 1 | Gross Incremental Annual Gas Savings_MMBTU | n-Heat: Efficiency of heating system | 70% | Illinois TRM 2012
880 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (After 2006)" Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 13 | Illinois TRM 2012
880 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | kWh Savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * CDD] / (1000 * n-Cool) E80
880 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
880 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
880 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
880 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
880 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
880 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
880 | 1 | Gross Incremental Annual Gas Savings_MMBTU | HDD: Cooling Degree Days | 4535 | National Climatic Data Center
880 | 1 | Gross Incremental Annual Gas Savings_MMBTU | A_attic: Total area of insulated ceiling/attic (ft2) | 950
880 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1646 | National Climatic Data Center
880 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
880 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (Before 2006): Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 10 | Illinois TRM 2012
880 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 1510.1
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 19
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SEER | 10.868712 | These default system efficiencies are based on the applicable minimum Federal Standards. In 2006 the Federal Standard for Central AC was adjusted. While one would expect the average system efficiency to be higher than this minimum, the likely degradation of efficiencies over time mean that using the minimum standard is appropriate.
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1646 | NOAA @65 degrees @ Lambert. National Climatic Data Center, Cooling Degree Days are based on a base temp of 65°F. There is a county mapping table in the Appendix providing the appropriate city to use for each county of Illinois.
880 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
880 | 2 | Gross Incremental Annual Gas Savings_MMBTU | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 19 | An estimate based on review of Madison Gas and Electric, Exterior Wall Insulation, R-value for no insulation in walls, and NREL's Building Energy Simulation Test for Existing Homes (BESTEST-EX).
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Factor is used directly for walls, but reduced by 1/2 for attics, assuming that the average joist is 5.5" and R-38 requires 11" of cellulose, therefore at each joist, 1/2 the thickness of insulation has been added as between the joists.
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 1560
880 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Savings Algorithm3 | Therm Savings = [ ((1/R old - 1/R attic) * A attic * (1-Framing factor/2)) * 24 * HDD) / (?Heat * 100,067 Btu/therm)) ]
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Discretionary Use Adjustment | 0.75
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm2 | kWh Heat Savings = [ (1/R old - 1/R attic) * A attic * (1-Framing factor/2)) * 24 * HDD) / (COP * 3413) ]
880 | 2 | Gross Incremental Annual Gas Savings_MMBTU | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 49
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 49
880 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Insulation Cost Table_Residential.docx
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | COP | 65% - 100%
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
880 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Btu/therm | 100067
880 | 2 | Gross Incremental Annual Gas Savings_MMBTU | A_attic: Total area of insulated ceiling/attic (ft2) | 1000-1784
880 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Framing_factor: Adjustment to account for area of framing | 0.15 | Factor is used directly for walls, but reduced by 1/2 for attics, assuming that the average joist is 5.5" and R-38 requires 11" of cellulose, therefore at each joist, 1/2 the thickness of insulation has been added as between the joists.
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HDD: Heating Degree Days | 4535
880 | 2 | Measure Life | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Btu/kBtu | 1000
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 49
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 5
880 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Converts hours to days | 24
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm1 | kWh Cool Savings = [ (1/R old - 1/R attic) * A attic * (1-Framing factor/2)) * 24 * CDD * DUA] / (1000 * SEER) ]
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15
880 | 2 | Gross Incremental Annual Gas Savings_MMBTU | n-Heat | 84% | Use actual values if known
880 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Btu/kWh | 3413
880 | 2 | Gross Incremental Annual Gas Savings_MMBTU | HDD: Heating Degree Days | 4535 | NOAA @65 degrees @ Lambert. National Climatic Data Center, Cooling Degree Days are based on a base temp of 65°F. There is a county mapping table in the Appendix providing the appropriate city to use for each county of Illinois.
1209 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
1209 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (After 2006) Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 13 | Illinois TRM 2012
1209 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1606 | National Climatic Data Center
1209 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 5
1209 | 1 | Total Gross Incremental Annual Electric Savings_kWh | DUA | 1
1209 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
1209 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
1209 | 1 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 1
1209 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | kWh Savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * CDD] / (1000 * n-Cool) E80
1209 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
1209 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (Before 2006): Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 10 | Illinois TRM 2012
1209 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
1208 | 1 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 1
1208 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
1208 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (After 2006) Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 13 | Illinois TRM 2012
1208 | 1 | Total Gross Incremental Annual Electric Savings_kWh | DUA | 1
1208 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1606 | National Climatic Data Center
1208 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
1208 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | kWh Savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * CDD] / (1000 * n-Cool) E80
1208 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
1208 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
1208 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
1208 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 5
1208 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (Before 2006): Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 10 | Illinois TRM 2012
1208 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | kWh Savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * CDD] / (1000 * n-Cool) E80
1208 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
1208 | 2 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (Before 2006): Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 10 | Illinois TRM 2012
1208 | 2 | Total Gross Incremental Annual Electric Savings_kWh | DUA | 1
1208 | 2 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1606 | National Climatic Data Center
1208 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
1208 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
1208 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 5
1208 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
1208 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
1208 | 2 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (After 2006) Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 13 | Illinois TRM 2012
1208 | 2 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 1
875 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Converts hours to days | 24
875 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
875 | 2 | Gross Incremental Annual Gas Savings_MMBTU | HDD: Cooling Degree Days | 4535 | National Climatic Data Center
875 | 2 | Measure Life | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
875 | 2 | Gross Incremental Annual Gas Savings_MMBTU | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
875 | 2 | Gross Incremental Annual Gas Savings_MMBTU | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
875 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | kWh Savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * CDD] / (1000 * n-Cool) E80
875 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Savings Algorithm | Gas savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * HDD] / (100,067 * nHeat)
875 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
875 | 2 | Gross Incremental Annual Gas Savings_MMBTU | n-Heat: Efficiency of heating system | 70% | Illinois TRM 2012
875 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Converts Btu to kBtu | 1000
875 | 2 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 1
875 | 2 | Total Gross Incremental Annual Electric Savings_kWh | DUA | 1
875 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
875 | 2 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (Before 2006): Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 10 | Illinois TRM 2012
875 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
875 | 2 | Gross Incremental Annual Gas Savings_MMBTU | A_attic: Total area of insulated ceiling/attic (ft2) | 950
875 | 2 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1606 | National Climatic Data Center
875 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
875 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
875 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 5
875 | 2 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (After 2006) Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 13 | Illinois TRM 2012
876 | 2 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 1
876 | 2 | Gross Incremental Annual Gas Savings_MMBTU | n-Heat: Efficiency of heating system | 70% | Illinois TRM 2012
876 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
876 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 5
876 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
876 | 2 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (After 2006) Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 13 | Illinois TRM 2012
876 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
876 | 2 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1606 | National Climatic Data Center
876 | 2 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (Before 2006): Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 10 | Illinois TRM 2012
876 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
876 | 2 | Gross Incremental Annual Gas Savings_MMBTU | HDD: Cooling Degree Days | 4535 | National Climatic Data Center
876 | 2 | Gross Incremental Annual Gas Savings_MMBTU | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
876 | 2 | Measure Life | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
876 | 2 | Gross Incremental Annual Gas Savings_MMBTU | A_attic: Total area of insulated ceiling/attic (ft2) | 950
876 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
876 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 38
876 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Converts Btu to kBtu | 1000
876 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
876 | 2 | Total Gross Incremental Annual Electric Savings_kWh | DUA | 1
876 | 2 | Gross Incremental Annual Gas Savings_MMBTU | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
876 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Savings Algorithm | Gas savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * HDD] / (100,067 * nHeat)
876 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Converts hours to days | 24
876 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | kWh Savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * CDD] / (1000 * n-Cool) E80
876 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HDD: Heating Degree Days | 4535 | NOAA @65 degrees @ Lambert. National Climatic Data Center, Cooling Degree Days are based on a base temp of 65°F. There is a county mapping table in the Appendix providing the appropriate city to use for each county of Illinois.
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 49
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (After 2006) Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 10
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 1
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | DUA | .75
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1646 | NOAA @65 degrees @ Lambert. National Climatic Data Center, Cooling Degree Days are based on a base temp of 65°F. There is a county mapping table in the Appendix providing the appropriate city to use for each county of Illinois.
881 | 2 | Measure Life | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Factor is used directly for walls, but reduced by 1/2 for attics, assuming that the average joist is 5.5" and R-38 requires 11" of cellulose, therefore at each joist, 1/2 the thickness of insulation has been added as between the joists.
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 49
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Home Energy Analysis Evaluation Report_FINAL_5 15 15.pdf
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 5
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Discretionary Use Adjustment | 0.75
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 5
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Factor is used directly for walls, but reduced by 1/2 for attics, assuming that the average joist is 5.5" and R-38 requires 11" of cellulose, therefore at each joist, 1/2 the thickness of insulation has been added as between the joists.
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Btu/kWh | kWh Cool Savings = [ (1/R old - 1/R attic) * A attic * (1-Framing factor/2)) * 24 * CDD * DUA] / (1000 * SEER) ]
881 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm2 | kWh Heat Savings = [ (1/R old - 1/R attic) * A attic * (1-Framing factor/2)) * 24 * HDD) / (COP * 3413) ]
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 5
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | COP |  | Use actual values if known
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
881 | 2 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 1
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (After 2006) Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 10
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 5
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm2 | kWh Heat Savings = [ (1/R old - 1/R attic) * A attic * (1-Framing factor/2)) * 24 * HDD) / (COP * 3413) ]
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 950
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HDD: Heating Degree Days | 4535 | NOAA @65 degrees @ Lambert. National Climatic Data Center, Cooling Degree Days are based on a base temp of 65°F. There is a county mapping table in the Appendix providing the appropriate city to use for each county of Illinois.
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEER | 10.727736 | These default system efficiencies are based on the applicable minimum Federal Standards. In 2006 the Federal Standard for Central AC was adjusted. While one would expect the average system efficiency to be higher than this minimum, the likely degradation of efficiencies over time mean that using the minimum standard is appropriate.
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 49
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Btu/kWh | kWh Cool Savings = [ (1/R old - 1/R attic) * A attic * (1-Framing factor/2)) * 24 * CDD * DUA] / (1000 * SEER) ]
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 950
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | COP |  | Use actual values if known
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Factor is used directly for walls, but reduced by 1/2 for attics, assuming that the average joist is 5.5" and R-38 requires 11" of cellulose, therefore at each joist, 1/2 the thickness of insulation has been added as between the joists
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Discretionary Use Adjustment | 0.75
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Factor is used directly for walls, but reduced by 1/2 for attics, assuming that the average joist is 5.5" and R-38 requires 11" of cellulose, therefore at each joist, 1/2 the thickness of insulation has been added as between the joists.
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | DUA | .75
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1646 | NOAA @65 degrees @ Lambert. National Climatic Data Center, Cooling Degree Days are based on a base temp of 65°F. There is a county mapping table in the Appendix providing the appropriate city to use for each county of Illinois.
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 5
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 49
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
1210 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Btu/kWh | 3413
881 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (Before 2006): Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 10 | Illinois TRM 2012
881 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts Btu to kBtu | 1000
881 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | kWh Savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * CDD] / (1000 * n-Cool) E80
881 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Converts hours to days | 24
881 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
881 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
881 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CDD: Cooling Degree Days | 1646 | National Climatic Data Center
881 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
881 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R attic: R-value of new attic assembly (including all layers between inside air and outside air). | 30
881 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-Cool (After 2006)" Seasonal Energy Efficiency Ratio of cooling system (kBtu/kWh) - Actual (where it is possible to measure or reasonably estimate). If unknown assume the following | 13 | Illinois TRM 2012
881 | 1 | Total Gross Incremental Annual Electric Savings_kWh | A_attic: Total area of insulated ceiling/attic (ft2) | 950
881 | 1 | Gross Incremental Annual Gas Savings_MMBTU | n-Heat: Efficiency of heating system | 70% | Illinois TRM 2012
881 | 1 | Total Gross Incremental Annual Electric Savings_kWh | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
881 | 1 | Gross Incremental Annual Gas Savings_MMBTU | HDD: Cooling Degree Days | 4535 | National Climatic Data Center
881 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts Btu to kBtu | 1000
881 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
881 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Savings Algorithm | Gas savings = [(1/R_old - 1/R_attic) * A_attic * (1-Framing_factor/2) * 24 * HDD] / (100,067 * nHeat)
881 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
881 | 1 | Gross Incremental Annual Gas Savings_MMBTU | R_old: R-value value of existing assemble and any existing insulation. (Minimum of R-5 for uninsulated assemblies ) | 11
881 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Framing_factor: Adjustment to account for area of framing | 0.15 | Oak Ridge National Lab, Technology Fact Sheet for Wall Insulation
881 | 1 | Gross Incremental Annual Gas Savings_MMBTU | A_attic: Total area of insulated ceiling/attic (ft2) | 950
881 | 1 | Measure Life | Source Documentation |  |  | Illinois_Statewide_TRM_Final_Review.pdf
881 | 1 | Gross Incremental Annual Gas Savings_MMBTU | Converts hours to days | 24
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 45 | Morgan Measure Libraries
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren MO PY2 EMV Report
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 45 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13 | Morgan Measure Libraries
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
858 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
858 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use | 2.7 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
858 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren MO PY2 EMV Report
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
858 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
858 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
858 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
858 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
858 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
858 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
858 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 60
858 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
858 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
858 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
858 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
858 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
858 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91
858 | 2 | Efficient Case Value | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
858 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13
858 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
858 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =(((Base Watts-Efficient Watts)× HOU × 365)/1000 ) x WHF
858 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
858 | 2 | Baseline Value | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren MO PY2 EMV Report
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use | 2.7 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 45 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
883 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
883 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13 | Morgan Measure Libraries
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
883 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 45 | Morgan Measure Libraries
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
883 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
883 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
883 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.45
883 | 2 | Efficient Case Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
883 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
883 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
883 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
883 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 43
883 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
883 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
883 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
883 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
883 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
883 | 2 | Baseline Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
883 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
883 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (((Base Watts-WattNEW)×Hours×Days)/1,000) × WHF
883 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
883 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13
883 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13 | Morgan Measure Libraries
954 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 45 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
954 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use | 2.7 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren MO PY2 EMV Report
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 45 | Morgan Measure Libraries
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
954 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
954 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
954 | 2 | Baseline Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1 | This value is assumed to be 1.0 due to the difficulty in identifying and quantifying interactive effects. Interactive effects most certainly exist, and future TRMs will incorporate a specific value to the extent it is identified and measured in a future potential study or future EMV report after more research is conducted.
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× %RES x ISR x (1-LKG) x (Hours x Days x WHF))/1000
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
954 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
954 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 59.3
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 0.965
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
954 | 2 | Efficient Case Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13.3
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 0.89
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
954 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1078 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 45 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13 | Morgan Measure Libraries
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1078 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use | 2.7 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren MO PY2 EMV Report
1078 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 45 | Morgan Measure Libraries
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1078 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1188 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91 | Based on PY 2 EMV results
1188 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1 | This value is assumed to be 1.0 for this TRM. This value is included within any measures stemming from PY 2 EMV results.
1188 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
1188 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13
1188 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1188 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1188 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1188 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1188 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1 | This value is assumed to be 1.0 due to the difficulty in identifying and quantifying interactive effects. Interactive effects most certainly exist, and future TRMs will incorporate a specific value to the extent it is identified and measured in a future potential study or future EMV report after more research is conducted.
1188 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1188 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 58.6
1188 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1188 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1 | This value is assumed to be 1.0 due to the difficulty in identifying and quantifying interactive effects. Interactive effects most certainly exist, and future TRMs will incorporate a specific value to the extent it is identified and measured in a future potential study or future EMV report after more research is conducted.
1189 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1189 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13
1189 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1 | This value is assumed to be 1.0 for this TRM. This value is included within any measures stemming from PY 2 EMV results.
1189 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
1189 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1 | This value is assumed to be 1.0 due to the difficulty in identifying and quantifying interactive effects. Interactive effects most certainly exist, and future TRMs will incorporate a specific value to the extent it is identified and measured in a future potential study or future EMV report after more research is conducted.
1189 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1189 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1189 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri's PY 2 EMV reports
1189 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 58.6
1189 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri's PY 2 EMV reports
1189 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1189 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91 | Based on PY 2 EMV results
1189 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1 | This value is assumed to be 1.0 due to the difficulty in identifying and quantifying interactive effects. Interactive effects most certainly exist, and future TRMs will incorporate a specific value to the extent it is identified and measured in a future potential study or future EMV report after more research is conducted.
1186 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1186 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
1186 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1 | This value is assumed to be 1.0 for this TRM. This value is included within any measures stemming from PY 2 EMV results.
1186 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1 | This value is assumed to be 1.0 due to the difficulty in identifying and quantifying interactive effects. Interactive effects most certainly exist, and future TRMs will incorporate a specific value to the extent it is identified and measured in a future potential study or future EMV report after more research is conducted.
1186 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13
1186 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1186 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1186 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1 | This value is assumed to be 1.0 due to the difficulty in identifying and quantifying interactive effects. Interactive effects most certainly exist, and future TRMs will incorporate a specific value to the extent it is identified and measured in a future potential study or future EMV report after more research is conducted.
1186 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1186 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1186 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 58.6
1186 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1186 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91 | Based on PY 2 EMV results
1187 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13
1187 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1187 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1187 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1 | This value is assumed to be 1.0 due to the difficulty in identifying and quantifying interactive effects. Interactive effects most certainly exist, and future TRMs will incorporate a specific value to the extent it is identified and measured in a future potential study or future EMV report after more research is conducted.
1187 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1 | This value is assumed to be 1.0 due to the difficulty in identifying and quantifying interactive effects. Interactive effects most certainly exist, and future TRMs will incorporate a specific value to the extent it is identified and measured in a future potential study or future EMV report after more research is conducted.
1187 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1187 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
1187 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 58.6
1187 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1187 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91 | Based on PY 2 EMV results
1187 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1 | This value is assumed to be 1.0 for this TRM. This value is included within any measures stemming from PY 2 EMV results.
1187 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1187 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1190 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1190 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
1190 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1190 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91 | Based on PY 2 EMV results
1190 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13
1190 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1190 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1190 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 58.6
1190 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1 | This value is assumed to be 1.0 due to the difficulty in identifying and quantifying interactive effects. Interactive effects most certainly exist, and future TRMs will incorporate a specific value to the extent it is identified and measured in a future potential study or future EMV report after more research is conducted.
1190 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1190 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1 | This value is assumed to be 1.0 for this TRM. This value is included within any measures stemming from PY 2 EMV results.
1190 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1 | This value is assumed to be 1.0 due to the difficulty in identifying and quantifying interactive effects. Interactive effects most certainly exist, and future TRMs will incorporate a specific value to the extent it is identified and measured in a future potential study or future EMV report after more research is conducted.
1190 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1008 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1008 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1008 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1008 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1008 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
1008 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1008 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1008 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1008 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13 | Morgan Measure Libraries
1008 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe
1008 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1008 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 45 | Morgan Measure Libraries
1008 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1008 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1008 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1008 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1008 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 45 | Morgan Measure Libraries
1008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13 | Morgan Measure Libraries
1008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1008 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe
1008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1008 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
1008 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1009 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe
1009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13 | Morgan Measure Libraries
1009 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1009 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
1009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 45 | Morgan Measure Libraries
1009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1009 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1009 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1009 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 13 | Morgan Measure Libraries
1009 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1009 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1009 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1009 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe
1009 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1009 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1009 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1009 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1009 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
1009 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 45 | Morgan Measure Libraries
1009 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1009 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1009 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1009 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1010 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1010 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1010 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1010 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 56 | Morgan Measure Libraries
1010 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
1010 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1010 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1010 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1010 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1010 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1010 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
1010 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1010 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1010 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1010 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1010 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1010 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (((Base Watts-WattNEW)×Hours×Days)/1,000) × WHF
1010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
1010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
1010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
1010 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1010 | 2 | Baseline Value | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 63
1010 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.62
1010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.83
1010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
1011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 56 | Morgan Measure Libraries
1011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
1011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1011 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1011 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1011 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1011 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1011 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.83
1011 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1011 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1011 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
1011 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1011 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
1011 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1011 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 63
1011 | 2 | Baseline Value | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1011 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (((Base Watts-WattNEW)×Hours×Days)/1,000) × WHF
1011 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1011 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
1011 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1011 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.62
1011 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
884 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
884 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
884 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
884 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
884 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
884 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
884 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
884 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
884 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
884 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
884 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 56 | Morgan Measure Libraries
884 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
884 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
884 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
884 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
884 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
884 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.45
884 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
884 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
884 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
884 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
884 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
884 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
884 | 2 | Baseline Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
884 | 2 | Efficient Case Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
884 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 53
884 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
884 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
884 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
884 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
884 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
884 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (((Base Watts-WattNEW)×Hours×Days)/1,000) × WHF
955 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
955 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
955 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
955 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
955 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
955 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
955 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
955 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
955 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
955 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
955 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
955 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
955 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
955 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
955 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
955 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
955 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 56 | Morgan Measure Libraries
955 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 53
955 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
955 | 2 | Baseline Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
955 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
955 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18.6
955 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
955 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91
955 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 0.89
955 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
955 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
955 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× %RES x ISR x (1-LKG) x (Hours x Days x WHF))/1000
955 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 0.965
955 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
955 | 2 | Efficient Case Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1079 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1079 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1079 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1079 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1079 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1079 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1079 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1079 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1079 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1079 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
1079 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
1079 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1079 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 56 | Morgan Measure Libraries
1079 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1079 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1079 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1012 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1012 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 23
1012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 75 | Morgan Measure Libraries
1012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
1012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1012 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1012 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1012 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1012 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.62
1012 | 2 | Baseline Value | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1012 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1012 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1012 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 23
1012 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.83
1012 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (((Base Watts-WattNEW)×Hours×Days)/1,000) × WHF
1012 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1012 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
1012 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1012 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1012 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 72
1012 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1012 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
1013 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1013 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1013 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1013 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1013 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1013 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
1013 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1013 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1013 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 23
1013 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1013 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1013 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1013 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1013 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1013 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 75 | Morgan Measure Libraries
1013 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1013 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (((Base Watts-WattNEW)×Hours×Days)/1,000) × WHF
1013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
1013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1013 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 72
1013 | 2 | Baseline Value | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1013 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 23
1013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
1013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.62
1013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.83
885 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
885 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
885 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
885 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
885 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
885 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
885 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
885 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
885 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
885 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
885 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
885 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 23
885 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
885 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
885 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
885 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 75 | Morgan Measure Libraries
885 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
885 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 72
885 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
885 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 23
885 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
885 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
885 | 2 | Baseline Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
885 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
885 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
885 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
885 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
885 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (((Base Watts-WattNEW)×Hours×Days)/1,000) × WHF
885 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
885 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.45
885 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
885 | 2 | Efficient Case Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
885 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
885 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
956 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
956 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
956 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
956 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
956 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
956 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
956 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
956 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
956 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 23
956 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 75 | Morgan Measure Libraries
956 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
956 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
956 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
956 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
956 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
956 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
956 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
956 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× %RES x ISR x (1-LKG) x (Hours x Days x WHF))/1000
956 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
956 | 2 | Efficient Case Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
956 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 72
956 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
956 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
956 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
956 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 0.89
956 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
956 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 23.4
956 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91
956 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
956 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
956 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
956 | 2 | Baseline Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
956 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
956 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 0.965
1080 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1080 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1080 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1080 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1080 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1080 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 75 | Morgan Measure Libraries
1080 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1080 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1080 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1080 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1080 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1080 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7 | Morgan Measure Libraries
1080 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1080 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1080 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1080 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 23
1080 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1014 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1014 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1014 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1014 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1014 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 156
1014 | 1 | Efficient Case Value | Source Documentation |  |  | Ameren Missouri - PY3 LA Evaluation Report_FINAL_29MAR2012.pdf
1014 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91 | Based on PY 2 EMV results
1014 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - PY3 LA Evaluation Report_FINAL_29MAR2012.pdf
1014 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 39 | Based on PY 2 EMV results
1014 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1014 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1014 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1014 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1014 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY3 LA Evaluation Report_FINAL_29MAR2012.pdf
1014 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1014 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1014 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
886 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
886 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - PY3 LA Evaluation Report_FINAL_29MAR2012.pdf
886 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
886 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
886 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 39 | Based on PY 2 EMV results
886 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
886 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
886 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
886 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91 | Based on PY 2 EMV results
886 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
886 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
886 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY3 LA Evaluation Report_FINAL_29MAR2012.pdf
886 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 156
886 | 1 | Efficient Case Value | Source Documentation |  |  | Ameren Missouri - PY3 LA Evaluation Report_FINAL_29MAR2012.pdf
886 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
886 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
886 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
957 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
957 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
957 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
957 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY3 LA Evaluation Report_FINAL_29MAR2012.pdf
957 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
957 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
957 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
957 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
957 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - PY3 LA Evaluation Report_FINAL_29MAR2012.pdf
957 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
957 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 156
957 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
957 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
957 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
957 | 1 | Efficient Case Value | Source Documentation |  |  | Ameren Missouri - PY3 LA Evaluation Report_FINAL_29MAR2012.pdf
957 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91 | Based on PY 2 EMV results
957 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 39 | Based on PY 2 EMV results
1081 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - PY3 LA Evaluation Report_FINAL_29MAR2012.pdf
1081 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1081 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 39 | Based on PY 2 EMV results
1081 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1081 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 156
1081 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1081 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1081 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1081 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY3 LA Evaluation Report_FINAL_29MAR2012.pdf
1081 | 1 | Efficient Case Value | Source Documentation |  |  | Ameren Missouri - PY3 LA Evaluation Report_FINAL_29MAR2012.pdf
1081 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1081 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1081 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1081 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1081 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1081 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91 | Based on PY 2 EMV results
1081 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
887 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
887 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.3 | Morgan Measure Libraries
887 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
887 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
887 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 199.6
887 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
887 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
887 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
887 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
887 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 65
887 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
887 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
887 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
887 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
887 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
887 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.45
887 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (((Base Watts-WattNEW)×Hours×Days)/1,000) × WHF
887 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 199.6
887 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
887 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
887 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 42
887 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
887 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
887 | 2 | Efficient Case Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
887 | 2 | Baseline Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
887 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
887 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
887 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
887 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
887 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
887 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
958 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
958 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.3 | Morgan Measure Libraries
958 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
958 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
958 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
958 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 65
958 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
958 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
958 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
958 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
958 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
958 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
958 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
958 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
958 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 199.6
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | .99
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1.1
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 0.89
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× %RES x ISR x (1-LKG) x (Hours x Days x WHF))/1000
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.91
958 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
958 | 2 | Baseline Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0.033
958 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 47.6
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 187.8
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
958 | 2 | Efficient Case Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 0.965
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
958 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
1082 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1082 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1082 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1082 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1082 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1082 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1082 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.3 | Morgan Measure Libraries
1082 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 65
1082 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1082 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1082 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1082 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1082 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1082 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 199.6
1082 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1015 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1015 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 65
1015 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1015 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1015 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 199.6
1015 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1015 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.3 | Morgan Measure Libraries
1015 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1015 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1015 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1015 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1015 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1015 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1015 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1015 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1016 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1016 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1016 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.3 | Morgan Measure Libraries
1016 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1016 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1016 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1016 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 20 | Morgan Measure Libraries
1016 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1016 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 72.5
1016 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1016 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1016 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1016 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1016 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1016 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1016 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1016 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
888 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
888 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
888 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
888 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.3 | Morgan Measure Libraries
888 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 72.5
888 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
888 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
888 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
888 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
888 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 20 | Morgan Measure Libraries
888 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
888 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
888 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
888 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
888 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
888 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
888 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
888 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
888 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (((Base Watts-WattNEW)×Hours×Days)/1,000) × WHF
888 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.45
888 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 20
888 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
888 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
888 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
888 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
888 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
888 | 2 | Baseline Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
888 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
888 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
888 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
888 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
888 | 2 | Efficient Case Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
888 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 63
888 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
959 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
959 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
959 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
959 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.3 | Morgan Measure Libraries
959 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
959 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 20 | Morgan Measure Libraries
959 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
959 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 72.5
959 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
959 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
959 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
959 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
959 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
959 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
959 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
959 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
959 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
959 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 0.965
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91
959 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
959 | 2 | Baseline Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
959 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 15.8
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× %RES x ISR x (1-LKG) x (Hours x Days x WHF))/1000
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 60.9
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 0.89
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
959 | 2 | Efficient Case Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
959 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1083 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1083 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1083 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1083 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1083 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1083 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1083 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1083 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 20 | Morgan Measure Libraries
1083 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1083 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1083 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1083 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1083 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 72.5
1083 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1083 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.3 | Morgan Measure Libraries
1083 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1083 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1017 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1017 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1017 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1017 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1017 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 26.5
1017 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1017 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 79
1017 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1017 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1017 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1017 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1017 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1017 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1017 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1017 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.3 | Morgan Measure Libraries
1017 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1017 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
889 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
889 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 79
889 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.3 | Morgan Measure Libraries
889 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
889 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
889 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
889 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
889 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
889 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
889 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 26.5
889 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
889 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
889 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
889 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
889 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
889 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
889 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
889 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
889 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
889 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
889 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
889 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (((Base Watts-WattNEW)×Hours×Days)/1,000) × WHF
889 | 2 | Efficient Case Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
889 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
889 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
889 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.45
889 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
889 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
889 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 12.9
889 | 2 | Baseline Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
889 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
889 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
889 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 52.7
889 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
960 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
960 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 79
960 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
960 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
960 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
960 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.3 | Morgan Measure Libraries
960 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
960 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
960 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
960 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 26.5
960 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
960 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
960 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
960 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
960 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
960 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
960 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× %RES x ISR x (1-LKG) x (Hours x Days x WHF))/1000
960 | 2 | Baseline Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 0.89
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
960 | 2 | Efficient Case Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 12.8
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
960 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 52.6
960 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 0.965
960 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1084 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1084 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1084 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1084 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1084 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1084 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1084 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 79
1084 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1084 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1084 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1084 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1084 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1084 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 26.5
1084 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1084 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.3 | Morgan Measure Libraries
1084 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1084 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
961 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
961 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 55
961 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
961 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
961 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
961 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
961 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.3 | Morgan Measure Libraries
961 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
961 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
961 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
961 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
961 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
961 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
961 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 250.4
961 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
961 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | ApplianceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | ApplianceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
986 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
986 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
986 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
986 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
927 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
927 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
927 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
927 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
927 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
927 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
927 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
927 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
927 | 3 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
927 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
927 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
927 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
987 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
987 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
987 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
987 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
928 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
928 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
928 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
928 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
928 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
928 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
928 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
928 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
928 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
928 | 3 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
928 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
928 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1056 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1056 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1056 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1056 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
988 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
988 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
988 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
988 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
929 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
929 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
929 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
929 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
929 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
929 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
929 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
929 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
929 | 3 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
929 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
929 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
929 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1057 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1057 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1057 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1057 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
989 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
989 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
989 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
989 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
930 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
930 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
930 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
930 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
930 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
930 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
930 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
930 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
930 | 3 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
930 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
930 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
930 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1058 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1058 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1058 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1058 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
990 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
990 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
990 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
990 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
931 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
931 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
931 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
931 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
931 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
931 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
931 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
931 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
931 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
931 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
931 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
931 | 3 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1059 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1059 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1059 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1059 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1226 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLHcool | 869
1226 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EI | .15
1226 | 3 | Total Gross Incremental Annual Electric Savings_kWh | kWMotor | .5
1226 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Customer | .86
1226 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLHheat | 1496
1226 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ISR | .47
976 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
976 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
976 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
976 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
977 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
977 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
977 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
977 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
978 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
978 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
978 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
978 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
979 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
979 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
979 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
979 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
980 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
980 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
980 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
980 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
905 | 1 | Baseline Value | Source Documentation
905 | 1 | Efficient Case Value | Source Documentation
905 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
905 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
905 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
905 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
905 | 2 | Efficient Case Value | Source Documentation
905 | 2 | Baseline Value | Source Documentation
1046 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
1046 | 1 | Efficient Case Value | Source Documentation
1046 | 1 | Baseline Value | Source Documentation
1046 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
906 | 1 | Efficient Case Value | Source Documentation
906 | 1 | Baseline Value | Source Documentation
906 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
906 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
906 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
906 | 2 | Efficient Case Value | Source Documentation
906 | 2 | Baseline Value | Source Documentation
906 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
1047 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
1047 | 1 | Efficient Case Value | Source Documentation
1047 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
1047 | 1 | Baseline Value | Source Documentation
908 | 2 | Incremental Cost per Unit | Source Documentation
908 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
908 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
908 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - HVAC PY14 Evaluation Report_FINAL 6 16 15.pdf
908 | 3 | Incremental Cost per Unit | Source Documentation
908 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
908 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
908 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - HVAC PY14 Evaluation Report_FINAL 6 16 15.pdf
907 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
907 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
907 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
907 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
907 | 2 | Incremental Cost per Unit | Source Documentation
907 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
907 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
907 | 3 | Incremental Cost per Unit | Source Documentation
907 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Cont Fan Savings | 3488.4903
907 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
907 | 3 | Total Gross Incremental Annual Electric Savings_kWh | WI EFLHH | 2545.2
907 | 3 | Total Gross Incremental Annual Electric Savings_kWh | STL EFLHC | 1215
907 | 3 | Total Gross Incremental Annual Electric Savings_kWh | STLEFLHH | 2009
907 | 3 | Total Gross Incremental Annual Electric Savings_kWh | WI EFLHC | 542.5
907 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
907 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1028 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1028 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1028 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1028 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1029 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1029 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1029 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1029 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
911 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
911 | 2 | Total Gross Incremental Annual Electric Savings_kWh | WI EFLHH | 2545.25
911 | 2 | Total Gross Incremental Annual Electric Savings_kWh | WI EFLHC | 542.5
911 | 2 | Incremental Cost per Unit | Source Documentation
911 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
911 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
911 | 2 | Total Gross Incremental Annual Electric Savings_kWh | STL EFLHH | 2009
911 | 2 | Total Gross Incremental Annual Electric Savings_kWh | STL EFLHC | 1215
911 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
911 | 3 | Incremental Cost per Unit | Source Documentation
911 | 3 | Total Gross Incremental Annual Electric Savings_kWh | STL EFLHH | 2009
911 | 3 | Total Gross Incremental Annual Electric Savings_kWh | WI EFLHC | 542.5
911 | 3 | Total Gross Incremental Annual Electric Savings_kWh | WI EFLHH | 2545.25
911 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
911 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
911 | 3 | Total Gross Incremental Annual Electric Savings_kWh | STL EFLHC | 1215
910 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
910 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
910 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
910 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
910 | 2 | Total Gross Incremental Annual Electric Savings_kWh | WI EFLHH | 2545.25
910 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
910 | 2 | Total Gross Incremental Annual Electric Savings_kWh | WI EFLHC | 542.5
910 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
910 | 2 | Total Gross Incremental Annual Electric Savings_kWh | STL EFLHC | 1215
910 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
910 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
910 | 2 | Total Gross Incremental Annual Electric Savings_kWh | STL EFLHH | 2009
910 | 3 | Total Gross Incremental Annual Electric Savings_kWh | STL EFLHH | 2009
910 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
910 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
910 | 3 | Total Gross Incremental Annual Electric Savings_kWh | STL EFLHC | 1215
910 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
910 | 3 | Total Gross Incremental Annual Electric Savings_kWh | WI EFLHH | 2545.25
910 | 3 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
910 | 3 | Total Gross Incremental Annual Electric Savings_kWh | WI EFLHC | 542.5
908 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
908 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (Base kWh - Efficient kWh)
908 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
908 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.767 | Proctor Engineering Group
908 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
908 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
908 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
908 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 7780.2 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
908 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
908 | 1 | Incremental Cost per Unit | Base Cost | 215 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
908 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 6851.6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
908 | 1 | Incremental Cost per Unit | Efficient Cost | 340 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
908 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
911 | 1 | Incremental Cost per Unit | Efficient Cost | 340 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
911 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.767 | Proctor Engineering Group
911 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
911 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
911 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
911 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
911 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 10744.7 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
911 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
911 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
911 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (Base kWh - Efficient kWh)
911 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 7148 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
911 | 1 | Incremental Cost per Unit | Base Cost | 215 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
911 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1177 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SBes | .272
1177 | 3 | Total Gross Incremental Annual Electric Savings_kWh | CADR | 137.59
1177 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HRS | 16
1177 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFFes | 2.765
1177 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SBbl | 1
1177 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source |  |  | Ameren Missouri - PY14 Efficient Products Evaluation Report and Appendices_FINAL_5 15 15.pdf
1177 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFFbl | 1
968 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
968 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh=Base UEC-Efficient UEC
968 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
968 | 1 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
968 | 1 | Efficient Case Value | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
968 | 1 | Baseline Value | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
968 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
968 | 2 | Total Gross Incremental Annual Electric Savings_kWh | UEC new (kWh consumption of new unit) | 362
968 | 2 | Efficient Case Value | Source Documentation
968 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh= (UEC existing * Part Use Factor) - UEC new
968 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
968 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
968 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
968 | 2 | Total Gross Incremental Annual Electric Savings_kWh | UEC exisiting (kWh consumption of old unit) | 1268
968 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Part Use Factor | 1
968 | 2 | Baseline Value | Source Documentation
968 | 2 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
968 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
968 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh= (UEC existing * Part Use Factor) - UEC new
968 | 3 | Total Gross Incremental Annual Electric Savings_kWh | UEC new (kWh consumption of new unit) | 368
968 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
968 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Part Use Factor | 1
968 | 3 | Baseline Value | Source Documentation
968 | 3 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
968 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
968 | 3 | Total Gross Incremental Annual Electric Savings_kWh | UEC exisiting (kWh consumption of old unit) | 1256
968 | 3 | Efficient Case Value | Source Documentation
1221 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Part Use Factor | 1
1221 | 1 | Total Gross Incremental Annual Electric Savings_kWh | UEC exisiting (kWh consumption of old unit) | 1268
1221 | 1 | Total Gross Incremental Annual Electric Savings_kWh | UEC new (kWh consumption of new unit) | 362
1221 | 2 | Total Gross Incremental Annual Electric Savings_kWh | UEC exisiting (kWh consumption of old unit) | 1268
1221 | 2 | Total Gross Incremental Annual Electric Savings_kWh | UEC new (kWh consumption of new unit) | 362
1221 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Part Use Factor | 1
1180 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Equation | kWh savings = (KWHbase - KWHeff)*365
1180 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Consumption per day for an efficient unit (KWHeff) | 0.16
1180 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Consumption per day for conventional unit (KWHbase) | 0.29
1181 | 3 | Total Gross Incremental Annual Electric Savings_kWh | DEUbl | 1.0835
1181 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source |  |  | Ameren Missouri - PY14 Efficient Products Evaluation Report and Appendices_FINAL_5 15 15.pdf
1181 | 3 | Total Gross Incremental Annual Electric Savings_kWh | DEUes | .7
2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh=(Base UEC-Efficienct UEC)x In-Situ factor | Ameren MO PY2 EMV Report
2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base UEC (kWh) | 1664 | Ameren MO PY2 EMV Report
2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient UEC (kWh) |  | Ameren MO PY2 EMV Report
2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In-Situ Factor: factor considering appliances not plugged in year-round (also known as part-use) | 0.7557 | Ameren MO PY2 EMV Report
2 | 1 | Efficient Case Value | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
2 | 1 | Baseline Value | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
2 | 1 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
2 | 2 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | ApplianceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | ApplianceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
2 | 2 | Baseline Value | Source Documentation |  |  | ApplianceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh= Base UEC*Part Use Factor
2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base UEC (kWh) | 1078.392809
2 | 2 | Efficient Case Value | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Part Use Factor | 0.898551
2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
932 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
932 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
932 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
932 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
932 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
932 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
932 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
932 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1060 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1060 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1060 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1060 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
933 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
933 | 1 | Incremental Cost per Unit | Efficient Cost | 7000 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
933 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
933 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
933 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
933 | 1 | Total Gross Average Annual Demand Reduction_kW | Current installed GSHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
933 | 1 | Efficient Case Value | Source Documentation
933 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
933 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
933 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
933 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 15949.2 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
933 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 14 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
933 | 1 | Total Gross Average Annual Demand Reduction_kW | Baseline GSHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
933 | 1 | Incremental Cost per Unit | Base Cost | 2835 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
933 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
933 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 12905.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
933 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
933 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
933 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
933 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
933 | 1 | Total Gross Average Annual Demand Reduction_kW | Efficient GSHP electric demand (kW) | 2.016 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
933 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
933 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
933 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 10823.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
933 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
933 | 2 | Total Gross Average Annual Demand Reduction_kW | Current installed GSHP electric demand (kW) | 3.375
933 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons)
933 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 12905.3
933 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
933 | 2 | Incremental Cost per Unit | Source Documentation
933 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 2009 | This represents a measure of energy use by season during the on-peak and off peak periods. This value will be determined by existing measured data of kWh during the period divided by kW at design conditions
933 | 2 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
933 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
933 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 10823.5
933 | 2 | Incremental Cost per Unit | Efficient Cost | 7000
933 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
933 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
933 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor )
933 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
933 | 2 | Incremental Cost per Unit | Base Cost | 2835
933 | 2 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
933 | 2 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
933 | 2 | Total Gross Average Annual Demand Reduction_kW | Baseline GSHP electric demand (kW) | 2.455
933 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 6.3
933 | 2 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
933 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 15949.2
933 | 2 | Total Gross Average Annual Demand Reduction_kW | Efficient GSHP electric demand (kW) | 2.016
933 | 2 | Measure Life | Source Documentation
933 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
933 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
933 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
933 | 2 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
933 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1061 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
1061 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
1061 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 14 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1061 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | delta kWh = EFLH x kBTU/hr x (((1/SEERbase)-(1/SEERee)))/1000
1061 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
1061 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
1061 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
1061 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 12905.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1061 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh | 10823.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1061 | 1 | Total Gross Average Annual Demand Reduction_kW | Current installed GSHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1061 | 1 | Efficient Case Value | Source Documentation
1061 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1061 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
1061 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 15949.2 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1061 | 1 | Total Gross Average Annual Demand Reduction_kW | Efficient GSHP electric demand (kW) | 2.016 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1061 | 1 | Incremental Cost per Unit | Base Cost | 2835 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1061 | 1 | Total Gross Average Annual Demand Reduction_kW | Baseline GSHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1061 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1061 | 1 | Incremental Cost per Unit | Efficient Cost | 7000 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1061 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
1061 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
1061 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
1061 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1061 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
934 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
934 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
934 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
934 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
934 | 1 | Total Gross Average Annual Demand Reduction_kW | Baseline GSHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
934 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh
934 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
934 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
934 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
934 | 1 | Incremental Cost per Unit | Base Cost | 2283 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
934 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
934 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 14 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
934 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
934 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
934 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
934 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
934 | 1 | Incremental Cost per Unit | Efficient Cost | 7000 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
934 | 1 | Total Gross Average Annual Demand Reduction_kW | Efficient GSHP electric demand (kW)
934 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
934 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
934 | 1 | Total Gross Average Annual Demand Reduction_kW | Current installed GSHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
934 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
934 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
934 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
934 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
934 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5
934 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
934 | 2 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
934 | 2 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 4.2
934 | 2 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
934 | 2 | Incremental Cost per Unit | Source Documentation
934 | 2 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 1805
934 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
934 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh
934 | 2 | Measure Life | Source Documentation
934 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.2
934 | 2 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
934 | 2 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
934 | 2 | Incremental Cost per Unit | Efficient Cost | 7000
934 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 21.471
934 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
934 | 2 | Total Gross Average Annual Demand Reduction_kW | Efficient GSHP electric demand (kW)
934 | 2 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
934 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 3.412
934 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3
934 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
934 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 4.2105
934 | 2 | Incremental Cost per Unit | Base Cost | 2283
934 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor ) | 21.471
934 | 2 | Total Gross Average Annual Demand Reduction_kW | Baseline GSHP electric demand (kW) | 2.455
934 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 2009 | This represents a measure of energy use by season during the on-peak and off peak periods. This value will be determined by existing measured data of kWh during the period divided by kW at design conditions
934 | 2 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
934 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
934 | 2 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
934 | 2 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
934 | 2 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
934 | 2 | Total Gross Average Annual Demand Reduction_kW | Current installed GSHP electric demand (kW) | 3.375
934 | 3 | Total Gross Average Annual Demand Reduction_kW | Efficient GSHP electric demand (kW)
934 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 20
934 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 2009 | This represents a measure of energy use by season during the on-peak and off peak periods. This value will be determined by existing measured data of kWh during the period divided by kW at design conditions
934 | 3 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
934 | 3 | Total Gross Average Annual Demand Reduction_kW | Current installed GSHP electric demand (kW) | 3.375
934 | 3 | Total Gross Average Annual Demand Reduction_kW | Equation D (Demand): Gross incremental annual demand savings (kW/yr) | delta kW = T * 12kBTU/ton * (1/EERbase - 1/EEReff) * cf
934 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
934 | 3 | Total Gross Average Annual Demand Reduction_kW | T: Capacity of unit (tons) | 4.2
934 | 3 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767
934 | 3 | Total Gross Average Annual Demand Reduction_kW | EERbase: Efficiency rating of the baseline unit.
934 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 3.65183
934 | 3 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03
934 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
934 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
934 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3
934 | 3 | Total Gross Average Annual Demand Reduction_kW | EEReff: Efficiency rating of the efficient unit
934 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.1
934 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 3.4
934 | 3 | Total Gross Average Annual Demand Reduction_kW | Baseline GSHP electric demand (kW) | 2.455
934 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 1805
934 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh
934 | 3 | Incremental Cost per Unit | Equation C (Cost): Total incremental cost | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
934 | 3 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6
934 | 3 | Incremental Cost per Unit | Base Cost | 2283
934 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5
934 | 3 | Total Gross Average Annual Demand Reduction_kW | CF: Coincidence Factor | 0.73
934 | 3 | Incremental Cost per Unit | Efficient Cost | 7000
934 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor ) | 20
934 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
934 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
934 | 3 | Measure Life | Source Documentation
934 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
934 | 3 | Incremental Cost per Unit | Source Documentation
1062 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13
1062 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 2 | delta kWh = (Base kWh - Efficient kWh)
1062 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: seasonal energy efficiency ratio of the efficient equipment (BTU/Watt-hours) | 14 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1062 | 1 | Measure Life | Measure Life Notes | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
1062 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
1062 | 1 | Incremental Cost per Unit | Base Cost | 2283 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1062 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm 1 | Existing Unit Remaining Useful Life (RUL): 6 years ; New ASHP Effective Useful Life (EUL): 18 years ; Remaining Effective Life (REL) after RUL: 12 years
1062 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
1062 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Full Load Hours
1062 | 1 | Total Gross Average Annual Demand Reduction_kW | Efficient GSHP electric demand (kW)
1062 | 1 | Total Gross Incremental Annual Electric Savings_kWh | the conversion factor between Wh and kWh (Wh/kWh) | 1000
1062 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient kWh
1062 | 1 | Incremental Cost per Unit | RDR: Real Discount Rate | 0.03 | Proctor Engineering Group
1062 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERcurrentbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1062 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Current Base kWh | 26664.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1062 | 1 | Incremental Cost per Unit | Equation C (Cost): Incremental Cost per Unit | Inc Cost_ER=Efficient Cost-(Base Cost*[(1+RDR)]^RUL)/[(1+UDR)]^RUL
1062 | 1 | Incremental Cost per Unit | UDR: Utility Discount Rate | 0.0767 | Proctor Engineering Group
1062 | 1 | Total Gross Average Annual Demand Reduction_kW | Baseline GSHP electric demand (kW) | 2.455 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1062 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBTU: The nominal rating of the capacity of AC unit in kBTU/hr. 1 Ton = 12 kBTU/hr | 36
1062 | 1 | Incremental Cost per Unit | Efficient Cost | 7000 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1062 | 1 | Total Gross Average Annual Demand Reduction_kW | Current installed GSHP electric demand (kW) | 3.375 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1062 | 1 | Incremental Cost per Unit | RUL: Remaining Useful Life | 6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1062 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1062 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base kWh | 25173.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
935 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
935 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
935 | 1 | Efficient Case Value | Source Documentation
935 | 1 | Baseline Value | Source Documentation
935 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 3.412
935 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 4.487
935 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
935 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.2
935 | 2 | Incremental Cost per Unit | Source Documentation
935 | 2 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 360
935 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Rating of unit (tons) | 4.5
935 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 2009
935 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
935 | 2 | Measure Life | Source Documentation
935 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
935 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 20.77
935 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor ) | 20.77 | Not Available
935 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
935 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =rating of unit (tons) * 12kbtu/ton *(EFLHheating * (1/HSPFbase - 1/HSPFeff))
935 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER metered | 15.1
935 | 3 | Measure Life | Source Documentation
935 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons Efficient | 3.79427
935 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
935 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Rating of unit (tons) | 4.5
935 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLH: Equivalent Full Load Hours | 2009
935 | 3 | Total Gross Incremental Annual Electric Savings_kWh | SEER Efficient | 20.77
935 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons metered | 3.1
935 | 3 | Incremental Cost per Unit | Source Documentation
935 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
935 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor ) | 3.412
935 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPFeff (Heating Seasonal Performance Factor ) | 20.77 | Not Available
935 | 3 | Total Gross Incremental Annual Electric Savings_kWh | metered kWh | 360
1063 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
1063 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
1063 | 1 | Efficient Case Value | Source Documentation
1063 | 1 | Baseline Value | Source Documentation
913 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
913 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
913 | 1 | Efficient Case Value | Source Documentation
913 | 1 | Baseline Value | Source Documentation
913 | 2 | Baseline Value | Source Documentation
913 | 2 | Efficient Case Value | Source Documentation
913 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
913 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
914 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
914 | 1 | Efficient Case Value | Source Documentation
914 | 1 | Baseline Value | Source Documentation
914 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
914 | 2 | Baseline Value | Source Documentation
914 | 2 | Efficient Case Value | Source Documentation
914 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
914 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation
1232 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HWT: hot water temperature (F) | 135
1232 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efbase: energy factor of baseline water heater | .9
1232 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efeff: energy factor of program qualified water heaters | 2.7
1232 | 2 | Total Gross Incremental Annual Electric Savings_kWh | GPD: gallons of hot water used per day | 64
1232 | 2 | Total Gross Incremental Annual Electric Savings_kWh | kWhcool***: cooling interaction due to heat removed from room to heat water | 180
1232 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1232 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1232 | 2 | Total Gross Incremental Annual Electric Savings_kWh | CWT: temperature in Fahrenheit of cold water supply | 61.3
1232 | 2 | Total Gross Incremental Annual Electric Savings_kWh | kWhheat - heat pumps**: heating interaction due to heat removed from room to heat water | 427.5
872 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
872 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CWT: temperature in Fahrenheit of cold water supply | 58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
872 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
872 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Equation | delta kWh =((1/(Base EF)-1/(Efficent EF))×(HWT-CWT) × 8.3 × GPD ×365)/3413 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
872 | 1 | Total Gross Incremental Annual Electric Savings_kWh | GPD: hot water used in gallons per day |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
872 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
872 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HWT: temperature in Fahrenheit of hot water | 135 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
872 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
872 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of water heater |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor (days/year) | 365
872 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor (Btu/kWh) | 3413
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings notes | ** Ameren heat pump saturation = 26% according to survey results
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efeff: energy factor of program qualified water heaters | 2.4
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings notes | *** Ameren CAC = 81% according to survey results
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | kWhcool***: cooling interaction due to heat removed from room to heat water | 163.8
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | kWhheat - heat pumps**: heating interaction due to heat removed from room to heat water | 399.38
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings notes | *Ameren electric resistence heat saturation = 15% according to survey results
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | CWT: temperature in Fahrenheit of cold water supply | 61.3
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | kWhheat - electric resistence*: heating interaction due to heat removed from room to heat water | 173.47
872 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HWT: hot water temperature (F) | 135
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | GPD: gallons of hot water used per day | 64
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Efficient Products Evaluation Report and Appendices_FINAL_5 15 15.pdf
872 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efbase: energy factor of baseline water heater | 0.9
872 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | kWhcool***: cooling interaction due to heat removed from room to heat water | 180
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | kWhheat - electric resistence*: heating interaction due to heat removed from room to heat water | 173.47
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | GPD: gallons of hot water used per day | 64
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings notes | *Ameren electric resistence heat saturation = 15% according to survey results
872 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efbase: energy factor of baseline water heater | 0.9
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | CWT: temperature in Fahrenheit of cold water supply | 61.3
872 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor (days/year) | 365
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Efficient Products Evaluation Report and Appendices_FINAL_5 15 15.pdf
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings notes | ** Ameren heat pump saturation = 26% according to survey results
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings notes | *** Ameren CAC = 81% according to survey results
872 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HWT: hot water temperature (F) | 135
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor (Btu/kWh) | 3413
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | kWhheat - heat pumps**: heating interaction due to heat removed from room to heat water | 427.5
872 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efeff: energy factor of program qualified water heaters | 2.7
902 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
902 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of water heater |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
902 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HWT: temperature in Fahrenheit of hot water | 135 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
902 | 1 | Total Gross Incremental Annual Electric Savings_kWh | GPD: hot water used in gallons per day |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
902 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
902 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
902 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CWT: temperature in Fahrenheit of cold water supply | 58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
902 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Equation | delta kWh =((1/(Base EF)-1/(Efficent EF))×(HWT-CWT) × 8.3 × GPD ×365)/3413 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
902 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1092 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of water heater |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1092 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1092 | 1 | Total Gross Incremental Annual Electric Savings_kWh | GPD: hot water used in gallons per day |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1092 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1092 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CWT: temperature in Fahrenheit of cold water supply | 58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1092 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HWT: temperature in Fahrenheit of hot water | 135 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1092 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((1/(Base EF)-1/(Efficent EF))×(HWT-CWT) × 8.3 × GPD ×365)/3413 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1092 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1092 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
952 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
952 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
952 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
952 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
952 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
952 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
952 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
952 | 1 | Baseline Value | Source Documentation |  |  | Assumptions from OSRAM SYLVANIA website on HID lighting.xlsx
952 | 1 | Efficient Case Value | Source Documentation |  |  | Assumptions from OSRAM SYLVANIA website on HID lighting.xlsx
952 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
952 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 8
952 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
952 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
952 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 50
952 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
952 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
952 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 256.5
952 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1077 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1077 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 50
1077 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1077 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1077 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1077 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1077 | 1 | Efficient Case Value | Source Documentation |  |  | Assumptions from OSRAM SYLVANIA website on HID lighting.xlsx
1077 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1077 | 1 | Baseline Value | Source Documentation |  |  | Assumptions from OSRAM SYLVANIA website on HID lighting.xlsx
1077 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 8
1077 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1077 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 256.5
1077 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1077 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1077 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1077 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1077 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1077 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1245 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Low Income Evaluation Report_FINAL_6 17 15.pdf
999 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
999 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
999 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
999 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
999 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Low Income Evaluation Report_FINAL_6 17 15.pdf
999 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
999 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
999 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
999 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
999 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Low Income Evaluation Report_FINAL_6 17 15.pdf
999 | 3 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
999 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
943 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
943 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
943 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
943 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
943 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
943 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
943 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
943 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
943 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
943 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
943 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
943 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1000 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1000 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1000 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1000 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1000 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1000 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1000 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1000 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
941 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
941 | 1 | Baseline Value | Source Documentation
941 | 1 | Efficient Case Value | Source Documentation
941 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - HVAC PY14 Evaluation Report_FINAL 6 16 15.pdf
941 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
941 | 2 | Measure Life | Source Documentation
941 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - HVAC PY14 Evaluation Report_FINAL 6 16 15.pdf
941 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
941 | 3 | Measure Life | Source Documentation
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1018 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 10.5
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 47
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1018 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 1.6
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 47
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 10.5
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 1.6
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365.25
1018 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1018 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 10.5
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 1.6
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 47
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1018 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1018 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 65.8
1019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1019 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 10.5
1019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1019 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.2
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 47
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 10.5
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1019 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365.25
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 47
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365.25
1019 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.2
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 10.5
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1019 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
890 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
890 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
890 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
890 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
890 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
890 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
890 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
890 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
890 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
890 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
890 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
890 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 10.5
890 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 65.8
890 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
890 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
890 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 65.8
890 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (((Base Watts-WattNEW)×Hours×Days)/1,000) × WHF
890 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
890 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
890 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
890 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
890 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
890 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
890 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
890 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
890 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 10.5
890 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
890 | 2 | Baseline Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
890 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.45 | Assumed same hours of use as listed in Morgan for CFLs
890 | 2 | Efficient Case Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
962 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
962 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
962 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
962 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
962 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
962 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
962 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
962 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
962 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
962 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 10.5
962 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 65.8
962 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
962 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1085 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1085 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 65.8
1085 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1085 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1085 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1085 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1085 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1085 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1085 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 10.5
1085 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1085 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1085 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1085 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1085 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
962 | 2 | Baseline Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
962 | 2 | Efficient Case Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
962 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
962 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
962 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 8
962 | 3 | Baseline Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
962 | 3 | Efficient Case Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
962 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 3.1
962 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
962 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Lighting Evaluation Report_Final 5-21-15.pdf
962 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | .99
962 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | .948
962 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
962 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
962 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 9.9
962 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | .0176
962 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | .95
962 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 42.2
962 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1.1
1204 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 9.9
1204 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient Watts | 9.26
1204 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Lighting Evaluation Report_Final 5-21-15.pdf
1204 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base Watts | 41.34
1204 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | .95
1204 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1.1
1204 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1204 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | .0176
1204 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 3.1
1204 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | .948
1204 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | .99
1203 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 43
1203 | 1 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1203 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1203 | 1 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1203 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Lighting Evaluation Report_Final 5-21-15.pdf
1203 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 12
1203 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365.25
1203 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1203 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1203 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1203 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.2
1203 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1203 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | .98
1203 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 43
1203 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 9
1203 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1203 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1203 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 3.1
1203 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Lighting Evaluation Report_Final 5-21-15.pdf
1203 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1203 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1203 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 9.9
1202 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 43
1202 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1202 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1202 | 1 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1202 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.2
1202 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Lighting Evaluation Report_Final 5-21-15.pdf
1202 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365.25
1202 | 1 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1202 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 12
1202 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1202 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1202 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1202 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.2
1202 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1202 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 10.5
1202 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1202 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1202 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1202 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1202 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 43
1202 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | .917
1202 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Lighting Evaluation Report_Final 5-21-15.pdf
1227 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Lighting Evaluation Report_Final 5-21-15.pdf
1227 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1227 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365.25
1227 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1227 | 1 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1227 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 43
1227 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1227 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 12
1227 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.2
1227 | 1 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1227 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1227 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 3.1
1227 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1227 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Lighting Evaluation Report_Final 5-21-15.pdf
1227 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 9
1227 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1227 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 43
1227 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1227 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | .98
1227 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1227 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 9.9
1227 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1227 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1227 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | .97
1227 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1227 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 43
1227 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 3.15
1227 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1227 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 9.9
1227 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 9
1227 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1227 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | .7912
1020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 12
1020 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 60.7
1020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.2
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 12
1020 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 43
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1020 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 43
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.2
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 12
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1020 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1020 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
891 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
891 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
891 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
891 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
891 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
891 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
891 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
891 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 12
891 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
891 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
891 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
891 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 60.7
891 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
891 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
891 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
891 | 2 | Efficient Case Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
891 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 60.7
891 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
891 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
891 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
891 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
891 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
891 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
891 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.45 | Assumed same hours of use as listed in Morgan for CFLs
891 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 12
891 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
891 | 2 | Baseline Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
891 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (((Base Watts-WattNEW)×Hours×Days)/1,000) × WHF
891 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
891 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
963 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
963 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
963 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
963 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
963 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 60.7
963 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
963 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
963 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
963 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 12
963 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
963 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
963 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
963 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
963 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
963 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
963 | 2 | Efficient Case Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
963 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
963 | 2 | Baseline Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
963 | 3 | Efficient Case Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
963 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
963 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 73.5
963 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 8.3
963 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 9.9
963 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1.1
963 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Lighting Evaluation Report_Final 5-21-15.pdf
963 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
963 | 3 | Baseline Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
963 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | .948
963 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
963 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 3.1
963 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | .95
963 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | .0176
963 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | .99
1086 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 60.7
1086 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 12
1086 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1086 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1086 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1086 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1086 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1086 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1086 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1086 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1086 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1086 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1086 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1086 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 60.7
1021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 12
1021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1021 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 43
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 12
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 1.6
1021 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1021 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 1.6
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 12
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 51
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1021 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1021 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1022 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50.5
1022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 15
1023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1023 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50.5
1023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 15
1023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
892 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
892 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
892 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
892 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
892 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50.5
892 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
892 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
892 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
892 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
892 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 15
892 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
892 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
892 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
892 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
892 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
892 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
892 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
892 | 2 | Efficient Case Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
892 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
892 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
892 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.45 | Assumed same hours of use as listed in Morgan for CFLs
892 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
892 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
892 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
892 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
892 | 2 | Baseline Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
892 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (((Base Watts-WattNEW)×Hours×Days)/1,000) × WHF
892 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50.5
892 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
892 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 15
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.2
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 15
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365.25
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
964 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
964 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1087 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1087 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1087 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1087 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50.5
1087 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1087 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 15
1087 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1087 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1087 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1087 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1087 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1087 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1087 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1087 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 1.6
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1022 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1022 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 15
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 1.6
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1022 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 69
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1022 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 15
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 15
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.2
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1023 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1023 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 15
1023 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.2
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1023 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
964 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
964 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 9.9
964 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1.1
964 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | .948
964 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | .0176
964 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 11.6
964 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | .95
964 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 3.1
964 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 62
964 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
964 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
964 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | .99
964 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Lighting Evaluation Report_Final 5-21-15.pdf
1205 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient Watts | 11.1
1205 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | .99
1205 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 9.9
1205 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | .0176
1205 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 3.1
1205 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | .948
1205 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | .95
1205 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Lighting Evaluation Report_Final 5-21-15.pdf
1205 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1205 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1.1
1205 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base Watts | 53
1024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50.5
1024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1024 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
1025 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1025 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1025 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1025 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1025 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1025 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50.5
1025 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1025 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1025 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1025 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1025 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1025 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1025 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1025 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
893 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50.5
893 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
893 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
893 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
893 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
893 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
893 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
893 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
893 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
893 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
893 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
893 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
893 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
893 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
893 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50.5
893 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.45 | Assumed same hours of use as listed in Morgan for CFLs
893 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
893 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
893 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
893 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
893 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
893 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
893 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
893 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
893 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
893 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
893 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (((Base Watts-WattNEW)×Hours×Days)/1,000) × WHF
893 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
893 | 2 | Baseline Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
893 | 2 | Efficient Case Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
965 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
965 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50.5
965 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
965 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
965 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
965 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
965 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
965 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
965 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
965 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
965 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
965 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
965 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
965 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1088 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1088 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1088 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1088 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
1088 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1088 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1088 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1088 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50.5
1088 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1088 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1088 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1088 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1088 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1088 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1024 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 1.6
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1024 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 1.6
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 69
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1024 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1024 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.2
1025 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
1025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 50
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1025 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.2
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 18
1025 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
965 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
965 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 3.1
965 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 16
965 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | .948
965 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | .99
965 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 9.9
965 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
965 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 90
965 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
965 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1.1
965 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | .0176
965 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | .95
965 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Lighting Evaluation Report_Final 5-21-15.pdf
1206 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | .948
1206 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 9.9
1206 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | .95
1206 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | .0176
1206 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1206 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 3.1
1206 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base Watts | 72
1206 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1.1
1206 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | .99
1206 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient Watts | 16.2
1206 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Lighting Evaluation Report_Final 5-21-15.pdf
1231 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 39.7
1231 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 9.9
1231 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1231 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | .0176
1231 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 4.5
1231 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1.1
1231 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | .95
1231 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Lighting Evaluation Report_Final 5-21-15.pdf
1231 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 3.1
1231 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | .948
1231 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | .99
1026 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1026 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1026 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1026 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1026 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1026 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1026 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 40.5
1026 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 8
1026 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1026 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1026 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1026 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1026 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1026 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1026 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 8
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 1.6
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 30
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1026 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 1.6
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 30
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1026 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 8
1027 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1027 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1027 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 8
1027 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1027 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1027 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1027 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1027 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1027 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1027 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1027 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1027 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1027 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1027 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 40.5
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 30
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 8
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1027 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.2
1027 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | 0
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 30
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 8.76
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 2.2
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | 1
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1027 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 8
1027 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | 1
894 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 8
894 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
894 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
894 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
894 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
894 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
894 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
894 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 40.5
894 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
894 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
894 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
894 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
894 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
894 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
894 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
894 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (((Base Watts-WattNEW)×Hours×Days)/1,000) × WHF
894 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.45 | Assumed same hours of use as listed in Morgan for CFLs
894 | 2 | Efficient Case Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
894 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
894 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
894 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 0.99
894 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 40.5
894 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
894 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
894 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
894 | 2 | Baseline Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
894 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 8
894 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
894 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
894 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
966 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
966 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 40.5
966 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
966 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
966 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
966 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
966 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
966 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 8
966 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
966 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
966 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
966 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
966 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
966 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
966 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
966 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
966 | 2 | Baseline Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
966 | 2 | Efficient Case Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
966 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUres | 3.1
966 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 41.9
966 | 3 | Baseline Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
966 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Non-Res | 1.1
966 | 3 | Total Gross Incremental Annual Electric Savings_kWh | LKG | .0176
966 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy Res | .99
966 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
966 | 3 | Efficient Case Value | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
966 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | .948
966 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
966 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 6
966 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HOUnonres | 9.9
966 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
966 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Lighting Evaluation Report_Final 5-21-15.pdf
966 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %RES | .95
1089 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1089 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1089 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 8
1089 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 40.5
1089 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1089 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1089 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1089 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1089 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.7
1089 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1089 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1089 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1089 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1089 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
903 | 1 | Incremental Cost per Unit | Source Documentation
903 | 1 | Measure Life | Source Documentation
904 | 1 | Incremental Cost per Unit | Source Documentation
904 | 1 | Measure Life | Source Documentation
1033 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference in temperatures of the faucet water and the water main | 18.7 | 2009 Vermont TRM
1033 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1033 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days: number of days per year a faucet is used | 365 | Ameren Missouri’s Multifamily PY2 Report
1033 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant derived from 3,413/8.33 | 409.7 | Ameren Missouri’s Multifamily PY2 Report
1033 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of People in dwelling | 1.2 | PY2 evaluation tenant survey
1033 | 1 | Baseline Value | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1033 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1033 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1033 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.7 | Ameren Missouri’s Multifamily PY2 Report
1033 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of the water heater | variable
1033 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×FT×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri’s Multifamily PY2 Report
1033 | 1 | Total Gross Incremental Annual Electric Savings_kWh | FT: faucet time in minutes | 5 | 1997 North American Residential End Use Study Progress Report by American Water Works Association Research Foundation
1033 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of Unit: number of faucets in home | 1.9 | PY2 evaluation site visit
1033 | 1 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1033 | 2 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1033 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 1.79
1033 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1033 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1033 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 80
1033 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1033 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1033 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.1
1033 | 2 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | 0.98
1033 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
1033 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1033 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 1
1033 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
1033 | 2 | Baseline Value | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1033 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Low Income Evaluation Report_FINAL_6 17 15.pdf
1033 | 2 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 3.7
1033 | 2 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.68
1033 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 2.03
1033 | 3 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.686
1033 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ISR | 1
1033 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1033 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
1033 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Low Income Evaluation Report_FINAL_6 17 15.pdf
1033 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.07
1033 | 3 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1033 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
1033 | 3 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 3.7
1033 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1033 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1033 | 3 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | 0.98
1033 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1033 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 80
1033 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1033 | 3 | Baseline Value | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1033 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 1
1034 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×FT×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri’s Multifamily PY2 Report
1034 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference in temperatures of the faucet water and the water main | 45 | Ameren Missouri’s Multifamily PY2 Report
1034 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1034 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1034 | 1 | Total Gross Incremental Annual Electric Savings_kWh | FT: faucet time in minutes | 5 | 1997 North American Residential End Use Study Progress Report by American Water Works Association Research Foundation
1034 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1034 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1034 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of the water heater | variable
1034 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.7 | Ameren Missouri’s Multifamily PY2 Report
1034 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant derived from 3,413/8.33 | 409.7 | Ameren Missouri’s Multifamily PY2 Report
1034 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days: number of days per year a faucet is used | 365 | Ameren Missouri’s Multifamily PY2 Report
1034 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1034 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of People in dwelling | 1.2 | PY2 evaluation tenant survey
1034 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of Unit: number of faucets in home | 1.9 | PY2 evaluation site visit
1034 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1034 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1034 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.53
1034 | 2 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 3.7
1034 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1034 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 80
1034 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 1
1034 | 2 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.7 | Ameren Missouri’s Multifamily PY2 Report
1034 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×FT×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri’s Multifamily PY2 Report
1034 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
1034 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 3.04
1034 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1034 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1034 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1034 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
1034 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1034 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1034 | 2 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | .98
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Customer | 1
1034 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 3.7
1034 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1034 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 3.04
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 80
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×FT×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri’s Multifamily PY2 Report
1034 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 1
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ISR | 1
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.7 | Ameren Missouri’s Multifamily PY2 Report
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.53
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | .98
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | 1
1034 | 3 | Total Gross Incremental Annual Electric Savings_kWh | DF | 1
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 2.4
865 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 86
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 1
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
865 | 3 | Baseline Value | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413 | Assume faucet outlet temperature is 80°F according to 2009 Vermont TRM. Assume cold water inlet temperature for St. Louis, MO is 61.3°F according to http://www.gfxtechnology.com/WaterTemp.pdf
865 | 3 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.7
865 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ISR | 1
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | FT: faucet time in minutes | 3.7
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×FT×Days×delta GPM× (Tfaucet - Tin) x Cp x Den)/(3413×RE×Number of Faucets)
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | 0.98
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.07
865 | 3 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 1.6
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 3.04
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | DF | 1
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 1.6
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | .7
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Customer | 1
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | .98
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 86
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | ISR | 1
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | 1
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 1
1228 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.67
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 86
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Customer | .86
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ISR | .57
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | DF | .9
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | .4
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 2.4
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 1.6
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 4.3
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | .7
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 1
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1228 | 3 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | .98
865 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×FT×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri’s Multifamily PY2 Report
865 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
865 | 1 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
865 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference in temperatures of the faucet water and the water main | 18.7 | 2009 Vermont TRM
865 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
865 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of the water heater | variable
865 | 1 | Baseline Value | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
865 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
865 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of People in dwelling | 1.2 | PY2 evaluation tenant survey
865 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days: number of days per year a faucet is used | 365 | Ameren Missouri’s Multifamily PY2 Report
865 | 1 | Total Gross Incremental Annual Electric Savings_kWh | FT: faucet time in minutes | 5 | 1997 North American Residential End Use Study Progress Report by American Water Works Association Research Foundation
865 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of Unit: number of faucets in home | 1.9 | PY2 evaluation site visit
865 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.7 | Ameren Missouri’s Multifamily PY2 Report
865 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant derived from 3,413/8.33 | 409.7 | Ameren Missouri’s Multifamily PY2 Report
865 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
865 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
865 | 2 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
865 | 2 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.7
865 | 2 | Baseline Value | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
865 | 2 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | 0.98
865 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
865 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413 | Assume faucet outlet temperature is 80°F according to 2009 Vermont TRM. Assume cold water inlet temperature for St. Louis, MO is 61.3°F according to http://www.gfxtechnology.com/WaterTemp.pdf
865 | 2 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 3.7
865 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
865 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
865 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 2.4
865 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 1.9
865 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 1
865 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 80
865 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
865 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×FT×Days×delta GPM× (Tfaucet - Tin) x Cp x Den)/(3413×RE×Number of Faucets)
865 | 2 | Total Gross Incremental Annual Electric Savings_kWh | FT: faucet time in minutes | 3.7
865 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1164 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference in temperatures of the faucet water and the water main | 18.7 | 2007CCPVerificationFinalReport.pdf
1164 | 1 | Total Gross Incremental Annual Electric Savings_kWh | FT: faucet time in minutes | 5 | 1997 North American Residential End Use Study Progress Report by American Water Works Association Research Foundation
1164 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days: number of days per year a faucet is used | 365 | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
1164 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.7 | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
1164 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of Unit: number of faucets in home | 1.9 | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
1164 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×FT×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
1164 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant derived from 3,413/8.33 | 409.7 | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
1164 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of People in dwelling | 1.2 | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
1164 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of the water heater | variable
864 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of Unit: number of faucets in home | 1.9 | PY2 evaluation site visit
864 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days: number of days per year a faucet is used | 365 | Ameren Missouri’s Multifamily PY2 Report
864 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
864 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of the water heater | variable
864 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant derived from 3,413/8.33 | 409.7 | Ameren Missouri’s Multifamily PY2 Report
864 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference in temperatures of the faucet water and the water main | 45 | Ameren Missouri’s Multifamily PY2 Report
864 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×FT×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri’s Multifamily PY2 Report
864 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of People in dwelling | 1.2 | PY2 evaluation tenant survey
864 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
864 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
864 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.7 | Ameren Missouri’s Multifamily PY2 Report
864 | 1 | Total Gross Incremental Annual Electric Savings_kWh | FT: faucet time in minutes | 5 | 1997 North American Residential End Use Study Progress Report by American Water Works Association Research Foundation
864 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
864 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
897 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.7 | Ameren Missouri’s Multifamily PY2 Report
897 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of the water heater | variable
897 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of Unit: number of faucets in home | 1.9 | PY2 evaluation site visit
897 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
897 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
897 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
897 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days: number of days per year a faucet is used | 365 | Ameren Missouri’s Multifamily PY2 Report
897 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×FT×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri’s Multifamily PY2 Report
897 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference in temperatures of the faucet water and the water main | 45 | Ameren Missouri’s Multifamily PY2 Report
897 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
897 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant derived from 3,413/8.33 | 409.7 | Ameren Missouri’s Multifamily PY2 Report
897 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of People in dwelling | 1.2 | PY2 evaluation tenant survey
897 | 1 | Total Gross Incremental Annual Electric Savings_kWh | FT: faucet time in minutes | 5 | 1997 North American Residential End Use Study Progress Report by American Water Works Association Research Foundation
897 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
864 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×FT×Days×delta GPM× (Tfaucet - Tin) x Cp x Den)/(3413×RE×Number of Faucets)
864 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
864 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %Days | .51
864 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
864 | 2 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 3.7
864 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
864 | 2 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.7
864 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
864 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
864 | 2 | Total Gross Incremental Annual Electric Savings_kWh | FT: faucet time in minutes | 3.7
864 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
864 | 2 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | 0.98
864 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 3.04
864 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.53
864 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
864 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
864 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
864 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 80
864 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | 1
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×FT×Days×delta GPM× (Tfaucet - Tin) x Cp x Den)/(3413×RE×Number of Faucets)
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | 0.98
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | ISR | .52
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Customer | 1
864 | 4 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
864 | 4 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 3.04
864 | 4 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 1
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.7
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.67
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | FT: faucet time in minutes | 3.7
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 80
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | DF | 1
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 3.73
864 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
864 | 4 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 1
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | .7
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.07
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 93
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | .98
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Customer | 1
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 4.5
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 2.4
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | DF | 1
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | 1
1273 | 1 | Total Gross Incremental Annual Electric Savings_kWh | ISR | 1
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Customer | 1
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | DF | 1
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | ISR | 1
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 1
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | .98
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | .7
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 4.5
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 3.04
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 93
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.67
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
1274 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | 1
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | .98
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | ISR | .53
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 4.5
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | .7
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Customer | .86
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 93
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 1.2
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 1
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 4.3
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | DF | .75
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | .4
1274 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
867 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 1.2 | PY2 evaluation tenant survey
867 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM | variable
867 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference in temperatures of the shower water and the water main | 43.7
867 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant derived from 3,413/8.33 | 409.7
867 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of the water heater | variable
867 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
867 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×ST×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri’s Multifamily PY2 Report
867 | 1 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
867 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
867 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days: number of days per year a shower is taken | 365
867 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of Unit: number of showerheads | 1
867 | 1 | Total Gross Incremental Annual Electric Savings_kWh | ST: shower time in minutes | 8.2 | 1997 North American Residential End Use Study Progress Report by American Water Works Association Research Foundation
867 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1166 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference in temperatures of the shower water and the water main (degree farenheit) | 43.7 | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
1166 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×ST×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
1166 | 1 | Total Gross Incremental Annual Electric Savings_kWh | ST: shower time in minutes | 8.2 | 1997 North American Residential End Use Study Progress Report by American Water Works Association Research Foundation
1166 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of Unit: number of showerheads | 1
1166 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 1.2 | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
1166 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days: number of days per year a shower is taken | 365
1166 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM | 0.5 | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
1166 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of the water heater
1166 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant derived from 3,413/8.33 | 409.7
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tshower: the average water temperature at the showerhead (F) | 105
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of Showerheads: the number of showerheads installed per home. | 1.4
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 1.9
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
867 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 1.4
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 0.66
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 105
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×ST×Days× %Days x delta GPM× (Tshower - Tin) x Cp x Den)/(3413×RE×Number of Showerheads)
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 8.66
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | ST: shower time in minutes | 8.66
867 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.75
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | 0.98
867 | 2 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
867 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ST: shower time in minutes | 8.66
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of Showerheads: the number of showerheads installed per home. | 1.4
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 105
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | 1
867 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×ST×Days× %Days x delta GPM× (Tshower - Tin) x Cp x Den)/(3413×RE×Number of Showerheads)
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 1.4
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | 0.98
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Customer | 1
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 7.8
867 | 3 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
867 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ISR | 1
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | DF | 1
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.07
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tshower: the average water temperature at the showerhead (F) | 105
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.75
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 0.6
867 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
866 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant derived from 3,413/8.33 | 409.7
866 | 1 | Total Gross Incremental Annual Electric Savings_kWh | ST: shower time in minutes | 8.2 | 1997 North American Residential End Use Study Progress Report by American Water Works Association Research Foundation
866 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
866 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of the water heater
866 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of Unit: number of showerheads | 1
866 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference in temperatures of the shower water and the water main (degree farenheit)
866 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM | 0.75 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
866 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days: number of days per year a shower is taken | 365
866 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
866 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
866 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×ST×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri’s Multifamily PY2 Report
866 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 1.2 | PY2 evaluation tenant survey
866 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
898 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of Unit: number of showerheads | 1
898 | 1 | Total Gross Incremental Annual Electric Savings_kWh | ST: shower time in minutes | 8.2 | 1997 North American Residential End Use Study Progress Report by American Water Works Association Research Foundation
898 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference in temperatures of the shower water and the water main (degree farenheit)
898 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
898 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of the water heater
898 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
898 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant derived from 3,413/8.33 | 409.7
898 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 1.2 | PY2 evaluation tenant survey
898 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM | 0.75 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
898 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days: number of days per year a shower is taken | 365
898 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
898 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
898 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×ST×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri’s Multifamily PY2 Report
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | ST: shower time in minutes | 8.66
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | 0.98
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 0.66
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×ST×Days× %Days x delta GPM× (Tshower - Tin) x Cp x Den)/(3413×RE×Number of Showerheads)
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.75
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tshower: the average water temperature at the showerhead (F) | 105
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of Showerheads: the number of showerheads installed per home. | 2.05
866 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.53
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
866 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 105
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 2.05
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 8.66
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
866 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
866 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.671
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %Days | .66
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ST: shower time in minutes | 8.66
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tshower: the average water temperature at the showerhead (F) | 105
866 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×ST×Days× %Days x delta GPM× (Tshower - Tin) x Cp x Den)/(3413×RE×Number of Showerheads)
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 105
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of Showerheads: the number of showerheads installed per home. | 2.05
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 8.66
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | DF | 1
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 2.05
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ISR | .47
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Customer | 1
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | 0.98
866 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | 1
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
866 | 3 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | 0.75
866 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.67
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | .75
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | 1
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 7.8
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 2.05
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | .98
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | DF | 1
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | ISR | 1
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 105
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %Days | .6
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Customer | 1
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
1229 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ISR | .65
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | DF | 1
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %Days | .6
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Customer | .86
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 7.8
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 2.1
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | .4
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 105
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | .98
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 4.3
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | .85
1229 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1035 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of the water heater | variable
1035 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference in temperatures of the shower water and the water main | 43.7
1035 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1035 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×ST×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri’s Multifamily PY2 Report
1035 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of Unit: number of showerheads | 1
1035 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1035 | 1 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1035 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days: number of days per year a shower is taken | 365
1035 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant derived from 3,413/8.33 | 409.7
1035 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM | variable
1035 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1035 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 1.2 | PY2 evaluation tenant survey
1035 | 1 | Total Gross Incremental Annual Electric Savings_kWh | ST: shower time in minutes | 8.2 | 1997 North American Residential End Use Study Progress Report by American Water Works Association Research Foundation
1035 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1035 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tshower: the average water temperature at the showerhead (F) | 105
1035 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1035 | 2 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 8.66
1035 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
1035 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1035 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of Showerheads: the number of showerheads installed per home. | 1.18
1035 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 1.09
1035 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.1
1035 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 0.66
1035 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
1035 | 2 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1035 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 105
1035 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1035 | 2 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | 0.98
1035 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1035 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Low Income Evaluation Report_FINAL_6 17 15.pdf
1035 | 2 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | .49
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 1.1
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | .499
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 105
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | 0.98
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Low Income Evaluation Report_FINAL_6 17 15.pdf
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.07
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 0.6595
1035 | 3 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ISR | 1
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tshower: the average water temperature at the showerhead (F) | 105
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 8.66
1035 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of Showerheads: the number of showerheads installed per home. | 1.18
1035 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1035 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1036 | 1 | Total Gross Incremental Annual Electric Savings_kWh | ST: shower time in minutes | 8.2 | 1997 North American Residential End Use Study Progress Report by American Water Works Association Research Foundation
1036 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1036 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 1.2 | PY2 evaluation tenant survey
1036 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1036 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Number of Unit: number of showerheads | 1
1036 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of the water heater | variable
1036 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days: number of days per year a shower is taken | 365
1036 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×ST×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri’s Multifamily PY2 Report
1036 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1036 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference in temperatures of the shower water and the water main
1036 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1036 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant derived from 3,413/8.33 | 409.7
1036 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM | variable
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 1
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference in temperatures of the shower water and the water main
1036 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1036 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.53 | PY2 evaluation tenant survey
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | ST: shower time in minutes | 8.2 | 1997 North American Residential End Use Study Progress Report by American Water Works Association Research Foundation
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | .98
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | .75
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant derived from 3,413/8.33 | 409.7
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 105
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days: number of days per year a shower is taken | 365
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM | variable
1036 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 8.66
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 2.05
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Number of Unit: number of showerheads | 1
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of the water heater | variable
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
1036 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×ST×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri’s Multifamily PY2 Report
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | %Days | 1
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ST: shower time in minutes | 8.2 | 1997 North American Residential End Use Study Progress Report by American Water Works Association Research Foundation
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tin: average inlet water temperature (Fahrenheit) | 61.3
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | 1
1036 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Cp: the specific water heat (Btu/lb degrees F) | 1
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference in temperatures of the shower water and the water main
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of People per dwelling | 2.53 | PY2 evaluation tenant survey
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of faucets: number of faucets in home | 2.05
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM: difference in gallons per minute for the base aerator and the new aerator | .75
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | DF | 1
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | delta GPM | variable
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Customer | 1
1036 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(Number of People ×ST×Days×delta GPM×delta Temp)/(409.7×EF×Number of Units) | Ameren Missouri’s Multifamily PY2 Report
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EF: energy factor of the water heater | variable
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tfaucet: average water temperature out of the faucet (Fahrenheit) | 105
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Number of Unit: number of showerheads | 1
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor(Btu/kWh)tures of the faucet water and the water main | 3413
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Den: the water density (lb/gal) | 8.33
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant derived from 3,413/8.33 | 409.7
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1036 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days: number of days per year a shower is taken | 365
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | RE: the water heater’s recovery efficiency | .98
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | FT or ST | 8.66
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ISR | 1
1036 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
953 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
953 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
953 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 8 | Morgan Measure Libraries
953 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
953 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | 100
953 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
953 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
953 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
953 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
953 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | 35
953 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
953 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
953 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
953 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
967 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
967 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
967 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
967 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
967 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
967 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
967 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
967 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
967 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | N/A
967 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | N/A
967 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
967 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | N/A
967 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
967 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
967 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
967 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =Watt_est x HOU x Days x SF
967 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF
967 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
967 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF | 0.3
967 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
967 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | 2.91
967 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | LightSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
967 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt_est | 117.8
967 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1 | typical aspect ratio factor. ASHRAE heating factor applies to perimeter zone heat therefore it must be adjusted to account for lighting in core zones. The assumed aspect ratio for residential buildings is 100%.
967 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
967 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
967 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
967 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1090 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1090 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use (HOU) = average hours of use per day | N/A
1090 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Aspect Ratio (AR) | 1
1090 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient watts | N/A
1090 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HVAC Interactive Effects Equation | delta MMBTU =((delta kWh))/WHFe x 0.003413 x AR x HF/EF | Ameren Missouri’s PY 2 EMV reports
1090 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion rate from kWh to MMBTU | 0.003413
1090 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1090 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate (ISR) | 1
1090 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency Factor (EF) = average heating system efficiency
1090 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1090 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Factor (HF) = ASHRAE heating factor for lighting waste heat
1090 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1090 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Waste Heat Factor for Energy (WHFe) | 1
1090 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((Base Watts-Efficient Watts)× HOU × 365)/1000 x ISR x WHFe | Ameren Missouri’s PY 2 EMV reports
1090 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base watts | N/A
942 | 1 | Baseline Value | Source Documentation
942 | 1 | Efficient Case Value | Source Documentation
942 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
942 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
942 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - HVAC PY14 Evaluation Report_FINAL 6 16 15.pdf
942 | 2 | Measure Life | Source Documentation
942 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - HVAC PY14 Evaluation Report_FINAL 6 16 15.pdf
942 | 3 | Measure Life | Source Documentation
942 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
868 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
868 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
868 | 1 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
868 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1168 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heat Loss: heat loss of the baseline pipe per foot | 28 | PY 2 EMV results
1168 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =Heat Loss ×Length of Pipe | Ameren Missouri’s Multifamily PY2 Report
1168 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1168 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heat Loss: heat loss of the baseline pipe per foot | 28 | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
1168 | 1 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1168 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Length of Pipe | 1 | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
1168 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Length of Pipe | 1 | PY 2 EMV results
1168 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1168 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1168 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =Heat Loss ×Length of Pipe | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
868 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - RebateSavers PY13 Report_FINAL_27MAY2014.pdf
868 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
868 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Rexist | 1 | Cadmus 2013 RebateSavers Report
868 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Recovery Efficiency (RE) | .98 | Cadmus 2013 RebateSavers Report
868 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
868 | 2 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
868 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Energy Savings Algorithm | Savings = ((1/Rexist-1.Rnew)*L*C*delta T*8760)/RE/3413 | Cadmus 2013 RebateSavers Report
868 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Delta T | 58.9 | Cadmus 2013 RebateSavers Report
868 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Rnew | 4 | Cadmus 2013 RebateSavers Report
868 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Length (L) | 1 | Cadmus 2013 RebateSavers Report
868 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Circumference | 0.196 | Cadmus 2013 RabateSavers Report
868 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | 1
868 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
868 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Rexist | 1 | Cadmus 2013 RebateSavers Report
868 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Length (L) | 1 | Cadmus 2013 RebateSavers Report
868 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Rnew | 4 | Cadmus 2013 RebateSavers Report
868 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Recovery Efficiency (RE) | .98 | Cadmus 2013 RebateSavers Report
868 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
868 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Delta T | 58.9 | Cadmus 2013 RebateSavers Report
868 | 3 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
868 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Customer | 1
868 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ISR | 1
868 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - RebateSavers PY13 Report_FINAL_27MAY2014.pdf
868 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Energy Savings Algorithm | Savings = ((1/Rexist-1.Rnew)*L*C*delta T*8760)/RE/3413 | Cadmus 2013 RebateSavers Report
868 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Circumference | 0.196 | Cadmus 2013 RabateSavers Report
1037 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =Heat Loss ×Length of Pipe | Ameren Missouri’s Multifamily PY2 Report
1037 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heat Loss: heat loss of the baseline pipe per foot | 28 | PY 2 EMV results
1037 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1037 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1037 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1037 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Length of Pipe | 1 | PY 2 EMV results
1037 | 1 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1037 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Recovery Efficiency (RE) | 0.98
1037 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1037 | 2 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1037 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Circumference | 0.196
1037 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Rnew | 3.6
1037 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Length (L) | 1
1037 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Delta T | 58.9
1037 | 2 | Total Gross Incremental Annual Electric Savings_kWh | 3413: the conversion rate between BTUs and kWhs (BTU/kWh). | 3413
1037 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1037 | 2 | Total Gross Incremental Annual Electric Savings_kWh | 8760: the number of hours during which heat loss occurs throughout the year (hr/yr). | 8760
1037 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1037 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = ((1/R exist - 1/R new) * L * C * delta T * 8760) / RE * 3413
1037 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Rexist | 1
1037 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Rexist | 1
1037 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Circumference | 0.196
1037 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Recovery Efficiency (RE) | 0.98
1037 | 3 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1037 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = ((1/R exist - 1/R new) * L * C * delta T * 8760) / RE * 3413
1037 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Length (L) | 1
1037 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ISR | 1
1037 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1037 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1037 | 3 | Total Gross Incremental Annual Electric Savings_kWh | 8760: the number of hours during which heat loss occurs throughout the year (hr/yr). | 8760
1037 | 3 | Total Gross Incremental Annual Electric Savings_kWh | 3413: the conversion rate between BTUs and kWhs (BTU/kWh). | 3413
1037 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Customer | 1
1037 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Rnew | 3.6
1037 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1037 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | 1
1037 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Delta T | 59.4
1167 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1167 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1167 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heat Loss: heat loss of the baseline pipe per foot | 28 | PY 2 EMV results
1167 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =Heat Loss ×Length of Pipe | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
1167 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1167 | 1 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1167 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Length of Pipe | 1 | PY 2 EMV results
1167 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Length of Pipe | 1 | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
1167 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =Heat Loss ×Length of Pipe | Ameren Missouri’s Multifamily PY2 Report
1167 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heat Loss: heat loss of the baseline pipe per foot | 28 | Ameren Missouri – 2010 MFIQ Evaluation Report FINAL 04 APR2011.pdf
899 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
899 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
899 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
899 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heat Loss: heat loss of the baseline pipe per foot
899 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
899 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
899 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Length of Pipe | 10 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
899 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
899 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
899 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =Heat Loss ×Length of Pipe
899 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1167 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Rexist | 1 | Cadmust 2013 RebateSavers Report
1167 | 2 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1167 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Rnew | 4
1167 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1167 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Length (L) | 12 | Cadmus 2013 RebateSavers Report
1167 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Recovery Efficiency (RE) | 0.981 | Cadmus 2013 RebateSavers Report
1167 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Circumference | 0.196 | Cadmus 2013 RebateSavers Report
1167 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - RebateSavers PY13 Report_FINAL_27MAY2014.pdf
1167 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1167 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Delta T | 67.5 | Cadmus 2013 RebateSavers Report
1167 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((1/Rexist-1/Rnew)*L*C*delta T*8760)/RE/3413 | Cadmus 2013 RebateSavers Report
1167 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - RebateSavers PY13 Report_FINAL_27MAY2014.pdf
1167 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | 1
1167 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1167 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Rexist | 1 | Cadmust 2013 RebateSavers Report
1167 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Circumference | 0.196 | Cadmus 2013 RebateSavers Report
1167 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Customer | 1
1167 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Rnew | 4
1167 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Recovery Efficiency (RE) | 0.98 | Cadmus 2013 RebateSavers Report
1167 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Length (L) | .41 | Cadmus 2013 RebateSavers Report
1167 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Delta T | 67.5 | Cadmus 2013 RebateSavers Report
1167 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((1/Rexist-1/Rnew)*L*C*delta T*8760)/RE/3413 | Cadmus 2013 RebateSavers Report
1167 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1167 | 3 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1167 | 3 | Total Gross Incremental Annual Electric Savings_kWh | ISR | 1
1038 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1038 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1038 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Length of Pipe | 10 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1038 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =Heat Loss ×Length of Pipe | Ameren Missouri’s Multifamily PY2 Report
1038 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heat Loss: heat loss of the baseline pipe per foot |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1038 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1038 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1038 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Heat Loss: heat loss of the baseline pipe per foot |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1038 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Rexist | 1
1038 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =Heat Loss ×Length of Pipe | Ameren Missouri’s Multifamily PY2 Report
1038 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1038 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1038 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Rnew | 3.4
1038 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Circumference | .196
1038 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Recovery Efficiency (RE) | .98
1038 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Length of Pipe | 10 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1038 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Length (L) | 1
1038 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1038 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1038 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Delta T | 67.5
1272 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Customer | 1
1272 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | 1
1272 | 1 | Total Gross Incremental Annual Electric Savings_kWh | ISR | 1
1272 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Delta T | 67.5
1272 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Rnew | 4
1272 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Rexist | 1
1272 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Recovery Efficiency (RE) | .98
1272 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Circumference | .196
1272 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Length (L) | 1
1272 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Length (L) | 1
1272 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Customer | .86
1272 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Delta T | 67.5
1272 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Recovery Efficiency (RE) | .98
1272 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Circumference | .196
1272 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Rexist | 1
1272 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Rnew | 4
1272 | 2 | Total Gross Incremental Annual Electric Savings_kWh | ISR | .74
1272 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | .4
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kWhbase | (HP*LFBase*0.746)/n-PumpBase*Hrs/day*days/year | Morgan Measure Libraries
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | conversion factor (CF) | 0.746 | Morgan Measure Libraries
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hrs/day | 2.515 | Morgan Measure Libraries
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Load factor of efficient motor (LFEff)
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Annual Hours of Operation (AOH) | 918 | Morgan Measure Libraries
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Load factor of baseline motor (LFBase)
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kWhEff | (HP*LFEff*0.746)/n-PumpEff*Hrs/day*days/year | Morgan Measure Libraries
860 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hrs/day | 2.515 | Morgan Measure Libraries
860 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh = kWhbase - kWhEff | Morgan Measure Libraries
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Annual Hours of Operation (AOH) | 918 | Morgan Measure Libraries
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-PumpBase = Efficiency of baseline motor
860 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days/yr | 365 | Morgan Measure Libraries
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Horsepower of motors (HP)
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Horsepower of motors (HP)
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-PumpEff = Efficiency of high efficiency motor
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days/yr | 365 | Morgan Measure Libraries
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
860 | 1 | Total Gross Incremental Annual Electric Savings_kWh | conversion factor (CF) | 0.746 | Morgan Measure Libraries
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Assumed annual hours of two speed pump at high speed (AOHEff2) | 918 | Morgan Measure Libraries
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Pump horse power (HP1) | 0.12 delta
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Pump horse power (HP2) | 0.0 delta
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Assumed annual hours of two speed pump at low speed (AOHEff1) | 918 | Morgan Measure Libraries
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Load factor of two speed motor at slow speed (LFEff1) | 55% delta
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kWhEff | (HP*LFEff1*0.746)/n-PumpEff1*AOH1+(HP*LFEff2*0.746)/n-PumpEff2*AOH2 | Morgan Measure Libraries
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficiency of two speed motor at high speed (n-PumpEff2) | 13% delta
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kWhbase | (HP*LFBase*0.746)/n-PumpBase*AOH | Morgan Measure Libraries
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-PumpBase = Efficiency of baseline motor
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Effiency of two speed motor at slow speed (n-PumpEff1) | 5% delta
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Annual Hours of Operation (AOHBase) = Assumed annual operating hours of baseline pump
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Horsepower of motors (HP)
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh = kWhbase - kWhEff | Morgan Measure Libraries
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor (CF) | 0.746 | Morgan Measure Libraries
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Load factor of two speed motor at high speed (LFEff2) | 1% delta
859 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Horsepower of motors (HP)
859 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
859 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Load factor of baseline motor (LFBase)
859 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor (CF) | 0.746 | Morgan Measure Libraries
859 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Energy factor in high speed using variable speed pump (EFhs) | 2.4
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Annual Hours of Operation (AOHBase) = Assumed annual operating hours of baseline pump
859 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day in low speed using variable speed pump (RTls) | 9.8
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Energy factor using single speed pump (EFss) | 2.1 | Cadmus September 2014 Memo
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute in high speed using dual speed pump (GPMhigh) | 56.0 | Cadmus September 2014 Memo
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day in high speed using variable speed pump | 2
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day using single speed pump (RTss) | 11.4 | Cadmus September 2014 Memo
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute in low speed using dual speed pump (GPMlow) | 31.0 | Cadmus September 2014 Memo
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Energy Factor in high speed using dual speed pump (EFhigh) | 2.4 | Cadmus September 2014 Memo
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day in high speed using dual speed pump (RThigh) | 2.0 | Cadmus September 2014 Memo
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - Eff Products_PerUnit Savings New Measures_30Sept2014 (3).docx
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute using single speed pump (GPMss) | 64.4 | Cadmus September 2014 Memo
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Energy factor in low speed using dual speed pump (EFlow) | 5.4 | Cadmus September 2014 Memo
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | kWhbase | Days oper * RTss * GPMss * 60/EFss/1000 | Cadmus September 2014 Memo
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Energy Factor in low speed using variable speed pump EFls) | 5.4
859 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute in high speed using variable speed pump (GPMhs) | 56
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day in low speed using dual speed pump (RTlow) | 9.8 | Cadmus September 2014 Memo
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days/year of operation | 121.6 | Cadmus September 2014 Memo
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | kWhEff | Days oper * (RThigh *GPMhigh*60/ERhigh/1000 + RTlow *GPMlow*60/EFlow/1000) | Cadmus September 2014 Memo
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh = kWhbase - kWhEff | Cadmus September 2014 Memo
859 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute in low speed using variable speed pump | 31
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute in low speed using variable speed pump | 31
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Energy Factor in high speed using dual speed pump (EFhigh) | 2.4 | Cadmus September 2014 Memo
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day in low speed using dual speed pump (RTlow) | 9.8 | Cadmus September 2014 Memo
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Annual Hours of Operation (AOHBase) = Assumed annual operating hours of baseline pump
859 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | kWhbase | Days oper * RTss * GPMss * 60/EFss/1000 | Cadmus September 2014 Memo
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days/year of operation | 121.6 | Cadmus September 2014 Memo
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Energy factor using single speed pump (EFss) | 2.1 | Cadmus September 2014 Memo
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute in high speed using variable speed pump (GPMhs) | 56
859 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Energy Factor in low speed using variable speed pump EFls) | 5.4
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Energy factor in low speed using dual speed pump (EFlow) | 5.4 | Cadmus September 2014 Memo
859 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day in low speed using variable speed pump (RTls) | 9.8
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute in high speed using dual speed pump (GPMhigh) | 56.0 | Cadmus September 2014 Memo
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Energy factor in high speed using variable speed pump (EFhs) | 2.4
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute in low speed using dual speed pump (GPMlow) | 31.0 | Cadmus September 2014 Memo
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh = kWhbase - kWhEff | Cadmus September 2014 Memo
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | kWhEff | Days oper * (RThigh *GPMhigh*60/ERhigh/1000 + RTlow *GPMlow*60/EFlow/1000) | Cadmus September 2014 Memo
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day in high speed using dual speed pump (RThigh) | 2.0 | Cadmus September 2014 Memo
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - Eff Products_PerUnit Savings New Measures_30Sept2014 (3).docx
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day in high speed using variable speed pump | 2
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day using single speed pump (RTss) | 11.4 | Cadmus September 2014 Memo
859 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute using single speed pump (GPMss) | 64.66 | Cadmus September 2014 Memo
1005 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1005 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1005 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1005 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1005 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1005 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1005 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1005 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
950 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
950 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
950 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
950 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1075 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1075 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1075 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1075 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1006 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1006 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1006 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1006 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1006 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1006 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1006 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1006 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
951 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
951 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
951 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
951 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1076 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1076 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1076 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1076 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
991 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
991 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
991 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
991 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
991 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
991 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
991 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
991 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
936 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
936 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
936 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
936 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1064 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1064 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1064 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1064 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
992 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
992 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
992 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
992 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
992 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
992 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
992 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
992 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
937 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
937 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
937 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
937 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1065 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1065 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1065 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1065 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
995 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
995 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
995 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
995 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
995 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
995 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
995 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
995 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
995 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
995 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
995 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
995 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
995 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
995 | 4 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
995 | 4 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
995 | 4 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
940 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
940 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
940 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
940 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
940 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Meter Tons | 3.26
940 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HSPF Base | 6.3
940 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EER Pre | 8.72199
940 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
940 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
940 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
940 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLHH | 2009
940 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - HVAC PY14 Evaluation Report_FINAL 6 16 15.pdf
940 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Meter Cons | 2835.6
940 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EER Post | 10.64138
940 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tons | 3.16
940 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - HVAC PY14 Evaluation Report_FINAL 6 16 15.pdf
940 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EFLHH | 2009
940 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EER Post | 10.64138
940 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
940 | 3 | Total Gross Incremental Annual Electric Savings_kWh | EER Pre | 8.72199
940 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
940 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Tons | 3.16
940 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Meter Tons | 3.26
940 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Meter Cons | 2835.6
940 | 3 | Total Gross Incremental Annual Electric Savings_kWh | HSPF Base | 6.3
940 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
996 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
996 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
996 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
996 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
996 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
996 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
996 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
996 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
996 | 3 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
996 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
996 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
996 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1068 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1068 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1068 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1068 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
997 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
997 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
997 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
997 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
997 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
997 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
997 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
997 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
998 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
998 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
998 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
998 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
998 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
998 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
998 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
998 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh=(Base UEC-Efficienct UEC)x In-Situ factor | Ameren MO PY2 EMV Report
3 | 1 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base UEC (kWh) | 1891 | Ameren MO PY2 EMV Report
3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient UEC (kWh) | 0.8654 | Ameren MO PY2 EMV Report
3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
3 | 1 | Baseline Value | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | In-Situ Factor: factor considering appliances not plugged in year-round (also known as part-use) |  | Ameren MO PY2 EMV Report
3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
3 | 1 | Efficient Case Value | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Part Use Factor | 0.86
3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | ApplianceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
3 | 2 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh= Base UEC*Part Use Factor
3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
3 | 2 | Baseline Value | Source Documentation |  |  | ApplianceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
3 | 2 | Efficient Case Value | Source Documentation |  |  | Ameren Missouri - 2010 Refrigerator Recycling Evaluation Report-FINAL_01APR11.pdf
3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base UEC (kWh) | 1178.299787
3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | ApplianceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
4 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
4 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
4 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | ApplianceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
4 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | ApplianceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | BTU/hr | 10000
4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion (Constant) | 1000
4 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
4 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (BTU/hr * (1/EER Base)*EFLH Cool) / 1000
4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFLH Cool | 556
4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EERbase | 6.7
993 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
993 | 1 | Efficient Case Value | Source Documentation
993 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
993 | 1 | Baseline Value | Source Documentation
993 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
993 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
993 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
993 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
993 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
993 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
993 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
993 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
855 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
855 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
855 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
855 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
938 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
938 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
938 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
938 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
994 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
994 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
994 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
994 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
994 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
994 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
994 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
994 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1066 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1066 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
856 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
856 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
856 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
856 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
856 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
856 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
856 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
856 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
939 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
939 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
939 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
939 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
939 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
939 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
939 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
939 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CoolSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1067 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1067 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1031 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1031 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate | 100
1031 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1031 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Motion Sensing Adder (%) | 0
1031 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Entertainment Center saturation (%) | 64
1031 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Energy Savings Equation | kWh Saved = (KWHoffice*%installedoffice = KWHentertainment * %installedentertaintment)*ISR
1031 | 3 | Total Gross Incremental Annual Electric Savings_kWh | KWH saved home entertainment | 74.8
1031 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1031 | 3 | Total Gross Incremental Annual Electric Savings_kWh | KWH saved home office | 31
1031 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Home Office Saturation (%) | 36
1030 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((Base Idle Watts - Efficient Idle Watts) x Idle Hour per day x 365)/1000 | Morgan Measure Libraries
1030 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Idle Hours per day | 19.5
1030 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1030 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1030 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1030 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient idle watts = average energy used by system when in standby mode and computer or TV is turned off |  | Morgan Measure Libraries
1030 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1030 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base Idle Watts = average energy used by system when in standby mode and computer or TV is turned off |  | Morgan Measure Libraries
1030 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1030 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1030 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Entertainment Center saturation (%) | 89
1030 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1030 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Home Office Saturation (%) | 11
1030 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate | 100
1030 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1030 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1030 | 2 | Total Gross Incremental Annual Electric Savings_kWh | KWH saved home entertainment | 75
1030 | 2 | Total Gross Incremental Annual Electric Savings_kWh | KWH saved home office | 31
1030 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Motion Sensing Adder (%) | 0
1030 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1030 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1030 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1030 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Entertainment Center saturation (%) | 89
1030 | 3 | Total Gross Incremental Annual Electric Savings_kWh | KWH saved home entertainment | 74.8
1030 | 3 | Total Gross Incremental Annual Electric Savings_kWh | KWH saved home office | 31
1030 | 3 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate | 100
1030 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Home Office Saturation (%) | 11
1030 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Motion Sensing Adder (%) | 0
1031 | 2 | Total Gross Incremental Annual Electric Savings_kWh | KWH saved home office | 31
1031 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Home Office Saturation (%) | 48
1031 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Energy Savings Equation | kWh Saved = (KWHoffice*%installedoffice = KWHentertainment * %installedentertaintment)*ISR
1031 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1031 | 2 | Total Gross Incremental Annual Electric Savings_kWh | In Service Rate | 100
1031 | 2 | Total Gross Incremental Annual Electric Savings_kWh | KWH saved home entertainment | 75.1
1031 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Motion Sensing Adder (%) | 0
1031 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1031 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1031 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Entertainment Center saturation (%) | 52
1031 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1031 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Idle Hours per day | 19.5
1031 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1031 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1031 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1031 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base Idle Watts = average energy used by system when in standby mode and computer or TV is turned off |  | Morgan Measure Libraries
1031 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1031 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((Base Idle Watts - Efficient Idle Watts) x Idle Hour per day x 365)/1000 | Morgan Measure Libraries
1031 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient idle watts = average energy used by system when in standby mode and computer or TV is turned off |  | Morgan Measure Libraries
1031 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
862 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
862 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
862 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
862 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient idle watts = average energy used by system when in standby mode and computer or TV is turned off |  | Morgan Measure Libraries
862 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base Idle Watts = average energy used by system when in standby mode and computer or TV is turned off |  | Morgan Measure Libraries
862 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
862 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
862 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
862 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((Base Idle Watts - Efficient Idle Watts) x Idle Hour per day x 365)/1000 | Morgan Measure Libraries
862 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Idle Hours per day | 19.5
862 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
862 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
895 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient idle watts = average energy used by system when in standby mode and computer or TV is turned off |  | Morgan Measure Libraries
895 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
895 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((Base Idle Watts - Efficient Idle Watts) x Idle Hour per day x 365)/1000 | Morgan Measure Libraries
895 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
895 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
895 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base Idle Watts = average energy used by system when in standby mode and computer or TV is turned off |  | Morgan Measure Libraries
895 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Idle Hours per day | 19.5
895 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
895 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
895 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
895 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
895 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
895 | 2 | Efficient Case Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
895 | 2 | Baseline Value | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
895 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
861 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Average % of full load use (FL) | 0.65 | Morgan Measure Libraries
861 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base Control Factor (CF) | 1 | Morgan Measure Libraries
861 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Motor Efficiency | 0.84 | Morgan Measure Libraries
861 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient Control Factor (CF) | 0.39 | Morgan Measure Libraries
861 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours of Use per day (HOU) | 8 | Morgan Measure Libraries
861 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor | 0.746 | Morgan Measure Libraries
861 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Motor Horsepower (HP) | 1.5 | Morgan Measure Libraries
861 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
861 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((Base CF-Efficient CF)× Conversion Factor ×Motor HP × FL × HOU ×365)/(Motor Efficiency) | Morgan Measure Libraries
861 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
861 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365 | Morgan Measure Libraries
861 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute in low speed using variable speed pump | 30.6
861 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days/year of operation | 121.6
861 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day using single speed pump (RTss) | 11.4
861 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute using single speed pump (GPMss) | 64.4
861 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Energy Factor in low speed using variable speed pump EFls) | 7.3
861 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - Eff Products_PerUnit Savings New Measures_30Sept2014 (3).docx
861 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Energy Factor using single speed pump (EFss) | 2.1
861 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
861 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Energy factor in high speed using variable speed pump (EFhs) | 3.8
861 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day in low speed using variable speed pump (RTls) | 10.0
861 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day in high speed using variable speed pump | 2.0
861 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute in high speed using variable speed pump (GPMhs) | 50
861 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute using single speed pump (GPMss) | 64.4
861 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day in low speed using variable speed pump (RTls) | 10.0
861 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days/year of operation | 121.6
861 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
861 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Energy Factor in low speed using variable speed pump EFls) | 7.3
861 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Energy factor in high speed using variable speed pump (EFhs) | 3.8
861 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day in high speed using variable speed pump | 2.0
861 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Energy Factor using single speed pump (EFss) | 2.1
861 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute in low speed using variable speed pump | 30.6
861 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Gallons per minute in high speed using variable speed pump (GPMhs) | 50
861 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Runtime in hours/day using single speed pump (RTss) | 11.4
861 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - Eff Products_PerUnit Savings New Measures_30Sept2014 (3).docx
969 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
969 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
969 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
969 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
871 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HWT: temperature in Fahrenheit of hot water | 135 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
871 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CWT: temperature in Fahrenheit of cold water supply | 58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
871 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
871 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
871 | 1 | Total Gross Incremental Annual Electric Savings_kWh | constant | 8.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
871 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
871 | 1 | Total Gross Incremental Annual Electric Savings_kWh | GPD: hot water used in gallons per day
871 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
871 | 1 | Total Gross Incremental Annual Electric Savings_kWh | constant | 3413 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
871 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base EF: energy factor of water heater | 64.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
871 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
871 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((1/(Base EF)-1/(Efficent EF))×(HWT-CWT) × 8.3 × GPD ×365)/3413 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
871 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient EF: energy factor of water heater | 0.9 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
871 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Density | 8.33
871 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((1/(Base EF)-1/(Efficent EF))×(HWT-CWT) × Den × GPD ×365 x Cp x (1/3413)
871 | 2 | Total Gross Incremental Annual Electric Savings_kWh | conversion factor | 3413
871 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
871 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Base EF: energy factor of water heater | 0.9
871 | 2 | Total Gross Incremental Annual Electric Savings_kWh | CWT: temperature in Fahrenheit of cold water supply | 61.3 | according to standard DOE test procedure
871 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Efficient EF: energy factor of water heater | 0.95
871 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
871 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HWT: temperature in Fahrenheit of hot water | 135 | according to standard DOE test procedure
871 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
871 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
871 | 2 | Total Gross Incremental Annual Electric Savings_kWh | GPD: hot water used in gallons per day | 64
871 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | RebateSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
901 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((1/(Base EF)-1/(Efficent EF))×(HWT-CWT) × 8.3 × GPD ×365)/3413 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
901 | 1 | Total Gross Incremental Annual Electric Savings_kWh | constant | 3413 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
901 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient EF: energy factor of water heater | 0.9 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
901 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
901 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
901 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
901 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
901 | 1 | Total Gross Incremental Annual Electric Savings_kWh | GPD: hot water used in gallons per day
901 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HWT: temperature in Fahrenheit of hot water | 135 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
901 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
901 | 1 | Total Gross Incremental Annual Electric Savings_kWh | constant | 8.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
901 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CWT: temperature in Fahrenheit of cold water supply | 58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
901 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base EF: energy factor of water heater | 64.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1091 | 1 | Total Gross Incremental Annual Electric Savings_kWh | GPD: hot water used in gallons per day
1091 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh =((1/(Base EF)-1/(Efficent EF))×(HWT-CWT) × 8.3 × GPD ×365)/3413 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1091 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1091 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CWT: temperature in Fahrenheit of cold water supply | 58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1091 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efficient EF: energy factor of water heater | 0.9 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1091 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1091 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1091 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1091 | 1 | Total Gross Incremental Annual Electric Savings_kWh | constant | 8.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1091 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HWT: temperature in Fahrenheit of hot water | 135 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1091 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1091 | 1 | Total Gross Incremental Annual Electric Savings_kWh | constant | 3413 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1091 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Base EF: energy factor of water heater | 64.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1039 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor (Constant) | 3413 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1039 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1039 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta UA: difference between overall heat loss coefficient of the baseline water heater and the overall heat loss with the wrap installed | 0.14 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1039 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference between the temperature setpoint of the water heater and the ambient air temperature | 56.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1039 | 1 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1039 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Equation | delta kWh =(delta UA ×8760×delta Temp)/(3413*n-elec) | Ameren Missouri’s Multifamily PY2 Report
1039 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours per year | 8760 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1039 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1039 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-elec: thermal efficiency coefficient | 97% | Pennsylvania TRM 2012
1039 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1039 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1039 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Equation | delta kWh = (Ubase - (1/(1/Ubase + Rwrap))) * Awrap * (Ttank - Tamb) * (8760/3413)
1039 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Rwrap: the installed water heater blanket’s R?value (hr? ft2? °F /BTU). | 11 | Morgan was appended to include information from Cadmus
1039 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Tamb: the temperature of ambient air surrounding the water heater (°F). | 67.5 | Morgan was appended to include information from Cadmus
1039 | 2 | Measure Life | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
1039 | 2 | Total Gross Incremental Annual Electric Savings_kWh | 3413: the conversion rate between BTUs and kWh (BTU/kWh). | 3413 | Morgan was appended to include information from Cadmus
1039 | 2 | Total Gross Incremental Annual Electric Savings_kWh | 8760: the number of hours during which heat loss occurs throughout the year (hr/yr). | 8760
1039 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Ubase: the water heater’s overall heat transfer coefficient before water heater blanket installation (BTU/hr?ft2? °F). | 0.03 | Morgan was appended to include information from Cadmus
1039 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | CommunitySavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1039 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Ttank: the tank thermostat setpoint temperature (°F). | 126.4
1039 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Awrap: the water heater’s surface area, excluding its base (ft2). | 23.82
1039 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Ameren Missouri - 2010 MFIQ Evaluation Report_FINAL_04APR2011.pdf
870 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
870 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-elec: thermal efficiency coefficient | 97% | Pennsylvania TRM 2012
870 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
870 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor (Constant) | 3413 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
870 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
870 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
870 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta UA: difference between overall heat loss coefficient of the baseline water heater and the overall heat loss with the wrap installed | 1.24 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
870 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference between the temperature setpoint of the water heater and the ambient air temperature | 56.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
870 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours per year | 8760 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
870 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Equation | delta kWh =(delta UA ×8760×delta Temp)/(3413*n-elec) | Ameren Missouri’s Multifamily PY2 Report
900 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
900 | 1 | Total Gross Incremental Annual Electric Savings_kWh | n-elec: thermal efficiency coefficient | 97% | Pennsylvania TRM 2012
900 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Equation | delta kWh =(delta UA ×8760×delta Temp)/(3413*n-elec) | Ameren Missouri’s Multifamily PY2 Report
900 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
900 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
900 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta UA: difference between overall heat loss coefficient of the baseline water heater and the overall heat loss with the wrap installed | 1.24 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
900 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
900 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours per year | 8760 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
900 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor (Constant) | 3413 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
900 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Temp: difference between the temperature setpoint of the water heater and the ambient air temperature | 56.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1032 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1032 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1032 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1032 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1215 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
863 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
863 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
863 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
863 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
863 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
863 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
863 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
863 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
896 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
896 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
896 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
896 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
896 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Conversion Factor (Btu/therm) | 100067
896 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
896 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
896 | 2 | Total Gross Incremental Annual Electric Savings_kWh | HWdishwasher (hot water used per cycle, in gallons) | 4.36
896 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Cycles (# of dishwasher cycles per year) | 215
896 | 2 | Gross Incremental Annual Gas Savings_MMBTU | EFgas | 0.521649
896 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh = [(HW dishwasher * Cycles * 8.3 * (T hot-base - T hot-new)) / EF dishwasher * 3413] * % Homes * % Boster Heater
896 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Density of water (lb/gal) | 8.3
896 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Homes | 0.84
896 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
896 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Booster Heater | 0.544
896 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Thot, new | 120
896 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Thot, base | 135
896 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Thot, new | 120
896 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Thot, base | 135
896 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Conversion Factor (days/year) | 365
896 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Density of water (lb/gal) | 8.3
896 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Conversion Factor (Btu/kWh) | 3413
896 | 2 | Gross Incremental Annual Gas Savings_MMBTU | HWday (hot water used per day, in gallons) | 7.32
896 | 2 | Total Gross Incremental Annual Electric Savings_kWh | EFdishwasher | 1
896 | 2 | Gross Incremental Annual Gas Savings_MMBTU | Savings Algorithm | delta therms = (HW,day * 365 * 8.3 * (T hot-base - T hot-new)) / Efgas * 100067
1212 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Document |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
970 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
970 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
970 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
970 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
970 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
970 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
970 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
970 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
971 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
971 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
971 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
971 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
882 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
882 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
882 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings per Square Foot | 4.413
882 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Home Energy Analysis Evaluation Report_FINAL_5 15 15.pdf
882 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Square Feet of Windows Replaced | 1
882 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
882 | 4 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
882 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ameren Missouri - PY14 Home Energy Analysis Evaluation Report_FINAL_5 15 15.pdf
882 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Square Feet of Windows Replaced | 1
882 | 4 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
882 | 4 | Total Gross Incremental Annual Electric Savings_kWh | Savings per Square Foot | 2.52
882 | 4 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
882 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
882 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
882 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
882 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1211 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh= Square Feet of Windows Replaced*Savings per Square Foot
1211 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PerformanceSavers - PY2013 Dashboard_FINAL_27MAY2014.xlsx
1211 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Square Feet of Windows Replaced | 1
1211 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings per Square Foot | 2.525
1045 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1045 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1045 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1045 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1045 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1045 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1045 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
726 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERbase: Efficiency rating of the baseline unit | 9.5 | ASHRAE 90.1-2004
726 | 1 | Baseline Value | Source Documentation |  |  | ashrae.90.1.2004.pdf
726 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
726 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
726 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (BtuH/1000) X (1/EERb-1/EERq) X EFLH | AmerenUE Business TRM 2008
726 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Note
726 | 1 | Total Gross Average Annual Demand Reduction_kW | CF = Coincidence Factor
726 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
726 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERq (Efficient): Efficiency rating of the High Efficiency unit | 11 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
726 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH (Full load hours) | 691
726 | 1 | Total Gross Incremental Annual Electric Savings_kWh | BtuH: Cooling capacity in Btu/Hour | 12000
726-1 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
726-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | BtuH: Cooling capacity in Btu/Hour | 12000
726-1 | 1 | Baseline Value | Source Documentation |  |  | ashrae.90.1.2004.pdf
726-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERbase: Efficiency rating of the baseline unit. | 9.5 | ASHRAE 90.1-2004
726-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLHcool | 362
726-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (BtuH/1000) X (1/EERb-1/EERq) X EFLH | AmerenUE Business TRM 2008
726-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERbase: Efficiency rating of the baseline unit | 9.5
726-1 | 1 | Total Gross Average Annual Demand Reduction_kW | CF = Coincidence Factor
726-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Note
726-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH (Full load hours) | 362
726-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERq: Efficiency rating of the High Efficiency unit | 11 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
726-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
726-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
726-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERq (Efficient): Efficiency rating of the High Efficiency unit | 11
727 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
727 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERbase: Efficiency rating of the baseline unit | 9 | ASHRAE 90.1-2004
727 | 1 | Total Gross Average Annual Demand Reduction_kW | CF = Coincidence Factor
727 | 1 | Baseline Value | Source Documentation |  |  | ashrae.90.1.2004.pdf
727 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
727 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
727 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERq (Efficient): Efficiency rating of the High Efficiency unit | 10 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
727 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Note
727 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (BtuH/1000) X (1/EERb-1/EERq) X EFLH | AmerenUE Business TRM 2008
727 | 1 | Total Gross Incremental Annual Electric Savings_kWh | BtuH: Cooling capacity in Btu/Hour | 12000
727 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH (Full load hours) | 691
728 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
728 | 1 | Total Gross Average Annual Demand Reduction_kW | CF = Coincidence Factor
728 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Note
728 | 1 | Total Gross Incremental Annual Electric Savings_kWh | BtuH: Cooling capacity in Btu/Hour | 12000
728 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
728 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (BtuH/1000) X (1/EERb-1/EERq) X EFLH | AmerenUE Business TRM 2008
728 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERq (Efficient): Efficiency rating of the High Efficiency unit | 14 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
728 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
728 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERbase: Efficiency rating of the baseline unit | 13 | National Appliance Energy Conservation Act (NAECA)
728 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH (Full load hours) | 989
728 | 1 | Baseline Value | Source Documentation |  |  | STATUTE-101-Pg103.pdf
691 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
691 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
691 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
691 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
692 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
692 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
692 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
692 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
674 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
674 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
674 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
674 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1169 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Commercial Custom Project Analysis Methodology Protocols.docx
1169 | 1 | Measure Life | Source Documentation |  |  | Commercial Custom Project Analysis Methodology Protocols.docx
1169 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Commercial Custom Project Analysis Methodology Protocols.docx
1169 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Commercial Custom Project Analysis Methodology Protocols.docx
693 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
693 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
693 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
693 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
679 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
679 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Watts: Base watts - Efficient watts | 48.2 | ENERGY STAR savings calculator
679 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
679 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (InternalVolume*(delta Watts/Volume)*(Hours/Year))/1000 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
679 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Volume | 20 | ENERGY STAR savings calculator
679 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours: Operating Hours per day | 15 | ENERGY STAR savings calculator
679 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
679 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
679 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
679 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Hours: Operating Hours per day | 15 | ENERGY STAR savings calculator
679 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
679 | 2 | Total Gross Incremental Annual Electric Savings_kWh | delta Watts: Base watts - Efficient watts | 48.2 | ENERGY STAR savings calculator
679 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Volume | 20 | ENERGY STAR savings calculator
679 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
679 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (InternalVolume*(delta Watts/Volume)*(Hours/Year))/1000 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
679 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
679 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
679 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
679 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
679 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
679 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (InternalVolume*(delta Watts/Volume)*(Hours/Year))/1000 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
679 | 3 | Total Gross Incremental Annual Electric Savings_kWh | delta Watts: Base watts - Efficient watts | 48.2 | ENERGY STAR savings calculator
679 | 3 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
679 | 3 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
679 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Volume | 20 | ENERGY STAR savings calculator
679 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Hours: Operating Hours per day | 15 | ENERGY STAR savings calculator
679 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1094 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours: Operating Hours per day | 15 | ENERGY STAR savings calculator
1094 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (InternalVolume*(delta Watts/Volume)*(Hours/Year))/1000 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1094 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Watts: Base watts - Efficient watts | 40.83 | ENERGY STAR savings calculator
1094 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Volume | 8 | ENERGY STAR savings calculator
1094 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1094 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1094 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1094 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1094 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1093 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
1093 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1093 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (InternalVolume*(delta Watts/Volume)*(Hours/Year))/1000 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
1093 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1093 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Volume | 12 | ENERGY STAR savings calculator
1093 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours: Operating Hours per day | 15 | ENERGY STAR savings calculator
1093 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1093 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Watts: Base watts - Efficient watts | 43.11 | ENERGY STAR savings calculator
1093 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Preheat energy (kWh/day) | 1.5
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | PTMM: average amount of time per day steamer is operated in manual (constant steam) mode. Expressed as percentage per day.
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Idle Energy - ES | 15916
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Idle Energy - Conventional | 41321
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | PC: production capacity (lbs/hr)
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Cooking Energy - Conventional | 11407
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | LbFood: Pounds of food cooked per day | 100
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efood: Energy to food | 0.0308
675 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IdleRate: Idle Energy Rate (kW) or (BTU/hr)
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = LBFood * (Efood/delta Efficiency)+ (1-PTMM)*delta IdleRate * (OpHrs - (LBFood/delta PC)-(TpreHT/60)) + EpreHT * Days | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
675 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
675 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Efficiency: Heavy Load Cooking Energy Efficiency % | 0.24
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Cooking Energy - ES | 6160
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Preheat time (minutes per day) | 15
675 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OpHrs: Operating Hours per day | 12
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Cooking Energy - ES | 6160
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OpHrs: Operating Hours per day | 12
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Preheat time (minutes per day) | 15
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IdleRate: Idle Energy Rate (kW) or (BTU/hr)
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Idle Energy - Conventional | 54337
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | PC: production capacity (lbs/hr)
676 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efood: Energy to food | 0.0308
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | LbFood: Pounds of food cooked per day | 128
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Preheat energy (kWh/day) | 1.5
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Cooking Energy - Conventional | 11407
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Idle Energy - ES | 26271
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | PTMM: average amount of time per day steamer is operated in manual (constant steam) mode. Expressed as percentage per day.
676 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = LBFood * (Efood/delta Efficiency)+ (1-PTMM)*delta IdleRate * (OpHrs - (LBFood/delta PC)-(TpreHT/60)) + EpreHT * Days | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
676 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Efficiency: Heavy Load Cooking Energy Efficiency % | 0.24
676 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Preheat energy (kWh/day) | 1.5
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Efficiency: Heavy Load Cooking Energy Efficiency % | 0.24
677 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Idle Energy - ES | 36499
677 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Cooking Energy - ES | 6160
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Preheat time (minutes per day) | 15
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OpHrs: Operating Hours per day | 12
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Idle Energy - Conventional | 67249
677 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efood: Energy to food | 0.0308
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | LbFood: Pounds of food cooked per day | 160
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Cooking Energy - Conventional | 11407
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | PC: production capacity (lbs/hr)
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | PTMM: average amount of time per day steamer is operated in manual (constant steam) mode. Expressed as percentage per day.
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = LBFood * (Efood/delta Efficiency)+ (1-PTMM)*delta IdleRate * (OpHrs - (LBFood/delta PC)-(TpreHT/60)) + EpreHT * Days | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
677 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IdleRate: Idle Energy Rate (kW) or (BTU/hr)
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Preheat time (minutes per day) | 15
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | delta Efficiency: Heavy Load Cooking Energy Efficiency % | 0.24
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OpHrs: Operating Hours per day | 12
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days per Year | 365
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Idle Energy - Conventional | 80110
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Cooking Energy - Conventional | 11407
678 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
678 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | LbFood: Pounds of food cooked per day | 192
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | PTMM: average amount of time per day steamer is operated in manual (constant steam) mode. Expressed as percentage per day.
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Efood: Energy to food | 0.0308
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Preheat energy (kWh/day) | 1.5
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IdleRate: Idle Energy Rate (kW) or (BTU/hr)
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | PC: production capacity (lbs/hr)
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = LBFood * (Efood/delta Efficiency)+ (1-PTMM)*delta IdleRate * (OpHrs - (LBFood/delta PC)-(TpreHT/60)) + EpreHT * Days | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Cooking Energy - ES | 6160
678 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Daily Idle Energy - ES | 43797
678 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
686 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
686 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERbase: Efficiency rating of the baseline unit | 13.4
686 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (BtuH/1000) X (1/EERb-1/EERq) X EFLH | AmerenUE Business TRM 2008
686 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERq (Efficient): Efficiency rating of the High Efficiency unit | 17
686 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
686 | 1 | Total Gross Incremental Annual Electric Savings_kWh | BtuH: Cooling capacity in Btu/Hour | 12000
686 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH (Full load hours) | 1266
686 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
686 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
687 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERbase: Efficiency rating of the baseline unit | 13.4
687 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
687 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
687 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (BtuH/1000) X (1/EERb-1/EERq) X EFLH | AmerenUE Business TRM 2008
687 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH (Full load hours) | 1157
687 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
687 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERq (Efficient): Efficiency rating of the High Efficiency unit | 19
687 | 1 | Total Gross Incremental Annual Electric Savings_kWh | BtuH: Cooling capacity in Btu/Hour | 12000
687 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
695 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Note
695 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Cooling Design Temp (degrees F) | 91 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
695 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Room Setpoint Temp (degrees F) | 71 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
695 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HCF: heating correction factor | 0.75 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
695 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HDD: annual heating degree days | 5329 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
695 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
695 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
695 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CDD: annual cooling degree days | 1295 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
695 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OPC: oversized percentage cooling | 0.15 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
695 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
695 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Note |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
695 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh=[(BTU*(1-OPC))/(Cooling design temp –room setpoint temp)*CDD*24*CCF]/12000*(12/9.7)+ [(BTU*(1-OPH))/(room setpoint temp -heating design temp)*HDD*24*HCF*ESF | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
695 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OPH: oversized percentage heating | 0.15 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
695 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Heating Design Temp (degrees F) | 7 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
695 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CCF: cooling correction factor | 1 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
695 | 1 | Total Gross Incremental Annual Electric Savings_kWh | BTU: BTU per ton | 2.91
695 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
695 | 1 | Total Gross Incremental Annual Electric Savings_kWh | ESF: energy savings factor | 0.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
683 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Note
683 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (BtuH/1000) X (1/EERb-1/EERq) X EFLH | AmerenUE Business TRM 2008
683 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
683 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CF (Coincidence Factor)
683 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
683 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERq (Efficient): Efficiency rating of the High Efficiency unit | 10 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
683 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
683 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | AmerenUE Business TRM 2008.xlsx
683 | 1 | Total Gross Incremental Annual Electric Savings_kWh | BtuH: Cooling capacity in Btu/Hour | 12000
683 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERbase: Efficiency rating of the baseline unit | 9.1 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
683 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH (Full load hours) | 1205
684 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLH (Full load hours) | 1070
684 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
684 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERbase: Efficiency rating of the baseline unit | 8.8 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
684 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
684 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CF (Coincidence Factor)
684 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Note
684 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EERq (Efficient): Efficiency rating of the High Efficiency unit | 10 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
684 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (BtuH/1000) X (1/EERb-1/EERq) X EFLH | AmerenUE Business TRM 2008
684 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | AmerenUE Business TRM 2008.xlsx
684 | 1 | Total Gross Incremental Annual Electric Savings_kWh | BtuH: Cooling capacity in Btu/Hour | 12000
684 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
685 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBtu/hcool: capacity of the cooling equipment in kBtu per hour
685 | 1 | Total Gross Average Annual Demand Reduction_kW | kBtu/h
685 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBtu/h | 12
685 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Annual kWh Savingsheat | delta kWhheat = (kBtu/h) * [(1/HSPFbase) - (1/HSPFee)] * EFLHheat | Ohio TRM 2009
685 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
685 | 1 | Total Gross Average Annual Demand Reduction_kW | EERee: Energy Efficiency Ratio of the energy efficient equipment.
685 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERbase: Seasonal Energy Efficiency Ratio of the baseline equipment | 13 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
685 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLHheat: heating mode equivalent full load hours | 825
685 | 1 | Total Gross Average Annual Demand Reduction_kW | CF: Coincident Factor
685 | 1 | Total Gross Incremental Annual Electric Savings_kWh | EFLHcool: cooling mode equivalent full load hours | 1070
685 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HSPFbase (Heating Seasonal Performance Factor of baseline equipment ) | 7.7 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
685 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SEERee: Seasonal Energy Efficiency Ratio of the energy efficient equipment. | 14 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
685 | 1 | Total Gross Incremental Annual Electric Savings_kWh | kBtu/hheat: cooling mode equivalent full load hours
685 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = Annual kWh Savingscool + Annual kWh Savingsheat | Ohio TRM 2009
685 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Btu per Wh (Constant) | 3412 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
685 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
685 | 1 | Total Gross Average Annual Demand Reduction_kW | EERbase: Energy Efficiency Ratio of the baseline equipment
685 | 1 | Total Gross Average Annual Demand Reduction_kW | Summer Coincident Peak kW Savings Equation | Summer Coincident Peak kW Savings = (kBtu/h) * [(1/EERbase) - (1/EERee)] *CF | Ohio TRM 2009
685 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Ohio TRM_Appendix_E_2011.pdf
685 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Note | (1 ton of cooling capacity equals 12 kBtu/h). =Actual installed
685 | 1 | Total Gross Incremental Annual Electric Savings_kWh | HSPFee (Heating Seasonal Performance Factor of efficient equipment) | 7.97 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
685 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Annual kWh Savingscool | delta kWhcool = (kBtu/h) * [(1/SEERbase) - (1/SEERee)] * EFLHcool | Ohio TRM 2009
685 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
1184 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Width | 1 | Width of the opening that the night covers protect (ft)
1184 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours | 2190 | Annual hours that the night covers are in use
1184 | 1 | Total Gross Average Annual Demand Reduction_kW | Width | Width of the opening that the night covers protect (ft)
1184 | 1 | Total Gross Average Annual Demand Reduction_kW | Equation E (Energy): Gross incremental annual demand savings (kW/yr) | delta kWh = (Width)(Save)
1184 | 1 | Total Gross Average Annual Demand Reduction_kW | Save | Savings factor based on the temperature of the cooler case (kW/ft)
1184 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (Width)(Save)(Hours)
1184 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Save | .02 | Savings factor based on the temperature of the cooler case (kW/ft)
697 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
697 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
697 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
697 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
681 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hours: Reduction of Hours block heater is used | 8 | Focus on Energy Evaluation Business Programs: Deemed Savings Manual v1.0 March 22, 2010
681 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Days: Number of operating days per year | 90 | Focus on Energy Evaluation Business Programs: Deemed Savings Manual v1.0 March 22, 2010
681 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | bpdeemedsavingsmanuav10_evaluationreport.pdf
681 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation
681 | 1 | Total Gross Incremental Annual Electric Savings_kWh | P=Power of engine block heater | 1000 | Focus on Energy Evaluation Business Programs: Deemed Savings Manual v1.0 March 22, 2010
681 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = (P*hours*days*UF)/1000 | Focus on Energy Evaluation Business Programs: Deemed Savings Manual v1.0 March 22, 2010
681 | 1 | Baseline Value | Source Documentation |  |  | bpdeemedsavingsmanuav10_evaluationreport.pdf
681 | 1 | Total Gross Incremental Annual Electric Savings_kWh | UF=Usage Factor | 0.8 | Focus on Energy Evaluation Business Programs: Deemed Savings Manual v1.0 March 22, 2010
673 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
673 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Equation E (Energy): Gross incremental annual electric savings (kWh/yr) | delta kWh = ?[(PPexist - PPret)*(CFM)*(Hr)]
673 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
673 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Ppexist: Package power of existing air compressor
673 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
673 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
673 | 1 | Total Gross Incremental Annual Electric Savings_kWh | CFM (Air use)
673 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Hr: Hours of use
673 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Ppret: Package power of retrofitted air compressor
671 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
671 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
671 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
671 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2732 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2732 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2732 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2732 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2732 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.3 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2732 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2732 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2732 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2732 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2733 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2733 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2733 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.36 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2733 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2733 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2733 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2733 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2733 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2733 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
705 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
705 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
705 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
705 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
705 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.39 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
705 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
705 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
705 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
705 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
705 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
705 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
705 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
705 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.39 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
705 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
705 | 2 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
705 | 2 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
705 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
705 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2734 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2734 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.41 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2734 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2734 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2734 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2734 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2734 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2734 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2734 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2735 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2735 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.48 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2735 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2735 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2735 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2735 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2735 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2735 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2735 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2736 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2736 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2736 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2736 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2736 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2736 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2736 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.34 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2736 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2736 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2737 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.4 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2737 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2737 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2737 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2737 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2737 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2737 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2737 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2737 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
706 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
706 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
706 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
706 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
706 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
706 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
706 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
706 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.43 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
706 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
706 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
706 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
706 | 2 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
706 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
706 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
706 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.43 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
706 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
706 | 2 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
706 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2738 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2738 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2738 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2738 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2738 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2738 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2738 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2738 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2738 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.46 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2739 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.54 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2739 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2739 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2739 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2739 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2739 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2739 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2739 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2739 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2740 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2740 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2740 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.63 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2740 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2740 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.38 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2740 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2740 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2740 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2740 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
707 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
707 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
707 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
707 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
707 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
707 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.45 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
707 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
707 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
707 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
707 | 2 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
707 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
707 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
707 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
707 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
707 | 2 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
707 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.63 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
707 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.45 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
707 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2741 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2741 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2741 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2741 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.48 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2741 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2741 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2741 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.63 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2741 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2741 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2742 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2742 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2742 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.63 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2742 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2742 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2742 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2742 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2742 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2742 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2721 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2721 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2721 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2721 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2721 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2721 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.46 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2721 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2721 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2721 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.28 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2722 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.33 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2722 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2722 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2722 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.46 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2722 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2722 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2722 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2722 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2722 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
708 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.55 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
708 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
708 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
708 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
708 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
708 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
708 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
708 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
708 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.35 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
708 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
708 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.46 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
708 | 2 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
708 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.35 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
708 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
708 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
708 | 2 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
708 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
708 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2723 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.46 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2723 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2723 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2723 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2723 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.37 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2723 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2723 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2723 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2723 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2724 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2724 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2724 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.44 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2724 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.46 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2724 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2724 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2724 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2724 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2724 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2725 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2725 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2725 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2725 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.31 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2725 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2725 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2725 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.52 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2725 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2725 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2726 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2726 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2726 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.52 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2726 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2726 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2726 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2726 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.37 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2726 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2726 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2727 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2727 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.39 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2727 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2727 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2727 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2727 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2727 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2727 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2727 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.52 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2728 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.52 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2728 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2728 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2728 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2728 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2728 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2728 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.42 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2728 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2728 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
709 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
709 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
709 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
709 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.55 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
709 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
709 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.49 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
709 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
709 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
709 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
709 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
709 | 2 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
709 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
709 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.52 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
709 | 2 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
709 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
709 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
709 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.49 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
709 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2729 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2729 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2729 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2729 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2729 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.35 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2729 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2729 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2729 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2729 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
710 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.41 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
710 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
710 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
710 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
710 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
710 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.55 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
710 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
710 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
710 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
710 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.41 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
710 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
710 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
710 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
710 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
710 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
710 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
710 | 2 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
710 | 2 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2730 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2730 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2730 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2730 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2730 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2730 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2730 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2730 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.44 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2730 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2731 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2731 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.47 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2731 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2731 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2731 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2731 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2731 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2731 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2731 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2709 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2709 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.34 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2709 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2709 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2709 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2709 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2709 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2709 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2709 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.67 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2710 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.67 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2710 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2710 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2710 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2710 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2710 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.4 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2710 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2710 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2710 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
711 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
711 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.43 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
711 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
711 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
711 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
711 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
711 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
711 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
711 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.67 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2712 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2712 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.46 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2712 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2712 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2712 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2712 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.67 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2712 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2712 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2712 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2713 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2713 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2713 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2713 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2713 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2713 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2713 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2713 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.67 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2713 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.53 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2714 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2714 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2714 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.67 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2714 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2714 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2714 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2714 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2714 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2714 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.38 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2715 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.67 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2715 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2715 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2715 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2715 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.45 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2715 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2715 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2715 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2715 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
712 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
712 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.48 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
712 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
712 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
712 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
712 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
712 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
712 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.67 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
712 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2716 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2716 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.67 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2716 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2716 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2716 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2716 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2716 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2716 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2716 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2717 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2717 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.67 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2717 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2717 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2717 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2717 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2717 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2717 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2717 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.6 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2718 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2718 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2718 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2718 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2718 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.42 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2718 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2718 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.67 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2718 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2718 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
713 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
713 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
713 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
713 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
713 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
713 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
713 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
713 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
713 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.67 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2719 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2719 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2719 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2719 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2719 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2719 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2719 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2719 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.53 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2719 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.67 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2720 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2720 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2720 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2720 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2720 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2720 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2720 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2720 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2720 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.67 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2771 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2771 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.34 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2771 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2771 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2771 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2771 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2771 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2771 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2771 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2772 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2772 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2772 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2772 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.37 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2772 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2772 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2772 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2772 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2772 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
714 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
714 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.4 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
714 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
714 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
714 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
714 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
714 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
714 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.63 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
714 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
714 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
714 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
714 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
714 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
714 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.4 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
714 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
714 | 2 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
714 | 2 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
714 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2773 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2773 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2773 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2773 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2773 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2773 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2773 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2773 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2773 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.43 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2774 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2774 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2774 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.45 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2774 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2774 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2774 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2774 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2774 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2774 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2775 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2775 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2775 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2775 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2775 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2775 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2775 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2775 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2775 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2776 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2776 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.65 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2776 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2776 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2776 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2776 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2776 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2776 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2776 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.39 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2777 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2777 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.65 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2777 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2777 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.42 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2777 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2777 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2777 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2777 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2777 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
715 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
715 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
715 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
715 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.63 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
715 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
715 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
715 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
715 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
715 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.45 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
715 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
715 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
715 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
715 | 2 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
715 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.45 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
715 | 2 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
715 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
715 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.65 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
715 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2778 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2778 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2778 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2778 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2778 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2778 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.48 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2778 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2778 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.65 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2778 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2779 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2779 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2779 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.65 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2779 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2779 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2779 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2779 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2779 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2779 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2780 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2780 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2780 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2780 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2780 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2780 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2780 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2780 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2780 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.65 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2781 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2781 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2781 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.43 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2781 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2781 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2781 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2781 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2781 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2781 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.72 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2782 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2782 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.47 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2782 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.72 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2782 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2782 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2782 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2782 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2782 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2782 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
716 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
716 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
716 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
716 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
716 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
716 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
716 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.63 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
716 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
716 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
716 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
716 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.72 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
716 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
716 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
716 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
716 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
716 | 2 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
716 | 2 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
716 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2783 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2783 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2783 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2783 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2783 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2783 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2783 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2783 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.72 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2783 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.54 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2784 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2784 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2784 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2784 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.72 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2784 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2784 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2784 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2784 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2784 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2757 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.31 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2757 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2757 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2757 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2757 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2757 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2757 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2757 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2757 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2758 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2758 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2758 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2758 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2758 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.33 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2758 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2758 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2758 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2758 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
717 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
717 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
717 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
717 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
717 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
717 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
717 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
717 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
717 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
717 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
717 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.36 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
717 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.36 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
717 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
717 | 2 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
717 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
717 | 2 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
717 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
717 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
717 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
717 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2759 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2759 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2759 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2759 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2759 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2759 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2759 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2759 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2759 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.38 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2760 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2760 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2760 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2760 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2760 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2760 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2760 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.4 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2760 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2760 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2761 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2761 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2761 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2761 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2761 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.46 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2761 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2761 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2761 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2761 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2762 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2762 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2762 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2762 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2762 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2762 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2762 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2762 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2762 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.35 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2763 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2763 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2763 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2763 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2763 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2763 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2763 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.37 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2763 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2763 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
718 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
718 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
718 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.4 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
718 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
718 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
718 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
718 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
718 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
718 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
718 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
718 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
718 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
718 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
718 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
718 | 2 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
718 | 2 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
718 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.4 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
718 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2764 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2764 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2764 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2764 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2764 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2764 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2764 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2764 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.43 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2764 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2765 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2765 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2765 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2765 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.45 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2765 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2765 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2765 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2765 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2765 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2766 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2766 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2766 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2766 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2766 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2766 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2766 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.58 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2766 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2766 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2767 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2767 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2767 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2767 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2767 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2767 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2767 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.38 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2767 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2767 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.64 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2768 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2768 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.42 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2768 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.64 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2768 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2768 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2768 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2768 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2768 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2768 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
719 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.45 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
719 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
719 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
719 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
719 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.57 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
719 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
719 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
719 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
719 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
719 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
719 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
719 | 2 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
719 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
719 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.64 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
719 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
719 | 2 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
719 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.45 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
719 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2769 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2769 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2769 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2769 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2769 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.48 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2769 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2769 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.64 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2769 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2769 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2770 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2770 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2770 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2770 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2770 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2770 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.64 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2770 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2770 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2770 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2743 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.63 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2743 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2743 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2743 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2743 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2743 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2743 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2743 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.38 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2743 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2744 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2744 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2744 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.63 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2744 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.41 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2744 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2744 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2744 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2744 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2744 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
720 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
720 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.44 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
720 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
720 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
720 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
720 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
720 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
720 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.68 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
720 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
720 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
720 | 2 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
720 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
720 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
720 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
720 | 2 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
720 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
720 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.63 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
720 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.44 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2745 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2745 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2745 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2745 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2745 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2745 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.63 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2745 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.47 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2745 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2745 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2746 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2746 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2746 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2746 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2746 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.63 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2746 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2746 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2746 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2746 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2747 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.63 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2747 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2747 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2747 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2747 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2747 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2747 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.56 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2747 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2747 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2748 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.43 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2748 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2748 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2748 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2748 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2748 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2748 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2748 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2748 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.71 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
721 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.68 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
721 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
721 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
721 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
721 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
721 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
721 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
721 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
721 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
721 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.5 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
721 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
721 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
721 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
721 | 2 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
721 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
721 | 2 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
721 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.71 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
721 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2750 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2750 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.71 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2750 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2750 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2750 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.43 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2750 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2750 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2750 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2750 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2751 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2751 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2751 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2751 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.56 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2751 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.71 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2751 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2751 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2751 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2751 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2752 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.63 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2752 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2752 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2752 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.71 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2752 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2752 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2752 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2752 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2752 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2753 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2753 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2753 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2753 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2753 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2753 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.47 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2753 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2753 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.79 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2753 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2754 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.79 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2754 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.51 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2754 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2754 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2754 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2754 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2754 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2754 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2754 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
722 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
722 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
722 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.68 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
722 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
722 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
722 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
722 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.55 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
722 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
722 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
722 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.55 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
722 | 2 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
722 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
722 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
722 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
722 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
722 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
722 | 2 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
722 | 2 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.79 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2755 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2755 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2755 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2755 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.79 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2755 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2755 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.59 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2755 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2755 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2755 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
2756 | 1 | Total Gross Incremental Annual Electric Savings_kWh | T: Capacity of chiller (tons) | 560 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2756 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVbase: Integrated Part Load Factor of base equipment | 0.79 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2756 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Change in usage calculation | delta kWh = T*(OH)*(IPLVbase-IPLVe) | AmerenUE Business TRM 2008
2756 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2756 | 1 | Total Gross Incremental Annual Electric Savings_kWh | IPLVee: Integrated Part Load Factor of efficient equipment | 0.62 | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xls
2756 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2756 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
2756 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | NSB_Business_Reporting_Template.xlsx
2756 | 1 | Total Gross Incremental Annual Electric Savings_kWh | OH: Equivalent full load annual operating hours (hr)
776-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
776-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-1 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
776-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-10 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
776-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-15 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-19 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
776-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
776-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-4 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-5 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
776-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
776-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-11 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-12 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
776-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-6 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
776-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
776-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-7 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
776-13 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
776-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-9 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
776-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-14 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-16 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
776-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-8 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
776-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
776-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-18 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-3 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
776-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
776-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
776-2 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-20 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25
776-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25
776-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
776-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
776-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
776-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
731-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
731-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-1 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-1 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-1 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
731-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-10 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
731-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-10 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-10 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-15 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
731-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-15 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-15 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
731-19 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-19 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-19 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-4 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-4 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
731-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-4 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
731-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-5 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-5 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-5 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
731-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-11 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-11 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-11 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-12 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-12 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
731-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-12 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
731-6 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-6 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-6 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-7 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-7 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
731-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-7 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-13 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-13 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-13 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
731-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-9 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
731-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-9 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-9 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
731-14 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-14 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-14 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-16 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
731-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-16 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-16 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-8 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-8 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-8 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
731-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-18 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-18 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
731-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-18 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-3 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-3 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-3 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
731-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-2 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
731-2 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-2 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
731-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185
731-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64
731-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
731-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-20 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-20 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
731-20 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
731-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
731-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W
731-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-1 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
738-1 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-1 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 - 250 watt
738-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-1 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-1 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-10 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-10 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 - 250 watt
738-10 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
738-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-10 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-10 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 - 250 watt
738-15 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-15 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-15 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-15 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-15 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
738-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-19 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-19 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-19 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-19 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
738-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 - 250 watt
738-19 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Saturation | 1
738-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-4 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
738-4 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-4 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-4 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Customer | 1
738-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 – 250 watt
738-4 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 – 250 watt
738-5 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
738-5 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-5 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-5 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-5 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 - 250 watt
738-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
738-11 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-11 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-11 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-11 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-11 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-12 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-12 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-12 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
738-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 - 250 watt
738-12 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-12 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 – 250 watt
738-6 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-6 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
738-6 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-6 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-6 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-7 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-7 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-7 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 – 250 watt
738-7 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
738-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-7 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-13 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-13 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-13 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-13 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
738-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-13 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 - 250 watt
738-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-9 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-9 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-9 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-9 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
738-9 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 – 250 watt
738-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
738-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-14 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-14 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 - 250 watt
738-14 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-14 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-14 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-16 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-16 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-16 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 - 250 watt
738-16 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
738-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-16 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-8 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-8 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-8 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-8 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 – 250 watt
738-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
738-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-8 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-18 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 - 250 watt
738-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
738-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-18 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-18 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-18 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-18 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
738-3 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-3 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-3 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 – 250 watt
738-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-3 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-3 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-2 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 – 250 watt
738-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-2 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
738-2 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-2 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-2 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
738-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-20 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
738-20 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-20 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 245.5 | MH 175 – 250 watt
738-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-20 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-20 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
739-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-1 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-1 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-1 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-1 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-1 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-10 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-10 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
739-10 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-10 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
739-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-10 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
739-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-15 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-15 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-15 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-15 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-15 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-19 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-19 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-19 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-19 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-19 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
739-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
739-4 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-4 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-4 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-4 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-4 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-5 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
739-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-5 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-5 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-5 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-5 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-11 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-11 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-11 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-11 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
739-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-11 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-12 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-12 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-12 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-12 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-12 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
739-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-6 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-6 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-6 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-6 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-6 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
739-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-7 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-7 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
739-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-7 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-7 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-7 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-13 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-13 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
739-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-13 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-13 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-13 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-9 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
739-9 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-9 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-9 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-9 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-14 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-14 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-14 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-14 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-14 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
739-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-16 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-16 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
739-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-16 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-16 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-16 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-8 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
739-8 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-8 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-8 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-8 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-18 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-18 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
739-18 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-18 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-18 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-3 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-3 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-3 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-3 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-3 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
739-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-2 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-2 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-2 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-2 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
739-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-2 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | MH 400 watt
739-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-20 | 3 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-20 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-20 | 3 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-20 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
739-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 368.5 | MH 400 watt
739-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
739-20 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-1 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
757-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-1 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-10 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
757-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-10 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-15 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-15 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
757-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-19 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
757-19 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-4 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
757-4 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
757-5 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-5 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
757-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-11 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-11 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-12 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-12 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
757-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-6 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-6 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
757-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-7 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
757-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-7 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
757-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-13 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-13 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-9 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
757-9 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-14 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-14 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
757-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
757-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-16 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-16 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
757-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-8 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-8 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-18 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
757-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-18 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-3 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
757-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-3 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
757-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
757-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-2 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
757-2 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-20 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
757-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 179
757-20 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
757-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
757-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 295
757-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
757-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
758-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-1 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-1 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
758-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
758-10 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-10 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
758-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-15 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
758-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-15 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-19 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
758-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-19 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
758-4 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-4 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-5 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-5 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
758-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
758-11 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-11 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-12 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
758-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-12 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
758-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-6 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-6 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
758-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-7 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-7 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-13 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-13 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
758-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-9 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-9 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
758-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
758-14 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-14 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-16 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
758-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-16 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
758-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-8 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-8 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
758-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-18 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-18 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-3 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-3 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
758-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
758-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
758-2 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-2 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-20 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-20 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
758-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
758-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
758-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
759-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
759-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-1 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-1 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-1 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
759-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
759-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-10 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-10 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-10 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-15 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-15 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
759-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-15 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-19 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
759-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-19 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-19 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-4 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-4 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
759-4 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
759-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-5 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-5 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-5 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-11 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
759-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-11 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-11 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-12 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-12 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
759-12 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-6 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
759-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-6 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-6 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-7 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-7 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-7 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
759-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-13 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
759-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-13 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-13 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
759-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-9 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-9 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-9 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-14 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-14 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
759-14 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
759-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-16 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-16 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-16 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-8 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-8 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
759-8 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
759-18 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-18 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-18 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
759-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-3 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-3 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-3 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
759-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
759-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-2 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-2 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
759-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-2 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
759-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-20 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-20 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-20 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
759-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Constant | 1000
759-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290.764706
759-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
759-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
759-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 98.376471
760-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-1 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
760-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-1 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-1 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
760-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
760-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-10 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-10 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-10 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-15 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-15 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-15 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
760-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-19 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-19 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
760-19 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-4 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
760-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-4 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-4 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-5 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-5 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-5 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
760-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
760-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-11 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-11 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-11 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-12 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-12 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
760-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-12 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
760-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-6 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-6 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-6 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-7 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-7 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-7 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
760-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-13 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-13 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-13 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
760-9 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-9 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-9 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
760-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
760-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-14 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-14 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-14 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-16 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-16 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-16 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
760-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-8 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-8 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-8 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
760-18 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
760-18 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-18 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
760-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-3 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-3 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-3 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
760-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
760-2 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-2 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-2 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-20 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
760-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 452.889375
760-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
760-20 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
760-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
760-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 206.067171
760-20 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
761-1 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-1 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-1 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-10 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-10 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
761-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-10 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
761-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-15 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-15 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-15 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
761-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-19 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
761-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-19 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-19 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-4 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
761-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-4 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-4 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-5 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
761-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-5 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-5 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-11 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-11 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-11 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
761-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
761-12 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-12 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-12 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
761-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-6 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-6 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-6 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-7 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-7 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-7 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
761-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-13 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
761-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-13 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-13 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-9 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-9 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-9 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
761-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
761-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-14 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-14 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-14 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-16 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-16 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-16 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
761-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-8 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
761-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-8 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-8 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-18 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-18 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-18 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
761-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-3 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-3 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
761-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-3 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-2 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-2 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
761-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-2 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
761-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
761-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 598
761-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
761-20 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
761-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
761-20 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
761-20 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
761-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
761-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
762-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
762-1 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-1 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-1 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-1 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-1 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-10 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-10 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-10 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-10 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
762-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-10 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
762-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-15 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-15 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-15 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-15 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-15 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
762-19 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-19 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
762-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-19 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-19 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-19 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-4 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-4 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-4 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-4 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-4 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
762-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-5 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-5 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
762-5 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-5 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-5 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-11 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-11 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-11 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-11 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
762-11 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-12 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-12 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-12 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
762-12 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-12 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
762-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-6 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-6 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-6 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-6 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-6 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-7 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
762-7 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-7 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-7 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-7 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-13 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-13 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-13 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-13 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-13 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
762-9 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-9 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-9 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
762-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-9 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-9 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-14 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-14 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-14 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-14 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
762-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-14 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-16 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-16 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-16 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-16 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-16 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
762-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-8 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-8 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
762-8 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-8 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-8 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-18 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-18 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-18 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-18 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
762-18 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-3 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-3 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-3 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
762-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-3 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-3 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
762-2 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-2 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
762-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
762-2 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-2 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-2 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-20 | 3 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
762-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
762-20 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-20 | 3 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
762-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 293.894737
762-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
762-20 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
762-20 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
762-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
3003 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 85
3003 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
3003 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 250
3003 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 443
779-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-1 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-10 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-15 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-19 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-4 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-5 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-11 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-12 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-6 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-7 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-13 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-9 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-14 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-16 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-8 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-18 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-3 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-2 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
779-20 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
3004-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
3004-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
3004-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 311
3004-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 100
3004-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
3004-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 311
3004-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
3004-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 100
3005-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
3005-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
3005-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 400
3005-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
3005-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
3005-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
3005-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 400
3005-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
3006-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
3006-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 52
3006-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
3006-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 175
3006-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 52
3006-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
3006-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
3006-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 175
3007 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3007 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 52.8
3007 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 13
3007 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
3007-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
3007-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3007-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 64.1
3007-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 10.1
3008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 61
3008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
3008 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 15
3010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 5
3010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 40
3010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3010 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6570
3009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2920
3009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 14
3009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 63
3009 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 36
3011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2920
3011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 8
3011 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
8001 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
8001 | 1 | Vintage | Efficient watts | 3
8001 | 1 | Vintage | In Service Rate (ISR) | 1
8001 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
8001 | 1 | Vintage | HOU | 8760
8001 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
8001 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 18
8001 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
8001 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Ameren Missouri PY 2 EMV report
8001 | 1 | Vintage | Base watts | 18
8001 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm |  | Ohio TRM 2009
8001 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
8001 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes
8001 | 1 | Vintage | Waste Heat Factor for Energy (WHFe) | 1
8001 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
8000 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment
8000 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
8000 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) |  | Ameren Missouri PY 2 EMV report
8000 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
8000 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
8000 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm |  | Ohio TRM 2009
8000 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes
8000 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment
8000 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF)
8000 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-1 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-1 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-1 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-10 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-10 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-10 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
793-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-15 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-15 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-15 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-19 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-19 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-19 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-4 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-4 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-4 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-5 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-5 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-5 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-11 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-11 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-11 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-12 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-12 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-12 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-6 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-6 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-6 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-7 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-7 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-7 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-13 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-13 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-13 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-9 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-9 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-9 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-14 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-14 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-14 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-16 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-16 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-16 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-8 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-8 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-8 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-18 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-18 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-18 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-3 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-3 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-3 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-2 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
793-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
793-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-2 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-2 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
793-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 30
793-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
793-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 3
793-20 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
793-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-20 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-20 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
793-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
793-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
3012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
3012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 12
3012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 50
3012 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 8
3013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
3013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3013 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 75
3023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 14
3023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 25
3023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2920
3023 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 14
3024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 28
3024 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2920
3025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 32
3025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 14
3025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3025 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2920
3026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 14
3026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 32
3026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3026 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2920
3019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
3019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 32
3019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 28
3019 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
3020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 28
3020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3020 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 32
3021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 25
3021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
3021 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 32
3022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 32
3022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
3022 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 25
786-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
786-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-1 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-10 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
786-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
786-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-15 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-19 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
786-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
786-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-4 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-5 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
786-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-11 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
786-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
786-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-12 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
786-6 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-7 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
786-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-13 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
786-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
786-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-9 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-14 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
786-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
786-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-16 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
786-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-8 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
786-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-18 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
786-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-3 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-2 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
786-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
786-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
786-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 750
786-20 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
786-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
786-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
786-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
786-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
786-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-1 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
787-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
787-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-10 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
787-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-15 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
787-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-19 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
787-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-4 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-5 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
787-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-11 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
787-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
787-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-12 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
787-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-6 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-7 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
787-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-13 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
787-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
787-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-9 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-14 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
787-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
787-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-16 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
787-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-8 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
787-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-18 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
787-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-3 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
787-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-2 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
787-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
787-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
787-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.2
787-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 300
787-20 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
787-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
787-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
787-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
781-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-1 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-10 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-15 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-19 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-4 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-5 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-11 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-12 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-6 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-7 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-13 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-9 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-14 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-16 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-8 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-18 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-3 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-2 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-20 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
781-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-1 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-10 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-15 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-19 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-4 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-5 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-11 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-12 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-6 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-7 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-13 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-9 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-14 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-16 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-8 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-18 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-3 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-2 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
780-20 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-1 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-1 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-10 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-10 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-15 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-15 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-19 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-19 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-4 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-4 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-5 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-5 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-11 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-11 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-12 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-12 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-6 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-6 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-7 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-7 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-13 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-13 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-9 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-9 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-14 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-14 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-16 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-16 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-8 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-8 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-18 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-18 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-3 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-3 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-2 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1102-2 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1102-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1102-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 243
1102-20 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1102-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1102-20 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1102-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1102-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-1 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-1 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-1 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-1 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
1106-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-10 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-15 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-15 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-15 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-15 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-19 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-19 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-19 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-19 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-4 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-4 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-4 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-4 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-5 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-5 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-5 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-5 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-11 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-11 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-11 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-11 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-12 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-12 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 560
1106-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-12 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-12 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-6 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-6 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-6 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-6 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-7 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-7 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-7 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-7 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-13 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-13 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-13 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-13 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-9 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-9 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-9 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-9 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-14 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-14 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-14 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-14 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-16 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-16 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-16 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-16 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-8 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-8 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-8 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-8 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-18 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-18 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-18 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-18 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-3 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-3 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-3 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-3 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
1106-2 | 3 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Constant (1000) | 1000
1106-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-2 | 3 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
1106-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-2 | 3 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
1106-2 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
1106-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 365
1106-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 454
1106-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
1106-20 | 3 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
776-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-1 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-10 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-15 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-19 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-4 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-5 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-11 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-12 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-6 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-7 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-13 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-9 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-14 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-16 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-8 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-18 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-3 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-2 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
776-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
776-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.25 | Morgan Measure Libraries
776-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
776-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.25 | Morgan Measure Libraries
776-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
776-20 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
776-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-1 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-1 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-1 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-10 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-10 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-10 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 - 200 W | Morgan Measure Libraries
731-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-15 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-15 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-15 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-19 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-19 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-19 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-4 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-4 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-4 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-5 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-5 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-5 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-11 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-11 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-11 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-12 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-12 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-12 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-6 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-6 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-6 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-7 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-7 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-7 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-13 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-13 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-13 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-9 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-9 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-9 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-14 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-14 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-14 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-16 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-16 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-16 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-8 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-8 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-8 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-18 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-18 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-18 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-3 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-3 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-3 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-2 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-2 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 – 200 W | Morgan Measure Libraries
731-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-2 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 64 | Morgan Measure Libraries
731-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes2 | Pulse-start MH 150 - 200 W | Morgan Measure Libraries
731-20 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 185 | Morgan Measure Libraries
731-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
731-20 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
731-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
731-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
731-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
731-20 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
3001 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2920
3001 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 23
3001 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 63
3001 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3002 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 11
3002 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 36
3002 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1.04
3002 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2920
746-1 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
746-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
746-1 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
746-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
746-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
746-1 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
746-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
746-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
746-1 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
746-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
746-1 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
746-1 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-10 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-10 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-10 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-10 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-10 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-10 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-10 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-10 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
745-10 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-15 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-15 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-15 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-15 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
745-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-15 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-15 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-19 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-19 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-19 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-19 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-19 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
745-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-19 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-4 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-4 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-4 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-4 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-4 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
745-4 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-5 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-5 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-5 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-5 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
745-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-5 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-5 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-11 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-11 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-11 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
745-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-11 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-11 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-11 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-12 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-12 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-12 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-12 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-12 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
745-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-12 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-6 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-6 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-6 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-6 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-6 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-6 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
745-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-7 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-7 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-7 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-7 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
745-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-7 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-7 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-13 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-13 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-13 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-13 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-13 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
745-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-13 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-9 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-9 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-9 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-9 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-9 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
745-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-9 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-14 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-14 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-14 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-14 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
745-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-14 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-14 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-16 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-16 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-16 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-16 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-16 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
745-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-16 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-8 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-8 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-8 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-8 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-8 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-8 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
745-18 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-18 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-18 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-18 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-18 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
745-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-18 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-3 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-3 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-3 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-3 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
745-3 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-3 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-2 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-2 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-2 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
745-2 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-2 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-2 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
745-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74 | Morgan Measure Libraries
745-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
745-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
745-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-20 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-20 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19 | Morgan Measure Libraries
745-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Morgan Measure Libraries
745-20 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
745-20 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
745-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-20 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
745-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 74
745-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
745-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-20 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
745-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 19
745-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
749-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-1 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-1 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-1 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-1 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-1 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.4 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-1 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-10 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-10 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-10 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-10 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-10 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-10 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-15 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-15 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-15 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-15 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-15 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-15 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-19 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-19 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-19 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-19 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-19 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-19 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-4 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-4 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-4 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-4 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-4 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-4 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-5 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-5 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-5 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.2 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-5 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-5 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-5 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-11 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-11 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-11 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-11 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-11 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6148 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-11 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-12 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-12 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-12 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-12 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-12 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-12 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-6 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-6 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-6 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-6 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.8 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-6 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-6 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-7 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-7 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-7 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.8 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-7 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-7 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-7 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-13 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-13 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-13 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-13 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-13 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-13 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-9 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-9 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-9 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-9 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-9 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.3 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-9 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-14 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-14 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-14 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-14 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-14 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.4 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-14 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-16 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-16 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-16 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-16 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-16 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-16 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-8 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-8 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-8 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-8 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4656 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-8 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-8 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-18 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-18 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-18 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-18 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-18 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-18 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-3 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-3 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-3 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-3 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-3 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-3 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-2 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-2 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-2 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-2 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-2 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-2 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-20 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-20 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3680 | Commercial_AmerenTRM_HoursOfUse_Table.docx
749-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-20 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-20 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 65 | Morgan Measure Libraries
749-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
749-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 200 | Morgan Measure Libraries
749-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
749-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5047 |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
749-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
749-20 | 2 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-20 | 2 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
749-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-1 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
773-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-1 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-10 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-10 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
773-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-15 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
773-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-15 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-19 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
773-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-19 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-4 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-4 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
773-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-5 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-5 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
773-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-11 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-11 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
773-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-12 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
773-12 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-6 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-6 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
773-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-7 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
773-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-7 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-13 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-13 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
773-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-9 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-9 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
773-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-14 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
773-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-14 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-16 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-16 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
773-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-8 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
773-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-8 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-18 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
773-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-18 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-3 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-3 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
773-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-2 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
773-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
773-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-2 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000 | Ohio TRM 2009
773-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3 | Morgan Measure Libraries
773-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3 | Morgan Measure Libraries
773-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | hours = hours of operation | 3680 | Morgan Measure Libraries
773-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-20 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000 | Morgan Measure Libraries
773-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
773-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
773-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | % Reduction | 0.3
773-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Watt/SF = watt per square feet of controlled lighting space | 1.3
773-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | SF = square feet of controlled lighting space | 10000
773-20 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
773-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
773-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =(SF*watt/SF*hours*% reduction)/1000
784-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-1 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-10 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-15 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-19 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-4 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-5 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-11 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-12 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-6 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-7 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-13 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-9 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-14 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-16 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-8 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-18 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-3 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-2 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-20 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
784-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
738-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-1 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-1 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-1 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-1 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 - 250 watt
738-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
738-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-1 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-1 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-10 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-10 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-10 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-10 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
738-10 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 - 250 watt
738-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-10 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-15 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-15 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-15 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-15 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-15 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
738-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-15 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 - 250 watt
738-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-19 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-19 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-19 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-19 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-19 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-19 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 - 250 watt
738-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
738-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-4 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-4 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-4 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-4 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-4 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 – 250 watt
738-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
738-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-4 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-5 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-5 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-5 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-5 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 – 250 watt
738-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-5 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
738-5 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-11 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-11 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-11 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-11 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-11 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 - 250 watt
738-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-11 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
738-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-12 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-12 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-12 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-12 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-12 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 - 250 watt
738-12 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
738-6 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-6 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-6 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 – 250 watt
738-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-6 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-6 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-6 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
738-7 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-7 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-7 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-7 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-7 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
738-7 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 – 250 watt
738-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-13 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-13 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-13 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-13 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-13 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
738-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 - 250 watt
738-13 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-9 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-9 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-9 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
738-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-9 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 – 250 watt
738-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-9 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-9 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-14 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-14 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-14 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-14 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-14 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-14 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 - 250 watt
738-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
738-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-16 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-16 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-16 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
738-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-16 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 - 250 watt
738-16 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-16 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-8 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-8 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-8 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-8 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
738-8 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 – 250 watt
738-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-8 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-18 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-18 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-18 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
738-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 - 250 watt
738-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 - 250 watt
738-18 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-18 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-18 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-3 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-3 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-3 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 – 250 watt
738-3 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-3 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
738-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-3 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-2 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-2 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-2 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-2 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
738-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
738-2 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-2 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 – 250 watt
738-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
738-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-20 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | Morgan Measure Libraries
738-20 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | Morgan Measure Libraries
738-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
738-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
738-20 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 160 | MH 175 – 250 watt
738-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-20 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-20 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
738-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
738-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
738-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
738-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
738-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 267 | MH 175 – 250 watt
738-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
738-20 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-1 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-1 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-1 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-1 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-1 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
739-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-1 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-10 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-10 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-10 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-10 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-10 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
739-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
739-10 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-15 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-15 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-15 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-15 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-15 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
739-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-15 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-19 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-19 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-19 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-19 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-19 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-19 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
739-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-4 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-4 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-4 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-4 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
739-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-4 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-4 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-5 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-5 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-5 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-5 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-5 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-5 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
739-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-11 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-11 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-11 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-11 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
739-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-11 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-11 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-12 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-12 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-12 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-12 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
739-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-12 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-12 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-6 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-6 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-6 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-6 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
739-6 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-6 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-7 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-7 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-7 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-7 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-7 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
739-7 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-13 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-13 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-13 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-13 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-13 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
739-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-13 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-9 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-9 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-9 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-9 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
739-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-9 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-9 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-14 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-14 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-14 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-14 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-14 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
739-14 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-16 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-16 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-16 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
739-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-16 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-16 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-16 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-8 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-8 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-8 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-8 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
739-8 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-8 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-18 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-18 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-18 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-18 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-18 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-18 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
739-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-3 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-3 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-3 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-3 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-3 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-3 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
739-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-2 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-2 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-2 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
739-2 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
739-2 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-2 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-20 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 279 | Morgan Measure Libraries
739-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | Morgan Measure Libraries
739-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760 | Commercial_AmerenTRM_HoursOfUse_Table.docx
739-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | Morgan Measure Libraries
739-20 | 1 | Efficient Case Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
739-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-20 | 1 | Baseline Value | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-20 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
739-20 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
739-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
739-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 152.907407 | MH 400 watt
739-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
739-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 461 | MH 400 watt
739-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-20 | 2 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
739-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
739-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-1 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-1 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-1 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-1 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-1 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
742-1 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-10 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-10 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-10 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-10 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
742-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-10 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
742-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-10 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-15 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-15 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-15 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-15 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-15 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
742-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-15 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-19 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-19 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-19 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-19 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-19 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
742-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-19 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-4 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-4 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-4 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-4 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-4 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
742-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-4 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-5 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-5 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-5 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-5 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-5 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
742-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-5 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-11 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-11 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-11 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-11 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
742-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-11 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-11 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-12 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-12 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-12 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-12 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
742-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-12 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-12 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-6 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-6 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-6 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
742-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-6 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-6 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-6 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-7 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-7 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-7 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-7 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-7 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
742-7 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-13 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-13 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-13 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-13 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
742-13 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-13 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-9 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-9 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-9 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-9 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-9 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-9 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
742-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-14 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-14 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-14 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
742-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-14 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-14 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-14 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-16 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-16 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-16 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-16 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
742-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-16 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-16 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-8 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-8 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-8 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-8 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
742-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-8 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-8 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-18 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-18 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-18 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-18 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-18 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
742-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-18 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-3 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-3 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-3 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-3 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-3 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-3 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
742-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-2 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-2 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-2 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-2 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
742-2 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
742-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-2 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
742-20 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-20 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
742-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
742-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
742-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
742-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-20 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-20 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-20 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
742-20 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
742-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
742-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
742-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
742-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
742-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
742-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
743-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-1 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-1 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-1 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-1 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-1 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-1 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-1 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-1 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6151.423913
743-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-1 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-10 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-10 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-10 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-10 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
743-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 2422
743-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-10 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-10 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-10 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-10 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-10 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-15 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-15 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-15 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-15 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-15 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-15 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-15 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-15 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4380
743-15 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-19 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-19 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-19 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-19 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-19 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-19 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 8760
743-19 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-19 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-19 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-4 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-4 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-4 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-4 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 3540
743-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-4 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-4 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-4 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-4 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-4 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-5 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-5 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-5 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6504.163265
743-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-5 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-5 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-5 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-5 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-5 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-5 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-11 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-11 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-11 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-11 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-11 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-11 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-11 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-11 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 6147.983607
743-11 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-12 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-12 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-12 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4311
743-12 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-12 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-12 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-12 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-12 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-12 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-6 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-6 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-6 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-6 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-6 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-6 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-6 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5254.833333
743-6 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-6 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-7 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-7 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-7 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-7 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 7730.797101
743-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-7 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-7 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-7 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-7 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-7 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-13 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-13 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-13 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-13 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-13 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-13 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-13 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-13 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 777
743-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-13 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-9 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-9 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-9 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5798.34375
743-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-9 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-9 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-9 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-9 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-9 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-9 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-14 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-14 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-14 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5542.356808
743-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-14 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-14 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-14 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-14 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-14 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-14 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-16 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-16 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-16 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-16 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5950
743-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-16 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-16 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-16 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-16 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-16 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-8 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-8 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-8 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-8 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-8 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-8 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-8 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4655.962406
743-8 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-8 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-18 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-18 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-18 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-18 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-18 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-18 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 1664
743-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-18 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-18 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-18 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-3 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-3 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-3 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-3 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5747.5
743-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-3 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-3 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-3 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-3 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-3 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-2 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-2 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-2 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-2 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-2 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-2 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-2 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5054.034091
743-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000
743-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-2 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-2 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100 | Ameren Missouri PY 2 EMV report from ADM
743-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21 | Ameren Missouri PY 2 EMV report from ADM
743-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
743-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-20 | 1 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
743-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-20 | 1 | Efficient Case Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5202 | Ameren Missouri PY 2 EMV report from ADM
743-20 | 1 | Baseline Value | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
743-20 | 2 | Incremental Cost per Unit | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 100
743-20 | 2 | Baseline Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-20 | 2 | Measure Life | Source Documentation |  |  | Final Custom and Standard BEEP Evaluation Report 03-31-11.doc
743-20 | 2 | Efficient Case Value | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1 | assumed to be 1 for the first 3 year implementation program until further data can be gathered and consensus can be built.
743-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 5046.964539
743-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 21
743-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-20 | 2 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | PY1 - PY5 Com Lighting Data 07.28.14 - Delta Watts_v2ComLightingSavings.xlsx
743-20 | 2 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase – WATTSee) * HOURS * IF) /1000
757-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
757-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
757-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
757-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
757-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
757-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
757-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 182
757-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
758-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
758-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
758-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Morgan Measure Libraries
758-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 730
758-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
758-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
758-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 1080
759-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-1 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-10 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-15 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-19 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-4 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-5 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-11 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-12 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-6 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-7 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-13 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-9 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-14 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-16 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-16 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-8 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-8 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-8 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-8 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-18 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-18 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-18 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-18 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-3 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-3 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-3 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-3 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
759-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
759-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-2 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-2 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-2 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-2 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 290
759-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
759-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 142
759-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
759-20 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-20 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-20 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
759-20 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
760-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 455
760-1 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
760-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
760-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
760-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 224
760-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-1 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-1 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-1 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
760-10 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
760-10 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 455
760-10 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 224
760-10 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
760-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 455
760-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
760-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 224
760-15 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
760-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
760-15 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-15 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-15 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
760-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 224
760-19 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-19 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 455
760-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-19 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
760-19 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
760-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-4 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
760-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 455
760-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
760-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
760-4 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-4 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-4 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 224
760-5 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-5 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 224
760-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-5 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
760-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
760-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
760-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 455
760-5 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
760-11 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 224
760-11 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
760-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 455
760-11 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-11 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
760-12 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-12 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 455
760-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
760-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
760-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-12 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 224
760-12 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
760-6 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
760-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
760-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-6 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 224
760-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
760-6 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 455
760-6 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-7 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
760-7 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
760-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 224
760-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
760-7 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 455
760-7 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
760-13 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
760-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 455
760-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 224
760-13 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-13 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
760-13 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 455
760-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 224
760-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
760-9 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-9 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
760-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
760-9 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-9 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 224
760-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 455
760-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Interactive Factor (IF) | 1
760-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
760-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | annual operating hours (HOURS) | 4160 | Commercial_AmerenTRM_HoursOfUse_Table.docx
760-14 | 1 | Incremental Cost per Unit | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-14 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-14 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-14 | 1 | Measure Life | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsbase = Power draw (expressed in Watts) of base (existing) interior electrical equipment | 455
760-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx
760-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Notes | If the appropriate field data required to complete this equation cannot be obtained, the deemed savings values in the table are to be used for each measure.
760-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Savings Algorithm | delta kWh =((WATTSbase - WATTSee) * HOURS * IF) /1000 | Ohio TRM 2009
760-16 | 1 | Total Gross Incremental Annual Electric Savings_kWh | Wattsee = Power draw (expressed in Watts) of efficient (replacement) electrical equipment | 224
760-16 | 1 | Total Gross Average Annual Demand Reduction_kW | Source Documentation |  |  | MorganMeasureLibraries_Master_Measure_Database_AmerenMO_DISTRIBUTED-2010-10-11.xlsx