North | 09 - Nebraska | 28S | Normal | Tie-SLG-18 | SLG fault on S3456 to CBLUFFS3 345kV crt 1, near S3456 for 16 cycles. Clear fault by tripping the faulted crt and S3456 to S3458 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-SLG-19 | SLG fault on COOPER to ST JOE 345kV crt 1, near COOPER for 16 cycles. Clear fault by tripping the faulted crt and COOPER to ATCHSN 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-SLG-20 | SLG fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER for 16 cycles. Clear fault by tripping the faulted crt and COOPER 345/161/13.8kV TF T5. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-SLG-21 | SLG fault on S3451 to RAUN 345kV crt 1, near S3451 for 16 cycles. Clear fault by tripping the faulted crt and S3451 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-SLG-22 | SLG fault on HOSKINS3 to RAUN 345kV crt 1, near HOSKINS3 for 16 cycles. Clear fault by tripping the faulted crt and HOSKINS3 345/161/13.8kV TF T4. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-SLG-23 | SLG fault on HOSKINS3 to RAUN 345kV crt 1, near HOSKINS3 for 16 cycles. Clear fault by tripping the faulted crt and HOSKINS3 345/230/13.8kV TF T2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-SLG-24 | SLG fault on REDWILO3 to MINGO 345kV crt 1, near REDWILO3 for 16 cycles. Clear fault by tripping the faulted crt, REDWILO3 to GENTLMN3 345kV crt 1 and REDWILO3 345/115/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-SLG-25 | SLG fault on KEYSTON3 to SD.LS-LR-MB3 345kV crt 1, near KEYSTON3 for 16 cycles. Clear fault by tripping the faulted crt, KEYSTON3 to GENTLMN3 345kV crt 1 and KEYSTON3 345/115/13.8kV TF T1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-SLG-26 | SLG fault on S3458 to HOLT 345kV crt 1, near S3458 for 16 cycles. Clear fault by tripping the faulted crt and S3458 to COOPER 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-SLG-27 | SLG fault on ANTELOPE to HOLT.CO3 345kV crt 1, near ANTELOPE for 16 cycles. Clear fault by tripping ANTELOPE 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-SLG-28 | SLG fault on THEDFRD3 to HOLT.CO3 345kV crt 1, near THEDFRD3 for 16 cycles. Clear fault by tripping THEDFRD3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-SLG-29 | SLG fault on GRPRAR2-LNX3 to FTTHOM2-LNX3 345kV crt 1, near GRPRAR2-LNX3 for 16 cycles. Clear fault by tripping the faulted crt, GR PRAIRIE 345kV bus, G16-075 Gen and GRPR11W/12W/21W/22W Gen. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-SLG-30 | SLG fault on MEADOWGROVE to FTRANDL4 230kV crt 1, near MEADOWGROVE for 16 cycles. Clear fault by tripping MEADOWGROVE 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-31 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-32 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on S3458 to HOLT 345kV crt 1, near S3458. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-33 | Prior Outage of COOPER to ST JOE 345kV crt 1. 3-ph fault on REDWILO to MINGO 345kV crt 1, near REDWILO. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-34 | Prior Outage of COOPER to 7FAIRPT 345kV crt 1. 3-ph fault on COOPER to ST JOE 345kV crt 1. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-35 | Prior Outage of COOPER to 7FAIRPT 345kV crt 1. 3-ph fault on S3458 to HOLT 345kV crt 1, near S3458. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-36 | Prior Outage of S3458 to HOLT 345kV crt 1. 3-ph fault on COOPER to ST JOE 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-37 | Prior Outage of S3458 to HOLT 345kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-38 | Prior Outage of S3456 to CBLUFFS3 345kV crt 1. 3-ph fault on S3451 to RAUN 345kV crt 1, near S3451. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 09 - Nebraska | 28S | Normal | Tie-3ph-39 | Outage of MEADOWGROVE to FTRANDL4 230kV crt 1. 3-ph fault on COOPER to 7FAIRPT 345kV crt 1, near COOPER for 6 cycles. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_1_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to STLGENS4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_1_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to STLGENS4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_1_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to STLGENS4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_1_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to STLGENS4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_2_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to FTHUMBG4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_2_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to FTHUMBG4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_2_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to FTHUMBG4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_2_P1_ARSHILL4 | Apply 3-phase fault on ARSHILL4 to FTHUMBG4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_3_P1_NMARKET2 | Apply 3-phase fault on ARSHILL2 to NMARKET2 69kV line CKT 1, near NMARKET2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_3_P1_NMARKET2 | Apply 3-phase fault on ARSHILL2 to NMARKET2 69kV line CKT 1, near NMARKET2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_3_P1_NMARKET2 | Apply 3-phase fault on ARSHILL2 to NMARKET2 69kV line CKT 1, near NMARKET2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_3_P1_NMARKET2 | Apply 3-phase fault on ARSHILL2 to NMARKET2 69kV line CKT 1, near NMARKET2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_4_P1_BLOOMBG2 | Apply 3-phase fault on BLOOMBG2 to IPC TAP2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_4_P1_BLOOMBG2 | Apply 3-phase fault on BLOOMBG2 to IPC TAP2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.22pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_4_P1_BLOOMBG2 | Apply 3-phase fault on BLOOMBG2 to IPC TAP2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_4_P1_BLOOMBG2 | Apply 3-phase fault on BLOOMBG2 to IPC TAP2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and S_TEXARK to TEXARK 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open S_TEXARK to TEXARK 2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_5_P1_BLOOMBG2 | Apply 3-phase fault on ATLANTA2 to BLOOMBG2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed :MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_5_P1_BLOOMBG2 | Apply 3-phase fault on ATLANTA2 to BLOOMBG2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_5_P1_BLOOMBG2 | Apply 3-phase fault on ATLANTA2 to BLOOMBG2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_5_P1_BLOOMBG2 | Apply 3-phase fault on ATLANTA2 to BLOOMBG2 69kV line CKT 1, near BLOOMBG2 69kV for 7 cycles. Open the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and ATLANTA2 to WATLANT2 69kV line CKT 1 and ATLANTA2 to WATLANT2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1. Simultaneously re-open ATLANTA2 to WATLANT2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_6_P1_TEXARK2 | Apply 3-phase fault on TEXARK 2 to WASHST 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Open the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_6_P1_TEXARK2 | Apply 3-phase fault on TEXARK 2 to WASHST 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Open the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_6_P1_TEXARK2 | Apply 3-phase fault on TEXARK 2 to WASHST 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Open the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_6_P1_TEXARK2 | Apply 3-phase fault on TEXARK 2 to WASHST 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Open the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUGHLET2 to TEX12ST2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUGHLET2 to TEX12ST2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_7_P1_TEXARK2 | Apply 3-phase fault on SETEXAR2 to TEXARK 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_7_P1_TEXARK2 | Apply 3-phase fault on SETEXAR2 to TEXARK 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_7_P1_TEXARK2 | Apply 3-phase fault on SETEXAR2 to TEXARK 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_7_P1_TEXARK2 | Apply 3-phase fault on SETEXAR2 to TEXARK 2 69kV line CKT 1, near TEXARK 2 69kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_8_P1_WATLANT2 | Apply 3-phase fault on WATLANT2 69kV/138kV/13.19kV transformer CKT 1, near WATLANT2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_8_P1_WATLANT2 | Apply 3-phase fault on WATLANT2 69kV/138kV/13.19kV transformer CKT 1, near WATLANT2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_8_P1_WATLANT2 | Apply 3-phase fault on WATLANT2 69kV/138kV/13.19kV transformer CKT 1, near WATLANT2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_8_P1_WATLANT2 | Apply 3-phase fault on WATLANT2 69kV/138kV/13.19kV transformer CKT 1, near WATLANT2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_9_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to CASSTP4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_9_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to CASSTP4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_9_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to CASSTP4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_9_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to CASSTP4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_10_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to WILKES 4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_10_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to WILKES 4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_10_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to WILKES 4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_10_P1_WATLANT4 | Apply 3-phase fault on WATLANT4 to WILKES 4 138kV line CKT 1, near WATLANT4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_11_P1_HOSSTON2 | Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_11_P1_HOSSTON2 | Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_11_P1_HOSSTON2 | Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_11_P1_HOSSTON2 | Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_12_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_12_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_12_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_12_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_13_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to GODFREYRDTP2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_13_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to GODFREYRDTP2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_13_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to GODFREYRDTP2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_13_P1_HOSSTON2 | Apply 3-phase fault on HOSSTON2 to GODFREYRDTP2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and BLOOMBG2 to RODESSA2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open BLOOMBG2 to RODESSA2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_14_P1_LIEBERM2 | Apply 3-phase fault on LIEBERM2 69kV/138kV/13.19kV transformer CKT 3, near LIEBERM2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_14_P1_LIEBERM2 | Apply 3-phase fault on LIEBERM2 69kV/138kV/13.19kV transformer CKT 3, near LIEBERM2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_14_P1_LIEBERM2 | Apply 3-phase fault on LIEBERM2 69kV/138kV/13.19kV transformer CKT 3, near LIEBERM2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_14_P1_LIEBERM2 | Apply 3-phase fault on LIEBERM2 69kV/138kV/13.19kV transformer CKT 3, near LIEBERM2 69kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_15_P1_LIEBERM2 | Apply 3-phase fault on BLANCH-2 to LIEBERM2 69kV line CKT 1, near LIEBERM2 69kV for 7 cycles. Open the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_15_P1_LIEBERM2 | Apply 3-phase fault on BLANCH-2 to LIEBERM2 69kV line CKT 1, near LIEBERM2 69kV for 7 cycles. Open the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_15_P1_LIEBERM2 | Apply 3-phase fault on BLANCH-2 to LIEBERM2 69kV line CKT 1, near LIEBERM2 69kV for 7 cycles. Open the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_15_P1_LIEBERM2 | Apply 3-phase fault on BLANCH-2 to LIEBERM2 69kV line CKT 1, near LIEBERM2 69kV for 7 cycles. Open the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NMARKET2 to BLANCHR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NMARKET2 to BLANCHR2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_16_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to IPCJEFF4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Open the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_16_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to IPCJEFF4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Open the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_16_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to IPCJEFF4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Open the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_16_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to IPCJEFF4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Open the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and IPCJEFF4 to JEFFRSN4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open IPCJEFF4 to JEFFRSN4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_17_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to LONGWD 4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_17_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to LONGWD 4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_17_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to LONGWD 4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_17_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to LONGWD 4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_18_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to G16-167-TAP 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_18_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to G16-167-TAP 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_18_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to G16-167-TAP 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_18_P1_LIEBERM4 | Apply 3-phase fault on LIEBERM4 to G16-167-TAP 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_19_P1_LIEBERM4 | Apply 3-phase fault on ARSHILL4 to LIEBERM4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_19_P1_LIEBERM4 | Apply 3-phase fault on ARSHILL4 to LIEBERM4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_19_P1_LIEBERM4 | Apply 3-phase fault on ARSHILL4 to LIEBERM4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_19_P1_LIEBERM4 | Apply 3-phase fault on ARSHILL4 to LIEBERM4 138kV line CKT 1, near LIEBERM4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_20_P1_LONGWD4 | Apply 3-phase fault on LONGWD 4 138kV/345kV/13.19kV transformer CKT 1, near LONGWD 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_20_P1_LONGWD4 | Apply 3-phase fault on LONGWD 4 138kV/345kV/13.19kV transformer CKT 1, near LONGWD 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_20_P1_LONGWD4 | Apply 3-phase fault on LONGWD 4 138kV/345kV/13.19kV transformer CKT 1, near LONGWD 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_20_P1_LONGWD4 | Apply 3-phase fault on LONGWD 4 138kV/345kV/13.19kV transformer CKT 1, near LONGWD 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_21_P1_LONGWD7 | Apply 3-phase fault on LONGWD 7 to WILKES 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_21_P1_LONGWD7 | Apply 3-phase fault on LONGWD 7 to WILKES 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_21_P1_LONGWD7 | Apply 3-phase fault on LONGWD 7 to WILKES 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_21_P1_LONGWD7 | Apply 3-phase fault on LONGWD 7 to WILKES 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_22_P1_LONGWD7 | Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_22_P1_LONGWD7 | Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_22_P1_LONGWD7 | Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_22_P1_LONGWD7 | Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_23_P1_NBENTON4 | Apply 3-phase fault on LINTNRD4 to NBENTON4 138kV line CKT 1, near NBENTON4 138kV for 7 cycles. Open the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_23_P1_NBENTON4 | Apply 3-phase fault on LINTNRD4 to NBENTON4 138kV line CKT 1, near NBENTON4 138kV for 7 cycles. Open the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_23_P1_NBENTON4 | Apply 3-phase fault on LINTNRD4 to NBENTON4 138kV line CKT 1, near NBENTON4 138kV for 7 cycles. Open the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_23_P1_NBENTON4 | Apply 3-phase fault on LINTNRD4 to NBENTON4 138kV line CKT 1, near NBENTON4 138kV for 7 cycles. Open the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and RDPOINT4 to DEENPNT4 138kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_24_P1_SUPEROR2 | Apply 3-phase fault on OILCITY2 to SUPEROR2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_24_P1_SUPEROR2 | Apply 3-phase fault on OILCITY2 to SUPEROR2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_24_P1_SUPEROR2 | Apply 3-phase fault on OILCITY2 to SUPEROR2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_24_P1_SUPEROR2 | Apply 3-phase fault on OILCITY2 to SUPEROR2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and LIEBERM2 to OILCITY2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_25_P1_SUPEROR2 | Apply 3-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_25_P1_SUPEROR2 | Apply 3-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_25_P1_SUPEROR2 | Apply 3-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_25_P1_SUPEROR2 | Apply 3-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 7 cycles. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open JEFFRSN2 to WOODLWN2 69kV line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_26_P1_WILKES4 | Apply 3-phase fault on WILKES 4 138kV/345kV/13.19kV transformer CKT 1, near WILKES 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_26_P1_WILKES4 | Apply 3-phase fault on WILKES 4 138kV/345kV/13.19kV transformer CKT 1, near WILKES 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_26_P1_WILKES4 | Apply 3-phase fault on WILKES 4 138kV/345kV/13.19kV transformer CKT 1, near WILKES 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_26_P1_WILKES4 | Apply 3-phase fault on WILKES 4 138kV/345kV/13.19kV transformer CKT 1, near WILKES 4 138kV for 7 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_27_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_27_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_27_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - G17-065-GEN2[1]. G17-065-GEN2[1] tripped on overfrequency. When the protection relay is disabled and the simulation is repeated, the unit becomes stable. The tripping is observed in BC and TC for this contingency.
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_27_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - G17-065-GEN2[1]. G17-065-GEN2[1] tripped on overfrequency. When the protection relay is disabled and the simulation is repeated, the unit becomes stable. The tripping is observed in BC and TC for this contingency.
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_28_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | NO | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_28_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | NO | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_28_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_28_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_29_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | NO | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_29_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | NO | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_29_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_29_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_30_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.)
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_30_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_30_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.)
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_30_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.)
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_31_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.)
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_31_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_31_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.)
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_31_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV line CKT &1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Multi-Section Line. Wait 20 cycles. Re-close the faulted Multi-Section Line. Re-open the faulted Multi-Section Line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.)
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_32_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_32_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_32_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_32_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_33_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_33_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_33_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_33_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_34_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_34_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_34_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_34_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_35_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_35_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_35_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_35_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | NO | LVRT VIOL - - LANoGSU10.60[W1]. LANOGSU10.60[W1] tripped on undervoltage protection. (Due to size and location of the unit, no further simulation was peroformed.) Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_36_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed :MaxV: 1.24pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_36_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_36_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_36_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_37_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.31pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_37_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_37_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.36pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_37_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.36pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_38_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_38_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_38_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_38_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_39_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_39_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_39_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_39_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_40_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_40_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_40_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_40_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_41_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.27pu, MaxDur: 0.03s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_41_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_41_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.27pu, MaxDur: 0.03s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_41_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.26pu, MaxDur: 0.03s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_42_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.23pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_42_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_42_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.22pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_42_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_43_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_43_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_43_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_43_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_44_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed - MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_44_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_44_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_44_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_45_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed - MaxV: 1.33pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_45_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_45_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.33pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_45_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.33pu, MaxDur: 0.02s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_46_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_46_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_46_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_46_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_47_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_47_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_47_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_47_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_48_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_48_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_48_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed ; MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_48_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_49_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_49_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_49_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.06s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_49_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.07s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_50_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_50_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_50_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_50_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_51_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_51_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_51_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_51_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_52_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_52_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_52_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_52_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_53_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_53_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_53_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_53_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_54_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_54_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_54_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_54_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_55_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_55_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_55_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_55_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_56_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_56_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_56_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_56_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.00s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_57_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_57_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_57_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_57_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_58_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_58_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_58_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_58_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_59_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_59_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_59_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_59_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_60_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_60_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_60_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_60_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_61_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_61_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_61_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_61_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_62_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_62_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_62_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_62_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_63_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and BLOOMBG2 to RODESSA2 69kV line CKT 1 and HOSSTON2 to GODFREYRDTP2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.24pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_63_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and BLOOMBG2 to RODESSA2 69kV line CKT 1 and HOSSTON2 to GODFREYRDTP2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_63_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and BLOOMBG2 to RODESSA2 69kV line CKT 1 and HOSSTON2 to GODFREYRDTP2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.24pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_63_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and BLOOMBG2 to RODESSA2 69kV line CKT 1 and HOSSTON2 to GODFREYRDTP2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed :MaxV: 1.24pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_64_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and GILLIAM2 to HOSSTON2 69kV line CKT 1 and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_64_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and GILLIAM2 to HOSSTON2 69kV line CKT 1 and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.26pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_64_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and GILLIAM2 to HOSSTON2 69kV line CKT 1 and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed :MaxV: 1.25pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_64_P4_HOSSTON2 | Apply single-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 16 cycles with stuck breaker at HOSSTON2. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and GILLIAM2 to HOSSTON2 69kV line CKT 1 and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.25pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_65_P4_NBENTON4 | Apply single-phase fault on NBENTON2 69kV/138kV/13.19kV transformer CKT 1, near NBENTON4 138kV for 16 cycles with stuck breaker at NBENTON4. Open the faulted Three Winding and LINTNRD4 to NBENTON4 138kV line CKT 1 and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_65_P4_NBENTON4 | Apply single-phase fault on NBENTON2 69kV/138kV/13.19kV transformer CKT 1, near NBENTON4 138kV for 16 cycles with stuck breaker at NBENTON4. Open the faulted Three Winding and LINTNRD4 to NBENTON4 138kV line CKT 1 and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.22pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_65_P4_NBENTON4 | Apply single-phase fault on NBENTON2 69kV/138kV/13.19kV transformer CKT 1, near NBENTON4 138kV for 16 cycles with stuck breaker at NBENTON4. Open the faulted Three Winding and LINTNRD4 to NBENTON4 138kV line CKT 1 and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_65_P4_NBENTON4 | Apply single-phase fault on NBENTON2 69kV/138kV/13.19kV transformer CKT 1, near NBENTON4 138kV for 16 cycles with stuck breaker at NBENTON4. Open the faulted Three Winding and LINTNRD4 to NBENTON4 138kV line CKT 1 and RDPOINT4 to DEENPNT4 138kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_66_P4_SUPEROR2 | Apply single-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 16 cycles with stuck breaker at SUPEROR2. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and OILCITY2 to SUPEROR2 69kV line CKT 1 and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.28pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_66_P4_SUPEROR2 | Apply single-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 16 cycles with stuck breaker at SUPEROR2. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and OILCITY2 to SUPEROR2 69kV line CKT 1 and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.29pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_66_P4_SUPEROR2 | Apply single-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 16 cycles with stuck breaker at SUPEROR2. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and OILCITY2 to SUPEROR2 69kV line CKT 1 and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.28pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_66_P4_SUPEROR2 | Apply single-phase fault on SUPEROR2 to JEFFRSN2 69kV line CKT 1, near SUPEROR2 69kV for 16 cycles with stuck breaker at SUPEROR2. Open the faulted line and JEFFRSN2 to WOODLWN2 69kV line CKT 1 and OILCITY2 to SUPEROR2 69kV line CKT 1 and LIEBERM2 to OILCITY2 69kV line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed :MaxV: 1.28pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_67_P6_ARSHILL4 | Prior Outage of ARSHILL4 to FTHUMBG4 138kV line CKT 1Apply 3-phase fault on ARSHILL4 to MCWILLI4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_67_P6_ARSHILL4 | Prior Outage of ARSHILL4 to FTHUMBG4 138kV line CKT 1Apply 3-phase fault on ARSHILL4 to MCWILLI4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_67_P6_ARSHILL4 | Prior Outage of ARSHILL4 to FTHUMBG4 138kV line CKT 1Apply 3-phase fault on ARSHILL4 to MCWILLI4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_67_P6_ARSHILL4 | Prior Outage of ARSHILL4 to FTHUMBG4 138kV line CKT 1Apply 3-phase fault on ARSHILL4 to MCWILLI4 138kV line CKT 1, near ARSHILL4 138kV for 7 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_68_P6_HOSSTON2 | Prior Outage of HOSSTON2 to GODFREYRDTP2 69kV line CKT 1Prior Outage of BLOOMBG2 to RODESSA2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.22pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_68_P6_HOSSTON2 | Prior Outage of HOSSTON2 to GODFREYRDTP2 69kV line CKT 1Prior Outage of BLOOMBG2 to RODESSA2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.23pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_68_P6_HOSSTON2 | Prior Outage of HOSSTON2 to GODFREYRDTP2 69kV line CKT 1Prior Outage of BLOOMBG2 to RODESSA2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.22pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_68_P6_HOSSTON2 | Prior Outage of HOSSTON2 to GODFREYRDTP2 69kV line CKT 1Prior Outage of BLOOMBG2 to RODESSA2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to PLAINDL2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and NBENTON2 to MOTT TP2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open NBENTON2 to MOTT TP2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed :- MaxV: 1.22pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_69_P6_HOSSTON2 | Prior Outage of HOSSTON2 to VIVIAN 2 69kV line CKT 1Prior Outage of SUPEROR2 to VIVIAN 2 69kV line CKT 1Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.33pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_69_P6_HOSSTON2 | Prior Outage of HOSSTON2 to VIVIAN 2 69kV line CKT 1Prior Outage of SUPEROR2 to VIVIAN 2 69kV line CKT 1Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Vltage spike observed : MaxV: 1.24pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_69_P6_HOSSTON2 | Prior Outage of HOSSTON2 to VIVIAN 2 69kV line CKT 1Prior Outage of SUPEROR2 to VIVIAN 2 69kV line CKT 1Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed :MaxV: 1.33pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_69_P6_HOSSTON2 | Prior Outage of HOSSTON2 to VIVIAN 2 69kV line CKT 1Prior Outage of SUPEROR2 to VIVIAN 2 69kV line CKT 1Apply 3-phase fault on GILLIAM2 to HOSSTON2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and GILLIAM2 to SUPEROR2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open GILLIAM2 to SUPEROR2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.33pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_70_P6_HOSSTON2 | Prior Outage of HOSSTON2 to PLAINDL2 69kV line CKT 1Prior Outage of NBENTON2 to MOTT TP2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.20pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_70_P6_HOSSTON2 | Prior Outage of HOSSTON2 to PLAINDL2 69kV line CKT 1Prior Outage of NBENTON2 to MOTT TP2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes | Voltage spike observed : MaxV: 1.21pu, MaxDur: 0.01s
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_70_P6_HOSSTON2 | Prior Outage of HOSSTON2 to PLAINDL2 69kV line CKT 1Prior Outage of NBENTON2 to MOTT TP2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_70_P6_HOSSTON2 | Prior Outage of HOSSTON2 to PLAINDL2 69kV line CKT 1Prior Outage of NBENTON2 to MOTT TP2 69kV line CKT 1Apply 3-phase fault on HOSSTON2 to VIVIAN 2 69kV line CKT 1, near HOSSTON2 69kV for 7 cycles. Open the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. Wait 20 cycles. Re-close the faulted line and SUPEROR2 to VIVIAN 2 69kV line CKT 1. Re-open the faulted line after 7 cycles. Simultaneously re-open SUPEROR2 to VIVIAN 2 69kV line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 19W | Transfer | FLT_71_P6_LONGWD7 | Prior Outage of LONGWD 7 to WILKES 7 345kV line CKT 1Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21L | Transfer | FLT_71_P6_LONGWD7 | Prior Outage of LONGWD 7 to WILKES 7 345kV line CKT 1Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 21S | Transfer | FLT_71_P6_LONGWD7 | Prior Outage of LONGWD 7 to WILKES 7 345kV line CKT 1Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes
South | 10 - Southeast Oklahoma/Northeast Texas | 28S | Transfer | FLT_71_P6_LONGWD7 | Prior Outage of LONGWD 7 to WILKES 7 345kV line CKT 1Apply 3-phase fault on SW SHV 7 to LONGWD 7 345kV line CKT 1, near LONGWD 7 345kV for 6 cycles. Clear fault by tripping the faulted line. Wait 20 cycles. Re-close the faulted line. Re-open the faulted line after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | NO | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT44-3PH | 3 Phase fault on FARMNGTN 5 (504020) 161 kV Bus a. Apply fault at the FARMNGTN 5 (504020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARMNGTN 5 (504020) 161.0 kV to FARM_1 2 (504021) 69.0 kV to FARM_T1 1 (504022) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT36-3PH | 3 Phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILOAM-1 (506917) 13.2 kV to SILOAM 5 (506948) 161.0 kV to SILOAM 2 (506973) 69.0 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | NO | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT55-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT56-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT63-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT67-PO | Prior Outage: DARDANE5 (505508) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit 3 Phase Fault on DARDANE5 (505508) 161 kV Bus a. Apply fault at the DARDANE5 (505508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RUSSELVL.S (337904) 161.0 kV to 5RUSSELVL.E! (337905) 161.0 kV Transmission Circuit b.2. 5RUSSELVL.S (337904) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit b.3. 5DARDANELLE (337903) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit b.4. 5DANVLE AR! (337902) 161.0 kV to 5DARDANELLE (337903) 161.0 kV Transmission Circuit b.5. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT48-PO | Prior Outage: GREC TAP5 (512865) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT78-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT76-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT74-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT29-PO | Prior Outage: CAR395 5 (547485) 161.0 kV to Trip Bus PUR421 5 (547491) 161.0 kV to Trip Bus 3 Phase Fault on ASB349 5 (547476) 161 kV Bus a. Apply fault at the ASB349 5 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT4-3PH | 3 Phase fault on LAR382 5 (547479) 161 kV Bus a. Apply fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT1-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on CARTHAG5 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT2-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on SPRGFLD5 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT65-SB | Single Phase Fault with Stuck Breaker on DARDANE5 (505508) 161 kV Bus a. Apply Fault at the DARDANE5 (505508) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DARDANE5 (505508) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT21-SB | Single Phase Fault with Stuck Breaker on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT62-SB | Single Phase Fault with Stuck Breaker on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT27-SB | Single Phase Fault with Stuck Breaker on ASB349 5 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 19W | Transfer | G12_FLT64-SB | Single Phase Fault with Stuck Breaker on FIREWHL-TAP (588839) 345 kV Bus a. Apply Fault at the FIREWHL-TAP (588839) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIREWHL-TAP (588839) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT44-3PH | 3 Phase fault on FARMNGTN 5 (504020) 161 kV Bus a. Apply fault at the FARMNGTN 5 (504020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARMNGTN 5 (504020) 161.0 kV to FARM_1 2 (504021) 69.0 kV to FARM_T1 1 (504022) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT55-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT56-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT63-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT48-PO | Prior Outage: GREC TAP5 (512865) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT78-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | NO | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT76-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | NO | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT74-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | NO | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT29-PO | Prior Outage: CAR395 5 (547485) 161.0 kV to Trip Bus PUR421 5 (547491) 161.0 kV to Trip Bus 3 Phase Fault on ASB349 5 (547476) 161 kV Bus a. Apply fault at the ASB349 5 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT30-PO | Prior Outage: LITCH 5 (532932) 161.0 kV to ASB349 5 (547476) 161.0 kV Transmission Circuit 3 Phase Fault on ASB349 5 (547476) 161 kV Bus a. Apply fault at the ASB349 5 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT4-3PH | 3 Phase fault on LAR382 5 (547479) 161 kV Bus a. Apply fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | NO | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT1-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on CARTHAG5 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT2-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on SPRGFLD5 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT21-SB | Single Phase Fault with Stuck Breaker on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT62-SB | Single Phase Fault with Stuck Breaker on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21L | Transfer | G12_FLT27-SB | Single Phase Fault with Stuck Breaker on ASB349 5 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT44-3PH | 3 Phase fault on FARMNGTN 5 (504020) 161 kV Bus a. Apply fault at the FARMNGTN 5 (504020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARMNGTN 5 (504020) 161.0 kV to FARM_1 2 (504021) 69.0 kV to FARM_T1 1 (504022) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT36-3PH | 3 Phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILOAM-1 (506917) 13.2 kV to SILOAM 5 (506948) 161.0 kV to SILOAM 2 (506973) 69.0 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | NO | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT15-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV TwoWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT55-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT56-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT63-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT67-PO | Prior Outage: DARDANE5 (505508) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit 3 Phase Fault on DARDANE5 (505508) 161 kV Bus a. Apply fault at the DARDANE5 (505508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RUSSELVL.S (337904) 161.0 kV to 5RUSSELVL.E! (337905) 161.0 kV Transmission Circuit b.2. 5RUSSELVL.S (337904) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit b.3. 5DARDANELLE (337903) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit b.4. 5DANVLE AR! (337902) 161.0 kV to 5DARDANELLE (337903) 161.0 kV Transmission Circuit b.5. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT16-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOG4G (515223) 18.0 kV to MUSKOGE7 (515224) 345.0 kV TwoWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT78-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT76-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT74-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT29-PO | Prior Outage: CAR395 5 (547485) 161.0 kV to Trip Bus PUR421 5 (547491) 161.0 kV to Trip Bus 3 Phase Fault on ASB349 5 (547476) 161 kV Bus a. Apply fault at the ASB349 5 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT4-3PH | 3 Phase fault on LAR382 5 (547479) 161 kV Bus a. Apply fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | NO | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT1-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on CARTHAG5 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT2-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on SPRGFLD5 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT18-SB | Single Phase Fault with Stuck Breaker on CARTHAG5 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | NO | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT65-SB | Single Phase Fault with Stuck Breaker on DARDANE5 (505508) 161 kV Bus a. Apply Fault at the DARDANE5 (505508) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DARDANE5 (505508) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT21-SB | Single Phase Fault with Stuck Breaker on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT62-SB | Single Phase Fault with Stuck Breaker on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT26-SB | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT27-SB | Single Phase Fault with Stuck Breaker on ASB349 5 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT64-SB | Single Phase Fault with Stuck Breaker on FIREWHL-TAP (588839) 345 kV Bus a. Apply Fault at the FIREWHL-TAP (588839) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIREWHL-TAP (588839) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 21S | Transfer | G12_FLT48-PO | Prior Outage: GREC TAP5 (512865) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT44-3PH | 3 Phase fault on FARMNGTN 5 (504020) 161 kV Bus a. Apply fault at the FARMNGTN 5 (504020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARMNGTN 5 (504020) 161.0 kV to FARM_1 2 (504021) 69.0 kV to FARM_T1 1 (504022) 13.8 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT36-3PH | 3 Phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILOAM-1 (506917) 13.2 kV to SILOAM 5 (506948) 161.0 kV to SILOAM 2 (506973) 69.0 kV ThreeWinding | P1 | Stable | Yes | Yes | Yes | NO | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT15-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV TwoWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT55-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT56-SB | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit b.2. R.S.S.-7 (509782) 345.0 kV to RSS T2 4 (509875) 138.0 kV to RSST2 T1 (509876) 13.8 kV ThreeWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT63-PO | Prior Outage: R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit 3 Phase Fault on REDBUD 7 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT67-PO | Prior Outage: DARDANE5 (505508) 161.0 kV to CLARKSV5 (505514) 161.0 kV Transmission Circuit 3 Phase Fault on DARDANE5 (505508) 161 kV Bus a. Apply fault at the DARDANE5 (505508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RUSSELVL.S (337904) 161.0 kV to 5RUSSELVL.E! (337905) 161.0 kV Transmission Circuit b.2. 5RUSSELVL.S (337904) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit b.3. 5DARDANELLE (337903) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit b.4. 5DANVLE AR! (337902) 161.0 kV to 5DARDANELLE (337903) 161.0 kV Transmission Circuit b.5. 5HILLTOP% (338110) 161.0 kV to DARDANE5 (505508) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT16-SB | Single Phase Fault with Stuck Breaker on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FIREWHL-TAP (588839) 345.0 kV Transmission Circuit b.2. MUSKOG4G (515223) 18.0 kV to MUSKOGE7 (515224) 345.0 kV TwoWinding | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT48-PO | Prior Outage: GREC TAP5 (512865) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit 3 Phase Fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT78-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT76-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT74-PO | Prior Outage: 3 Phase Fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-009-TAP (588544) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT29-PO | Prior Outage: CAR395 5 (547485) 161.0 kV to Trip Bus PUR421 5 (547491) 161.0 kV to Trip Bus 3 Phase Fault on ASB349 5 (547476) 161 kV Bus a. Apply fault at the ASB349 5 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT4-3PH | 3 Phase fault on LAR382 5 (547479) 161 kV Bus a. Apply fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | Yes | Yes | NO | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT1-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on CARTHAG5 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT2-PO | Prior Outage: LAR382 5 (547479) 161.0 kV to GEN-2017-060 (588980) 161.0 kV Transmission Circuit 3 Phase Fault on SPRGFLD5 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT18-SB | Single Phase Fault with Stuck Breaker on CARTHAG5 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | NO | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT65-SB | Single Phase Fault with Stuck Breaker on DARDANE5 (505508) 161 kV Bus a. Apply Fault at the DARDANE5 (505508) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DARDANE5 (505508) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT21-SB | Single Phase Fault with Stuck Breaker on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT62-SB | Single Phase Fault with Stuck Breaker on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT26-SB | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT27-SB | Single Phase Fault with Stuck Breaker on ASB349 5 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 12 - Northwest Arkansas | 28S | Transfer | G12_FLT64-SB | Single Phase Fault with Stuck Breaker on FIREWHL-TAP (588839) 345 kV Bus a. Apply Fault at the FIREWHL-TAP (588839) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIREWHL-TAP (588839) 345.0 kV Trip Bus | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT1-3PH | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT2-3PH | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT3-3PH | 3 Phase fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT5-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT6-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT8-3PH | 3 Phase fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT10-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT11-3PH | 3 Phase fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT12-3PH | 3 Phase fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT13-3PH | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT14-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT15-3PH | 3 Phase fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT16-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT17-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT18-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT19-3PH | 3 Phase fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 11 (541150) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT20-3PH | 3 Phase fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN1 (541402) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT21-3PH | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASH T11 (543640) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT22-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT23-3PH | 3 Phase fault on LAKE RD5 (541255) 161 kV Bus a. Apply fault at the LAKE RD5 (541255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKE RD5 (541255) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT24-3PH | 3 Phase fault on ST JOE 5 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT25-3PH | 3 Phase fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT26-3PH | 3 Phase fault on GRNWD 5 (541218) 161 kV Bus a. Apply fault at the GRNWD 5 (541218) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT27-3PH | 3 Phase fault on PHILL 5 (541225) 161 kV Bus a. Apply fault at the PHILL 5 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKWINGB5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit b.2. PHILL 5 (541225) 161.0 kV to LKWINGB5 (541243) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT28-3PH | 3 Phase fault on BELTONS5 (541340) 161 kV Bus a. Apply fault at the BELTONS5 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT29-3PH | 3 Phase fault on STILWEL5 (542969) 161 kV Bus a. Apply fault at the STILWEL5 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT30-3PH | 3 Phase fault on STILWEL5 (542969) 161 kV Bus a. Apply fault at the STILWEL5 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTIOCH5 (543050) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT31-3PH | 3 Phase fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 5BUTLER (301342) 161.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT32-3PH | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2BUTLERE (300690) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT33-3PH | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2CRESTH (300697) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT34-3PH | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2PL GAP (300707) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT35-3PH | 3 Phase fault on HSNVL 5 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 5 (541239) 161.0 kV to HSNVL 2 (541295) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT36-3PH | 3 Phase fault on HSNVL 5 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SHARSNV (300709) 69.0 kV to HSNVL 5 (541239) 161.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT37-3PH | 3 Phase fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to S.HARP 2 (541343) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT38-3PH | 3 Phase fault on NEVADA 5 (541208) 161 kV Bus a. Apply fault at the NEVADA 5 (541208) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVADA 5 (541208) 161.0 kV to NEVADA 2 (541308) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT39-3PH | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT40-3PH | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT41-3PH | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT42-3PH | 3 Phase fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL T (541361) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT43-3PH | 3 Phase fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT44-3PH | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT45-3PH | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT46-3PH | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT47-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT48-3PH | 3 Phase fault on PHILL 5 (541225) 161 kV Bus a. Apply fault at the PHILL 5 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT49-3PH | 3 Phase fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT50-3PH | 3 Phase fault on 5CLARK (300070) 161 kV Bus a. Apply fault at the 5CLARK (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT51-3PH | 3 Phase fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT52-3PH | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULRT (541372) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT53-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STIL T22 (543648) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT54-3PH | 3 Phase fault on HOLT 7 (541510) 345 kV Bus a. Apply fault at the HOLT 7 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT55-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT56-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT57-3PH | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT58-3PH | 3 Phase fault on 5THMHLB3 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 (300133) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT59-3PH | 3 Phase fault on 5MOBERLY (345221) 161 kV Bus a. Apply fault at the 5MOBERLY (345221) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT60-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT61-3PH | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT62-3PH | 3 Phase fault on G17-004-TAP (588494) 345 kV Bus a. Apply fault at the G17-004-TAP (588494) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT63-3PH | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT64-3PH | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT65-3PH | 3 Phase fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT66-3PH | 3 Phase fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT1-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit 3 Phase Fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT2-PO | Prior Outage: EASTOWN1 (541402) 13.8 kV to Trip Bus 3 Phase Fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT3-PO | Prior Outage: IATAN 11 (541150) 13.8 kV to Trip Bus 3 Phase Fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT4-PO | Prior Outage: NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit 3 Phase Fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT6-PO | Prior Outage: IATAN 11 (541150) 13.8 kV to Trip Bus 3 Phase Fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT7-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit 3 Phase Fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT8-PO | Prior Outage: NASH T11 (543640) 13.8 kV to Trip Bus 3 Phase Fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT10-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit 3 Phase Fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT13-PO | Prior Outage: ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit 3 Phase Fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT14-PO | Prior Outage: ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit 3 Phase Fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT15-PO | Prior Outage: ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit 3 Phase Fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT16-PO | Prior Outage: 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit 3 Phase Fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 589283: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION 589287: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION |  |  |  |  | 11 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.804 pu
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT17-PO | Prior Outage: S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit 3 Phase Fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT18-PO | Prior Outage: PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT19-PO | Prior Outage: PECULRT (541372) 13.8 kV to Trip Bus 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT20-PO | Prior Outage: STIL T22 (543648) 13.8 kV to Trip Bus 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULRT (541372) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT21-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT22-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT23-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT24-PO | Prior Outage: STIL T11 (543647) 13.8 kV to Trip Bus 3 Phase Fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STIL T22 (543648) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT25-PO | Prior Outage: PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL T (541361) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT26-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT27-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT28-PO | Prior Outage: COOPER 3 (640139) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit 3 Phase Fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT29-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit 3 Phase Fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to 7FAIRPT (300039) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT30-PO | Prior Outage: MC REAC1 (541411) 345.0 kV to Trip Bus MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit MC REAC2 (541412) 345.0 kV to Trip Bus 3 Phase Fault on HOLT_REACT7 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit b.2. HOLT_REACT7 (541517) 345.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT31-PO | Prior Outage: HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit 3 Phase Fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT32-PO | Prior Outage: SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit 3 Phase Fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT33-PO | Prior Outage: 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit 3 Phase Fault on SIB REA1 (541414) 345 kV Bus a. Apply fault at the SIB REA1 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIB REA1 (541414) 345.0 kV to Trip Bus b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT35-PO | Prior Outage: STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit 3 Phase Fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT36-PO | Prior Outage: HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit 3 Phase Fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT37-PO | Prior Outage: STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit 3 Phase Fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT38-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT39-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit 3 Phase Fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT40-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT41-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT42-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT43-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit 3 Phase Fault on 87TH 7 (532775) 345 kV Bus a. Apply fault at the 87TH 7 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT44-PO | Prior Outage: 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit 3 Phase Fault on BRUNSWK5 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit b.2. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT45-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT46-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT47-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT48-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT49-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT50-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT51-PO | Prior Outage: NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit 3 Phase Fault on EMANHAT6 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT52-PO | Prior Outage: SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit 3 Phase Fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT53-PO | Prior Outage: MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit 3 Phase Fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT55-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT56-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT57-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT58-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT61-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | NO | YES |  | REDUCE WOLFCREEK TO 1100 MW |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT62-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | NO | YES |  | REDUCE WOLFCREEK TO 1100 MW |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT63-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT64-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT65-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT66-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT67-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT68-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT69-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT70-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT71-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT72-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT73-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | NO | YES |  | REDUCE WOLFCREEK TO 1100 MW |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT74-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | NO | YES |  | REDUCE WOLFCREEK TO 1100 MW |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT6-SB | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT10-SB | Single Phase Fault with Stuck Breaker on PECULR 5 (541342) 161 kV Bus a. Apply Fault at the PECULR 5 (541342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT11-SB | Single Phase Fault with Stuck Breaker on STILWEL5 (542969) 161 kV Bus a. Apply Fault at the STILWEL5 (542969) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT12-SB | Single Phase Fault with Stuck Breaker on 5CLARK (300070) 161 kV Bus a. Apply Fault at the 5CLARK (300070) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLARK (300070) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT13-SB | Single Phase Fault with Stuck Breaker on 5CLINTN (300071) 161 kV Bus a. Apply Fault at the 5CLINTN (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.866 pu
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT14-SB | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT15-SB | Single Phase Fault with Stuck Breaker on ARCHIE 5 (541207) 161 kV Bus a. Apply Fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCHIE 5 (541207) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT16-SB | Single Phase Fault with Stuck Breaker on 5BUTLER (301342) 161 kV Bus a. Apply Fault at the 5BUTLER (301342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BUTLER (301342) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT17-SB | Single Phase Fault with Stuck Breaker on HSNVL 5 (541239) 161 kV Bus a. Apply Fault at the HSNVL 5 (541239) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVL 5 (541239) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT18-SB | Single Phase Fault with Stuck Breaker on S.HARP 5 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 5 (541341) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT19-SB | Single Phase Fault with Stuck Breaker on NEVADA 5 (541208) 161 kV Bus a. Apply Fault at the NEVADA 5 (541208) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVADA 5 (541208) 161.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 8 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.696 pu
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT21-SB | Single Phase Fault with Stuck Breaker on ST JOE 3 (541199) 345 kV Bus a. Apply Fault at the ST JOE 3 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 3 (541199) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT22-SB | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT23-SB | Single Phase Fault with Stuck Breaker on HOYT 7 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT24-SB | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT25-SB | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT26-SB | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT27-SB | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT28-SB | Single Phase Fault with Stuck Breaker on SALSBRY5 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALSBRY5 (543062) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT29-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT30-SB | Single Phase Fault with Stuck Breaker on NMANHT6 (532865) 230 kV Bus a. Apply Fault at the NMANHT6 (532865) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NMANHT6 (532865) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT31-SB | Single Phase Fault with Stuck Breaker on MORRIS 6 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT35-SB | Single Phase Fault with Stuck Breaker on PECULR 7 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV ThreeWinding b.3. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT36-SB | Single Phase Fault with Stuck Breaker on PHILL 7 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit b.2. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV ThreeWinding b.3. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT37-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT38-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT39-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT40-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT41-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT42-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT43-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding and remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT44-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT45-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT46-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 19W | Normal | G13_FLT47-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT1-3PH | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT2-3PH | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT3-3PH | 3 Phase fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT5-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT6-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT8-3PH | 3 Phase fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT10-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT11-3PH | 3 Phase fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT12-3PH | 3 Phase fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT13-3PH | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT14-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT15-3PH | 3 Phase fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT16-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT17-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT18-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT19-3PH | 3 Phase fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 11 (541150) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT20-3PH | 3 Phase fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN1 (541402) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT21-3PH | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASH T11 (543640) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT22-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT23-3PH | 3 Phase fault on LAKE RD5 (541255) 161 kV Bus a. Apply fault at the LAKE RD5 (541255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKE RD5 (541255) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT24-3PH | 3 Phase fault on ST JOE 5 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT25-3PH | 3 Phase fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT26-3PH | 3 Phase fault on GRNWD 5 (541218) 161 kV Bus a. Apply fault at the GRNWD 5 (541218) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT27-3PH | 3 Phase fault on PHILL 5 (541225) 161 kV Bus a. Apply fault at the PHILL 5 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKWINGB5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit b.2. PHILL 5 (541225) 161.0 kV to LKWINGB5 (541243) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT28-3PH | 3 Phase fault on BELTONS5 (541340) 161 kV Bus a. Apply fault at the BELTONS5 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT29-3PH | 3 Phase fault on STILWEL5 (542969) 161 kV Bus a. Apply fault at the STILWEL5 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT30-3PH | 3 Phase fault on STILWEL5 (542969) 161 kV Bus a. Apply fault at the STILWEL5 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTIOCH5 (543050) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT31-3PH | 3 Phase fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 5BUTLER (301342) 161.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT32-3PH | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2BUTLERE (300690) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT33-3PH | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2CRESTH (300697) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT34-3PH | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2PL GAP (300707) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT35-3PH | 3 Phase fault on HSNVL 5 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 5 (541239) 161.0 kV to HSNVL 2 (541295) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT36-3PH | 3 Phase fault on HSNVL 5 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SHARSNV (300709) 69.0 kV to HSNVL 5 (541239) 161.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT37-3PH | 3 Phase fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to S.HARP 2 (541343) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT38-3PH | 3 Phase fault on NEVADA 5 (541208) 161 kV Bus a. Apply fault at the NEVADA 5 (541208) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVADA 5 (541208) 161.0 kV to NEVADA 2 (541308) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT39-3PH | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT40-3PH | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT41-3PH | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT42-3PH | 3 Phase fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL T (541361) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT43-3PH | 3 Phase fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT44-3PH | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT45-3PH | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT46-3PH | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT47-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT48-3PH | 3 Phase fault on PHILL 5 (541225) 161 kV Bus a. Apply fault at the PHILL 5 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT49-3PH | 3 Phase fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT50-3PH | 3 Phase fault on 5CLARK (300070) 161 kV Bus a. Apply fault at the 5CLARK (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT51-3PH | 3 Phase fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT52-3PH | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULRT (541372) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT53-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STIL T22 (543648) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT54-3PH | 3 Phase fault on HOLT 7 (541510) 345 kV Bus a. Apply fault at the HOLT 7 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT55-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT56-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT57-3PH | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT58-3PH | 3 Phase fault on 5THMHLB3 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 (300133) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT59-3PH | 3 Phase fault on 5MOBERLY (345221) 161 kV Bus a. Apply fault at the 5MOBERLY (345221) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT60-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT61-3PH | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT62-3PH | 3 Phase fault on G17-004-TAP (588494) 345 kV Bus a. Apply fault at the G17-004-TAP (588494) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT63-3PH | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT64-3PH | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT65-3PH | 3 Phase fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT66-3PH | 3 Phase fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT1-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit 3 Phase Fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT2-PO | Prior Outage: EASTOWN1 (541402) 13.8 kV to Trip Bus 3 Phase Fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT3-PO | Prior Outage: IATAN 11 (541150) 13.8 kV to Trip Bus 3 Phase Fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT4-PO | Prior Outage: NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit 3 Phase Fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT6-PO | Prior Outage: IATAN 11 (541150) 13.8 kV to Trip Bus 3 Phase Fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT7-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit 3 Phase Fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT8-PO | Prior Outage: NASH T11 (543640) 13.8 kV to Trip Bus 3 Phase Fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT10-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit 3 Phase Fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT13-PO | Prior Outage: ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit 3 Phase Fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT14-PO | Prior Outage: ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit 3 Phase Fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT15-PO | Prior Outage: ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit 3 Phase Fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT16-PO | Prior Outage: 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit 3 Phase Fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT17-PO | Prior Outage: S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit 3 Phase Fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT18-PO | Prior Outage: PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT19-PO | Prior Outage: PECULRT (541372) 13.8 kV to Trip Bus 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT20-PO | Prior Outage: STIL T22 (543648) 13.8 kV to Trip Bus 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULRT (541372) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT21-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT22-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT23-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT24-PO | Prior Outage: STIL T11 (543647) 13.8 kV to Trip Bus 3 Phase Fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STIL T22 (543648) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT25-PO | Prior Outage: PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL T (541361) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT26-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT27-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT28-PO | Prior Outage: COOPER 3 (640139) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit 3 Phase Fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT29-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit 3 Phase Fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to 7FAIRPT (300039) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT30-PO | Prior Outage: MC REAC1 (541411) 345.0 kV to Trip Bus MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit MC REAC2 (541412) 345.0 kV to Trip Bus 3 Phase Fault on HOLT_REACT7 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit b.2. HOLT_REACT7 (541517) 345.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT31-PO | Prior Outage: HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit 3 Phase Fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT32-PO | Prior Outage: SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit 3 Phase Fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT33-PO | Prior Outage: 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit 3 Phase Fault on SIB REA1 (541414) 345 kV Bus a. Apply fault at the SIB REA1 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIB REA1 (541414) 345.0 kV to Trip Bus b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT35-PO | Prior Outage: STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit 3 Phase Fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT36-PO | Prior Outage: HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit 3 Phase Fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT37-PO | Prior Outage: STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit 3 Phase Fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT38-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT39-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit 3 Phase Fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT40-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT41-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT42-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT43-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit 3 Phase Fault on 87TH 7 (532775) 345 kV Bus a. Apply fault at the 87TH 7 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT44-PO | Prior Outage: 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit 3 Phase Fault on BRUNSWK5 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit b.2. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT45-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT46-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT47-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT48-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT49-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT50-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT51-PO | Prior Outage: NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit 3 Phase Fault on EMANHAT6 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT52-PO | Prior Outage: SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit 3 Phase Fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT53-PO | Prior Outage: MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit 3 Phase Fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT55-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT56-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT57-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT58-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT61-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT62-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT63-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT64-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT65-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT66-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT67-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT68-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT69-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT70-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT71-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT72-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT73-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT74-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT6-SB | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT10-SB | Single Phase Fault with Stuck Breaker on PECULR 5 (541342) 161 kV Bus a. Apply Fault at the PECULR 5 (541342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT11-SB | Single Phase Fault with Stuck Breaker on STILWEL5 (542969) 161 kV Bus a. Apply Fault at the STILWEL5 (542969) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT12-SB | Single Phase Fault with Stuck Breaker on 5CLARK (300070) 161 kV Bus a. Apply Fault at the 5CLARK (300070) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLARK (300070) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT13-SB | Single Phase Fault with Stuck Breaker on 5CLINTN (300071) 161 kV Bus a. Apply Fault at the 5CLINTN (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT14-SB | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT15-SB | Single Phase Fault with Stuck Breaker on ARCHIE 5 (541207) 161 kV Bus a. Apply Fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCHIE 5 (541207) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT16-SB | Single Phase Fault with Stuck Breaker on 5BUTLER (301342) 161 kV Bus a. Apply Fault at the 5BUTLER (301342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BUTLER (301342) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT17-SB | Single Phase Fault with Stuck Breaker on HSNVL 5 (541239) 161 kV Bus a. Apply Fault at the HSNVL 5 (541239) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVL 5 (541239) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT18-SB | Single Phase Fault with Stuck Breaker on S.HARP 5 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 5 (541341) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT19-SB | Single Phase Fault with Stuck Breaker on NEVADA 5 (541208) 161 kV Bus a. Apply Fault at the NEVADA 5 (541208) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVADA 5 (541208) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT21-SB | Single Phase Fault with Stuck Breaker on ST JOE 3 (541199) 345 kV Bus a. Apply Fault at the ST JOE 3 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 3 (541199) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT22-SB | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT23-SB | Single Phase Fault with Stuck Breaker on HOYT 7 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT24-SB | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT25-SB | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT26-SB | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT27-SB | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT28-SB | Single Phase Fault with Stuck Breaker on SALSBRY5 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALSBRY5 (543062) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT29-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT30-SB | Single Phase Fault with Stuck Breaker on NMANHT6 (532865) 230 kV Bus a. Apply Fault at the NMANHT6 (532865) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NMANHT6 (532865) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT31-SB | Single Phase Fault with Stuck Breaker on MORRIS 6 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT35-SB | Single Phase Fault with Stuck Breaker on PECULR 7 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV ThreeWinding b.3. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT36-SB | Single Phase Fault with Stuck Breaker on PHILL 7 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit b.2. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV ThreeWinding b.3. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT37-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT38-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT39-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT40-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT41-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT42-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT43-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding and remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT44-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT45-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT46-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21L | Normal | G13_FLT47-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT1-3PH | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT2-3PH | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT3-3PH | 3 Phase fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT5-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT6-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT8-3PH | 3 Phase fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT10-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT11-3PH | 3 Phase fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT12-3PH | 3 Phase fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT13-3PH | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT14-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT15-3PH | 3 Phase fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT16-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT17-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT18-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT19-3PH | 3 Phase fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 11 (541150) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT20-3PH | 3 Phase fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN1 (541402) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT21-3PH | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASH T11 (543640) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT22-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT23-3PH | 3 Phase fault on LAKE RD5 (541255) 161 kV Bus a. Apply fault at the LAKE RD5 (541255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKE RD5 (541255) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT24-3PH | 3 Phase fault on ST JOE 5 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT25-3PH | 3 Phase fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT26-3PH | 3 Phase fault on GRNWD 5 (541218) 161 kV Bus a. Apply fault at the GRNWD 5 (541218) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT27-3PH | 3 Phase fault on PHILL 5 (541225) 161 kV Bus a. Apply fault at the PHILL 5 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKWINGB5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit b.2. PHILL 5 (541225) 161.0 kV to LKWINGB5 (541243) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT28-3PH | 3 Phase fault on BELTONS5 (541340) 161 kV Bus a. Apply fault at the BELTONS5 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT29-3PH | 3 Phase fault on STILWEL5 (542969) 161 kV Bus a. Apply fault at the STILWEL5 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT30-3PH | 3 Phase fault on STILWEL5 (542969) 161 kV Bus a. Apply fault at the STILWEL5 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTIOCH5 (543050) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT31-3PH | 3 Phase fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 5BUTLER (301342) 161.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT32-3PH | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2BUTLERE (300690) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT33-3PH | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2CRESTH (300697) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT34-3PH | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2PL GAP (300707) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT35-3PH | 3 Phase fault on HSNVL 5 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 5 (541239) 161.0 kV to HSNVL 2 (541295) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT36-3PH | 3 Phase fault on HSNVL 5 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SHARSNV (300709) 69.0 kV to HSNVL 5 (541239) 161.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT37-3PH | 3 Phase fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to S.HARP 2 (541343) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT38-3PH | 3 Phase fault on NEVADA 5 (541208) 161 kV Bus a. Apply fault at the NEVADA 5 (541208) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVADA 5 (541208) 161.0 kV to NEVADA 2 (541308) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT39-3PH | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT40-3PH | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT41-3PH | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT42-3PH | 3 Phase fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL T (541361) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT43-3PH | 3 Phase fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT44-3PH | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT45-3PH | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT46-3PH | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT47-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT48-3PH | 3 Phase fault on PHILL 5 (541225) 161 kV Bus a. Apply fault at the PHILL 5 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT49-3PH | 3 Phase fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT50-3PH | 3 Phase fault on 5CLARK (300070) 161 kV Bus a. Apply fault at the 5CLARK (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT51-3PH | 3 Phase fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT52-3PH | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULRT (541372) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT53-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STIL T22 (543648) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT54-3PH | 3 Phase fault on HOLT 7 (541510) 345 kV Bus a. Apply fault at the HOLT 7 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT55-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT56-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT57-3PH | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT58-3PH | 3 Phase fault on 5THMHLB3 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 (300133) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT59-3PH | 3 Phase fault on 5MOBERLY (345221) 161 kV Bus a. Apply fault at the 5MOBERLY (345221) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT60-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT61-3PH | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT62-3PH | 3 Phase fault on G17-004-TAP (588494) 345 kV Bus a. Apply fault at the G17-004-TAP (588494) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT63-3PH | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT64-3PH | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT65-3PH | 3 Phase fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT66-3PH | 3 Phase fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT1-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit 3 Phase Fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT2-PO | Prior Outage: EASTOWN1 (541402) 13.8 kV to Trip Bus 3 Phase Fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT3-PO | Prior Outage: IATAN 11 (541150) 13.8 kV to Trip Bus 3 Phase Fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT4-PO | Prior Outage: NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit 3 Phase Fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT6-PO | Prior Outage: IATAN 11 (541150) 13.8 kV to Trip Bus 3 Phase Fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT7-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit 3 Phase Fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT8-PO | Prior Outage: NASH T11 (543640) 13.8 kV to Trip Bus 3 Phase Fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT10-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit 3 Phase Fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT13-PO | Prior Outage: ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit 3 Phase Fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT14-PO | Prior Outage: ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit 3 Phase Fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.878 pu
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT15-PO | Prior Outage: ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit 3 Phase Fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.881 pu
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT16-PO | Prior Outage: 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit 3 Phase Fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 589283: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION 589287: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION |  |  |  |  | 15 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.756 pu
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT17-PO | Prior Outage: S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit 3 Phase Fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT18-PO | Prior Outage: PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT19-PO | Prior Outage: PECULRT (541372) 13.8 kV to Trip Bus 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT20-PO | Prior Outage: STIL T22 (543648) 13.8 kV to Trip Bus 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULRT (541372) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT21-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT22-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT23-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT24-PO | Prior Outage: STIL T11 (543647) 13.8 kV to Trip Bus 3 Phase Fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STIL T22 (543648) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT25-PO | Prior Outage: PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL T (541361) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT26-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT27-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT28-PO | Prior Outage: COOPER 3 (640139) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit 3 Phase Fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT29-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit 3 Phase Fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to 7FAIRPT (300039) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT30-PO | Prior Outage: MC REAC1 (541411) 345.0 kV to Trip Bus MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit MC REAC2 (541412) 345.0 kV to Trip Bus 3 Phase Fault on HOLT_REACT7 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit b.2. HOLT_REACT7 (541517) 345.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT31-PO | Prior Outage: HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit 3 Phase Fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT32-PO | Prior Outage: SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit 3 Phase Fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT33-PO | Prior Outage: 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit 3 Phase Fault on SIB REA1 (541414) 345 kV Bus a. Apply fault at the SIB REA1 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIB REA1 (541414) 345.0 kV to Trip Bus b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT35-PO | Prior Outage: STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit 3 Phase Fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT36-PO | Prior Outage: HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit 3 Phase Fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT37-PO | Prior Outage: STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit 3 Phase Fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT38-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT39-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit 3 Phase Fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT40-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT41-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT42-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT43-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit 3 Phase Fault on 87TH 7 (532775) 345 kV Bus a. Apply fault at the 87TH 7 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT44-PO | Prior Outage: 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit 3 Phase Fault on BRUNSWK5 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit b.2. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT45-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT46-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT47-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT48-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT49-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT50-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT51-PO | Prior Outage: NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit 3 Phase Fault on EMANHAT6 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT52-PO | Prior Outage: SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit 3 Phase Fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT53-PO | Prior Outage: MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit 3 Phase Fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT55-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT56-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT57-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT58-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT61-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT62-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT63-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT64-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT65-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT66-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT67-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT68-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT69-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT70-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT71-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT72-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT73-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT74-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT6-SB | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT10-SB | Single Phase Fault with Stuck Breaker on PECULR 5 (541342) 161 kV Bus a. Apply Fault at the PECULR 5 (541342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT11-SB | Single Phase Fault with Stuck Breaker on STILWEL5 (542969) 161 kV Bus a. Apply Fault at the STILWEL5 (542969) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT12-SB | Single Phase Fault with Stuck Breaker on 5CLARK (300070) 161 kV Bus a. Apply Fault at the 5CLARK (300070) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLARK (300070) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT13-SB | Single Phase Fault with Stuck Breaker on 5CLINTN (300071) 161 kV Bus a. Apply Fault at the 5CLINTN (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.89 pu
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT14-SB | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT15-SB | Single Phase Fault with Stuck Breaker on ARCHIE 5 (541207) 161 kV Bus a. Apply Fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCHIE 5 (541207) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT16-SB | Single Phase Fault with Stuck Breaker on 5BUTLER (301342) 161 kV Bus a. Apply Fault at the 5BUTLER (301342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BUTLER (301342) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT17-SB | Single Phase Fault with Stuck Breaker on HSNVL 5 (541239) 161 kV Bus a. Apply Fault at the HSNVL 5 (541239) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVL 5 (541239) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT18-SB | Single Phase Fault with Stuck Breaker on S.HARP 5 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 5 (541341) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT19-SB | Single Phase Fault with Stuck Breaker on NEVADA 5 (541208) 161 kV Bus a. Apply Fault at the NEVADA 5 (541208) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVADA 5 (541208) 161.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 8 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.677 pu
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT21-SB | Single Phase Fault with Stuck Breaker on ST JOE 3 (541199) 345 kV Bus a. Apply Fault at the ST JOE 3 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 3 (541199) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT22-SB | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT23-SB | Single Phase Fault with Stuck Breaker on HOYT 7 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT24-SB | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT25-SB | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT26-SB | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT27-SB | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT28-SB | Single Phase Fault with Stuck Breaker on SALSBRY5 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALSBRY5 (543062) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT29-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT30-SB | Single Phase Fault with Stuck Breaker on NMANHT6 (532865) 230 kV Bus a. Apply Fault at the NMANHT6 (532865) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NMANHT6 (532865) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT31-SB | Single Phase Fault with Stuck Breaker on MORRIS 6 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT35-SB | Single Phase Fault with Stuck Breaker on PECULR 7 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV ThreeWinding b.3. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT36-SB | Single Phase Fault with Stuck Breaker on PHILL 7 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit b.2. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV ThreeWinding b.3. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT37-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT38-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT39-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT40-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT41-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT42-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT43-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding and remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT44-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT45-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT46-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 21S | Normal | G13_FLT47-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT1-3PH | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT2-3PH | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT3-3PH | 3 Phase fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT5-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT6-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT8-3PH | 3 Phase fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT10-3PH | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT11-3PH | 3 Phase fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT12-3PH | 3 Phase fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT13-3PH | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT14-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT15-3PH | 3 Phase fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT16-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT17-3PH | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT18-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT19-3PH | 3 Phase fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 11 (541150) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT20-3PH | 3 Phase fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN1 (541402) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT21-3PH | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASH T11 (543640) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT22-3PH | 3 Phase fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT23-3PH | 3 Phase fault on LAKE RD5 (541255) 161 kV Bus a. Apply fault at the LAKE RD5 (541255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKE RD5 (541255) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT24-3PH | 3 Phase fault on ST JOE 5 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT25-3PH | 3 Phase fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT26-3PH | 3 Phase fault on GRNWD 5 (541218) 161 kV Bus a. Apply fault at the GRNWD 5 (541218) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT27-3PH | 3 Phase fault on PHILL 5 (541225) 161 kV Bus a. Apply fault at the PHILL 5 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKWINGB5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit b.2. PHILL 5 (541225) 161.0 kV to LKWINGB5 (541243) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT28-3PH | 3 Phase fault on BELTONS5 (541340) 161 kV Bus a. Apply fault at the BELTONS5 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT29-3PH | 3 Phase fault on STILWEL5 (542969) 161 kV Bus a. Apply fault at the STILWEL5 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT30-3PH | 3 Phase fault on STILWEL5 (542969) 161 kV Bus a. Apply fault at the STILWEL5 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTIOCH5 (543050) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT31-3PH | 3 Phase fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 5BUTLER (301342) 161.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT32-3PH | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2BUTLERE (300690) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT33-3PH | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2CRESTH (300697) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT34-3PH | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2PL GAP (300707) 69.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT35-3PH | 3 Phase fault on HSNVL 5 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 5 (541239) 161.0 kV to HSNVL 2 (541295) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT36-3PH | 3 Phase fault on HSNVL 5 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SHARSNV (300709) 69.0 kV to HSNVL 5 (541239) 161.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT37-3PH | 3 Phase fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to S.HARP 2 (541343) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT38-3PH | 3 Phase fault on NEVADA 5 (541208) 161 kV Bus a. Apply fault at the NEVADA 5 (541208) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVADA 5 (541208) 161.0 kV to NEVADA 2 (541308) 69.0 kV TwoWinding | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT39-3PH | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT40-3PH | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT41-3PH | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT42-3PH | 3 Phase fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL T (541361) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT43-3PH | 3 Phase fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT44-3PH | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT45-3PH | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT46-3PH | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT47-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT48-3PH | 3 Phase fault on PHILL 5 (541225) 161 kV Bus a. Apply fault at the PHILL 5 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT49-3PH | 3 Phase fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT50-3PH | 3 Phase fault on 5CLARK (300070) 161 kV Bus a. Apply fault at the 5CLARK (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT51-3PH | 3 Phase fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT52-3PH | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULRT (541372) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT53-3PH | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STIL T22 (543648) 13.8 kV Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT54-3PH | 3 Phase fault on HOLT 7 (541510) 345 kV Bus a. Apply fault at the HOLT 7 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT55-3PH | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT56-3PH | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT57-3PH | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT58-3PH | 3 Phase fault on 5THMHLB3 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 (300133) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT59-3PH | 3 Phase fault on 5MOBERLY (345221) 161 kV Bus a. Apply fault at the 5MOBERLY (345221) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT60-3PH | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT61-3PH | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT62-3PH | 3 Phase fault on G17-004-TAP (588494) 345 kV Bus a. Apply fault at the G17-004-TAP (588494) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT63-3PH | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT64-3PH | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT65-3PH | 3 Phase fault on NMANHT6 (532865) 230 kV Bus a. Apply fault at the NMANHT6 (532865) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT66-3PH | 3 Phase fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT1-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit 3 Phase Fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT2-PO | Prior Outage: EASTOWN1 (541402) 13.8 kV to Trip Bus 3 Phase Fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT3-PO | Prior Outage: IATAN 11 (541150) 13.8 kV to Trip Bus 3 Phase Fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT4-PO | Prior Outage: NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit 3 Phase Fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to G17-030-TAP (588736) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT6-PO | Prior Outage: IATAN 11 (541150) 13.8 kV to Trip Bus 3 Phase Fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT7-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit 3 Phase Fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT8-PO | Prior Outage: NASH T11 (543640) 13.8 kV to Trip Bus 3 Phase Fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT10-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit 3 Phase Fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit b.2. 7FAIRPT (300039) 345.0 kV to 5FAIRPT (300076) 161.0 kV TwoWinding b.3. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT13-PO | Prior Outage: ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit 3 Phase Fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STJOE 2T (541371) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT14-PO | Prior Outage: ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit 3 Phase Fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.86 pu
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT15-PO | Prior Outage: ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit 3 Phase Fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.862 pu
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT16-PO | Prior Outage: 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit 3 Phase Fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | NO | YES | YES | NO 589283: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION 589287: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION |  |  |  |  | 15 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.746 pu
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT17-PO | Prior Outage: S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit 3 Phase Fault on S.HARP 5 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT18-PO | Prior Outage: PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT19-PO | Prior Outage: PECULRT (541372) 13.8 kV to Trip Bus 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT20-PO | Prior Outage: STIL T22 (543648) 13.8 kV to Trip Bus 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULRT (541372) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT21-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT22-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT23-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT24-PO | Prior Outage: STIL T11 (543647) 13.8 kV to Trip Bus 3 Phase Fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STIL T22 (543648) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT25-PO | Prior Outage: PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL T (541361) 13.8 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT26-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT27-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT28-PO | Prior Outage: COOPER 3 (640139) 345.0 kV to ST JOE 3 (541199) 345.0 kV Transmission Circuit 3 Phase Fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 635020: MACHINE TRIPPED DUE TO UNDERVOLTAGE PROTECTION
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT29-PO | Prior Outage: ST JOE 3 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit 3 Phase Fault on ST JOE 3 (541199) 345 kV Bus a. Apply fault at the ST JOE 3 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 3 (541199) 345.0 kV to 7FAIRPT (300039) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT30-PO | Prior Outage: MC REAC1 (541411) 345.0 kV to Trip Bus MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit MC REAC2 (541412) 345.0 kV to Trip Bus 3 Phase Fault on HOLT_REACT7 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit b.2. HOLT_REACT7 (541517) 345.0 kV to Trip Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT31-PO | Prior Outage: HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit 3 Phase Fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT32-PO | Prior Outage: SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit 3 Phase Fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT33-PO | Prior Outage: 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit 3 Phase Fault on SIB REA1 (541414) 345 kV Bus a. Apply fault at the SIB REA1 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIB REA1 (541414) 345.0 kV to Trip Bus b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT35-PO | Prior Outage: STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit 3 Phase Fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT36-PO | Prior Outage: HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit 3 Phase Fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT37-PO | Prior Outage: STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit 3 Phase Fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT38-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT39-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit 3 Phase Fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT40-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT41-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT42-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT43-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit 3 Phase Fault on 87TH 7 (532775) 345 kV Bus a. Apply fault at the 87TH 7 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT44-PO | Prior Outage: 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit 3 Phase Fault on BRUNSWK5 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit b.2. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT45-PO | Prior Outage: NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT46-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT47-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | NO 589063: MACHINE TRIPPED DUE TO UNKNOWN |  |  |  |  | 28 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.328 pu
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT48-PO | Prior Outage: W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT49-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT50-PO | Prior Outage: STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT51-PO | Prior Outage: NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit 3 Phase Fault on EMANHAT6 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT52-PO | Prior Outage: SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit 3 Phase Fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT53-PO | Prior Outage: MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit 3 Phase Fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P6 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT55-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT56-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT57-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT58-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT61-PO | Prior Outage: WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT62-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT63-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT64-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT65-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT66-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT67-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT68-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT69-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT70-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT71-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT72-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT73-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT74-PO | Prior Outage: WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit 3 Phase Fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit | P6 | Stable | YES | YES | YES | YES | YES | YES |  |  |  |  | RECLOSING NOT STUDIED
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT6-SB | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT10-SB | Single Phase Fault with Stuck Breaker on PECULR 5 (541342) 161 kV Bus a. Apply Fault at the PECULR 5 (541342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT11-SB | Single Phase Fault with Stuck Breaker on STILWEL5 (542969) 161 kV Bus a. Apply Fault at the STILWEL5 (542969) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT12-SB | Single Phase Fault with Stuck Breaker on 5CLARK (300070) 161 kV Bus a. Apply Fault at the 5CLARK (300070) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLARK (300070) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT13-SB | Single Phase Fault with Stuck Breaker on 5CLINTN (300071) 161 kV Bus a. Apply Fault at the 5CLINTN (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 1 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.895 pu
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT14-SB | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT15-SB | Single Phase Fault with Stuck Breaker on ARCHIE 5 (541207) 161 kV Bus a. Apply Fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCHIE 5 (541207) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT16-SB | Single Phase Fault with Stuck Breaker on 5BUTLER (301342) 161 kV Bus a. Apply Fault at the 5BUTLER (301342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BUTLER (301342) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT17-SB | Single Phase Fault with Stuck Breaker on HSNVL 5 (541239) 161 kV Bus a. Apply Fault at the HSNVL 5 (541239) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVL 5 (541239) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT18-SB | Single Phase Fault with Stuck Breaker on S.HARP 5 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 5 (541341) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT19-SB | Single Phase Fault with Stuck Breaker on NEVADA 5 (541208) 161 kV Bus a. Apply Fault at the NEVADA 5 (541208) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVADA 5 (541208) 161.0 kV Trip Bus | P4 | Stable | YES | YES | NO | YES | YES | YES |  |  |  |  | 8 BUS/BUSES BELOW 0.9. LOWEST VOLTAGE 0.706 pu
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT21-SB | Single Phase Fault with Stuck Breaker on ST JOE 3 (541199) 345 kV Bus a. Apply Fault at the ST JOE 3 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 3 (541199) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT22-SB | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT23-SB | Single Phase Fault with Stuck Breaker on HOYT 7 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT24-SB | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT25-SB | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT26-SB | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT27-SB | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT28-SB | Single Phase Fault with Stuck Breaker on SALSBRY5 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALSBRY5 (543062) 161.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT29-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT30-SB | Single Phase Fault with Stuck Breaker on NMANHT6 (532865) 230 kV Bus a. Apply Fault at the NMANHT6 (532865) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NMANHT6 (532865) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT31-SB | Single Phase Fault with Stuck Breaker on MORRIS 6 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV Trip Bus | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT35-SB | Single Phase Fault with Stuck Breaker on PECULR 7 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV ThreeWinding b.3. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT36-SB | Single Phase Fault with Stuck Breaker on PHILL 7 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit b.2. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV ThreeWinding b.3. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT37-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT38-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT39-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT40-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT41-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT42-SB | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT43-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding and remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT44-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT45-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT46-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
Central | 13 - Northeast Kansas/Northwest Missouri | 28S | Normal | G13_FLT47-SB | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b.1. After 3.6 cycles, trip the WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV ThreeWinding b.2. After 6.6 additional cycles, remove fault | P4 | Stable | YES | YES | YES | YES | YES | YES
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | Angular and system instability was observed under this contingency only in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 19W | Base | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | reduce the fault clearing time to 4.5 cycles |  |  | HUGO1 (#520947) was unstable. The primary mitigation was applied and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | HUGO1 (#520947) was also unstable in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | reduce the fault clearing time to 5 cycles |  |  | HUGO1 (#520947) was unstable. The primary mitigation was applied and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | HUGO1 (#520947) was also unstable in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 21S | Base | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | reduce the fault clearing time to 5 cycles |  |  | HUGO1 (#520947) was unstable. The primary mitigation was applied and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | HUGO1 (#520947) was also unstable in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | reduce the fault clearing time to 5 cycles |  |  | HUGO1 (#520947) was unstable. The primary mitigation was applied and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 28S | Base | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | reduce the fault clearing time to 4.5 cycles |  |  | HUGO1 (#520947) was unstable. The primary mitigation was applied and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | N/A |  |  | HUGO1 (#520947) was also unstable in the SC. No mitigation action was performed in the sensitivity scenario for this contingency.
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Unstable | NO | NO | NO | NO | NO | NO |  | reduce the fault clearing time to 5 cycles |  |  | HUGO1 (#520947) was unstable. The primary mitigation was applied and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 19W | Base | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_01_P1_G16-063-TAP | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_02_P1_HUGO | Apply 3-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_03_P1_VALIANT7 | Apply 3-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_04_P1_HUGO | Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_05_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_05_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_05_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_05_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_05_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_05_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_05_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_05_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_05_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_05_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_05_P1_JOHNCO7 | Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_06_P1_VALIANT7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_07_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_08_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to SEMINOL7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_09_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_10_P1_SEMINOL7 | Apply 3-phase fault on DRAPER 7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_11_P1_SEMINOL7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_12_P1_SEMINOL7 | Apply 3-phase fault on ARCADIA7 to SEMINOL7 345kV transmission line CKT 1, near SEMINOL7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_13_P1_VALIANT7 | Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_14_P1_VALIANT7 | Apply 3-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_15_P1_LYDIA | Apply 3-phase fault on NWTXARK7 to LYDIA 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_16_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK7 to WELSH 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_17_P1_NWTXARK7 | Apply 3-phase fault on TURK to NWTXARK7 345kV transmission line CKT 1, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_18_P1_NWTXARK7 | Apply 3-phase fault on NWTXARK4 138kV/345kV/13.8kV transformer CKT 2, near NWTXARK7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_19_P1_LYDIA | Apply 3-phase fault on LYDIA to WELSH 345kV transmission line CKT 1, near LYDIA 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_20_P1_G16-063-TAP | Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_21_P1_SUNNYSD7 | Apply 3-phase fault on JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_22_P1_JOHNCO7 | Apply 3-phase fault on JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_23_P1_SUNNYSD7 | Apply 3-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_24_P1_SUNNYSD7 | Apply 3-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_25_P1_TERRYRD7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near TERRYRD7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G1140G1204G1[1] |  |  |  |  | G1140G1204G1 tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further issues were observed. However, 588183[G16-126-GEN] showed high frequency oscillation, which is likely due to a modelling issue. Since this is observed in BC, TC and SC, no action is taken.
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G1140G1204G1[1] |  |  |  |  | G1140G1204G1 tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further issues were observed. However, 588183[G16-126-GEN] showed high frequency oscillation, which is likely due to a modelling issue. Since this is observed in BC, TC and SC, no action is taken.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G1140G1204G1[1] |  |  |  |  | G1140G1204G1 tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further issues were observed. However, 588183[G16-126-GEN] showed high frequency oscillation, which is likely due to a modelling issue. Since this is observed in BC, TC and SC, no action is taken.
South | 14 - South Central Oklahoma | 21S | Base | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_26_P1_LES-7 | Apply 3-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G1140G1204G1[1] |  |  |  |  | G1140G1204G1 tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further issues were observed. However, 588183[G16-126-GEN] showed high frequency oscillation, which is likely due to a modelling issue. Since this is observed in BC, TC and SC, no action is taken.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_27_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_28_P1_LES-7 | Apply 3-phase fault on L.E.S.-4 138kV/345kV/13.8kV transformer CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G15-045-GEN1[1] |  |  |  |  | G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G15-045-GEN1[1] |  |  |  |  | G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G15-045-GEN1[1] |  |  |  |  | G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Base | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G15-045-GEN1[1] |  |  |  |  | G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G15-045-GEN1[1] |  |  |  |  | G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G15-045-GEN1[1] |  |  |  |  | G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21S | Base | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G15-045-GEN1[1] |  |  |  |  | G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G15-045-GEN1[1] |  |  |  |  | G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G15-045-GEN1[1] |  |  |  |  | G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 28S | Base | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G15-045-GEN1[1] |  |  |  |  | G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G15-045-GEN1[1] |  |  |  |  | G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_29_P1_RUSHSPR7 | Apply 3-phase fault on RUSHSPR7 345kV/34.5kV/13.8kV transformer CKT 1, near RUSHSPR7 345kV for 6 cycles. Clear fault by tripping the faulted Three Winding. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G15-045-GEN1[1] |  |  |  |  | G15-045-GEN1 tripped on undervoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 19W | Base | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_30_P1_GRACMNT7 | Apply 3-phase fault on MINCO to GRACMNT7 345kV transmission line CKT 1, near GRACMNT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_31_P1_HUGOPP4 | Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_32_P1_HUGOPP4 | Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_33_P1_FROGVIL4 | Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV transmission line CKT 1, near BENNGTN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV transmission line CKT 1, near BENNGTN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV transmission line CKT 1, near BENNGTN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV transmission line CKT 1, near BENNGTN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV transmission line CKT 1, near BENNGTN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV transmission line CKT 1, near BENNGTN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV transmission line CKT 1, near BENNGTN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV transmission line CKT 1, near BENNGTN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV transmission line CKT 1, near BENNGTN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV transmission line CKT 1, near BENNGTN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV transmission line CKT 1, near BENNGTN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_34_P1_BENNGTN4 | Apply 3-phase fault on BENNGTN4 to DURANTP4 138kV transmission line CKT 1, near BENNGTN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open S BROWN4 to KRSYJCTN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_35_P1_HUGOPP4 | Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BOGYDPT4 to BOGGY4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BOGYDPT4 to BOGGY4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BOGYDPT4 to BOGGY4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BOGYDPT4 to BOGGY4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BOGYDPT4 to BOGGY4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BOGYDPT4 to BOGGY4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BOGYDPT4 to BOGGY4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BOGYDPT4 to BOGGY4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BOGYDPT4 to BOGGY4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BOGYDPT4 to BOGGY4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BOGYDPT4 to BOGGY4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_36_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to ATKWEST4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BOGYDPT4 to BOGGY4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BOGYDPT4 to BOGGY4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TUPELO 4 to ALLENGT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TUPELO 4 to ALLENGT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TUPELO 4 to ALLENGT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TUPELO 4 to ALLENGT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TUPELO 4 to ALLENGT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TUPELO 4 to ALLENGT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TUPELO 4 to ALLENGT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TUPELO 4 to ALLENGT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TUPELO 4 to ALLENGT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TUPELO 4 to ALLENGT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TUPELO 4 to ALLENGT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_37_P1_ATOKA--4 | Apply 3-phase fault on ATOKA--4 to LEHIGH-4 138kV transmission line CKT 1, near ATOKA--4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close TUPELO 4 to ALLENGT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open TUPELO 4 to ALLENGT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_38_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to BOGGY4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV transmission line CKT 1, near BOGGY4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close WAPANUCKA to STNWLTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV transmission line CKT 1, near BOGGY4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close WAPANUCKA to STNWLTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV transmission line CKT 1, near BOGGY4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close WAPANUCKA to STNWLTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV transmission line CKT 1, near BOGGY4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close WAPANUCKA to STNWLTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV transmission line CKT 1, near BOGGY4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close WAPANUCKA to STNWLTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV transmission line CKT 1, near BOGGY4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close WAPANUCKA to STNWLTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV transmission line CKT 1, near BOGGY4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close WAPANUCKA to STNWLTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV transmission line CKT 1, near BOGGY4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close WAPANUCKA to STNWLTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV transmission line CKT 1, near BOGGY4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close WAPANUCKA to STNWLTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV transmission line CKT 1, near BOGGY4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close WAPANUCKA to STNWLTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV transmission line CKT 1, near BOGGY4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close WAPANUCKA to STNWLTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_39_P1_BOGGY4 | Apply 3-phase fault on WAPANUCKA to BOGGY4 138kV transmission line CKT 1, near BOGGY4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close WAPANUCKA to STNWLTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open WAPANUCKA to STNWLTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_40_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to STNWLSW4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_41_P1_TUPELO4 | Apply 3-phase fault on ALLEN to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_42_P1_TUPELO4 | Apply 3-phase fault on TUPELO 4 to TUPELO 4 138kV transmission line CKT 1, near TUPELO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_43_P1_VALIANT4 | Apply 3-phase fault on IDABEL-4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV transmission line CKT 1, near CLAYTON4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SARDIS 4 to ENOWILT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV transmission line CKT 1, near CLAYTON4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SARDIS 4 to ENOWILT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV transmission line CKT 1, near CLAYTON4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SARDIS 4 to ENOWILT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 21L | Base | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV transmission line CKT 1, near CLAYTON4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SARDIS 4 to ENOWILT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.44pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV transmission line CKT 1, near CLAYTON4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SARDIS 4 to ENOWILT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV transmission line CKT 1, near CLAYTON4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SARDIS 4 to ENOWILT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.44pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 21S | Base | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV transmission line CKT 1, near CLAYTON4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SARDIS 4 to ENOWILT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV transmission line CKT 1, near CLAYTON4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SARDIS 4 to ENOWILT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.44pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV transmission line CKT 1, near CLAYTON4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SARDIS 4 to ENOWILT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 28S | Base | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV transmission line CKT 1, near CLAYTON4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SARDIS 4 to ENOWILT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV transmission line CKT 1, near CLAYTON4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SARDIS 4 to ENOWILT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_44_P1_CLAYTON4 | Apply 3-phase fault on CLAYTON4 to SARDIS 4 138kV transmission line CKT 1, near CLAYTON4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SARDIS 4 to ENOWILT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SARDIS 4 to ENOWILT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | Voltage Spike: 1.43pu, MaxDur: 0.01s
South | 14 - South Central Oklahoma | 19W | Base | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV transmission line CKT 1, near CRAIGJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV transmission line CKT 1, near CRAIGJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV transmission line CKT 1, near CRAIGJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV transmission line CKT 1, near CRAIGJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV transmission line CKT 1, near CRAIGJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV transmission line CKT 1, near CRAIGJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV transmission line CKT 1, near CRAIGJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV transmission line CKT 1, near CRAIGJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV transmission line CKT 1, near CRAIGJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV transmission line CKT 1, near CRAIGJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV transmission line CKT 1, near CRAIGJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_45_P1_CRAIGJT4 | Apply 3-phase fault on CRAIGJT4 to MTRIVER4 138kV transmission line CKT 1, near CRAIGJT4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to MTRIVER4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV transmission line CKT 1, near BRKN BW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV transmission line CKT 1, near BRKN BW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV transmission line CKT 1, near BRKN BW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV transmission line CKT 1, near BRKN BW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV transmission line CKT 1, near BRKN BW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV transmission line CKT 1, near BRKN BW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV transmission line CKT 1, near BRKN BW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV transmission line CKT 1, near BRKN BW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV transmission line CKT 1, near BRKN BW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV transmission line CKT 1, near BRKN BW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV transmission line CKT 1, near BRKN BW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_46_P1_BRKNBW4 | Apply 3-phase fault on HOCHJCT4 to HOCHTWN4 138kV transmission line CKT 1, near BRKN BW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BRKN BW4 to HOCHTWN4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV transmission line CKT 1, near BROKNBW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV transmission line CKT 1, near BROKNBW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV transmission line CKT 1, near BROKNBW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV transmission line CKT 1, near BROKNBW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV transmission line CKT 1, near BROKNBW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV transmission line CKT 1, near BROKNBW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV transmission line CKT 1, near BROKNBW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV transmission line CKT 1, near BROKNBW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV transmission line CKT 1, near BROKNBW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV transmission line CKT 1, near BROKNBW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV transmission line CKT 1, near BROKNBW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_47_P1_BROKNBW4 | Apply 3-phase fault on BROKNBW4 to GOLDENSW4 138kV transmission line CKT 1, near BROKNBW4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HOCHJCT4 to DOMINJCT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROWNTP4 to STRRDTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROWNTP4 to STRRDTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROWNTP4 to STRRDTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROWNTP4 to STRRDTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROWNTP4 to STRRDTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROWNTP4 to STRRDTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROWNTP4 to STRRDTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROWNTP4 to STRRDTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROWNTP4 to STRRDTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROWNTP4 to STRRDTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROWNTP4 to STRRDTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_48_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to BROWN 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROWNTP4 to STRRDTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROWNTP4 to STRRDTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close RUSSET-4 to RUSSETT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close RUSSET-4 to RUSSETT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close RUSSET-4 to RUSSETT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close RUSSET-4 to RUSSETT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G16-030-GEN1[1] |  |  |  |  | G16-030-GEN1[1] tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close RUSSET-4 to RUSSETT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G16-030-GEN1[1] |  |  |  |  | G16-030-GEN1[1] tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close RUSSET-4 to RUSSETT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G16-030-GEN1[1] |  |  |  |  | G16-030-GEN1[1] tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21S | Base | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close RUSSET-4 to RUSSETT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close RUSSET-4 to RUSSETT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close RUSSET-4 to RUSSETT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close RUSSET-4 to RUSSETT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close RUSSET-4 to RUSSETT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_49_P1_SBROWN4 | Apply 3-phase fault on S BROWN4 to RUSSETT4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close RUSSET-4 to RUSSETT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close MADINDT4 to CANEYCK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close MADINDT4 to CANEYCK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close MADINDT4 to CANEYCK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close MADINDT4 to CANEYCK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close MADINDT4 to CANEYCK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close MADINDT4 to CANEYCK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close MADINDT4 to CANEYCK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close MADINDT4 to CANEYCK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close MADINDT4 to CANEYCK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close MADINDT4 to CANEYCK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close MADINDT4 to CANEYCK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_50_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to GLASSES4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close MADINDT4 to CANEYCK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open MADINDT4 to CANEYCK4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_51_P1_RUSSET-4 | Apply 3-phase fault on JOHNCO 4 to RUSSET-4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_52_P1_RUSSET-4 | Apply 3-phase fault on RUSSET-4 to STIRLNG4 138kV transmission line CKT 1, near RUSSET-4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SPRNDAL4 to DRPSPRG4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_53_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to CANEYCK4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV transmission line CKT 1, near SPRNDAL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FNDTION4 to CHIKSAW4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV transmission line CKT 1, near SPRNDAL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FNDTION4 to CHIKSAW4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV transmission line CKT 1, near SPRNDAL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FNDTION4 to CHIKSAW4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV transmission line CKT 1, near SPRNDAL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FNDTION4 to CHIKSAW4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV transmission line CKT 1, near SPRNDAL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FNDTION4 to CHIKSAW4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV transmission line CKT 1, near SPRNDAL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FNDTION4 to CHIKSAW4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV transmission line CKT 1, near SPRNDAL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FNDTION4 to CHIKSAW4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV transmission line CKT 1, near SPRNDAL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FNDTION4 to CHIKSAW4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV transmission line CKT 1, near SPRNDAL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FNDTION4 to CHIKSAW4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV transmission line CKT 1, near SPRNDAL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FNDTION4 to CHIKSAW4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV transmission line CKT 1, near SPRNDAL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FNDTION4 to CHIKSAW4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_54_P1_SPRNDAL4 | Apply 3-phase fault on FNDTION4 to SPRNDAL4 138kV transmission line CKT 1, near SPRNDAL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close FNDTION4 to CHIKSAW4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open FNDTION4 to CHIKSAW4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_55_P1_JOHNCO4 | Apply 3-phase fault on JOHNCO 4 to SXMLCKT4 138kV transmission line CKT 1, near JOHNCO 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ARBUCKL4 to MILLCKT4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_56_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_57_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to CHIKSAW4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_58_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close CARTER 4 to ARDWEST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_59_P1_CARTER4 | Apply 3-phase fault on CARTER 4 to HONEYCK4 138kV transmission line CKT 1, near CARTER 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_60_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to VANOSTP4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV transmission line CKT 1, near PARKLN 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VANOSS 4 to VANOSTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV transmission line CKT 1, near PARKLN 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VANOSS 4 to VANOSTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV transmission line CKT 1, near PARKLN 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VANOSS 4 to VANOSTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV transmission line CKT 1, near PARKLN 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VANOSS 4 to VANOSTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV transmission line CKT 1, near PARKLN 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VANOSS 4 to VANOSTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV transmission line CKT 1, near PARKLN 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VANOSS 4 to VANOSTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV transmission line CKT 1, near PARKLN 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VANOSS 4 to VANOSTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV transmission line CKT 1, near PARKLN 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VANOSS 4 to VANOSTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV transmission line CKT 1, near PARKLN 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VANOSS 4 to VANOSTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV transmission line CKT 1, near PARKLN 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VANOSS 4 to VANOSTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV transmission line CKT 1, near PARKLN 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VANOSS 4 to VANOSTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_61_P1_PARKLN4 | Apply 3-phase fault on VANOSS 4 to PARKLN 4 138kV transmission line CKT 1, near PARKLN 4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close VANOSS 4 to VANOSTP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open VANOSS 4 to VANOSTP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_62_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to PARKLN 4 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_63_P1_SEMINOL4 | Apply 3-phase fault on SEMINOL4 to MAUD 138kV transmission line CKT 1, near SEMINOL4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_64_P1_CARTRCO4 | Apply 3-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_65_P1_CARTRCO4 | Apply 3-phase fault on POOLVIL4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HLTNTAP4 to DILLARD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HLTNTAP4 to DILLARD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HLTNTAP4 to DILLARD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HLTNTAP4 to DILLARD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HLTNTAP4 to DILLARD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HLTNTAP4 to DILLARD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HLTNTAP4 to DILLARD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HLTNTAP4 to DILLARD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HLTNTAP4 to DILLARD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HLTNTAP4 to DILLARD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HLTNTAP4 to DILLARD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_66_P1_SUNNYSD4 | Apply 3-phase fault on SUNNYSD4 to LONEGRV4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close HLTNTAP4 to DILLARD4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open HLTNTAP4 to DILLARD4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV transmission line CKT 1, near RATLIFF4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV transmission line CKT 1, near RATLIFF4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV transmission line CKT 1, near RATLIFF4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV transmission line CKT 1, near RATLIFF4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV transmission line CKT 1, near RATLIFF4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV transmission line CKT 1, near RATLIFF4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV transmission line CKT 1, near RATLIFF4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV transmission line CKT 1, near RATLIFF4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV transmission line CKT 1, near RATLIFF4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV transmission line CKT 1, near RATLIFF4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV transmission line CKT 1, near RATLIFF4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_67_P1_RATLIFF4 | Apply 3-phase fault on RATLIFF4 to PRARPNT4 138kV transmission line CKT 1, near RATLIFF4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open SEMINOL4 to PAOLI- 4 138kV transmission line CKT 1 and clear the fault. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_68_P1_CARTRCO4 | Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_69_P1_OKU-7 | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near O.K.U.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_70_P1_TUCO_INT | Apply 3-phase fault on O.K.U.-7 to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_71_P1_TUCO_INT | Apply 3-phase fault on BORDER to TUCO_INT 345kV transmission line CKT 1, near TUCO_INT 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 21L | Base | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 28S | Base | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_72_P1_WHEELER | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near WHEELER 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 19W | Base | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 21L | Base | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 28S | Base | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_73_P1_SWEETWT6 | Apply 3-phase fault on WHEELER to SWEETWT6 230kV transmission line CKT 1, near SWEETWT6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 19W | Base | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 21L | Base | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 28S | Base | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_74_P1_POTTER_CO | Apply 3-phase fault on POTTER_CO to HITCHLAND 345kV transmission line CKT 1, near POTTER_CO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 19W | Base | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_75_P1_CHAN+TASCOS6 | Apply 3-phase fault on XIT_INTG to CHAN+TASCOS6 230kV transmission line CKT 1, near CHAN+TASCOS6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 21L | Base | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 28S | Base | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_76_P1_POTTER_CO | Apply 3-phase fault on MOORE_CNTY 6 to POTTER_CO 230kV transmission line CKT 1, near POTTER_CO 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 19W | Base | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 21L | Base | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 28S | Base | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_77_P1_HARRNG_EST6 | Apply 3-phase fault on PRINGLE to HARRNG_EST 6 230kV transmission line CKT 1, near HARRNG_EST 6 230kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - LANOGSU10.60[W1] |  |  |  |  | LANOGSU10.60[W1] tripped on undervoltage protection under several contingencies in both BC, TC and SC cases. Due to the size and location of the unit no further simulations was performed.
South | 14 - South Central Oklahoma | 19W | Base | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_78_P1_BADGER7 | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near BADGER 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_79_P1_G16-003-TAP | Apply 3-phase fault on BADGER 7 to G16-003-TAP 345kV transmission line CKT 1, near G16-003-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_80_P1_CARPENTER | Apply 3-phase fault on CARPENTER to FINNEY 345kV transmission line CKT 1, near CARPENTER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_81_P1_LES-7 | Apply 3-phase fault on L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_82_P1_MINCO | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near MINCO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_83_P1_CIMARON7 | Apply 3-phase fault on MINCO to CIMARON7 345kV transmission line CKT 1, near CIMARON7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_84_P1_TATONGA7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near TATONGA7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_85_P1_MATHWSN7 | Apply 3-phase fault on TATONGA7 to MATHWSN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_86_P1_WWRDEHV7 | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near WWRDEHV7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_87_P1_BORDER | Apply 3-phase fault on WWRDEHV7 to BORDER 345kV transmission line CKT 1, near BORDER 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_88_P1_SPRNGCK7 | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near SPRNGCK7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_89_P1_G16-100-TAP | Apply 3-phase fault on SPRNGCK7 to G16-100-TAP 345kV transmission line CKT 1, near G16-100-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | It was observed that POWR587300[G16-045-GEN30.6900]1, POWR587303[G16-045-GEN10.6900]1, POWR587307[G16-045-GEN20.6900]1 and POWR587380[G16-057-GEN30.6900]1 start reducing in the post-fault period, which seems like a modeling issue. Since this issue has occurred in the BC, it's considered as a pre-existing issue and no further action was taken.
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G16-045-GEN2[1] G16-057-GEN2[1] G16-045-GEN1[1] G16-057-GEN1[1] G16-045-GEN3[1] G16-057-GEN3[1] |  |  |  |  | G16-045-GEN2[1], G16-057-GEN2[1], G16-045-GEN1[1], G16-057-GEN1[1], G16-045-GEN3[1] and G16-057-GEN3[1] tripped on undervoltage protection.The protection was disabled and the simulation was rerun. No further tripping or stability issues were observed. However, some online units reduced their post-contingency power output. Since the issue was observed in the BC as well and it does not impact the overall stability of the system, no further action was taken.
South | 14 - South Central Oklahoma | 21L | Base | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_90_P1_MATHWSN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near MATHWSN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_91_P1_REDNGTN7 | Apply 3-phase fault on MATHWSN7 to REDNGTN7 345kV transmission line CKT 1, near REDNGTN7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_92_P1_HUGO | Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_93_P1_PITTSB-7 | Apply 3-phase fault on PITTSB-7 to VALIANT7 345kV transmission line CKT 1, near PITTSB-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 511939[OECGT1-1],511940[OECGT1-2], 511942[OECGT2-1] and 511943[OECGT2-2]: These have shown abnormal fluctuations in the post-contingency period in BC, SC and TC for several contingencies across all cases, identified as a modeling issue.
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 511939[OECGT1-1],511940[OECGT1-2], 511942[OECGT2-1] and 511943[OECGT2-2]: These have shown abnormal fluctuations in the post-contingency period in BC, SC and TC for several contingencies across all cases, identified as a modeling issue.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_94_P1_RSS-7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near R.S.S.-7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_95_P1_REDBUD7 | Apply 3-phase fault on R.S.S.-7 to REDBUD 7 345kV transmission line CKT 1, near REDBUD 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_96_P1_C-RIVER7 | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near C-RIVER7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_97_P1_FIREWHL-TAP | Apply 3-phase fault on C-RIVER7 to FIREWHL-TAP 345kV transmission line CKT 1, near FIREWHL-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 511939[OECGT1-1],511940[OECGT1-2], 511942[OECGT2-1] and 511943[OECGT2-2]: These have shown abnormal fluctuations in the post-contingency period in BC, SC and TC for several contingencies across all cases, identified as a modeling issue.
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes |  |  |  |  | 511939[OECGT1-1],511940[OECGT1-2], 511942[OECGT2-1] and 511943[OECGT2-2]: These have shown abnormal fluctuations in the post-contingency period in BC, SC and TC for several contingencies across all cases, identified as a modeling issue.
South | 14 - South Central Oklahoma | 28S | Base | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_98_P1_MUSKOGE7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_99_P1_FTSMITH7 | Apply 3-phase fault on MUSKOGE7 to FTSMITH7 345kV transmission line CKT 1, near FTSMITH7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 511939[OECGT1-1],511940[OECGT1-2], 511942[OECGT2-1] and 511943[OECGT2-2]: These have shown abnormal fluctuations in the post-contingency period in BC, SC and TC for several contingencies across all cases, identified as a modeling issue.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_100_P1_MUSKOGE7 | Apply 3-phase fault on SEMINOL7 to MUSKOGE7 345kV transmission line CKT 1, near MUSKOGE7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 511939[OECGT1-1],511940[OECGT1-2], 511942[OECGT2-1] and 511943[OECGT2-2]: These have shown abnormal fluctuations in the post-contingency period in BC, SC and TC for several contingencies across all cases, identified as a modeling issue.
South | 14 - South Central Oklahoma | 19W | Base | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 588183[G16-126-GEN] showed high frequency oscillations, which is likely due to the modelling issue. since this is observed in BC, TC and SC, and it does not impact overall stability of the system no action is taken.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_101_P4_HUGO | Apply single-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 16 cycles with stuck breaker at HUGO. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | NO - Min: 0.84pu | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | NO - Min: 0.86pu | Yes | Yes | NO - G1140G1204G1[1] |  |  |  |  | G1140G1204G1 tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further stability or tripping issues were observed. However, 588183[G16-126-GEN] showed high frequency oscillations, which is likely due to the modelling issue. since this is observed in BC, TC and SC, and it does not impact overall stability of the system no action is taken.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_102_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open NWTXARK7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_103_P4_VALIANT7 | Apply single-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_104_P4_VALIANT7 | Apply single-phase fault on NWTXARK7 to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 16 cycles with stuck breaker at VALIANT7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to VALIANT7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_105_P4_SUNNYSD7 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Three Winding. Simultaneously open SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_106_P4_SUNNYSD7 | Apply single-phase fault on TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1, near SUNNYSD7 345kV for 16 cycles with stuck breaker at SUNNYSD7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_107_P4_JOHNCO7 | Apply single-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 16 cycles with stuck breaker at JOHNCO 7. Open the faulted Transmission Circuit. Simultaneously open JOHNCO 4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to SEMINOL7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to SEMINOL7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to SEMINOL7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to SEMINOL7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to SEMINOL7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G1140G1204G1[1] |  |  |  |  | G1140G1204G1 tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further stability or tripping issues were observed. However, 588183[G16-126-GEN] showed high frequency oscillations, which is likely due to the modelling issue. since this is observed in BC, TC and SC, and it does not impact overall stability of the system no action is taken.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to SEMINOL7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to SEMINOL7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to SEMINOL7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to SEMINOL7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to SEMINOL7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to SEMINOL7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_108_P4_PITTSB-7 | Apply single-phase fault on PITTSB-7 to C-RIVER7 345kV transmission line CKT 1, near PITTSB-7 345kV for 16 cycles with stuck breaker at PITTSB-7. Open the faulted Transmission Circuit. Simultaneously open PITTSB-7 to SEMINOL7 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G1140G1204G1[1] |  |  |  |  | G1140G1204G1 tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further stability or tripping issues were observed. However, 588183[G16-126-GEN] showed high frequency oscillations, which is likely due to the modelling issue. since this is observed in BC, TC and SC, and it does not impact overall stability of the system no action is taken.
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G1140G1204G1[1] |  |  |  |  | G1140G1204G1 tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further stability or tripping issues were observed. However, 588183[G16-126-GEN] showed high frequency oscillations, which is likely due to the modelling issue. since this is observed in BC, TC and SC, and it does not impact overall stability of the system no action is taken.
South | 14 - South Central Oklahoma | 21S | Base | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_109_P4_LES-7 | Apply single-phase fault on O.K.U.-7 to L.E.S.-7 345kV transmission line CKT 1, near L.E.S.-7 345kV for 16 cycles with stuck breaker at L.E.S.-7. Open the faulted Transmission Circuit. Simultaneously open L.E.S.-7 to G16-091-TAP 345kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_110_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_111_P4_HUGOPP4 | Apply single-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Simultaneously open HUGO 345kV/138kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding. Simultaneously open VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding. Simultaneously open VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding. Simultaneously open VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding. Simultaneously open VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding. Simultaneously open VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding. Simultaneously open VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding. Simultaneously open VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding. Simultaneously open VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding. Simultaneously open VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding. Simultaneously open VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding. Simultaneously open VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_112_P4_VALIANT4 | Apply single-phase fault on VALIANT4 138kV/345kV/13.8kV transformer CKT 2, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Three Winding. Simultaneously open VALIANT4 138kV/345kV/13.8kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_113_P4_SBROWN4 | Apply single-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_114_P4_SBROWN4 | Apply single-phase fault on TUPELO 4 to S BROWN4 138kV transmission line CKT 1, near S BROWN4 138kV for 16 cycles with stuck breaker at S BROWN4. Open the faulted Transmission Circuit. Simultaneously open S BROWN4 to RUSSETT4 138kV transmission line CKT 1.Simultaneously open RUSSET-4 to RUSSETT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open RATLIFF4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open RATLIFF4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open RATLIFF4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open RATLIFF4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open RATLIFF4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 588183[G16-126-GEN] showed high frequency oscillations, which is likely due to the modelling issue. since this is SC only, and it does not impact overall stability of the system no action is taken.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open RATLIFF4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open RATLIFF4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open RATLIFF4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open RATLIFF4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open RATLIFF4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open RATLIFF4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_115_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open RATLIFF4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | NO - G1140G1204G2[1] G1140G1204G1[1] |  |  |  |  | G1140G1204G2[1] and G1140G1204G1[1] tripped on overvoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | NO - G1140G1204G2[1] G1140G1204G1[1] |  |  |  |  | G1140G1204G2[1] and G1140G1204G1[1] tripped on overvoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.14pu | Yes | NO - G1140G1204G2[1] G1140G1204G1[1] |  |  |  |  | G1140G1204G2[1] and G1140G1204G1[1] tripped on overvoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.15pu | Yes | NO - G1140G1204G2[1] G1140G1204G1[1] |  |  |  |  | G1140G1204G2[1] and G1140G1204G1[1] tripped on overvoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21S | Base | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - G1140G1204G2[1] G1140G1204G1[1] |  |  |  |  | G1140G1204G2[1] and G1140G1204G1[1] tripped on overvoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G1140G1204G2[1] G1140G1204G1[1] |  |  |  |  | G1140G1204G2[1] and G1140G1204G1[1] tripped on overvoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_116_P4_CARTRCO4 | Apply single-phase fault on SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 16 cycles with stuck breaker at CARTRCO4. Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Simultaneously open DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_117_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD7 345kV/138kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_118_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Three Winding. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_119_P4_SUNNYSD4 | Apply single-phase fault on SUNNYSD4 to ROCKYPT4 138kV transmission line CKT 1, near SUNNYSD4 138kV for 16 cycles with stuck breaker at SUNNYSD4. Open the faulted Transmission Circuit. Simultaneously open SUNNYSD4 to UNIROY 4 138kV transmission line CKT 1.Simultaneously open CARTER 4 to ARDWEST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO PP4 to VALLANT4 138kV transmission line CKT 1.Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO PP4 to VALLANT4 138kV transmission line CKT 1.Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO PP4 to VALLANT4 138kV transmission line CKT 1.Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO PP4 to VALLANT4 138kV transmission line CKT 1.Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO PP4 to VALLANT4 138kV transmission line CKT 1.Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO PP4 to VALLANT4 138kV transmission line CKT 1.Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO PP4 to VALLANT4 138kV transmission line CKT 1.Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO PP4 to VALLANT4 138kV transmission line CKT 1.Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO PP4 to VALLANT4 138kV transmission line CKT 1.Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO PP4 to VALLANT4 138kV transmission line CKT 1.Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO PP4 to VALLANT4 138kV transmission line CKT 1.Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_120_P4_HUGOPP4 | Apply single-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Transmission Circuit. Simultaneously open HUGO PP4 to VALLANT4 138kV transmission line CKT 1.Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding. Simultaneously open SAWYER4 to HUGO PP4 138kV transmission line CKT 1.Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding. Simultaneously open SAWYER4 to HUGO PP4 138kV transmission line CKT 1.Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding. Simultaneously open SAWYER4 to HUGO PP4 138kV transmission line CKT 1.Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding. Simultaneously open SAWYER4 to HUGO PP4 138kV transmission line CKT 1.Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding. Simultaneously open SAWYER4 to HUGO PP4 138kV transmission line CKT 1.Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding. Simultaneously open SAWYER4 to HUGO PP4 138kV transmission line CKT 1.Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding. Simultaneously open SAWYER4 to HUGO PP4 138kV transmission line CKT 1.Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding. Simultaneously open SAWYER4 to HUGO PP4 138kV transmission line CKT 1.Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding. Simultaneously open SAWYER4 to HUGO PP4 138kV transmission line CKT 1.Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding. Simultaneously open SAWYER4 to HUGO PP4 138kV transmission line CKT 1.Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding. Simultaneously open SAWYER4 to HUGO PP4 138kV transmission line CKT 1.Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_121_P4_HUGOPP4 | Apply single-phase fault on HUGO 345kV/138kV/13.8kV transformer CKT 1, near HUGO PP4 138kV for 16 cycles with stuck breaker at HUGO PP4. Open the faulted Three Winding. Simultaneously open SAWYER4 to HUGO PP4 138kV transmission line CKT 1.Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Transmission Circuit. Simultaneously open IDABEL-4 to VALIANT4 138kV transmission line CKT 1.Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Transmission Circuit. Simultaneously open IDABEL-4 to VALIANT4 138kV transmission line CKT 1.Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Transmission Circuit. Simultaneously open IDABEL-4 to VALIANT4 138kV transmission line CKT 1.Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Transmission Circuit. Simultaneously open IDABEL-4 to VALIANT4 138kV transmission line CKT 1.Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Transmission Circuit. Simultaneously open IDABEL-4 to VALIANT4 138kV transmission line CKT 1.Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Transmission Circuit. Simultaneously open IDABEL-4 to VALIANT4 138kV transmission line CKT 1.Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Transmission Circuit. Simultaneously open IDABEL-4 to VALIANT4 138kV transmission line CKT 1.Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Transmission Circuit. Simultaneously open IDABEL-4 to VALIANT4 138kV transmission line CKT 1.Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Transmission Circuit. Simultaneously open IDABEL-4 to VALIANT4 138kV transmission line CKT 1.Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Transmission Circuit. Simultaneously open IDABEL-4 to VALIANT4 138kV transmission line CKT 1.Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Transmission Circuit. Simultaneously open IDABEL-4 to VALIANT4 138kV transmission line CKT 1.Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_122_P4_VALIANT4 | Apply single-phase fault on V-WEYCO4 to VALIANT4 138kV transmission line CKT 1, near VALIANT4 138kV for 16 cycles with stuck breaker at VALIANT4. Open the faulted Transmission Circuit. Simultaneously open IDABEL-4 to VALIANT4 138kV transmission line CKT 1.Simultaneously open B.BOWTP4 to CRAIGJT4 138kV transmission line CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding. Simultaneously open SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding. Simultaneously open SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding. Simultaneously open SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding. Simultaneously open SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding. Simultaneously open SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding. Simultaneously open SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding. Simultaneously open SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding. Simultaneously open SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding. Simultaneously open SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding. Simultaneously open SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding. Simultaneously open SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_123_P4_SEMINOL4 | Apply single-phase fault on SEMINOL4 138kV/345kV/14.39kV transformer CKT 1, near SEMINOL4 138kV for 16 cycles with stuck breaker at SEMINOL4. Open the faulted Three Winding. Simultaneously open SEMINOL4 138kV/345kV/14.39kV transformer CKT 1 and clear the fault. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_124_P6_G16-063-TAP | Prior Outage of SUNNYSD4 138kV/345kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_125_P6_G16-063-TAP | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G1140G1204G1[1] |  |  |  |  | G1140G1204G1 tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further stability or tripping issues were observed. However, 588183[G16-126-GEN] showed high frequency oscillations, which is likely due to the modelling issue. since this is observed in BC, TC and SC, and it does not impact overall stability of the system no action is taken.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_126_P6_G16-063-TAP | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_127_P6_HUGO | Prior Outage of TERRYRD7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_128_P6_HUGO | Prior Outage of JOHNCO 7 to SUNNYSD7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_129_P6_G16-063-TAP | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_130_P6_G16-063-TAP | Prior Outage of VALIANT7 to HUGO 345kV transmission line CKT 1Apply 3-phase fault on SUNNYSD7 to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_131_P6_JOHNCO7 | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on PITTSB-7 to JOHNCO 7 345kV transmission line CKT 1, near JOHNCO 7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_132_P6_G16-063-TAP | Prior Outage of L.E.S.-7 to TERRYRD7 345kV transmission line CKT 1Apply 3-phase fault on HUGO to G16-063-TAP 345kV transmission line CKT 1, near G16-063-TAP 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G1140G1204G1[1] |  |  |  |  | G1140G1204G1 tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further stability or tripping issues were observed. However, G1140G1204G1 and 588183[G16-126-GEN] showed high frequency oscillations, which is likely due to the modelling issue. since this is observed in BC, TC and SC, and it does not impact overall stability of the system no action is taken.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_133_P6_HUGO | Prior Outage of PITTSB-7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on VALIANT7 to HUGO 345kV transmission line CKT 1, near HUGO 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.85pu | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | NO - Min: 0.86pu | Yes | Yes | NO - G1140G1204G1[1] |  |  |  |  | G1140G1204G1 tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further stability or tripping issues were observed. However, G1140G1204G1 and 588183[G16-126-GEN] showed high frequency oscillations, which is likely due to the modelling issue. since this is observed in BC, TC and SC, and it does not impact overall stability of the system no action is taken.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_134_P6_VALIANT7 | Prior Outage of NWTXARK7 to VALIANT7 345kV transmission line CKT 1Apply 3-phase fault on LYDIA to VALIANT7 345kV transmission line CKT 1, near VALIANT7 345kV for 6 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 6 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | NO - G1140G1204G2[1] G1140G1204G1[1] |  |  |  |  | G1140G1204G2[1] and G1140G1204G1[1] tripped on overvoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | NO - MaxV: 1.50pu, MaxDur: 7.14s | Yes | Yes | Yes | NO - G1140G1204G2[1] G1140G1204G1[1] |  |  |  |  | G1140G1204G2[1] and G1140G1204G1[1] tripped on overvoltage protection. The protection was disabled and the simulation was rerun. It was observed that G17-027-GEN units has sustained high frequency oscillations. Adjustments were made, to bring down the terminal voltage of this unit bellow 1.05pu in the N-1 power flow case. Following this adjustment, the simulation was reran and this issue was resolved.
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | Yes |  |  |  |  | It was observed that G17-027-GEN unit has sustained high frequency oscillations. Adjustments were made, to bring down the terminal voltage of this unit bellow 1.05pu in the N-1 power flow case. Following this adjustment, the simulation was reran and this issue was resolved. Voltage Spike: 1.40pu, MaxDur: 0.07s.
South | 14 - South Central Oklahoma | 21L | Base | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | NO - G1140G1204G2[1] G1140G1204G1[1] |  |  |  |  | G1140G1204G2[1] and G1140G1204G1[1] tripped on overvoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.15pu | Yes | NO - G1140G1204G2[1] G1140G1204G1[1] |  |  |  |  | G1140G1204G2[1] and G1140G1204G1[1] tripped on overvoltage protection. The protection was disabled and the simulation was rerun. It was observed that 17-027-GEN units has sustained high frequency oscillations. Adjustments were made, to bring down the terminal voltage of this unit bellow 1.05pu in the N-1 power flow case. Following this adjustment, the simulation was reran and this issue was resolved.
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.16pu | Yes | NO - G1140G1204G2[1] G1140G1204G1[1] |  |  |  |  | G1140G1204G2[1] and G1140G1204G1[1] tripped on overvoltage protection. The protection was disabled and the simulation was rerun. It was observed that G17-027-GEN units has sustained high frequency oscillations. Adjustments were made, to bring down the terminal voltage of this unit bellow 1.05pu in the N-1 power flow case. Following this adjustment, the simulation was reran and this issue was resolved. Voltage Spike: 1.26pu, MaxDur: 0.02s;
South | 14 - South Central Oklahoma | 21S | Base | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - G1140G1204G2[1] G1140G1204G1[1] |  |  |  |  | G1140G1204G2[1] and G1140G1204G1[1] tripped on overvoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed. Voltage Spike: 1.24pu, MaxDur: 0.02s
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.13pu | Yes | NO - G1140G1204G2[1] G1140G1204G1[1] |  |  |  |  | G1140G1204G2[1] and G1140G1204G1[1] tripped on overvoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.11pu | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.10pu | Yes | NO - G1140G1204G2[1] G1140G1204G1[1] |  |  |  |  | G1140G1204G2[1] and G1140G1204G1[1] tripped on overvoltage protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | NO - Max: 1.12pu | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_135_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close POOLVIL4 to CARTRCO4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open POOLVIL4 to CARTRCO4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | It was observed that G17-027-GEN units have sustained high frequency oscillations. Adjustments were made, to bring down the terminal voltage of this unit bellow 1.05pu in the N-1 power flow case. Following this adjustment, the simulation was reran and thi
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_136_P6_CARTRCO4 | Prior Outage of SUNNYSD4 to CARTRCO4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV transmission line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV transmission line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV transmission line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV transmission line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV transmission line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV transmission line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV transmission line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV transmission line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV transmission line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV transmission line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV transmission line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_137_P6_CARTRCO4 | Prior Outage of POOLVIL4 to CARTRCO4 138kV transmission line CKT 1Prior Outage of DUNDEE 4 to HLTNTAP4 138kV transmission line CKT 1Apply 3-phase fault on RATLIFF4 to CARTRCO4 138kV transmission line CKT 1, near CARTRCO4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_138_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on VALIANT4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_139_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_140_P6_FROGVIL4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_141_P6_HUGOPP4 | Prior Outage of HUGO 345kV/138kV/13.8kV transformer CKT 1Apply 3-phase fault on SAWYER4 to HUGO PP4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close ATOKA--4 to ATKEAST4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open ATOKA--4 to ATKEAST4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV transmission line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV transmission line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV transmission line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV transmission line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV transmission line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV transmission line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV transmission line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV transmission line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV transmission line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV transmission line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV transmission line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_142_P6_HUGOPP4 | Prior Outage of VALIANT4 to HUGO PP4 138kV transmission line CKT 1Apply 3-phase fault on HUGO PP4 to VALLANT4 138kV transmission line CKT 1, near HUGO PP4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BROKNBW4 to HOLYCRK4 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV transmission line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV transmission line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV transmission line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV transmission line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV transmission line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV transmission line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV transmission line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV transmission line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV transmission line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV transmission line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV transmission line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV transmission line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Base | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV transmission line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV transmission line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV transmission line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV transmission line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV transmission line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV transmission line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV transmission line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV transmission line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV transmission line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV transmission line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_143_P6_FROGVIL4 | Prior Outage of SAWYER4 to HUGO PP4 138kV transmission line CKT 1Prior Outage of ATOKA--4 to ATKEAST4 138kV transmission line CKT 1Apply 3-phase fault on FROGVIL4 to WSBNKTP4 138kV transmission line CKT 1, near FROGVIL4 138kV for 7 cycles.Open the faulted Transmission Circuit. Simultaneously open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault.Wait 20 cycles. Re-close the faulted Transmission Circuit.Simultaneously re-close BENNGTN4 to UNGER 138kV transmission line CKT 1.Re-open the faulted Transmission Circuit after 7 cycles.Simultaneously re-open BENNGTN4 to UNGER 138kV transmission line CKT 1 and clear the fault. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Base | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV transmission line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV transmission line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Sensitivity | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV transmission line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV transmission line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 19W | Transfer | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV transmission line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV transmission line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Base | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV transmission line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV transmission line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G16-030-GEN1[1] |  |  |  |  | G16-030-GEN1[1] tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21L | Sensitivity | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV transmission line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV transmission line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21L | Transfer | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV transmission line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV transmission line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | NO - G16-030-GEN1[1] |  |  |  |  | G16-030-GEN1[1] tripped on overfrequency protection. The protection was disabled and the simulation was rerun. No further issues were observed.
South | 14 - South Central Oklahoma | 21S | Base | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV transmission line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV transmission line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Sensitivity | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV transmission line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV transmission line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 21S | Transfer | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV transmission line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV transmission line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Base | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV transmission line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV transmission line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Sensitivity | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV transmission line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV transmission line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
South | 14 - South Central Oklahoma | 28S | Transfer | FLT_144_P6_SBROWN4 | Prior Outage of S BROWN4 to RUSSETT4 138kV transmission line CKT 1Prior Outage of RUSSET-4 to RUSSETT4 138kV transmission line CKT 1Apply 3-phase fault on S BROWN4 to COLBRTP4 138kV transmission line CKT 1, near S BROWN4 138kV for 7 cycles. Clear fault by tripping the faulted Transmission Circuit. Wait 20 cycles. Re-close the faulted Transmission Circuit.Re-open the faulted Transmission Circuit after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-1 | 3-phase fault on G17-094-TAP to Fort Thompson 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-2 | 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-3 | 3-phase fault on Huron to Broadland 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-4 | 3-phase fault on Huron to Capenter 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-5 | 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-6 | 3-phase fault on Huron 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-7 | 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-8 | 3-phase fault on Fault Thompson to Leland Olds 345 kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-9 | 3-phase fault on CAPENTER 230/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-10 | 3-phase fault on CAPENTER to WATERTN 230 kV Circuit 1, near CAPENTER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-11 | 3-phase fault on WATERTN to BLAIR 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-12 | 3-phase fault on WATERTN to APPLEDORN 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-13 | 3-phase fault on WATERTN 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-14 | 3-phase fault on WATERTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-15 | 3-phase fault on WATERTN to G09_001IST 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-16 | 3-phase fault on WATERTN to WHITE 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-17 | 3-phase fault on Huron to HURONWP 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-18 | 3-phase fault on Huron to Redfield 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-19 | 3-phase fault on Huron to WOONSKT 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-20 | 3-phase fault on HURON 115/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-21 | 3-phase fault on Broadland 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-22 | 3-phase fault on Broadland to ANTELOPE 345 kV Circuit 1, near Broadland. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-23 | 3-phase fault on LETCHER to SIOUXFL 230 kV Circuit 1, near LETCHER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-24 | 3-phase fault on LETCHER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-25 | 3-phase fault on OAHE to PHILIP 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-26 | 3-phase fault on OAHE to SULLYBT 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-27 | 3-phase fault on OAHE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-28 | 3-phase fault on FTRANDL to SIOUXCY 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-29 | 3-phase fault on FTRANDL to UTICAJC 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-30 | 3-phase fault on FTRANDL to MEADOWGROVE 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-31 | 3-phase fault on FTRANDL to LAKPLAT 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-3PH-32 | 3-phase fault on FTRANDL 230/115 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-PO-1-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-PO-1-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-PO-1-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-PO-1-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-PO-1-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-PO-2-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-PO-2-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-PO-2-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-PO-2-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-PO-2-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-SB-1 | SLG fault on G17-094-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-094-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-SB-2 | SLG fault on Fort Thompson 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-SB-3 | SLG fault on Huron 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-SB-4 | SLG fault on Fort Thompson 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-SB-5 | SLG fault on Huron 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-SB-6 | SLG fault on FTRANDL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of FTRANDL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-SB-7 | SLG fault on OAHE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of OAHE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | 094-SB-8 | SLG fault on WATERTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WATERTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-3PH-10 | 3-phase fault on GRPR1 to GR PRAIRIE 345 kV Circuit 1, near GRPR1. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3 . Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO to White 345 kV Circuit1 and BRKNGCO 345/115/13.8 kV Transformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 19W | Normal | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-1 | 3-phase fault on G17-094-TAP to Fort Thompson 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-2 | 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-3 | 3-phase fault on Huron to Broadland 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-4 | 3-phase fault on Huron to Capenter 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-5 | 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-6 | 3-phase fault on Huron 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-8 | 3-phase fault on Fault Thompson to Leland Olds 345 kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-9 | 3-phase fault on CAPENTER 230/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-10 | 3-phase fault on CAPENTER to WATERTN 230 kV Circuit 1, near CAPENTER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-11 | 3-phase fault on WATERTN to BLAIR 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-12 | 3-phase fault on WATERTN to APPLEDORN 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-13 | 3-phase fault on WATERTN 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-14 | 3-phase fault on WATERTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-15 | 3-phase fault on WATERTN to G09_001IST 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-16 | 3-phase fault on WATERTN to WHITE 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-17 | 3-phase fault on Huron to HURONWP 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-18 | 3-phase fault on Huron to Redfield 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-19 | 3-phase fault on Huron to WOONSKT 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-20 | 3-phase fault on HURON 115/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-21 | 3-phase fault on Broadland 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-22 | 3-phase fault on Broadland to ANTELOPE 345 kV Circuit 1, near Broadland. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-23 | 3-phase fault on LETCHER to SIOUXFL 230 kV Circuit 1, near LETCHER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-24 | 3-phase fault on LETCHER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-25 | 3-phase fault on OAHE to PHILIP 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-26 | 3-phase fault on OAHE to SULLYBT 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-27 | 3-phase fault on OAHE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-28 | 3-phase fault on FTRANDL to SIOUXCY 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-29 | 3-phase fault on FTRANDL to UTICAJC 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-30 | 3-phase fault on FTRANDL to MEADOWGROVE 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-31 | 3-phase fault on FTRANDL to LAKPLAT 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-32 | 3-phase fault on FTRANDL 230/115 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-PO-1-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-PO-1-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-PO-1-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-PO-1-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-PO-1-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-PO-2-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-PO-2-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-PO-2-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-PO-2-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-PO-2-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-SB-1 | SLG fault on G17-094-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-094-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-SB-2 | SLG fault on Fort Thompson 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-SB-3 | SLG fault on Huron 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-SB-4 | SLG fault on Fort Thompson 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-SB-5 | SLG fault on Huron 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-SB-6 | SLG fault on FTRANDL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of FTRANDL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-SB-7 | SLG fault on OAHE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of OAHE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-SB-8 | SLG fault on WATERTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WATERTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-3PH-10 | 3-phase fault on GRPR1 to GR PRAIRIE 345 kV Circuit 1, near GRPR1. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3 . Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO to White 345 kV Circuit1 and BRKNGCO 345/115/13.8 kV Transformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-1 | 3-phase fault on G17-094-TAP to Fort Thompson 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-2 | 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-3 | 3-phase fault on Huron to Broadland 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-4 | 3-phase fault on Huron to Capenter 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-5 | 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-6 | 3-phase fault on Huron 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-7 | 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-8 | 3-phase fault on Fault Thompson to Leland Olds 345 kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-9 | 3-phase fault on CAPENTER 230/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-10 | 3-phase fault on CAPENTER to WATERTN 230 kV Circuit 1, near CAPENTER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-11 | 3-phase fault on WATERTN to BLAIR 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-12 | 3-phase fault on WATERTN to APPLEDORN 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-13 | 3-phase fault on WATERTN 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-14 | 3-phase fault on WATERTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-15 | 3-phase fault on WATERTN to G09_001IST 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-16 | 3-phase fault on WATERTN to WHITE 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-17 | 3-phase fault on Huron to HURONWP 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-18 | 3-phase fault on Huron to Redfield 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-19 | 3-phase fault on Huron to WOONSKT 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-20 | 3-phase fault on HURON 115/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-21 | 3-phase fault on Broadland 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-22 | 3-phase fault on Broadland to ANTELOPE 345 kV Circuit 1, near Broadland. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-23 | 3-phase fault on LETCHER to SIOUXFL 230 kV Circuit 1, near LETCHER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-24 | 3-phase fault on LETCHER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-25 | 3-phase fault on OAHE to PHILIP 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-26 | 3-phase fault on OAHE to SULLYBT 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-27 | 3-phase fault on OAHE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-28 | 3-phase fault on FTRANDL to SIOUXCY 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-29 | 3-phase fault on FTRANDL to UTICAJC 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-30 | 3-phase fault on FTRANDL to MEADOWGROVE 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-31 | 3-phase fault on FTRANDL to LAKPLAT 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-3PH-32 | 3-phase fault on FTRANDL 230/115 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-PO-1-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-PO-1-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-PO-1-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-PO-1-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-PO-1-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-PO-2-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-PO-2-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-PO-2-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-PO-2-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-PO-2-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-SB-1 | SLG fault on G17-094-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-094-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-SB-2 | SLG fault on Fort Thompson 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-SB-3 | SLG fault on Huron 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-SB-4 | SLG fault on Fort Thompson 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-SB-5 | SLG fault on Huron 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-SB-6 | SLG fault on FTRANDL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of FTRANDL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-SB-7 | SLG fault on OAHE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of OAHE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | 094-SB-8 | SLG fault on WATERTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WATERTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-3PH-10 | 3-phase fault on GRPR1 to GR PRAIRIE 345 kV Circuit 1, near GRPR1. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3 . Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO to White 345 kV Circuit1 and BRKNGCO 345/115/13.8 kV Transformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21S | Normal | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-1 | 3-phase fault on G17-094-TAP to Fort Thompson 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-10 | 3-phase fault on CAPENTER to WATERTN 230 kV Circuit 1, near CAPENTER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-11 | 3-phase fault on WATERTN to BLAIR 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-12 | 3-phase fault on WATERTN to APPLEDORN 230 kV Circuit 1, near WATERTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-13 | 3-phase fault on WATERTN 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-14 | 3-phase fault on WATERTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-15 | 3-phase fault on WATERTN to G09_001IST 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-16 | 3-phase fault on WATERTN to WHITE 345 kV Circuit 1, near WATERTN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-17 | 3-phase fault on Huron to HURONWP 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-18 | 3-phase fault on Huron to Redfield 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-19 | 3-phase fault on Huron to WOONSKT 115 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-2 | 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-20 | 3-phase fault on HURON 115/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-21 | 3-phase fault on Broadland 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-22 | 3-phase fault on Broadland to ANTELOPE 345 kV Circuit 1, near Broadland. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-23 | 3-phase fault on LETCHER to SIOUXFL 230 kV Circuit 1, near LETCHER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-24 | 3-phase fault on LETCHER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-25 | 3-phase fault on OAHE to PHILIP 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-26 | 3-phase fault on OAHE to SULLYBT 230 kV Circuit 1, near OAHE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-27 | 3-phase fault on OAHE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-28 | 3-phase fault on FTRANDL to SIOUXCY 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-29 | 3-phase fault on FTRANDL to UTICAJC 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-3 | 3-phase fault on Huron to Broadland 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-30 | 3-phase fault on FTRANDL to MEADOWGROVE 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-31 | 3-phase fault on FTRANDL to LAKPLAT 230 kV Circuit 1, near FTRANDL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-32 | 3-phase fault on FTRANDL 230/115 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-4 | 3-phase fault on Huron to Capenter 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-5 | 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-6 | 3-phase fault on Huron 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-7 | 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-8 | 3-phase fault on Fault Thompson to Leland Olds 345 kV Circuit 1, near Fort Thompson. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-3PH-9 | 3-phase fault on CAPENTER 230/69 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-PO-1-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-PO-1-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-PO-1-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-PO-1-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-PO-1-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-PO-2-1 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Fort Thompson 230kV Circuit 2, near G17-04-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-PO-2-2 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on G17-094-TAP to Huron 230 kV Circuit 2, near G17-094-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-PO-2-3 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to LETCHER 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-PO-2-4 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Fort Thompson to FTRANDL 230kV Circuit 1, near Fort Thompson. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-PO-2-5 | Prior Outage of G17-094-TAP to Fort Thompson 230kV Circuit 1. 3-phase fault on Huron to WATERTN 230 kV Circuit 1, near Huron. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-SB-1 | SLG fault on G17-094-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-094-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-SB-2 | SLG fault on Fort Thompson 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-SB-3 | SLG fault on Huron 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-SB-4 | SLG fault on Fort Thompson 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of Fort Thompson 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-SB-5 | SLG fault on Huron 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of Huron 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-SB-6 | SLG fault on FTRANDL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of FTRANDL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-SB-7 | SLG fault on OAHE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of OAHE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | 094-SB-8 | SLG fault on WATERTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WATERTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-3PH-10 | 3-phase fault on GRPR1 to GR PRAIRIE 345 kV Circuit 1, near GRPR1. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3 . Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO to White 345 kV Circuit1 and BRKNGCO 345/115/13.8 kV Transformer 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 21L | Normal | 094-3PH-7 | 3-phase fault on Fort Thompson 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 15 - Eastern South Dakota | 28S | Normal | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-1 | 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-2 | 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-3 | 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-5 | 3-phase fault on DAGLUM to BRADYWND 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-6 | 3-phase fault on BOWMAN to HERINGR 230 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-7 | 3-phase fault on BOWMAN 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-8 | 3-phase fault on BAKER to MI CTYE 230 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-9 | 3-phase fault on BAKER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-10 | 3-phase fault on BELFELD to DICKINSN 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-11 | 3-phase fault on BELFELD to S.HEART 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-12 | 3-phase fault on BELFELD to MEDORA 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-13 | 3-phase fault on BELFELD 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-14 | 3-phase fault on BELFELD to CHARL_CK 345 kV Circuit 1, near BELFELD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-15 | 3-phase fault on BOWMAN to NBURR 115 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-16 | 3-phase fault on HETINGR to BISON 230 kV Circuit 1, near HERINGR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-17 | 3-phase fault on HETINGR 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-18 | 3-phase fault on BAKER to CABINCR 115 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-19 | 3-phase fault on BAKER 115/69 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-20 | 3-phase fault on MI CTYE to DAWSON 230 kV Circuit 1, near MI CTYE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-21 | 3-phase fault on MI CTYE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-PO-1-1 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-PO-1-2 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-PO-2-1 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-PO-2-2 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-PO-3-1 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-PO-3-2 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-1 | SLG fault on RHAME 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of RHAME 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-2 | SLG fault on DALGUM 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of DALGUM 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-3 | SLG fault on BOWMAN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOWMAN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-4 | SLG fault on BAKER 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BAKER 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-6 | SLG fault on BELFELD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-7 | SLG fault on HETINGR 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of HETINGR 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-8 | SLG fault on MI CTYE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of MI CTYE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-1 | 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-2 | 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-3 | 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-4 | 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-5 | 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-6 | 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-7 | 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-8 | 3-phase fault on TIOGA 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-9 | 3-phase fault on WILISTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-10 | 3-phase fault on WILISTN to JUDSON 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-11 | 3-phase fault on WILISTN to WATFORD 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-12 | 3-phase fault on WHEELOCK to ELLISVIL 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-13 | 3-phase fault on WHEELOCK to WHEELS_T 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-14 | 3-phase fault on BLAISDEL to LOGAN 230 kV Circuit 1, near BLAISDEL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-15 | 3-phase fault on BLAISDEL 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-16 | 3-phase fault on BD to REGINA 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-17 | 3-phase fault on BD to AUBURNTON 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-18 | 3-phase fault on BD to SHAND 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-19 | 3-phase fault on BD to KISBEY TAP 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-20 | 3-phase fault on BD 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-21 | 3-phase fault on NESET to TANDE 230 kV Circuit 1, near NESET. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-22 | 3-phase fault on NESET 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-23 | 3-phase fault on TIOGA to NESET 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-24 | 3-phase fault on TIOGA to STANLEY 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-3PH-25 | 3-phase fault on TIOGA to RAY JCT 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-1-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-1-2 | Apply 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-1-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-1-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-2-1 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-2-2 | Apply 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-2-3 | Apply 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-3-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-3-2 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-3-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-PO-3-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-1 | SLG fault on G17-048-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-048-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-2 | SLG fault on WHEELOCK 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WHEELOCK 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-4 | SLG fault on TIOGA 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-5 | SLG fault on WILISTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WILISTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-6 | SLG fault on BLAISDEL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BLAISDEL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-7 | SLG fault on BD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BD to Regina 230 kV Circuit 1, BD to AUBURNTON 230 kV Circuit 1, BD to KISBEY 230 kV Circuit 1, BD Generator 5 and BD Generator 6. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-8 | SLG fault on NESET 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of NESET 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-1 | 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-2 | 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-3 | 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-5 | 3-phase fault on DAGLUM to BRADYWND 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-6 | 3-phase fault on BOWMAN to HERINGR 230 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-7 | 3-phase fault on BOWMAN 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-8 | 3-phase fault on BAKER to MI CTYE 230 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-9 | 3-phase fault on BAKER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-10 | 3-phase fault on BELFELD to DICKINSN 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-11 | 3-phase fault on BELFELD to S.HEART 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-12 | 3-phase fault on BELFELD to MEDORA 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-13 | 3-phase fault on BELFELD 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-14 | 3-phase fault on BELFELD to CHARL_CK 345 kV Circuit 1, near BELFELD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-15 | 3-phase fault on BOWMAN to NBURR 115 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-16 | 3-phase fault on HETINGR to BISON 230 kV Circuit 1, near HERINGR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-17 | 3-phase fault on HETINGR 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-18 | 3-phase fault on BAKER to CABINCR 115 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-19 | 3-phase fault on BAKER 115/69 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-20 | 3-phase fault on MI CTYE to DAWSON 230 kV Circuit 1, near MI CTYE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-21 | 3-phase fault on MI CTYE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-PO-1-1 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-PO-1-2 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-PO-2-1 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-PO-2-2 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-PO-3-1 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-PO-3-2 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-1 | SLG fault on RHAME 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of RHAME 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-2 | SLG fault on DALGUM 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of DALGUM 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-3 | SLG fault on BOWMAN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOWMAN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-4 | SLG fault on BAKER 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BAKER 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-6 | SLG fault on BELFELD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-7 | SLG fault on HETINGR 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of HETINGR 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-8 | SLG fault on MI CTYE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of MI CTYE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-1 | 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-2 | 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-3 | 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-4 | 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-5 | 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-6 | 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-7 | 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-8 | 3-phase fault on TIOGA 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-9 | 3-phase fault on WILISTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-10 | 3-phase fault on WILISTN to JUDSON 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-11 | 3-phase fault on WILISTN to WATFORD 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-12 | 3-phase fault on WHEELOCK to ELLISVIL 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-13 | 3-phase fault on WHEELOCK to WHEELS_T 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-14 | 3-phase fault on BLAISDEL to LOGAN 230 kV Circuit 1, near BLAISDEL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-15 | 3-phase fault on BLAISDEL 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-16 | 3-phase fault on BD to REGINA 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND and 672303 BD generators rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-17 | 3-phase fault on BD to AUBURNTON 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND and 672303 BD generators rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-18 | 3-phase fault on BD to SHAND 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-19 | 3-phase fault on BD to KISBEY TAP 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND and 672303 BD generators rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-20 | 3-phase fault on BD 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-21 | 3-phase fault on NESET to TANDE 230 kV Circuit 1, near NESET. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-22 | 3-phase fault on NESET 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-23 | 3-phase fault on TIOGA to NESET 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-24 | 3-phase fault on TIOGA to STANLEY 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-3PH-25 | 3-phase fault on TIOGA to RAY JCT 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-1-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-1-2 | Apply 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-1-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-1-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-2-1 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-2-2 | Apply 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-2-3 | Apply 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-3-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-3-2 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-3-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-PO-3-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-1 | SLG fault on G17-048-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-048-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-2 | SLG fault on WHEELOCK 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WHEELOCK 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-3 | SLG fault on TIOGA 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-4 | SLG fault on TIOGA 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-5 | SLG fault on WILISTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WILISTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-6 | SLG fault on BLAISDEL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BLAISDEL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-7 | SLG fault on BD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BD to Regina 230 kV Circuit 1, BD to AUBURNTON 230 kV Circuit 1, BD to KISBEY 230 kV Circuit 1, BD Generator 5 and BD Generator 6. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | 048-SB-8 | SLG fault on NESET 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of NESET 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21L | Transfer | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-1 | 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-2 | 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-3 | 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-5 | 3-phase fault on DAGLUM to BRADYWND 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-6 | 3-phase fault on BOWMAN to HERINGR 230 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-7 | 3-phase fault on BOWMAN 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-8 | 3-phase fault on BAKER to MI CTYE 230 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-9 | 3-phase fault on BAKER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-10 | 3-phase fault on BELFELD to DICKINSN 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-11 | 3-phase fault on BELFELD to S.HEART 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-12 | 3-phase fault on BELFELD to MEDORA 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-13 | 3-phase fault on BELFELD 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-14 | 3-phase fault on BELFELD to CHARL_CK 345 kV Circuit 1, near BELFELD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-15 | 3-phase fault on BOWMAN to NBURR 115 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-16 | 3-phase fault on HETINGR to BISON 230 kV Circuit 1, near HERINGR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-17 | 3-phase fault on HETINGR 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-18 | 3-phase fault on BAKER to CABINCR 115 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-19 | 3-phase fault on BAKER 115/69 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-20 | 3-phase fault on MI CTYE to DAWSON 230 kV Circuit 1, near MI CTYE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-21 | 3-phase fault on MI CTYE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-PO-1-1 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-PO-1-2 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-PO-2-1 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-PO-2-2 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-PO-3-1 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-PO-3-2 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-1 | SLG fault on RHAME 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of RHAME 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-2 | SLG fault on DALGUM 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of DALGUM 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-3 | SLG fault on BOWMAN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOWMAN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-4 | SLG fault on BAKER 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BAKER 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-6 | SLG fault on BELFELD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-7 | SLG fault on HETINGR 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of HETINGR 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-8 | SLG fault on MI CTYE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of MI CTYE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-1 | 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-2 | 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-3 | 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-4 | 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-5 | 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-7 | 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-8 | 3-phase fault on TIOGA 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-9 | 3-phase fault on WILISTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-10 | 3-phase fault on WILISTN to JUDSON 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-11 | 3-phase fault on WILISTN to WATFORD 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-12 | 3-phase fault on WHEELOCK to ELLISVIL 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-13 | 3-phase fault on WHEELOCK to WHEELS_T 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-14 | 3-phase fault on BLAISDEL to LOGAN 230 kV Circuit 1, near BLAISDEL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-15 | 3-phase fault on BLAISDEL 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-16 | 3-phase fault on BD to REGINA 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND and 672303 BD generators rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-17 | 3-phase fault on BD to AUBURNTON 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-18 | 3-phase fault on BD to SHAND 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-19 | 3-phase fault on BD to KISBEY TAP 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND and 672303 BD generators rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-20 | 3-phase fault on BD 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-21 | 3-phase fault on NESET to TANDE 230 kV Circuit 1, near NESET. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-22 | 3-phase fault on NESET 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-23 | 3-phase fault on TIOGA to NESET 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-24 | 3-phase fault on TIOGA to STANLEY 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-25 | 3-phase fault on TIOGA to RAY JCT 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-1-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-1-2 | Apply 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-1-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-2-1 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-2-2 | Apply 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-2-3 | Apply 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-3-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-3-2 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-3-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-1 | SLG fault on G17-048-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-048-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-2 | SLG fault on WHEELOCK 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WHEELOCK 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-4 | SLG fault on TIOGA 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-5 | SLG fault on WILISTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WILISTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-6 | SLG fault on BLAISDEL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BLAISDEL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-7 | SLG fault on BD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BD to Regina 230 kV Circuit 1, BD to AUBURNTON 230 kV Circuit 1, BD to KISBEY 230 kV Circuit 1, BD Generator 5 and BD Generator 6. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-8 | SLG fault on NESET 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of NESET 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 21S | Transfer | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-1 | 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-2 | 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-3 | 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-4 | 3-phase fault on DAGLUM to BELFELD 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-5 | 3-phase fault on DAGLUM to BRADYWND 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-6 | 3-phase fault on BOWMAN to HERINGR 230 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-7 | 3-phase fault on BOWMAN 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-8 | 3-phase fault on BAKER to MI CTYE 230 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-9 | 3-phase fault on BAKER 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-10 | 3-phase fault on BELFELD to DICKINSN 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-11 | 3-phase fault on BELFELD to S.HEART 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-12 | 3-phase fault on BELFELD to MEDORA 230 kV Circuit 1, near BELFELD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-13 | 3-phase fault on BELFELD 345/230/13.8 kV Transformer 1. Clear fault after 6 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-14 | 3-phase fault on BELFELD to CHARL_CK 345 kV Circuit 1, near BELFELD. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-15 | 3-phase fault on BOWMAN to NBURR 115 kV Circuit 1, near BOWMAN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-16 | 3-phase fault on HETINGR to BISON 230 kV Circuit 1, near HERINGR. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-17 | 3-phase fault on HETINGR 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-18 | 3-phase fault on BAKER to CABINCR 115 kV Circuit 1, near BAKER. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-19 | 3-phase fault on BAKER 115/69 kV Transformer 2. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-20 | 3-phase fault on MI CTYE to DAWSON 230 kV Circuit 1, near MI CTYE. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-3PH-21 | 3-phase fault on MI CTYE 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-PO-1-1 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-PO-1-2 | Prior Outage of RHAME to DAGLUM 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-PO-2-1 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-PO-2-2 | Prior Outage of RHAME to BOWMAN 230 kV Circuit 1. 3-phase fault on RHAME to BAKER 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-PO-3-1 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to DAGLUM 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-PO-3-2 | Prior Outage of RHAME to BAKER 230 kV Circuit 1. 3-phase fault on RHAME to BOWMAN 230 kV Circuit 1, near RHAME. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-1 | SLG fault on RHAME 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of RHAME 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-2 | SLG fault on DALGUM 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of DALGUM 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-3 | SLG fault on BOWMAN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOWMAN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-4 | SLG fault on BAKER 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BAKER 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-6 | SLG fault on BELFELD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-7 | SLG fault on HETINGR 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of HETINGR 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-8 | SLG fault on MI CTYE 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of MI CTYE 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-1 | 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-2 | 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-3 | 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-4 | 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-5 | 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-6 | 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-7 | 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-8 | 3-phase fault on TIOGA 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-9 | 3-phase fault on WILISTN 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-10 | 3-phase fault on WILISTN to JUDSON 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-11 | 3-phase fault on WILISTN to WATFORD 230 kV Circuit 1, near WILISTN. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-12 | 3-phase fault on WHEELOCK to ELLISVIL 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-13 | 3-phase fault on WHEELOCK to WHEELS_T 115 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-14 | 3-phase fault on BLAISDEL to LOGAN 230 kV Circuit 1, near BLAISDEL. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-15 | 3-phase fault on BLAISDEL 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-16 | 3-phase fault on BD to REGINA 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND and 672303 BD generators rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-17 | 3-phase fault on BD to AUBURNTON 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-18 | 3-phase fault on BD to SHAND 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Unstable | Yes | Yes | Yes | Yes | Yes | No | 672321 SHAND generator rotor angle unstable (first swing) and tripped | Remove high speed reclose
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-19 | 3-phase fault on BD to KISBEY TAP 230 kV Circuit 1, near BD. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-20 | 3-phase fault on BD 230/115 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-21 | 3-phase fault on NESET to TANDE 230 kV Circuit 1, near NESET. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-22 | 3-phase fault on NESET 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-23 | 3-phase fault on TIOGA to NESET 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-24 | 3-phase fault on TIOGA to STANLEY 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-3PH-25 | 3-phase fault on TIOGA to RAY JCT 115 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-1-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-1-2 | Apply 3-phase fault on TIOGA to NESET 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-1-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-1-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-2-1 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-2-2 | Apply 3-phase fault on WHEELOCK to WILISTN 230 kV Circuit 1, near WHEELOCK. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-2-3 | Apply 3-phase fault on WHEELOCK 230/115/13.8 kV Transformer 1. Clear fault after 7 cycles by tripping the faulted circuit. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-3-1 | Apply 3-phase fault on G17-048-TAP to TIOGA 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-3-2 | Apply 3-phase fault on G17-048-TAP to WHEELOCK 230 kV Circuit 1, near G17-048-TAP. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-3-3 | Apply 3-phase fault on TIOGA to BLAISDEL 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-PO-3-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-1 | SLG fault on G17-048-TAP 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of G17-048-TAP 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-2 | SLG fault on WHEELOCK 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WHEELOCK 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-3 | SLG fault on TIOGA 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-4 | SLG fault on TIOGA 115 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 115 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-5 | SLG fault on WILISTN 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of WILISTN 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-6 | SLG fault on BLAISDEL 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BLAISDEL 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-7 | SLG fault on BD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BD to Regina 230 kV Circuit 1, BD to AUBURNTON 230 kV Circuit 1, BD to KISBEY 230 kV Circuit 1, BD Generator 5 and BD Generator 6. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | 048-SB-8 | SLG fault on NESET 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of NESET 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-1 | 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-2 | 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-3 | 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 1, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-4 | 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-5 | 3-phase fault on KEYSTON to SD.LS-KS 345 kV Circuit 1, near KEYSTON3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-6 | 3-phase fault on THEDFRD to HOLT. CO 345 kV Circuit 1, near THEDFRD3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-7 | 3-phase fault on HOLT. CO to ANTELOPE 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-8 | 3-phase fault on HOLT. CO to GR ISLD 345 kV Circuit 1, near HOLT. CO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-3PH-9 | 3-phase fault on BOBCAT.C to STEGALL 345 kV Circuit 1, near BOBCAT.C3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-1-1 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-1-2 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-1-3 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-1-4 | Prior Outage of BRKNGCO to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-2-1 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-2-2 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on SPLT RK3 to SIOUXCY 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-2-3 | Prior Outage of SPLT RK3 to WHITE 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-3-1 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on BRKNGCO to WHITE 345 kV Circuit 2, near BRKNGCO3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-3-2 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK33-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-PO-3-3 | Prior Outage of SPLT RK3 to SIOUXCY 345kV Circuit 1. 3-phase fault on RAUN to SIOUXCY 345 kV Circuit 1, near RAUN3-phase fault on SPLT RK3 to WHITE 345 kV Circuit 1, near SPLT RK3. Clear fault after 6 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-SB-1 | SLG fault on BRKNGCO 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BRKNGCO 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-SB-2 | SLG fault on SPLT RK3 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SPLT RK3 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-SB-3 | SLG fault on RAUN 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of RAUN 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-SB-4 | SLG fault on KEYSTON 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of KEYSTON 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-SB-5 | SLG fault on THEDFRD 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of THEDFRD 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-SB-6 | SLG fault on BOBCAT.C 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of BOBCAT.C 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 28S | Transfer | TIE-SB-7 | SLG fault on SIOUXCY 345 kV, stuck breaker results delayed clearing after 16 cycles with loss of SIOUXCY 345 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 16 - Western North Dakota | 19W | Transfer | 010-SB-5 | SLG fault on BELFELD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 230 kV bus. | P4 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage collapse at Rhame. G17-010 tripped. | Model Correction
North | 16 - Western North Dakota | 21L | Transfer | 010-SB-5 | SLG fault on BELFELD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 230 kV bus. | P4 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage collapse at Rhame. G17-010 tripped. | Model Correction
North | 16 - Western North Dakota | 21S | Transfer | 010-SB-5 | SLG fault on BELFELD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 230 kV bus. | P4 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage collapse at Rhame. G17-010 tripped. | Model Correction
North | 16 - Western North Dakota | 28S | Transfer | 010-SB-5 | SLG fault on BELFELD 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of BELFELD 230 kV bus. | P4 | Stable | No | Yes | Yes | Yes | Yes | No | Voltage collapse at Rhame. G17-010 tripped. | Model Correction
North | 16 - Western North Dakota | 19W | Transfer | 010-3PH-4 | 3-phase fault on DAGLUM to BELFELD 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | No | No | Yes | Yes | Yes | No | Voltage collapse at Rhame. G17-010 tripped. | Model Correction
North | 16 - Western North Dakota | 21L | Transfer | 010-3PH-4 | 3-phase fault on DAGLUM to BELFELD 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | No | No | Yes | Yes | Yes | No | Voltage collapse at Rhame. G17-010 tripped. BRADYWNDGN2W tripped. G15-096 tripped. | Model Correction
North | 16 - Western North Dakota | 21S | Transfer | 010-3PH-4 | 3-phase fault on DAGLUM to BELFELD 230 kV Circuit 1, near DAGLUM. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | No | No | Yes | Yes | Yes | No | Voltage collapse at Rhame. G17-010 tripped. | Model Correction
North | 16 - Western North Dakota | 19W | Transfer | 048-SB-3 | SLG fault on TIOGA 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Small ripple undamped. Observed on LELAND, GARISN, GRE-STATION generators | Model Correction
North | 16 - Western North Dakota | 21S | Transfer | 048-3PH-6 | 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | No | Yes | Small ripple undamped. Observed on LELAND, GARISN, GRE-STATION generators | Model Correction
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-1-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Small ripple undamped. Observed on LELAND, GARISN, GRE-STATION generators | Model Correction
North | 16 - Western North Dakota | 21S | Transfer | 048-PO-3-4 | Apply 3-phase fault on TIOGA to BDV 230 kV Circuit 1, near TIOGA. Clear fault after 7 cycles by tripping the faulted circuit. After 20 cycles, re-close the faulted line and apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | No | Yes | Small ripple undamped. Observed on LELAND, GARISN, GRE-STATION generators | Model Correction
North | 16 - Western North Dakota | 21S | Transfer | 048-SB-3 | SLG fault on TIOGA 230 kV, stuck breaker results delayed clearing after 16 cycles with loss of TIOGA 230 kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | No | Yes | Small ripple undamped. Observed on LELAND, GARISN, GRE-STATION generators | Model Correction
North | 17 - Western South Dakota | 19W | Normal | 3ph-01 | 3-ph fault on Philip TAP to Underwood 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-03 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-04 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-05 | 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-06 | 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-07 | 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-08 | 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-09 | 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-11 | 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-12 | 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-13 | 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-14 | 3-ph fault on Philip Tap to Philip 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-15 | 3-ph fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 19W | Normal | 3ph-16 | 3-ph fault on Wayside to STEGALL 230kV crt 1, near Wayside. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-17 | 3-ph fault on Wayside 230/115/13.8kV TF T1, near Wayside 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-18 | 3-ph fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-19 | 3-ph fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-20 | 3-ph fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-21 | 3-ph fault on Philip to WANBLEE to MARTIN 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-22 | 3-ph fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-23 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-24 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-25 | 3-ph fault on OAHE to SULLYBT-ER4 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-26 | 3-ph fault on MAURINE to BISON 230kV crt 1, near MAURINE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-27 | 3-ph fault on MAURINE 230/115/13.8kV TF 1A, near MAURINE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-28 | 3-ph fault on STEGALL to DH_CS_EA-TS4 230kV crt 1, near STEGALL. Clear fault after 7 cycles by tripping the faulted crt, and DH_CS_EA-TS DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-29 | 3-ph fault on STEGALL to STEGALL_-MB4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-30 | 3-ph fault on STEGALL to VICTRYH4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-31 | 3-ph fault on DRYCREEK to RCDC 230kV crt 1, near DRYCREEK. Clear fault after 7 cycles by tripping the faulted crt, and RCDC DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-32 | 3-ph fault on DRYCREEK 230/115/13.8kV TF 1A, near DRYCREEK. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-33 | 3-ph fault on G14_001IST to MAURINE7 115kV crt 1, near G14_001IST. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-34 | 3-ph fault on Martin to SHANNON 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-35 | 3-ph fault on Martin to VETAL_TP 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-36 | 3-ph fault on IRVSIMM7 to OAHE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-37 | 3-ph fault on IRVSIMM7 to PIERRE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-56 | Prior Outage of Philip Tap to Underwood 230kV crt 1. 3-ph fault on Philip Tap to OAHE 230kV crt 1, near Philip TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 19W | Normal | 3ph-57 | Prior Outage of Philip TAP to OAHE 230kV crt 1. 3-ph fault on Philip TAP to UNDERWOOD 230kV crt 1, near PHILIP TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 19W | Normal | 3ph-60 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-61 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-62 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-63 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-64 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-65 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-66 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-67 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-68 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-69 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-70 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to Philip TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-71 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-72 | Prior Outage of Underwood to DRYCREEK 230kV crt 1. 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | 3ph-73 | Prior Outage of Underwood-LNX5 to MAURINE 230kV crt 1. 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | SLG-38 | SLG fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Wayside 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | SLG-39 | SLG fault on G17-064-TAP to Underwood 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | SLG-40 | SLG fault on Philip TAP 230kV. Clear fault after 16 cycles by tripping the Philip Tap 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | SLG-41 | SLG fault on Underwood 230kV. Clear fault after 16 cycles by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | SLG-42 | SLG fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the RUSHMORE 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | SLG-43 | SLG fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the ELSWRTH7 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | SLG-44 | SLG fault on Underwood to WICKSVL7 to Philip 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the WICKSVL7 115kV bus, WALL 115kV bus and Philip 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | SLG-45 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to G16-094-TAP 230kV crt 1. | P4 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 19W | Normal | SLG-46 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 19W | Normal | SLG-47 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to SULLYBT 230kV crt 1. | P4 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 19W | Normal | SLG-48 | SLG fault on Wayside to STEGALL 230kV crt 1, near Wayside for 16 cycles. Clear fault by tripping the faulted crt and STEGALL4 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | SLG-49 | SLG fault on Underwood to DRYCREEK 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | SLG-50 | SLG fault on Underwood to MAURINE 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the MAURINE 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | SLG-51 | SLG fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the ELKCRK 7 115kV bus, NEWELL 115kV bus, meantime trip the G14_001IST 115kV bus and G14_001IS_3 generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-01 | 3-ph fault on Philip TAP to Underwood 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-03 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-04 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-05 | 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-06 | 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-07 | 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-08 | 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-09 | 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-11 | 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-12 | 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-13 | 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-14 | 3-ph fault on Philip Tap to Philip 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-15 | 3-ph fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. G17-097 tripped | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 21S | Normal | 3ph-16 | 3-ph fault on Wayside to STEGALL 230kV crt 1, near Wayside. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-17 | 3-ph fault on Wayside 230/115/13.8kV TF T1, near Wayside 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-18 | 3-ph fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-19 | 3-ph fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-20 | 3-ph fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-21 | 3-ph fault on Philip to WANBLEE to MARTIN 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-22 | 3-ph fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-23 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-24 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-25 | 3-ph fault on OAHE to SULLYBT-ER4 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-26 | 3-ph fault on MAURINE to BISON 230kV crt 1, near MAURINE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-27 | 3-ph fault on MAURINE 230/115/13.8kV TF 1A, near MAURINE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-28 | 3-ph fault on STEGALL to DH_CS_EA-TS4 230kV crt 1, near STEGALL. Clear fault after 7 cycles by tripping the faulted crt, and DH_CS_EA-TS DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-29 | 3-ph fault on STEGALL to STEGALL_-MB4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-30 | 3-ph fault on STEGALL to VICTRYH4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-31 | 3-ph fault on DRYCREEK to RCDC 230kV crt 1, near DRYCREEK. Clear fault after 7 cycles by tripping the faulted crt, and RCDC DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-32 | 3-ph fault on DRYCREEK 230/115/13.8kV TF 1A, near DRYCREEK. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-33 | 3-ph fault on G14_001IST to MAURINE7 115kV crt 1, near G14_001IST. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-34 | 3-ph fault on Martin to SHANNON 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-35 | 3-ph fault on Martin to VETAL_TP 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-36 | 3-ph fault on IRVSIMM7 to OAHE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-37 | 3-ph fault on IRVSIMM7 to PIERRE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-56 | Prior Outage of Philip Tap to Underwood 230kV crt 1. 3-ph fault on Philip Tap to OAHE 230kV crt 1, near Philip TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 21S | Normal | 3ph-57 | Prior Outage of Philip TAP to OAHE 230kV crt 1. 3-ph fault on Philip TAP to UNDERWOOD 230kV crt 1, near PHILIP TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590). And curtail G17-014 by 60MW.
North | 17 - Western South Dakota | 21S | Normal | 3ph-60 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-61 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-62 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-63 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-64 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-65 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-66 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-67 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-68 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-69 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-70 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to Philip TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-71 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-72 | Prior Outage of Underwood to DRYCREEK 230kV crt 1. 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | 3ph-73 | Prior Outage of Underwood-LNX5 to MAURINE 230kV crt 1. 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | SLG-38 | SLG fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Wayside 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | SLG-39 | SLG fault on G17-064-TAP to Underwood 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | SLG-40 | SLG fault on Philip TAP 230kV. Clear fault after 16 cycles by tripping the Philip Tap 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | SLG-41 | SLG fault on Underwood 230kV. Clear fault after 16 cycles by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | SLG-42 | SLG fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the RUSHMORE 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | SLG-43 | SLG fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the ELSWRTH7 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | SLG-44 | SLG fault on Underwood to WICKSVL7 to Philip 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the WICKSVL7 115kV bus, WALL 115kV bus and Philip 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | SLG-45 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to G16-094-TAP 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. G17-097 tripped | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 21S | Normal | SLG-46 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. G17-097 tripped | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 21S | Normal | SLG-47 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to SULLYBT 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. G17-097 tripped | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 21S | Normal | SLG-48 | SLG fault on Wayside to STEGALL 230kV crt 1, near Wayside for 16 cycles. Clear fault by tripping the faulted crt and STEGALL4 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | SLG-49 | SLG fault on Underwood to DRYCREEK 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | SLG-50 | SLG fault on Underwood to MAURINE 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the MAURINE 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | SLG-51 | SLG fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the ELKCRK 7 115kV bus, NEWELL 115kV bus, meantime trip the G14_001IST 115kV bus and G14_001IS_3 generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | SLG-52 | SLG fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the DRYCREEK 115kV bus and DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-01 | 3-ph fault on Philip TAP to Underwood 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-03 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-04 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-05 | 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-06 | 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-07 | 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-08 | 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-09 | 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-11 | 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-12 | 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-13 | 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-14 | 3-ph fault on Philip Tap to Philip 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-15 | 3-ph fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | No | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. G17-097 tripped | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-16 | 3-ph fault on Wayside to STEGALL 230kV crt 1, near Wayside. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-17 | 3-ph fault on Wayside 230/115/13.8kV TF T1, near Wayside 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-18 | 3-ph fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-19 | 3-ph fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-20 | 3-ph fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-21 | 3-ph fault on Philip to WANBLEE to MARTIN 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-22 | 3-ph fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-23 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-24 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-25 | 3-ph fault on OAHE to SULLYBT-ER4 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-26 | 3-ph fault on MAURINE to BISON 230kV crt 1, near MAURINE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-27 | 3-ph fault on MAURINE 230/115/13.8kV TF 1A, near MAURINE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-28 | 3-ph fault on STEGALL to DH_CS_EA-TS4 230kV crt 1, near STEGALL. Clear fault after 7 cycles by tripping the faulted crt, and DH_CS_EA-TS DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-29 | 3-ph fault on STEGALL to STEGALL_-MB4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-30 | 3-ph fault on STEGALL to VICTRYH4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-31 | 3-ph fault on DRYCREEK to RCDC 230kV crt 1, near DRYCREEK. Clear fault after 7 cycles by tripping the faulted crt, and RCDC DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-32 | 3-ph fault on DRYCREEK 230/115/13.8kV TF 1A, near DRYCREEK. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-33 | 3-ph fault on G14_001IST to MAURINE7 115kV crt 1, near G14_001IST. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-34 | 3-ph fault on Martin to SHANNON 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-35 | 3-ph fault on Martin to VETAL_TP 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-36 | 3-ph fault on IRVSIMM7 to OAHE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-37 | 3-ph fault on IRVSIMM7 to PIERRE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-56 | Prior Outage of Philip Tap to Underwood 230kV crt 1. 3-ph fault on Philip Tap to OAHE 230kV crt 1, near Philip TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-57 | Prior Outage of Philip TAP to OAHE 230kV crt 1. 3-ph fault on Philip TAP to UNDERWOOD 230kV crt 1, near PHILIP TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590). And curtail G17-014 by 60MW.
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-60 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-61 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-62 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-63 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-64 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-65 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-66 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-67 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-68 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-69 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-70 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to Philip TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-71 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-72 | Prior Outage of Underwood to DRYCREEK 230kV crt 1. 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | 3ph-73 | Prior Outage of Underwood-LNX5 to MAURINE 230kV crt 1. 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-38 | SLG fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Wayside 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-39 | SLG fault on G17-064-TAP to Underwood 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-40 | SLG fault on Philip TAP 230kV. Clear fault after 16 cycles by tripping the Philip Tap 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-41 | SLG fault on Underwood 230kV. Clear fault after 16 cycles by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-42 | SLG fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the RUSHMORE 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-43 | SLG fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the ELSWRTH7 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-44 | SLG fault on Underwood to WICKSVL7 to Philip 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the WICKSVL7 115kV bus, WALL 115kV bus and Philip 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-45 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to G16-094-TAP 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. G17-097 tripped | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-46 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. G17-097 tripped | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-47 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to SULLYBT 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. G17-097 tripped | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-48 | SLG fault on Wayside to STEGALL 230kV crt 1, near Wayside for 16 cycles. Clear fault by tripping the faulted crt and STEGALL4 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-49 | SLG fault on Underwood to DRYCREEK 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-50 | SLG fault on Underwood to MAURINE 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the MAURINE 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-51 | SLG fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the ELKCRK 7 115kV bus, NEWELL 115kV bus, meantime trip the G14_001IST 115kV bus and G14_001IS_3 generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-52 | SLG fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the DRYCREEK 115kV bus and DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-01 | 3-ph fault on Philip TAP to Underwood 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-03 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-04 | 3-ph fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-05 | 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-06 | 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-07 | 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-08 | 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-09 | 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-11 | 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-12 | 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-13 | 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-14 | 3-ph fault on Philip Tap to Philip 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-15 | 3-ph fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 28S | Normal | 3ph-16 | 3-ph fault on Wayside to STEGALL 230kV crt 1, near Wayside. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-17 | 3-ph fault on Wayside 230/115/13.8kV TF T1, near Wayside 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-18 | 3-ph fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-19 | 3-ph fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-20 | 3-ph fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-21 | 3-ph fault on Philip to WANBLEE to MARTIN 115kV crt 1, near Philip. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-22 | 3-ph fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-23 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-24 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-25 | 3-ph fault on OAHE to SULLYBT-ER4 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-26 | 3-ph fault on MAURINE to BISON 230kV crt 1, near MAURINE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-27 | 3-ph fault on MAURINE 230/115/13.8kV TF 1A, near MAURINE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-28 | 3-ph fault on STEGALL to DH_CS_EA-TS4 230kV crt 1, near STEGALL. Clear fault after 7 cycles by tripping the faulted crt, and DH_CS_EA-TS DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-29 | 3-ph fault on STEGALL to STEGALL_-MB4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-30 | 3-ph fault on STEGALL to VICTRYH4 230kV crt 1, near STEGALL. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-31 | 3-ph fault on DRYCREEK to RCDC 230kV crt 1, near DRYCREEK. Clear fault after 7 cycles by tripping the faulted crt, and RCDC DC line. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-32 | 3-ph fault on DRYCREEK 230/115/13.8kV TF 1A, near DRYCREEK. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-33 | 3-ph fault on G14_001IST to MAURINE7 115kV crt 1, near G14_001IST. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-34 | 3-ph fault on Martin to SHANNON 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-35 | 3-ph fault on Martin to VETAL_TP 115kV crt 1, near Martin. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-36 | 3-ph fault on IRVSIMM7 to OAHE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-37 | 3-ph fault on IRVSIMM7 to PIERRE 115kV crt 1, near IRVSIMM7. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-56 | Prior Outage of Philip Tap to Underwood 230kV crt 1. 3-ph fault on Philip Tap to OAHE 230kV crt 1, near Philip TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 28S | Normal | 3ph-57 | Prior Outage of Philip TAP to OAHE 230kV crt 1. 3-ph fault on Philip TAP to UNDERWOOD 230kV crt 1, near PHILIP TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 28S | Normal | 3ph-60 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-61 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-62 | Prior Outage of Underwood to RUSHMORE 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-63 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-64 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood to WICKSVL7 to PHILIP 7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-65 | Prior Outage of Underwood to ELSWRTH7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-66 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-67 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-68 | Prior Outage of Underwood to WICKSVL7 115kV crt 1. 3-ph fault on Underwood 230/115/13.8kV TF 1A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-69 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood 230/115/13.8kV TF 2A, near Underwood 115kV. Clear fault after 7 cycles. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-70 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to Philip TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-71 | Prior Outage of Underwood 230/115/13.8kV TF 1A. 3-ph fault on Underwood to G17-064-TAP 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-72 | Prior Outage of Underwood to DRYCREEK 230kV crt 1. 3-ph fault on Underwood to MAURINE 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | 3ph-73 | Prior Outage of Underwood-LNX5 to MAURINE 230kV crt 1. 3-ph fault on Underwood to DRYCREEK 230kV crt 1, near Underwood. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | SLG-38 | SLG fault on G17-064-TAP to Wayside 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Wayside 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | SLG-39 | SLG fault on G17-064-TAP to Underwood 230kV crt 1, near G17-064-TAP for 16 cycles. Clear fault by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | SLG-40 | SLG fault on Philip TAP 230kV. Clear fault after 16 cycles by tripping the Philip Tap 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | SLG-41 | SLG fault on Underwood 230kV. Clear fault after 16 cycles by tripping the Underwood 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | SLG-42 | SLG fault on Underwood to RUSHMORE to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the RUSHMORE 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | SLG-43 | SLG fault on Underwood to ELSWRTH7 to RAPIDCY7 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the ELSWRTH7 115kV bus and RAPIDCY7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | SLG-44 | SLG fault on Underwood to WICKSVL7 to Philip 115kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the WICKSVL7 115kV bus, WALL 115kV bus and Philip 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | SLG-45 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to G16-094-TAP 230kV crt 1. | P4 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 28S | Normal | SLG-46 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 28S | Normal | SLG-47 | SLG fault on Philip Tap to OAHE 230kV crt 1, near Philip Tap for 16 cycles. Clear fault by tripping the faulted crt and OAHE to SULLYBT 230kV crt 1. | P4 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 28S | Normal | SLG-48 | SLG fault on Wayside to STEGALL 230kV crt 1, near Wayside for 16 cycles. Clear fault by tripping the faulted crt and STEGALL4 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | SLG-49 | SLG fault on Underwood to DRYCREEK 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | SLG-50 | SLG fault on Underwood to MAURINE 230kV crt 1, near Underwood for 16 cycles. Clear fault by tripping the MAURINE 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | SLG-51 | SLG fault on RAPIDCY7 to ELKCRK 7 to G14_001IST 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the ELKCRK 7 115kV bus, NEWELL 115kV bus, meantime trip the G14_001IST 115kV bus and G14_001IS_3 generator. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | SLG-52 | SLG fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the DRYCREEK 115kV bus and DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | SLG-52 | SLG fault on RAPIDCY7 to DRYCREEK 115kV crt 1, near RAPIDCY7 for 16 cycles. Clear fault by tripping the DRYCREEK 115kV bus and DRYCREEK 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | SLG-53 | SLG fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the Midland 115kV bus and IRVSIMM7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | SLG-54 | SLG fault on Philip to WANBLEE to Martin 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the WANBLEE 115kV bus and Martin 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | SLG-55 | SLG fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV for 16 cycles. Clear fault with additional loss of Philip Tap 230 Kv bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-01 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV crt 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-02 | 3-ph fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-03 | 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-04 | 3-ph fault on SD.LS-LR-MB3 to KEYSTON3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-05 | 3-ph fault on HOLT.CO3 to THEDFRD3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-06 | 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-07 | 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-08 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-09 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-10 | 3-ph fault on OAHE 230/115/13.8kV TF OA No.5, near OAHE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-11 | 3-ph fault on FTTHOMP4 230/115/13.8kV TF FT2 KU1A, near FTTHOMP4 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-12 | 3-ph fault on BISON to HETINGR4 230kV crt 1, near BISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-19 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-20 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-21 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-22 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-23 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-24 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-25 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1, 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 76 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-26 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-27 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on OAHE to FTTHOMP4 230kV crt 4, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-28 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-3ph-29 | Prior Outage of BISON___-GE4 to HETINGR4 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-SLG-13 | SLG fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 for 16 cycles. Clear fault by tripping the faulted crt and HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-SLG-14 | SLG fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3 for 16 cycles. Clear fault by tripping the SIOUXCY3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | SLG-53 | SLG fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the Midland 115kV bus and IRVSIMM7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | SLG-54 | SLG fault on Philip to WANBLEE to Martin 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the WANBLEE 115kV bus and Martin 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | SLG-55 | SLG fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV for 16 cycles. Clear fault with additional loss of Philip Tap 230 Kv bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-01 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV crt 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-02 | 3-ph fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-03 | 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-04 | 3-ph fault on SD.LS-LR-MB3 to KEYSTON3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-05 | 3-ph fault on HOLT.CO3 to THEDFRD3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-06 | 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-07 | 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-08 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-09 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-10 | 3-ph fault on OAHE 230/115/13.8kV TF OA No.5, near OAHE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-11 | 3-ph fault on FTTHOMP4 230/115/13.8kV TF FT2 KU1A, near FTTHOMP4 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-12 | 3-ph fault on BISON to HETINGR4 230kV crt 1, near BISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-19 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-20 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-21 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-22 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-23 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-24 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-25 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1, 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 76 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-26 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-27 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on OAHE to FTTHOMP4 230kV crt 4, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-28 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-3ph-29 | Prior Outage of BISON___-GE4 to HETINGR4 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-SLG-13 | SLG fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 for 16 cycles. Clear fault by tripping the faulted crt and HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-SLG-14 | SLG fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3 for 16 cycles. Clear fault by tripping the SIOUXCY3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-SLG-15 | SLG fault on SD.LS-KS-MB3 to KEYSTON 345kV crt 1, near SD.LS-KS-MB3 for 16 cycles. Clear fault by tripping the SD.LS-KS-MB3 345kV and SIDNEY 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-53 | SLG fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the Midland 115kV bus and IRVSIMM7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-54 | SLG fault on Philip to WANBLEE to Martin 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the WANBLEE 115kV bus and Martin 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | SLG-55 | SLG fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV for 16 cycles. Clear fault with additional loss of Philip Tap 230 Kv bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-01 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV crt 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-02 | 3-ph fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-03 | 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-04 | 3-ph fault on SD.LS-LR-MB3 to KEYSTON3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-05 | 3-ph fault on HOLT.CO3 to THEDFRD3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-06 | 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-07 | 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-08 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-09 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-10 | 3-ph fault on OAHE 230/115/13.8kV TF OA No.5, near OAHE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-11 | 3-ph fault on FTTHOMP4 230/115/13.8kV TF FT2 KU1A, near FTTHOMP4 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-12 | 3-ph fault on BISON to HETINGR4 230kV crt 1, near BISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-19 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-20 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-21 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-22 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-23 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-24 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-25 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1, 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 76 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-26 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-27 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on OAHE to FTTHOMP4 230kV crt 4, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-28 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-3ph-29 | Prior Outage of BISON___-GE4 to HETINGR4 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-SLG-13 | SLG fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 for 16 cycles. Clear fault by tripping the faulted crt and HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-SLG-14 | SLG fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3 for 16 cycles. Clear fault by tripping the SIOUXCY3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-SLG-15 | SLG fault on SD.LS-KS-MB3 to KEYSTON 345kV crt 1, near SD.LS-KS-MB3 for 16 cycles. Clear fault by tripping the SD.LS-KS-MB3 345kV and SIDNEY 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | SLG-53 | SLG fault on Philip to Midland to IRVSIMM7 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the Midland 115kV bus and IRVSIMM7 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | SLG-54 | SLG fault on Philip to WANBLEE to Martin 115kV crt 1, near Philip for 16 cycles. Clear fault by tripping the WANBLEE 115kV bus and Martin 115kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | SLG-55 | SLG fault on Philip 230/115/13.2kV TF 1A, near Philip 115kV for 16 cycles. Clear fault with additional loss of Philip Tap 230 Kv bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-01 | 3-ph fault on SIOUXCY-LNX3 to SPLT RK3 345kV crt 1, near SIOUXCY-LNX3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-02 | 3-ph fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-03 | 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-04 | 3-ph fault on SD.LS-LR-MB3 to KEYSTON3 345kV crt 1, near SD.LS-LR-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-05 | 3-ph fault on HOLT.CO3 to THEDFRD3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-06 | 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-07 | 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-08 | 3-ph fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-09 | 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-10 | 3-ph fault on OAHE 230/115/13.8kV TF OA No.5, near OAHE 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-11 | 3-ph fault on FTTHOMP4 230/115/13.8kV TF FT2 KU1A, near FTTHOMP4 230kV. Clear fault after 7 cycles. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-12 | 3-ph fault on BISON to HETINGR4 230kV crt 1, near BISON. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P1 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-19 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-20 | Prior Outage of HOLT.CO3 to ANTELOPE 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-21 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-22 | Prior Outage of HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. 3-ph fault on SD.LS-KS-MB3 to KEYSTON3 345kV crt 1, near SD.LS-KS-MB3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-23 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-24 | Prior Outage of SD.LS-KS-MB3 to KEYSTON3 345kV crt 1. 3-ph fault on HOLT.CO3 to GR ISLD-LNX3 345kV crt 1, near HOLT.CO3. Clear fault after 6 cycles and reclose after 20 cycles. Apply fault for 6 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-25 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1, 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 76 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-26 | Prior Outage of OAHE to G16-094-TAP 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-27 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on OAHE to FTTHOMP4 230kV crt 4, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-28 | Prior Outage of OAHE to FTTHOMP4 230kV crt 3. 3-ph fault on G17-064-TAP to WAYSIDE 230kV crt 1, near G17-064-TAP. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-3ph-29 | Prior Outage of BISON___-GE4 to HETINGR4 230kV crt 1. 3-ph fault on OAHE to FTTHOMP4 230kV crt 2, near OAHE. Clear fault after 7 cycles and reclose after 20 cycles. Apply fault for 7 cycles then reopen. | P6 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-SLG-13 | SLG fault on HOLT.CO3 to ANTELOPE 345kV crt 1, near HOLT.CO3 for 16 cycles. Clear fault by tripping the faulted crt and HOLT.CO3 to GR ISLD-LNX3 345kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-SLG-14 | SLG fault on SIOUXCY3 to RAUN 345kV crt 1, near SIOUXCY3 for 16 cycles. Clear fault by tripping the SIOUXCY3 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-SLG-15 | SLG fault on SD.LS-KS-MB3 to KEYSTON 345kV crt 1, near SD.LS-KS-MB3 for 16 cycles. Clear fault by tripping the SD.LS-KS-MB3 345kV and SIDNEY 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-SLG-15 | SLG fault on SD.LS-KS-MB3 to KEYSTON 345kV crt 1, near SD.LS-KS-MB3 for 16 cycles. Clear fault by tripping the SD.LS-KS-MB3 345kV and SIDNEY 345kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-SLG-16 | SLG fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-SLG-17 | SLG fault on OAHE to FTTHOMP4 230kV crt 2, near BISON for 16 cycles. Clear fault by tripping the faulted crt and OAHE to PHILIP_Tap 230kV crt 1. | P4 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 21S | Normal | Tie-SLG-16 | SLG fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21S | Normal | Tie-SLG-17 | SLG fault on OAHE to FTTHOMP4 230kV crt 2, near BISON for 16 cycles. Clear fault by tripping the faulted crt and OAHE to PHILIP_Tap 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. G17-097 tripped | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 21S | Normal | Tie-SLG-18 | SLG fault on BISON to HETINGR4 230kV crt 1, near BISON for 16 cycles. Clear fault by tripping the BISON 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-SLG-16 | SLG fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-SLG-17 | SLG fault on OAHE to FTTHOMP4 230kV crt 2, near BISON for 16 cycles. Clear fault by tripping the faulted crt and OAHE to PHILIP_Tap 230kV crt 1. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | No | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. G17-097 tripped | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 21L-AD0 | Normal | Tie-SLG-18 | SLG fault on BISON to HETINGR4 230kV crt 1, near BISON for 16 cycles. Clear fault by tripping the BISON 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-SLG-16 | SLG fault on OAHE to G16-094-TAP 230kV crt 1, near OAHE for 16 cycles. Clear fault by tripping the faulted crt and OAHE to FTTHOMP4 230kV crt 2. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 28S | Normal | Tie-SLG-17 | SLG fault on OAHE to FTTHOMP4 230kV crt 2, near BISON for 16 cycles. Clear fault by tripping the faulted crt and OAHE to PHILIP_Tap 230kV crt 1. | P4 | Stable | Unstable | Unstable | Unstable | Unstable | Unstable | Unstable | Insufficient reactive power in the area after losing 230 kV connection to OHAE. Voltage drops below 0.9 and keeps triggering LVRT of G17-014 and G17-097. | Build 2nd Ckt from Philip Tap to OHAE. | Add 30MVA SVC at G17-014 (588590)
North | 17 - Western South Dakota | 28S | Normal | Tie-SLG-18 | SLG fault on BISON to HETINGR4 230kV crt 1, near BISON for 16 cycles. Clear fault by tripping the BISON 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes
North | 17 - Western South Dakota | 19W | Normal | Tie-SLG-18 | SLG fault on BISON to HETINGR4 230kV crt 1, near BISON for 16 cycles. Clear fault by tripping the BISON 230kV bus. | P4 | Stable | Yes | Yes | Yes | Yes | Yes | Yes

## Sensitivity Dispatch
Gen Number | Bus | Close Proximity | Group | Season | MW Amount
GEN-2017-011 | 560071 | None | 01 - Woodward | None | None
GEN-2017-047 | 588863 | None | 02 - Hitchland | None | None
GEN-2017-100 | 589383 | Bus: 515905 ID: 1 Name: G08_047_311 | 02 - Hitchland | ALL | 249.9
GEN-2017-100 | 589383 | Bus: 523107 ID: 1 Name: G06_044_254 | 02 - Hitchland | ALL | 80
GEN-2017-100 | 589383 | Bus: 523121 ID: 1 Name: G02_008_159 | 02 - Hitchland | ALL | 79.5
GEN-2017-100 | 589383 | Bus: 523122 ID: 1 Name: G02_008_161 | 02 - Hitchland | ALL | 78
GEN-2017-100 | 589383 | Bus: 523123 ID: 1 Name: G02_008_160 | 02 - Hitchland | ALL | 82.5
GEN-2017-100 | 589383 | Bus: 523160 ID: 1 Name: G06_020_230 | 02 - Hitchland | ALL | 20
GEN-2017-100 | 589383 | Bus: 523170 ID: 1 Name: G07_046_281 | 02 - Hitchland | ALL | 20
GEN-2017-100 | 589383 | Bus: 523170 ID: 2 Name: G07_046_281 | 02 - Hitchland | ALL | 78
GEN-2017-100 | 589383 | Bus: 523201 ID: 1 Name: G02_009_163 | 02 - Hitchland | ALL | 80
GEN-2017-100 | 589383 | Bus: 524285 ID: 1 Name: G02_022_165 | 02 - Hitchland | ALL | 161
GEN-2017-100 | 589383 | Bus: 524287 ID: 1 Name: G02_022_166 | 02 - Hitchland | ALL | 78.2
GEN-2017-100 | 589383 | Bus: 539653 ID: 1 Name: CIM-PLT | 02 - Hitchland | ALL | 58
GEN-2017-100 | 589383 | Bus: 576400 ID: 1 Name: G10_014_359 | 02 - Hitchland | ALL | 177.1
GEN-2017-100 | 589383 | Bus: 576410 ID: 1 Name: G10_014_360 | 02 - Hitchland | ALL | 181.7
GEN-2017-100 | 589383 | Bus: 579373 ID: 1 Name: G06_044_255 | 02 - Hitchland | ALL | 80
GEN-2017-100 | 589383 | Bus: 579376 ID: 1 Name: G06_044_257 | 02 - Hitchland | ALL | 76
GEN-2017-100 | 589383 | Bus: 579380 ID: 1 Name: G06_044_256 | 02 - Hitchland | ALL | 134
GEN-2017-100 | 589383 | Bus: 579413 ID: 1 Name: G08_051_314 | 02 - Hitchland | ALL | 161
GEN-2017-100 | 589383 | Bus: 599106 ID: 1 Name: G08_051_313 | 02 - Hitchland | ALL | 161
GEN-2017-100 | 589383 | Bus: 599148 ID: 1 Name: G11_022_398 | 02 - Hitchland | ALL | 149.5
GEN-2017-100 | 589383 | Bus: 599150 ID: 1 Name: G11_022_397 | 02 - Hitchland | ALL | 149.5
GEN-2017-018 | 539801 | None | 03 - Spearville | None | None
GEN-2017-021 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 - Spearville | 19W | 384
GEN-2017-021 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 - Spearville | 21L | 384
GEN-2017-021 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 - Spearville | 21S | 384
GEN-2017-021 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 - Spearville | 28S | 384
GEN-2017-032 | 588754 | Bus: 599951 ID: 1 Name: Lamar | 03 - Spearville | 19W | 1000
GEN-2017-032 | 588754 | Bus: 599951 ID: 1 Name: Lamar | 03 - Spearville | 21L | 1000
GEN-2017-032 | 588754 | Bus: 599951 ID: 1 Name: Lamar | 03 - Spearville | 21S | 1000
GEN-2017-032 | 588754 | Bus: 599951 ID: 1 Name: Lamar | 03 - Spearville | 28S | 1000
GEN-2017-032 | 588754 | Bus: 531447 ID: 1 Name: Holcomb | 03 - Spearville | 19W | 384
GEN-2017-032 | 588754 | Bus: 531447 ID: 1 Name: Holcomb | 03 - Spearville | 21L | 384
GEN-2017-032 | 588754 | Bus: 531447 ID: 1 Name: Holcomb | 03 - Spearville | 21S | 384
GEN-2017-032 | 588754 | Bus: 531447 ID: 1 Name: Holcomb | 03 - Spearville | 28S | 384
GEN-2017-099 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 - Spearville | 19W | 384
GEN-2017-099 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 - Spearville | 21L | 384
GEN-2017-099 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 - Spearville | 21S | 384
GEN-2017-099 | 588654 | Bus: 531447 ID: 1 Name: Holcomb | 03 - Spearville | 28S | 384
GEN-2017-033 | 588763, 588767 | Name: G15-093-GEN20.6900 Bus Number: 563273 ID: 2 | 06 - South Texas Panhandle/New Mexico | ALL | 110
GEN-2017-033 | 588763, 588768 | Name: G16-091-GEN10.6900 Bus Number: 587743 ID: 1 | 06 - South Texas Panhandle/New Mexico | ALL | 303.6
GEN-2017-033 | 588763, 588769 | Name: G16-095-GEN10.6900 Bus Number: 587773 ID: 1 | 06 - South Texas Panhandle/New Mexico | ALL | 200
GEN-2017-033 | 588763, 588770 | Name: COM1-1 13.800 Bus Number: 511851 ID: 1 | 06 - South Texas Panhandle/New Mexico | 19W | 88
GEN-2017-033 | 588763, 588771 | Name: COM1-1 13.800 Bus Number: 511851 ID: 1 | 06 - South Texas Panhandle/New Mexico | 21L | 88
GEN-2017-033 | 588763, 588772 | Name: COM1-1 13.800 Bus Number: 511851 ID: 1 | 06 - South Texas Panhandle/New Mexico | 21S | 88
GEN-2017-033 | 588763, 588773 | Name: COM1-1 13.800 Bus Number: 511851 ID: 1 | 06 - South Texas Panhandle/New Mexico | 28S | 82
GEN-2017-033 | 588763, 588774 | Name: COM3-1 13.800 Bus Number: 511853 ID: 1 | 06 - South Texas Panhandle/New Mexico | 19W | 80
GEN-2017-033 | 588763, 588775 | Name: COM3-1 13.800 Bus Number: 511853 ID: 1 | 06 - South Texas Panhandle/New Mexico | 21L | 80
GEN-2017-033 | 588763, 588776 | Name: COM3-1 13.800 Bus Number: 511853 ID: 1 | 06 - South Texas Panhandle/New Mexico | 21S | 80
GEN-2017-033 | 588763, 588777 | Name: COM3-1 13.800 Bus Number: 511853 ID: 1 | 06 - South Texas Panhandle/New Mexico | 28S | 72
GEN-2017-033 | 588763, 588778 | Name: COM2-1 13.800 Bus Number: 511852 ID: 1 | 06 - South Texas Panhandle/New Mexico | 19W | 83.5
GEN-2017-033 | 588763, 588779 | Name: COM2-1 13.800 Bus Number: 511852 ID: 1 | 06 - South Texas Panhandle/New Mexico | 21L | 83.5
GEN-2017-033 | 588763, 588780 | Name: COM2-1 13.800 Bus Number: 511852 ID: 1 | 06 - South Texas Panhandle/New Mexico | 21S | 83.5
GEN-2017-033 | 588763, 588781 | Name: COM2-1 13.800 Bus Number: 511852 ID: 1 | 06 - South Texas Panhandle/New Mexico | 28S | 76.5
GEN-2017-033 | 588763, 588782 | Name: ELK_2 1 18.000 Bus Number: 525845 ID: 1 | 06 - South Texas Panhandle/New Mexico | 19W | 208
GEN-2017-033 | 588763, 588783 | Name: ELK_2 1 18.000 Bus Number: 525845 ID: 1 | 06 - South Texas Panhandle/New Mexico | 21L | 196
GEN-2017-033 | 588763, 588784 | Name: ELK_2 1 18.000 Bus Number: 525845 ID: 1 | 06 - South Texas Panhandle/New Mexico | 21S | 196
GEN-2017-033 | 588763, 588785 | Name: ELK_2 1 18.000 Bus Number: 525845 ID: 1 | 06 - South Texas Panhandle/New Mexico | 28S | 196
GEN-2017-033 | 588763, 588786 | Name: ELK_1 118.000 Bus Number: 525844 ID: 1 | 06 - South Texas Panhandle/New Mexico | 19W | 203
GEN-2017-033 | 588763, 588787 | Name: ELK_1 118.000 Bus Number: 525844 ID: 1 | 06 - South Texas Panhandle/New Mexico | 21L | 196
GEN-2017-033 | 588763, 588788 | Name: ELK_1 118.000 Bus Number: 525844 ID: 1 | 06 - South Texas Panhandle/New Mexico | 21S | 196
GEN-2017-033 | 588763, 588789 | Name: ELK_1 118.000 Bus Number: 525844 ID: 1 | 06 - South Texas Panhandle/New Mexico | 28S | 196
GEN-2017-033 | 588763, 588790 | Name: ANTELOPE_B Bus Number: 525842 ID: B1 | 06 - South Texas Panhandle/New Mexico | ALL | 55.122
GEN-2017-033 | 588763, 588791 | Name: ANTELOPE_A Bus Number: 525841 ID: A1 | 06 - South Texas Panhandle/New Mexico | ALL | 55.122
GEN-2017-033 | 588763, 588792 | Name: ANTELOPE_C Bus Number: 525843 ID: C1 | 06 - South Texas Panhandle/New Mexico | ALL | 55.122
GEN-2017-033 | 588763, 588793 | Name: G12-020-GEN Bus Number: 583346 ID: 1 | 06 - South Texas Panhandle/New Mexico | ALL | 48
GEN-2017-033 | 588763, 588794 | Name: G12-020-GEN Bus Number: 583343 ID: 1 | 06 - South Texas Panhandle/New Mexico | ALL | 430
GEN-2016-037 | 587233 | Bus: 587773 ID: 1 Name: G16_095_662 | 07 - Southwestern Oklahoma | ALL | 200
GEN-2016-037 | 587233 | Bus: 587743 ID: 1 Name: G16_091_658 | 07 - Southwestern Oklahoma | ALL | 303.6
GEN-2016-037 | 587233 | Bus: 563273 ID: 2 Name: G15-093-GEN | 07 - Southwestern Oklahoma | ALL | 110
GEN-2016-037 | 587233 | Bus: 563272 ID: 1 Name: G15-093-GEN | 07 - Southwestern Oklahoma | ALL | 140
GEN-2016-037 | 587233 | Bus: 521112 ID: 1 Name: ORME | 07 - Southwestern Oklahoma | ALL | 49.84
GEN-2016-037 | 587233 | Bus: 521111 ID: 1 Name : ORME | 07 - Southwestern Oklahoma | ALL | 48.5
GEN-2016-037 | 587233 | Bus: 521110 ID: 1 Name: ORME | 07 - Southwestern Oklahoma | ALL | 49.1
GEN-2016-037 | 587233 | Bus: 521102 ID: 1 Name: GENCO | 07 - Southwestern Oklahoma | ALL | 45.5
GEN-2016-037 | 587233 | Bus: 521101 ID: 1 Name: GENCO | 07 - Southwestern Oklahoma | ALL | 46.1
GEN-2016-037 | 587233 | Bus: 520813 ID: 1 Name: ANADRK | 07 - Southwestern Oklahoma | ALL | 96.8
GEN-2016-037 | 587233 | Bus: 520812 ID: 1 Name: ANADRK | 07 - Southwestern Oklahoma | ALL | 99.9
GEN-2016-037 | 587233 | Bus: 520811 ID: 1 Name: ANADRK | 07 - Southwestern Oklahoma | ALL | 98.3
GEN-2016-037 | 587233 | Bus: 520809 ID: 1 Name: ANADRK | 07 - Southwestern Oklahoma | ALL | 42.12
GEN-2016-037 | 587233 | Bus: 520808 ID: 1 Name: ANADRK | 07 - Southwestern Oklahoma | ALL | 14.3
GEN-2016-037 | 587233 | Bus: 520807 ID: 1 Name: ANADRK | 07 - Southwestern Oklahoma | ALL | 14.6
GEN-2016-037 | 587233 | Bus: 515921 ID 1 Name: MNCOWNG | 07 - Southwestern Oklahoma | ALL | 106.47
GEN-2016-037 | 587233 | Bus: 515907 ID: 1 Name: MNCOWNG | 07 - Southwestern Oklahoma | ALL | 202.5
GEN-2016-037 | 587233 | Bus: 511968 ID: W2 Name: G06_002_201 | 07 - Southwestern Oklahoma | ALL | 28.8
GEN-2016-037 | 587233 | Bus: 511968 ID: W1 Name: G06_002_202 | 07 - Southwestern Oklahoma | ALL | 72
GEN-2016-037 | 587233 | Bus: 511967 ID: 1 Name: ELK_CITY_WG | 07 - Southwestern Oklahoma | ALL | 98.9
GEN-2017-036 | 588783 | Bus: 584553 ID: 1 Name: G15_013_549 | 07 - Southwestern Oklahoma | ALL | 119.952
GEN-2017-036 | 588783 | Bus: 511852 ID: 1 Name: COM | 07 - Southwestern Oklahoma | 19W | 83.5
GEN-2017-036 | 588783 | Bus: 511852 ID: 1 Name: COM | 07 - Southwestern Oklahoma | 21L | 83.5
GEN-2017-036 | 588783 | Bus: 511852 ID: 1 Name: COM | 07 - Southwestern Oklahoma | 21S | 83.5
GEN-2017-036 | 588783 | Bus: 511852 ID: 1 Name: COM | 07 - Southwestern Oklahoma | 28S | 76.5
GEN-2017-036 | 588783 | Bus: 511851 ID: 1 Name: COM | 07 - Southwestern Oklahoma | 19W | 88
GEN-2017-036 | 588783 | Bus: 511851 ID: 1 Name: COM | 07 - Southwestern Oklahoma | 21L | 88
GEN-2017-036 | 588783 | Bus: 511851 ID: 1 Name: COM | 07 - Southwestern Oklahoma | 21S | 88
GEN-2017-036 | 588783 | Bus: 511851 ID: 1 Name: COM | 07 - Southwestern Oklahoma | 28S | 82
GEN-2017-036 | 588783 | Bus: 511850 ID: 1 Name: SWS | 07 - Southwestern Oklahoma | 19W | 85
GEN-2017-036 | 588783 | Bus: 511850 ID: 1 Name: SWS | 07 - Southwestern Oklahoma | 21L | 85
GEN-2017-036 | 588783 | Bus: 511850 ID: 1 Name: SWS | 07 - Southwestern Oklahoma | 21S | 85
GEN-2017-036 | 588783 | Bus: 511850 ID: 1 Name: SWS | 07 - Southwestern Oklahoma | 28S | 75
GEN-2017-036 | 588783 | Bus: 511849 ID: 1 Name: SWS | 07 - Southwestern Oklahoma | 19W | 85.8
GEN-2017-036 | 588783 | Bus: 511849 ID: 1 Name: SWS | 07 - Southwestern Oklahoma | 21L | 85.8
GEN-2017-036 | 588783 | Bus: 511849 ID: 1 Name: SWS | 07 - Southwestern Oklahoma | 21S | 85.8
GEN-2017-036 | 588783 | Bus: 511849 ID: 1 Name: SWS | 07 - Southwestern Oklahoma | 28S | 76.8
GEN-2017-036 | 588783 | Bus: 511848 ID: 1 Name: SWS | 07 - Southwestern Oklahoma | ALL | 328.5
GEN-2017-036 | 588783 | Bus: 511847 ID: 1 Name: SWS | 07 - Southwestern Oklahoma | ALL | 82.2
GEN-2017-036 | 588783 | Bus: 511846 ID:1 Name: SWS | 07 - Southwestern Oklahoma | 19W | 79.1
GEN-2017-036 | 588783 | Bus: 511846 ID:1 Name: SWS | 07 - Southwestern Oklahoma | 21L | 79.1
GEN-2017-036 | 588783 | Bus: 511846 ID:1 Name: SWS | 07 - Southwestern Oklahoma | 21S | 79.1
GEN-2017-036 | 588783 | Bus: 511846 ID:1 Name: SWS | 07 - Southwestern Oklahoma | 28S | 75.1
GEN-2017-005 | 588504 | Bus: 589203 ID: 1 Name: GEN-2017-082 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 24
GEN-2017-005 | 588504 | Bus: 589203 ID: 1 Name: GEN-2017-082 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 24
GEN-2017-005 | 588504 | Bus: 589203 ID: 1 Name: GEN-2017-082 | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 24
GEN-2017-005 | 588504 | Bus: 589203 ID: 1 Name: GEN-2017-082 | 08 - North Oklahoma/South Central Kansas | 28S | 24
GEN-2017-005 | 588504 | Bus: 589204 ID: 1 Name: GEN-2017-082 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 125.4
GEN-2017-005 | 588504 | Bus: 589204 ID: 1 Name: GEN-2017-082 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 125.4
GEN-2017-005 | 588504 | Bus: 589204 ID: 1 Name: GEN-2017-082 | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 125.4
GEN-2017-005 | 588504 | Bus: 589204 ID: 1 Name: GEN-2017-082 | 08 - North Oklahoma/South Central Kansas | 28S | 125.4
GEN-2017-005 | 588504 | Bus: 542955 ID: 1 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 810.8
GEN-2017-005 | 588504 | Bus: 542955 ID: 1 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 810.8
GEN-2017-005 | 588504 | Bus: 542955 ID: 1 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 810.8
GEN-2017-005 | 588504 | Bus: 542955 ID: 1 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 28S | 810.8
GEN-2017-005 | 588504 | Bus: 542956 ID: 2 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 717.8
GEN-2017-005 | 588504 | Bus: 542956 ID: 2 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 717.8
GEN-2017-005 | 588504 | Bus: 542956 ID: 2 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 717.8
GEN-2017-005 | 588504 | Bus: 542956 ID: 2 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 28S | 717.8
GEN-2017-005 | 588504 | Bus: 533774 ID: 1 Name: ASGI-2012-008 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 1.6
GEN-2017-005 | 588504 | Bus: 533774 ID: 1 Name: ASGI-2012-008 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 1.6
GEN-2017-005 | 588504 | Bus: 533774 ID: 1 Name: ASGI-2012-008 | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 1.6
GEN-2017-005 | 588504 | Bus: 533774 ID: 1 Name: ASGI-2012-008 | 08 - North Oklahoma/South Central Kansas | 28S | 1.6
GEN-2017-005 | 588504 | Bus: 533774 ID: 2 Name: ASGI-2012-008 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 1.95
GEN-2017-005 | 588504 | Bus: 533774 ID: 2 Name: ASGI-2012-008 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 1.95
GEN-2017-005 | 588504 | Bus: 533774 ID: 2 Name: ASGI-2012-008 | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 1.95
GEN-2017-005 | 588504 | Bus: 533774 ID: 2 Name: ASGI-2012-008 | 08 - North Oklahoma/South Central Kansas | 28S | 1.95
GEN-2017-005 | 588504 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 16
GEN-2017-005 | 588504 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 16
GEN-2017-005 | 588504 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 16
GEN-2017-005 | 588504 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 28S | 16
GEN-2017-005 | 588504 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 17
GEN-2017-005 | 588504 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 17
GEN-2017-005 | 588504 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 17
GEN-2017-005 | 588504 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 28S | 17
GEN-2017-005 | 588504 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 173.67
GEN-2017-005 | 588504 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 173.67
GEN-2017-005 | 588504 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 142
GEN-2017-005 | 588504 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 28S | 142
GEN-2017-005 | 588504 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 136.33
GEN-2017-005 | 588504 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 136.33
GEN-2017-005 | 588504 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 114
GEN-2017-005 | 588504 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 28S | 114
GEN-2017-005 | 588504 | Bus: 543069 ID: 5 Name: ASGI-2016-003 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 3.1
GEN-2017-005 | 588504 | Bus: 543069 ID: 5 Name: ASGI-2016-003 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 3.1
GEN-2017-005 | 588504 | Bus: 543069 ID: 5 Name: ASGI-2016-003 | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 3.1
GEN-2017-005 | 588504 | Bus: 543069 ID: 5 Name: ASGI-2016-003 | 08 - North Oklahoma/South Central Kansas | 28S | 3.1
GEN-2017-005 | 588504 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 121.488
GEN-2017-005 | 588504 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 121.488
GEN-2017-005 | 588504 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 85.3
GEN-2017-005 | 588504 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 28S | 85.3
GEN-2017-009 | 588544 | Bus: 542955 ID: 1 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 810.8
GEN-2017-009 | 588544 | Bus: 542955 ID: 1 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 810.8
GEN-2017-009 | 588544 | Bus: 542955 ID: 1 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 810.8
GEN-2017-009 | 588544 | Bus: 542955 ID: 1 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 28S | 810.8
GEN-2017-009 | 588544 | Bus: 542956 ID: 2 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 717.8
GEN-2017-009 | 588544 | Bus: 542956 ID: 2 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 717.8
GEN-2017-009 | 588544 | Bus: 542956 ID: 2 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 717.8
GEN-2017-009 | 588544 | Bus: 542956 ID: 2 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 28S | 717.8
GEN-2017-009 | 588544 | Bus: 532751 ID: 1 Name: Wolfcreek | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 1286
GEN-2017-009 | 588544 | Bus: 532751 ID: 1 Name: Wolfcreek | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 1261
GEN-2017-009 | 588544 | Bus: 532751 ID: 1 Name: Wolfcreek | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 1261
GEN-2017-009 | 588544 | Bus: 532751 ID: 1 Name: Wolfcreek | 08 - North Oklahoma/South Central Kansas | 28S | 1261
GEN-2017-009 | 588544 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 121.488
GEN-2017-009 | 588544 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 121.488
GEN-2017-009 | 588544 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 85.3
GEN-2017-009 | 588544 | Bus: 529201 ID: 1 Name: GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 28S | 85.3
GEN-2017-009 | 588544 | Bus: 511840 ID: 1 Name: Northeastern | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 499.7
GEN-2017-009 | 588544 | Bus: 511840 ID: 1 Name: Northeastern | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 499.7
GEN-2017-009 | 588544 | Bus: 511840 ID: 1 Name: Northeastern | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 499.7
GEN-2017-009 | 588544 | Bus: 511840 ID: 1 Name: Northeastern | 08 - North Oklahoma/South Central Kansas | 28S | 491.2
GEN-2017-009 | 588544 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 16
GEN-2017-009 | 588544 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 16
GEN-2017-009 | 588544 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 16
GEN-2017-009 | 588544 | Bus: 547647 ID: 1 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 28S | 16
GEN-2017-009 | 588544 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 17
GEN-2017-009 | 588544 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 17
GEN-2017-009 | 588544 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 17
GEN-2017-009 | 588544 | Bus: 547647 ID: 2 Name: GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 28S | 17
GEN-2017-009 | 588544 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 173.67
GEN-2017-009 | 588544 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 173.67
GEN-2017-009 | 588544 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 142
GEN-2017-009 | 588544 | Bus: 547642 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 28S | 142
GEN-2017-009 | 588544 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 136.33
GEN-2017-009 | 588544 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 136.33
GEN-2017-009 | 588544 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 114
GEN-2017-009 | 588544 | Bus: 547643 ID: 1 Name: GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 28S | 114
GEN-2017-022 | 588664 | Bus: 542955 ID: 1 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 810.8
GEN-2017-022 | 588664 | Bus: 542955 ID: 1 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 810.8
GEN-2017-022 | 588664 | Bus: 542955 ID: 1 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 810.8
GEN-2017-022 | 588664 | Bus: 542955 ID: 1 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 28S | 810.8
GEN-2017-022 | 588664 | Bus: 542956 ID: 2 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 717.8
GEN-2017-022 | 588664 | Bus: 542956 ID: 2 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 717.8
GEN-2017-022 | 588664 | Bus: 542956 ID: 2 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 717.8
GEN-2017-022 | 588664 | Bus: 542956 ID: 2 Name: Lacygne | 08 - North Oklahoma/South Central Kansas | 28S | 717.8
GEN-2017-022 | 588664 | Bus: 533592 ID: 1 Name: Getty | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity C) | 35
GEN-2017-022 | 588664 | Bus: 533592 ID: 1 Name: Getty | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity C) | 35
GEN-2017-022 | 588664 | Bus: 533592 ID: 1 Name: Getty | 08 - North Oklahoma/South Central Kansas | 21S (Sensitivity C) | 35
GEN-2017-022 | 588664 | Bus: 533592 ID: 1 Name: Getty | 08 - North Oklahoma/South Central Kansas | 28S | 35
GEN-2017-040 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 551
GEN-2017-040 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 551
GEN-2017-040 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 21S | 551
GEN-2017-040 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 28S | 551
GEN-2017-040 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 557
GEN-2017-040 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 557
GEN-2017-040 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 21S | 557
GEN-2017-040 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 28S | 557
GEN-2017-040 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 567
GEN-2017-040 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 567
GEN-2017-040 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 21S | 567
GEN-2017-040 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 28S | 567
GEN-2017-061 | 512742 | Bus: 512689 ID: 1 Name: GRDA | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 0
GEN-2017-061 | 512742 | Bus: 512689 ID: 1 Name: GRDA | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 0
GEN-2017-061 | 512742 | Bus: 512689 ID: 1 Name: GRDA | 08 - North Oklahoma/South Central Kansas | 21S | 0
GEN-2017-061 | 512742 | Bus: 512689 ID: 1 Name: GRDA | 08 - North Oklahoma/South Central Kansas | 28S | 0
GEN-2017-061 | 512742 | Bus: 512688 ID: 2 Name: GRDA | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 520
GEN-2017-061 | 512742 | Bus: 512688 ID: 2 Name: GRDA | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 520
GEN-2017-061 | 512742 | Bus: 512688 ID: 2 Name: GRDA | 08 - North Oklahoma/South Central Kansas | 21S | 520
GEN-2017-061 | 512742 | Bus: 512688 ID: 2 Name: GRDA | 08 - North Oklahoma/South Central Kansas | 28S | 520
GEN-2017-061 | 512742 | Bus: 300031 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 163.1
GEN-2017-061 | 512742 | Bus: 300031 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 154.9
GEN-2017-061 | 512742 | Bus: 300031 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 21S | 154.9
GEN-2017-061 | 512742 | Bus: 300031 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 28S | 154.9
GEN-2017-061 | 512742 | Bus: 300032 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 157
GEN-2017-061 | 512742 | Bus: 300032 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 149.1
GEN-2017-061 | 512742 | Bus: 300032 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 21S | 149.1
GEN-2017-061 | 512742 | Bus: 300032 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 28S | 149.1
GEN-2017-061 | 512742 | Bus: 300033 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 157
GEN-2017-061 | 512742 | Bus: 300033 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 149.1
GEN-2017-061 | 512742 | Bus: 300033 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 21S | 149.1
GEN-2017-061 | 512742 | Bus: 300033 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 28S | 149.1
GEN-2017-061 | 512742 | Bus: 300020 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 157
GEN-2017-061 | 512742 | Bus: 300020 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 0
GEN-2017-061 | 512742 | Bus: 300020 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 21S | 149.1
GEN-2017-061 | 512742 | Bus: 300020 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 28S | 149.1
GEN-2017-061 | 512742 | Bus: 300021 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 157
GEN-2017-061 | 512742 | Bus: 300021 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 149.1
GEN-2017-061 | 512742 | Bus: 300021 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 21S | 149.1
GEN-2017-061 | 512742 | Bus: 300021 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 28S | 149.1
GEN-2017-061 | 512742 | Bus: 300024 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 163.1
GEN-2017-061 | 512742 | Bus: 300024 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 154.9
GEN-2017-061 | 512742 | Bus: 300024 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 21S | 154.9
GEN-2017-061 | 512742 | Bus: 300024 ID: 1 Name: Choteau | 08 - North Oklahoma/South Central Kansas | 28S | 154.9
GEN-2017-061 | 512742 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 199.5
GEN-2017-061 | 512742 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 199.5
GEN-2017-061 | 512742 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 21S | 191.8
GEN-2017-061 | 512742 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 28S | 191.8
GEN-2017-061 | 512742 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 360
GEN-2017-061 | 512742 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 360
GEN-2017-061 | 512742 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 21S | 324.6
GEN-2017-061 | 512742 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 28S | 324.6
GEN-2017-061 | 512742 | Bus: 512608 ID: 1 Name: Salina | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512608 ID: 1 Name: Salina | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512608 ID: 1 Name: Salina | 08 - North Oklahoma/South Central Kansas | 21S | 43
GEN-2017-061 | 512742 | Bus: 512608 ID: 1 Name: Salina | 08 - North Oklahoma/South Central Kansas | 28S | 43
GEN-2017-061 | 512742 | Bus: 512612 ID: 5 Name: Salina | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512612 ID: 5 Name: Salina | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512612 ID: 5 Name: Salina | 08 - North Oklahoma/South Central Kansas | 21S | 43
GEN-2017-061 | 512742 | Bus: 512612 ID: 5 Name: Salina | 08 - North Oklahoma/South Central Kansas | 28S | 43
GEN-2017-061 | 512742 | Bus: 512611 ID: 4 Name: Salina | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512611 ID: 4 Name: Salina | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512611 ID: 4 Name: Salina | 08 - North Oklahoma/South Central Kansas | 21S | 43
GEN-2017-061 | 512742 | Bus: 512611 ID: 4 Name: Salina | 08 - North Oklahoma/South Central Kansas | 28S | 43
GEN-2017-061 | 512742 | Bus: 512609 ID: 2 Name: Salina | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512609 ID: 2 Name: Salina | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512609 ID: 2 Name: Salina | 08 - North Oklahoma/South Central Kansas | 21S | 43
GEN-2017-061 | 512742 | Bus: 512609 ID: 2 Name: Salina | 08 - North Oklahoma/South Central Kansas | 28S | 43
GEN-2017-061 | 512742 | Bus: 512613 ID: 6 Name: Salina | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512613 ID: 6 Name: Salina | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512613 ID: 6 Name: Salina | 08 - North Oklahoma/South Central Kansas | 21S | 43
GEN-2017-061 | 512742 | Bus: 512613 ID: 6 Name: Salina | 08 - North Oklahoma/South Central Kansas | 28S | 43
GEN-2017-061 | 512742 | Bus: 512610 ID: 3 Name: Salina | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512610 ID: 3 Name: Salina | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 43
GEN-2017-061 | 512742 | Bus: 512610 ID: 3 Name: Salina | 08 - North Oklahoma/South Central Kansas | 21S | 43
GEN-2017-061 | 512742 | Bus: 512610 ID: 3 Name: Salina | 08 - North Oklahoma/South Central Kansas | 28S | 43
GEN-2017-061 | 512742 | Bus: 512847 ID: 4 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512847 ID: 4 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512847 ID: 4 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 21S | 32
GEN-2017-061 | 512742 | Bus: 512847 ID: 4 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 28S | 32
GEN-2017-061 | 512742 | Bus: 512846 ID: 1 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512846 ID: 1 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512846 ID: 1 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 21S | 32
GEN-2017-061 | 512742 | Bus: 512846 ID: 1 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 28S | 32
GEN-2017-061 | 512742 | Bus: 512600 ID: 2 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512600 ID: 2 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512600 ID: 2 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 21S | 32
GEN-2017-061 | 512742 | Bus: 512600 ID: 2 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 28S | 32
GEN-2017-061 | 512742 | Bus: 512601 ID: 3 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512601 ID: 3 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 32
GEN-2017-061 | 512742 | Bus: 512601 ID: 3 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 21S | 32
GEN-2017-061 | 512742 | Bus: 512601 ID: 3 Name: Kerr | 08 - North Oklahoma/South Central Kansas | 28S | 32
GEN-2017-068 | 532796 | Bus: 532724 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 90
GEN-2017-068 | 532796 | Bus: 532724 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 76
GEN-2017-068 | 532796 | Bus: 532724 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 21S | 72
GEN-2017-068 | 532796 | Bus: 532724 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 28S | 72
GEN-2017-068 | 532796 | Bus: 532725 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 165
GEN-2017-068 | 532796 | Bus: 532725 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 155
GEN-2017-068 | 532796 | Bus: 532725 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 21S | 147
GEN-2017-068 | 532796 | Bus: 532725 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 28S | 147
GEN-2017-068 | 532796 | Bus: 532723 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 90
GEN-2017-068 | 532796 | Bus: 532723 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 76
GEN-2017-068 | 532796 | Bus: 532723 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 21S | 72
GEN-2017-068 | 532796 | Bus: 532723 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 28S | 72
GEN-2017-068 | 532796 | Bus: 532722 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 0
GEN-2017-068 | 532796 | Bus: 532722 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 0
GEN-2017-068 | 532796 | Bus: 532722 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 21S | 0
GEN-2017-068 | 532796 | Bus: 532722 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 28S | 0
GEN-2017-068 | 532796 | Bus: 532721 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 0
GEN-2017-068 | 532796 | Bus: 532721 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 0
GEN-2017-068 | 532796 | Bus: 532721 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 21S | 0
GEN-2017-068 | 532796 | Bus: 532721 ID: 1 Name: EEC | 08 - North Oklahoma/South Central Kansas | 28S | 0
GEN-2017-068 | 532796 | Bus: 532743 ID: 6 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 170
GEN-2017-068 | 532796 | Bus: 532743 ID: 6 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 164
GEN-2017-068 | 532796 | Bus: 532743 ID: 6 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 21S | 155
GEN-2017-068 | 532796 | Bus: 532743 ID: 6 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 28S | 155
GEN-2017-068 | 532796 | Bus: 532741 ID: 4 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 50
GEN-2017-068 | 532796 | Bus: 532741 ID: 4 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 49
GEN-2017-068 | 532796 | Bus: 532741 ID: 4 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 21S | 44
GEN-2017-068 | 532796 | Bus: 532741 ID: 4 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 28S | 44
GEN-2017-068 | 532796 | Bus: 532741 ID: 3 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 50
GEN-2017-068 | 532796 | Bus: 532741 ID: 3 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 49
GEN-2017-068 | 532796 | Bus: 532741 ID: 3 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 21S | 44
GEN-2017-068 | 532796 | Bus: 532741 ID: 3 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 28S | 44
GEN-2017-068 | 532796 | Bus: 532742 ID: 5 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 170
GEN-2017-068 | 532796 | Bus: 532742 ID: 5 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 164
GEN-2017-068 | 532796 | Bus: 532742 ID: 5 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 21S | 155
GEN-2017-068 | 532796 | Bus: 532742 ID: 5 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 28S | 155
GEN-2017-068 | 532796 | Bus: 532740 ID: 2 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 50
GEN-2017-068 | 532796 | Bus: 532740 ID: 2 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 49
GEN-2017-068 | 532796 | Bus: 532740 ID: 2 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 21S | 44
GEN-2017-068 | 532796 | Bus: 532740 ID: 2 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 28S | 44
GEN-2017-068 | 532796 | Bus: 532740 ID: 1 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 50
GEN-2017-068 | 532796 | Bus: 532740 ID: 1 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 49
GEN-2017-068 | 532796 | Bus: 532740 ID: 1 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 21S | 44
GEN-2017-068 | 532796 | Bus: 532740 ID: 1 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 28S | 44
GEN-2017-068 | 532796 | Bus: 532744 ID: 7 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 170
GEN-2017-068 | 532796 | Bus: 532744 ID: 7 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 164
GEN-2017-068 | 532796 | Bus: 532744 ID: 7 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 21S | 155
GEN-2017-068 | 532796 | Bus: 532744 ID: 7 Name: EMPEC | 08 - North Oklahoma/South Central Kansas | 28S | 155
GEN-2017-071 | 515417 | Bus: 505612 ID: 1 Name: Keystone | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 35
GEN-2017-071 | 515417 | Bus: 505612 ID: 1 Name: Keystone | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 35
GEN-2017-071 | 515417 | Bus: 505612 ID: 1 Name: Keystone | 08 - North Oklahoma/South Central Kansas | 21S | 35
GEN-2017-071 | 515417 | Bus: 505612 ID: 1 Name: Keystone | 08 - North Oklahoma/South Central Kansas | 28S | 35
GEN-2017-072 | 515417 | Bus: 505612 ID: 2 Name: Keystone | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 35
GEN-2017-072 | 515417 | Bus: 505612 ID: 2 Name: Keystone | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 35
GEN-2017-072 | 515417 | Bus: 505612 ID: 2 Name: Keystone | 08 - North Oklahoma/South Central Kansas | 21S | 35
GEN-2017-072 | 515417 | Bus: 505612 ID: 2 Name: Keystone | 08 - North Oklahoma/South Central Kansas | 28S | 35
GEN-2017-073 | 512629 | Bus: 512688 ID: 2 Name: GRDA | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 520
GEN-2017-073 | 512629 | Bus: 512688 ID: 2 Name: GRDA | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 520
GEN-2017-073 | 512629 | Bus: 512688 ID: 2 Name: GRDA | 08 - North Oklahoma/South Central Kansas | 21S | 520
GEN-2017-073 | 512629 | Bus: 512688 ID: 2 Name: GRDA | 08 - North Oklahoma/South Central Kansas | 28S | 520
GEN-2017-073 | 512629 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 360
GEN-2017-073 | 512629 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 360
GEN-2017-073 | 512629 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 21S | 324.6
GEN-2017-073 | 512629 | Bus: 512614 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 28S | 324.6
GEN-2017-073 | 512629 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 199.5
GEN-2017-073 | 512629 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 199.5
GEN-2017-073 | 512629 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 21S | 191.8
GEN-2017-073 | 512629 | Bus: 512615 ID: 1 Name: GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 28S | 191.8
GEN-2017-073 | 512629 | Bus: 512608 ID: 1 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512608 ID: 1 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512608 ID: 1 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 21S | 43
GEN-2017-073 | 512629 | Bus: 512608 ID: 1 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 28S | 43
GEN-2017-073 | 512629 | Bus: 512609 ID: 2 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512609 ID: 2 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512609 ID: 2 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 21S | 43
GEN-2017-073 | 512629 | Bus: 512609 ID: 2 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 28S | 43
GEN-2017-073 | 512629 | Bus: 512610 ID: 3 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512610 ID: 3 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512610 ID: 3 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 21S | 43
GEN-2017-073 | 512629 | Bus: 512610 ID: 3 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 28S | 43
GEN-2017-073 | 512629 | Bus: 512611 ID: 4 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512611 ID: 4 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512611 ID: 4 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 21S | 43
GEN-2017-073 | 512629 | Bus: 512611 ID: 4 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 28S | 43
GEN-2017-073 | 512629 | Bus: 512612 ID: 5 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512612 ID: 5 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512612 ID: 5 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 21S | 43
GEN-2017-073 | 512629 | Bus: 512612 ID: 5 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 28S | 43
GEN-2017-073 | 512629 | Bus: 512613 ID: 6 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512613 ID: 6 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 43
GEN-2017-073 | 512629 | Bus: 512613 ID: 6 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 21S | 43
GEN-2017-073 | 512629 | Bus: 512613 ID: 6 Name: Salinas Units | 08 - North Oklahoma/South Central Kansas | 28S | 43
GEN-2017-073 | 512629 | Bus: 300020 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 157
GEN-2017-073 | 512629 | Bus: 300020 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 0
GEN-2017-073 | 512629 | Bus: 300020 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 21S | 149.1
GEN-2017-073 | 512629 | Bus: 300020 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 28S | 149.1
GEN-2017-073 | 512629 | Bus: 300021 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 157
GEN-2017-073 | 512629 | Bus: 300021 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 149.1
GEN-2017-073 | 512629 | Bus: 300021 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 21S | 149.1
GEN-2017-073 | 512629 | Bus: 300021 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 28S | 149.1
GEN-2017-073 | 512629 | Bus: 300024 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 163.1
GEN-2017-073 | 512629 | Bus: 300024 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 154.9
GEN-2017-073 | 512629 | Bus: 300024 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 21S | 154.9
GEN-2017-073 | 512629 | Bus: 300024 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 28S | 154.9
GEN-2017-073 | 512629 | Bus: 300032 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 157
GEN-2017-073 | 512629 | Bus: 300032 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 149.1
GEN-2017-073 | 512629 | Bus: 300032 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 21S | 149.1
GEN-2017-073 | 512629 | Bus: 300032 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 28S | 149.1
GEN-2017-073 | 512629 | Bus: 300031 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 163.1
GEN-2017-073 | 512629 | Bus: 300031 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 154.9
GEN-2017-073 | 512629 | Bus: 300031 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 21S | 154.9
GEN-2017-073 | 512629 | Bus: 300031 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 28S | 154.9
GEN-2017-073 | 512629 | Bus: 300033 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 157
GEN-2017-073 | 512629 | Bus: 300033 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 149.1
GEN-2017-073 | 512629 | Bus: 300033 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 21S | 149.1
GEN-2017-073 | 512629 | Bus: 300033 ID: 1 Name: CHOTST | 08 - North Oklahoma/South Central Kansas | 28S | 149.1
GEN-2017-073 | 512629 | Bus: 512607 ID: 5 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512607 ID: 5 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512607 ID: 5 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 21S | 21
GEN-2017-073 | 512629 | Bus: 512607 ID: 5 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 28S | 21
GEN-2017-073 | 512629 | Bus: 512605 ID: 4 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512605 ID: 4 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512605 ID: 4 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 21S | 21
GEN-2017-073 | 512629 | Bus: 512605 ID: 4 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 28S | 21
GEN-2017-073 | 512629 | Bus: 512606 ID: 6 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512606 ID: 6 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512606 ID: 6 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 21S | 21
GEN-2017-073 | 512629 | Bus: 512606 ID: 6 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 28S | 21
GEN-2017-073 | 512629 | Bus: 512602 ID: 1 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512602 ID: 1 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512602 ID: 1 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 21S | 21
GEN-2017-073 | 512629 | Bus: 512602 ID: 1 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 28S | 21
GEN-2017-073 | 512629 | Bus: 512603 ID: 2 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512603 ID: 2 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512603 ID: 2 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 21S | 21
GEN-2017-073 | 512629 | Bus: 512603 ID: 2 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 28S | 21
GEN-2017-073 | 512629 | Bus: 512604 ID: 3 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512604 ID: 3 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 21
GEN-2017-073 | 512629 | Bus: 512604 ID: 3 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 21S | 21
GEN-2017-073 | 512629 | Bus: 512604 ID: 3 Name: PENSA | 08 - North Oklahoma/South Central Kansas | 28S | 21
GEN-2017-074 | 510419 | None | 08 - North Oklahoma/South Central Kansas | None | None
GEN-2017-077 | 589154 | None | 08 - North Oklahoma/South Central Kansas | None | None
GEN-2017-086 | 532798 | Bus: 588363 ID: 1 Name: Gen 16-153 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 134
GEN-2017-086 | 532798 | Bus: 588363 ID: 1 Name: Gen 16-153 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 134
GEN-2017-086 | 532798 | Bus: 588363 ID: 1 Name: Gen 16-153 | 08 - North Oklahoma/South Central Kansas | 21S | 134
GEN-2017-086 | 532798 | Bus: 588363 ID: 1 Name: Gen 16-153 | 08 - North Oklahoma/South Central Kansas | 28S | 134
GEN-2017-086 | 532798 | Bus: 539114 ID: 1 Name: GEN-2006-021 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 50
GEN-2017-086 | 532798 | Bus: 539114 ID: 1 Name: GEN-2006-021 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 50
GEN-2017-086 | 532798 | Bus: 539114 ID: 1 Name: GEN-2006-021 | 08 - North Oklahoma/South Central Kansas | 21S | 50
GEN-2017-086 | 532798 | Bus: 539114 ID: 1 Name: GEN-2006-021 | 08 - North Oklahoma/South Central Kansas | 28S | 50
GEN-2017-086 | 532798 | Bus: 578521 ID: 1 Name: GEN-2006-021 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 44
GEN-2017-086 | 532798 | Bus: 578521 ID: 1 Name: GEN-2006-021 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 44
GEN-2017-086 | 532798 | Bus: 578521 ID: 1 Name: GEN-2006-021 | 08 - North Oklahoma/South Central Kansas | 21S | 44
GEN-2017-086 | 532798 | Bus: 578521 ID: 1 Name: GEN-2006-021 | 08 - North Oklahoma/South Central Kansas | 28S | 44
GEN-2017-086 | 532798 | Bus: 588637 ID: 1 Name: GEN-2017-018 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 94.5
GEN-2017-086 | 532798 | Bus: 588637 ID: 1 Name: GEN-2017-018 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 94.5
GEN-2017-086 | 532798 | Bus: 588637 ID: 1 Name: GEN-2017-018 | 08 - North Oklahoma/South Central Kansas | 21S | 94.5
GEN-2017-086 | 532798 | Bus: 588637 ID: 1 Name: GEN-2017-018 | 08 - North Oklahoma/South Central Kansas | 28S | 94.5
GEN-2017-086 | 532798 | Bus: 588633 ID: 1 Name: GEN-2017-018 | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity A) | 94.5
GEN-2017-086 | 532798 | Bus: 588633 ID: 1 Name: GEN-2017-018 | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity A) | 94.5
GEN-2017-086 | 532798 | Bus: 588633 ID: 1 Name: GEN-2017-018 | 08 - North Oklahoma/South Central Kansas | 21S | 94.5
GEN-2017-086 | 532798 | Bus: 588633 ID: 1 Name: GEN-2017-018 | 08 - North Oklahoma/South Central Kansas | 28S | 94.5
GEN-2017-092 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 551
GEN-2017-092 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 551
GEN-2017-092 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 21S | 551
GEN-2017-092 | 588839 | Bus: 515226 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 28S | 551
GEN-2017-092 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 557
GEN-2017-092 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 557
GEN-2017-092 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 21S | 557
GEN-2017-092 | 588839 | Bus: 515225 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 28S | 557
GEN-2017-092 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 19W (Sensitivity B) | 567
GEN-2017-092 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 21L (Sensitivity B) | 567
GEN-2017-092 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 21S | 567
GEN-2017-092 | 588839 | Bus: 515223 ID: 1 Name: Muskogee | 08 - North Oklahoma/South Central Kansas | 28S | 567
GEN-2017-060 | 547479 | Bus: 547651 ID: 1 Name: L1G382 | 12 - Northwest Arkansas | 19W | 82
GEN-2017-060 | 547479 | Bus: 547651 ID: 1 Name: L1G382 | 12 - Northwest Arkansas | 21L | 82
GEN-2017-060 | 547479 | Bus: 547651 ID: 1 Name: L1G382 | 12 - Northwest Arkansas | 21S | 82
GEN-2017-060 | 547479 | Bus: 547651 ID: 1 Name: L1G382 | 12 - Northwest Arkansas | 28S | 0
GEN-2017-060 | 547479 | Bus: 547653 ID: 1 Name: GEN-2001-030/GEN-2016-013 | 12 - Northwest Arkansas | 19W | 60
GEN-2017-060 | 547479 | Bus: 547653 ID: 1 Name: GEN-2001-030/GEN-2016-013 | 12 - Northwest Arkansas | 21L | 60
GEN-2017-060 | 547479 | Bus: 547653 ID: 1 Name: GEN-2001-030/GEN-2016-013 | 12 - Northwest Arkansas | 21S | 60
GEN-2017-060 | 547479 | Bus: 547653 ID: 1 Name: GEN-2001-030/GEN-2016-013 | 12 - Northwest Arkansas | 28S | 60
GEN-2017-060 | 547479 | Bus: 547652 ID: 1 Name: L3G382 | 12 - Northwest Arkansas | 19W | 82
GEN-2017-060 | 547479 | Bus: 547652 ID: 1 Name: L3G382 | 12 - Northwest Arkansas | 21L | 82
GEN-2017-060 | 547479 | Bus: 547652 ID: 1 Name: L3G382 | 12 - Northwest Arkansas | 21S | 82
GEN-2017-060 | 547479 | Bus: 547652 ID: 1 Name: L3G382 | 12 - Northwest Arkansas | 28S | 82
GEN-2017-060 | 547479 | Bus: 505490 ID: 1 Name: Carthage | 12 - Northwest Arkansas | 19W | 20
GEN-2017-060 | 547479 | Bus: 505490 ID: 1 Name: Carthage | 12 - Northwest Arkansas | 21L | 20
GEN-2017-060 | 547479 | Bus: 505490 ID: 1 Name: Carthage | 12 - Northwest Arkansas | 21S | 20
GEN-2017-060 | 547479 | Bus: 505490 ID: 1 Name: Carthage | 12 - Northwest Arkansas | 28S | 20
GEN-2017-060 | 547479 | Bus: 547649 ID: 1 Name: A1G349 | 12 - Northwest Arkansas | 19W | 198
GEN-2017-060 | 547479 | Bus: 547649 ID: 1 Name: A1G349 | 12 - Northwest Arkansas | 21L | 198
GEN-2017-060 | 547479 | Bus: 547649 ID: 1 Name: A1G349 | 12 - Northwest Arkansas | 21S | 198
GEN-2017-060 | 547479 | Bus: 547649 ID: 1 Name: A1G349 | 12 - Northwest Arkansas | 28S | 198
GEN-2017-076 | 506944 | Bus: 509410 ID: 1 Name: Matison | 12 - Northwest Arkansas | 19W | 78.8
GEN-2017-076 | 506944 | Bus: 509410 ID: 1 Name: Matison | 12 - Northwest Arkansas | 21L | 78.8
GEN-2017-076 | 506944 | Bus: 509410 ID: 1 Name: Matison | 12 - Northwest Arkansas | 21S | 78.8
GEN-2017-076 | 506944 | Bus: 509410 ID: 1 Name: Matison | 12 - Northwest Arkansas | 28S | 71.8
GEN-2017-076 | 506944 | Bus: 509411 ID: 1 Name: Matison | 12 - Northwest Arkansas | 19W | 78
GEN-2017-076 | 506944 | Bus: 509411 ID: 1 Name: Matison | 12 - Northwest Arkansas | 21L | 78
GEN-2017-076 | 506944 | Bus: 509411 ID: 1 Name: Matison | 12 - Northwest Arkansas | 21S | 78
GEN-2017-076 | 506944 | Bus: 509411 ID: 1 Name: Matison | 12 - Northwest Arkansas | 28S | 71
GEN-2017-076 | 506944 | Bus: 509412 ID: 1 Name: Matison | 12 - Northwest Arkansas | 19W | 79.8
GEN-2017-076 | 506944 | Bus: 509412 ID: 1 Name: Matison | 12 - Northwest Arkansas | 21L | 79.8
GEN-2017-076 | 506944 | Bus: 509412 ID: 1 Name: Matison | 12 - Northwest Arkansas | 21S | 79.8
GEN-2017-076 | 506944 | Bus: 509412 ID: 1 Name: Matison | 12 - Northwest Arkansas | 28S | 71.8
GEN-2017-076 | 506944 | Bus: 509413 ID: 1 Name: Matison | 12 - Northwest Arkansas | 19W | 80
GEN-2017-076 | 506944 | Bus: 509413 ID: 1 Name: Matison | 12 - Northwest Arkansas | 21L | 80
GEN-2017-076 | 506944 | Bus: 509413 ID: 1 Name: Matison | 12 - Northwest Arkansas | 21S | 80
GEN-2017-076 | 506944 | Bus: 509413 ID: 1 Name: Matison | 12 - Northwest Arkansas | 28S | 71
GEN-2017-076 | 506944 | Bus: 509394 ID: 1 Name: Flint Creek | 12 - Northwest Arkansas | 19W | 562.2
GEN-2017-076 | 506944 | Bus: 509394 ID: 1 Name: Flint Creek | 12 - Northwest Arkansas | 21L | 562.2
GEN-2017-076 | 506944 | Bus: 509394 ID: 1 Name: Flint Creek | 12 - Northwest Arkansas | 21S | 562.2
GEN-2017-076 | 506944 | Bus: 509394 ID: 1 Name: Flint Creek | 12 - Northwest Arkansas | 28S | 562.2
GEN-2017-082 | 547476 | Bus: 588503 ID: 1 Name: GEN-2017-005 | 12 - Northwest Arkansas | 19W | 195
GEN-2017-082 | 547476 | Bus: 588503 ID: 1 Name: GEN-2017-005 | 12 - Northwest Arkansas | 21L | 195
GEN-2017-082 | 547476 | Bus: 588503 ID: 1 Name: GEN-2017-005 | 12 - Northwest Arkansas | 21S | 195
GEN-2017-082 | 547476 | Bus: 588503 ID: 1 Name: GEN-2017-005 | 12 - Northwest Arkansas | 28S | 195
GEN-2017-082 | 547476 | Bus: 533774 ID: 1 Name: sheffield | 12 - Northwest Arkansas | 19W | 1.6
GEN-2017-082 | 547476 | Bus: 533774 ID: 1 Name: sheffield | 12 - Northwest Arkansas | 21L | 1.6
GEN-2017-082 | 547476 | Bus: 533774 ID: 1 Name: sheffield | 12 - Northwest Arkansas | 21S | 1.6
GEN-2017-082 | 547476 | Bus: 533774 ID: 1 Name: sheffield | 12 - Northwest Arkansas | 28S | 1.6
GEN-2017-082 | 547476 | Bus: 533774 ID: 2 Name: sheffield | 12 - Northwest Arkansas | 19W | 1.95
GEN-2017-082 | 547476 | Bus: 533774 ID: 2 Name: sheffield | 12 - Northwest Arkansas | 21L | 1.95
GEN-2017-082 | 547476 | Bus: 533774 ID: 2 Name: sheffield | 12 - Northwest Arkansas | 21S | 1.95
GEN-2017-082 | 547476 | Bus: 533774 ID: 2 Name: sheffield | 12 - Northwest Arkansas | 28S | 1.95
GEN-2017-082 | 547476 | Bus: 547651 ID: 1 Name: L1G382 | 12 - Northwest Arkansas | 19W | 82
GEN-2017-082 | 547476 | Bus: 547651 ID: 1 Name: L1G382 | 12 - Northwest Arkansas | 21L | 82
GEN-2017-082 | 547476 | Bus: 547651 ID: 1 Name: L1G382 | 12 - Northwest Arkansas | 21S | 82
GEN-2017-082 | 547476 | Bus: 547651 ID: 1 Name: L1G382 | 12 - Northwest Arkansas | 28S | 0
GEN-2017-082 | 547476 | Bus: 547653 ID: 1 Name: L2G382 | 12 - Northwest Arkansas | 19W | 60
GEN-2017-082 | 547476 | Bus: 547653 ID: 1 Name: L2G382 | 12 - Northwest Arkansas | 21L | 60
GEN-2017-082 | 547476 | Bus: 547653 ID: 1 Name: L2G382 | 12 - Northwest Arkansas | 21S | 60
GEN-2017-082 | 547476 | Bus: 547653 ID: 1 Name: L2G382 | 12 - Northwest Arkansas | 28S | 60
GEN-2017-082 | 547476 | Bus: 547652 ID: 1 Name: L3G382 | 12 - Northwest Arkansas | 19W | 82
GEN-2017-082 | 547476 | Bus: 547652 ID: 1 Name: L3G382 | 12 - Northwest Arkansas | 21L | 82
GEN-2017-082 | 547476 | Bus: 547652 ID: 1 Name: L3G382 | 12 - Northwest Arkansas | 21S | 82
GEN-2017-082 | 547476 | Bus: 547652 ID: 1 Name: L3G382 | 12 - Northwest Arkansas | 28S | 82
GEN-2017-082 | 547476 | Bus: 547654 ID: 1 Name: G01-030&040_G16-013&-14 | 12 - Northwest Arkansas | 19W | 60
GEN-2017-082 | 547476 | Bus: 547654 ID: 1 Name: G01-030&040_G16-013&-14 | 12 - Northwest Arkansas | 21L | 60
GEN-2017-082 | 547476 | Bus: 547654 ID: 1 Name: G01-030&040_G16-013&-14 | 12 - Northwest Arkansas | 21S | 60
GEN-2017-082 | 547476 | Bus: 547654 ID: 1 Name: G01-030&040_G16-013&-14 | 12 - Northwest Arkansas | 28S | 60
GEN-2017-082 | 547476 | Bus: 505490 ID: 1 Name: Carthage | 12 - Northwest Arkansas | 19W | 20
GEN-2017-082 | 547476 | Bus: 505490 ID: 1 Name: Carthage | 12 - Northwest Arkansas | 21L | 20
GEN-2017-082 | 547476 | Bus: 505490 ID: 1 Name: Carthage | 12 - Northwest Arkansas | 21S | 20
GEN-2017-082 | 547476 | Bus: 505490 ID: 1 Name: Carthage | 12 - Northwest Arkansas | 28S | 20
GEN-2017-082 | 547476 | Bus: 533761 ID: 1 Name: Girard | 12 - Northwest Arkansas | 19W | 1.4
GEN-2017-082 | 547476 | Bus: 533761 ID: 1 Name: Girard | 12 - Northwest Arkansas | 21L | 1.4
GEN-2017-082 | 547476 | Bus: 533761 ID: 1 Name: Girard | 12 - Northwest Arkansas | 21S | 1.4
GEN-2017-082 | 547476 | Bus: 533761 ID: 1 Name: Girard | 12 - Northwest Arkansas | 28S | 1.4
GEN-2017-082 | 547476 | Bus: 533761 ID: 4 Name: Girard | 12 - Northwest Arkansas | 19W | 2
GEN-2017-082 | 547476 | Bus: 533761 ID: 4 Name: Girard | 12 - Northwest Arkansas | 21L | 2
GEN-2017-082 | 547476 | Bus: 533761 ID: 4 Name: Girard | 12 - Northwest Arkansas | 21S | 2
GEN-2017-082 | 547476 | Bus: 533761 ID: 4 Name: Girard | 12 - Northwest Arkansas | 28S | 2
GEN-2017-082 | 547476 | Bus: 533761 ID: 6 Name: Girard | 12 - Northwest Arkansas | 19W | 3.5
GEN-2017-082 | 547476 | Bus: 533761 ID: 6 Name: Girard | 12 - Northwest Arkansas | 21L | 3.5
GEN-2017-082 | 547476 | Bus: 533761 ID: 6 Name: Girard | 12 - Northwest Arkansas | 21S | 3.5
GEN-2017-082 | 547476 | Bus: 533761 ID: 6 Name: Girard | 12 - Northwest Arkansas | 28S | 3.5
GEN-2017-082 | 547476 | Bus: 533761 ID: 7 Name: Girard | 12 - Northwest Arkansas | 19W | 3.8
GEN-2017-082 | 547476 | Bus: 533761 ID: 7 Name: Girard | 12 - Northwest Arkansas | 21L | 3.8
GEN-2017-082 | 547476 | Bus: 533761 ID: 7 Name: Girard | 12 - Northwest Arkansas | 21S | 3.8
GEN-2017-082 | 547476 | Bus: 533761 ID: 7 Name: Girard | 12 - Northwest Arkansas | 28S | 3.8
GEN-2017-082 | 547476 | Bus: 547658 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 19W | 188
GEN-2017-082 | 547476 | Bus: 547658 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 21L | 188
GEN-2017-082 | 547476 | Bus: 547658 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 21S | 188
GEN-2017-082 | 547476 | Bus: 547658 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 28S | 188
GEN-2017-082 | 547476 | Bus: 547656 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 19W | 167
GEN-2017-082 | 547476 | Bus: 547656 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 21L | 167
GEN-2017-082 | 547476 | Bus: 547656 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 21S | 167
GEN-2017-082 | 547476 | Bus: 547656 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 28S | 167
GEN-2017-082 | 547476 | Bus: 547657 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 19W | 173
GEN-2017-082 | 547476 | Bus: 547657 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 21L | 173
GEN-2017-082 | 547476 | Bus: 547657 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 21S | 173
GEN-2017-082 | 547476 | Bus: 547657 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 28S | 173
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 19W | 94
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 21L | 94
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 21S | 94
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 28S | 94
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 19W | 94
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 21L | 94
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 21S | 94
GEN-2017-082 | 547476 | Bus: 547655 ID: 1 Name: Stateline | 12 - Northwest Arkansas | 28S | 94
GEN-2017-090 | 541240 | Bus: 541167 ID: 3 Name: S Harp | 13 - Northeast Kansas/Northwest Missouri | 19W | 96.7
GEN-2017-090 | 541240 | Bus: 541167 ID: 3 Name: S Harp | 13 - Northeast Kansas/Northwest Missouri | 21L | 96.7
GEN-2017-090 | 541240 | Bus: 541167 ID: 3 Name: S Harp | 13 - Northeast Kansas/Northwest Missouri | 21S | 96.7
GEN-2017-090 | 541240 | Bus: 541167 ID: 3 Name: S Harp | 13 - Northeast Kansas/Northwest Missouri | 28S | 96.7
GEN-2017-090 | 541240 | Bus: 541166 ID: 2 Name: S Harp | 13 - Northeast Kansas/Northwest Missouri | 19W | 97.5
GEN-2017-090 | 541240 | Bus: 541166 ID: 2 Name: S Harp | 13 - Northeast Kansas/Northwest Missouri | 21L | 97.5
GEN-2017-090 | 541240 | Bus: 541166 ID: 2 Name: S Harp | 13 - Northeast Kansas/Northwest Missouri | 21S | 97.5
GEN-2017-090 | 541240 | Bus: 541166 ID: 2 Name: S Harp | 13 - Northeast Kansas/Northwest Missouri | 28S | 97.5
GEN-2017-090 | 541240 | Bus: 541165 ID: 1 Name: S Harp | 13 - Northeast Kansas/Northwest Missouri | 19W | 97.9
GEN-2017-090 | 541240 | Bus: 541165 ID: 1 Name: S Harp | 13 - Northeast Kansas/Northwest Missouri | 21L | 97.9
GEN-2017-090 | 541240 | Bus: 541165 ID: 1 Name: S Harp | 13 - Northeast Kansas/Northwest Missouri | 21S | 97.9
GEN-2017-090 | 541240 | Bus: 541165 ID: 1 Name: S Harp | 13 - Northeast Kansas/Northwest Missouri | 28S | 97.9
GEN-2017-090 | 541240 | Bus: 541159 ID: 1 Name: Nevada | 13 - Northeast Kansas/Northwest Missouri | 19W | 19.4
GEN-2017-090 | 541240 | Bus: 541159 ID: 1 Name: Nevada | 13 - Northeast Kansas/Northwest Missouri | 21L | 19.4
GEN-2017-090 | 541240 | Bus: 541159 ID: 1 Name: Nevada | 13 - Northeast Kansas/Northwest Missouri | 21S | 19.4
GEN-2017-090 | 541240 | Bus: 541159 ID: 1 Name: Nevada | 13 - Northeast Kansas/Northwest Missouri | 28S | 19.4
GEN-2017-090 | 541240 | Bus: 300690 ID: 1 Name: Butlere | 13 - Northeast Kansas/Northwest Missouri | 19W | 11.6
GEN-2017-090 | 541240 | Bus: 300690 ID: 1 Name: Butlere | 13 - Northeast Kansas/Northwest Missouri | 21L | 11.6
GEN-2017-090 | 541240 | Bus: 300690 ID: 1 Name: Butlere | 13 - Northeast Kansas/Northwest Missouri | 21S | 11.6
GEN-2017-090 | 541240 | Bus: 300690 ID: 1 Name: Butlere | 13 - Northeast Kansas/Northwest Missouri | 28S | 11.6
GEN-2017-023 | 520948 | Bus: 505606 ID: 1 Name: DEN #1 1 13.800 | 14 - South Central Oklahoma | ALL | 40
GEN-2017-023 | 520948 | Bus: 505608 ID: 2 Name: DEN #2 1 13.800 | 14 - South Central Oklahoma | ALL | 40
GEN-2017-023 | 520948 | Bus: 511944 ID: 1 Name: KIOWA G1 18.000 | 14 - South Central Oklahoma | ALL | 177
GEN-2017-023 | 520948 | Bus: 511945 ID: 1 Name: KIOWA G2 18.000 | 14 - South Central Oklahoma | ALL | 177
GEN-2017-023 | 520948 | Bus: 511946 ID: 1 Name: KIOWA S1 18.000 | 14 - South Central Oklahoma | ALL | 320
GEN-2017-023 | 520948 | Bus: 511947 ID: 1 Name: KIOWA S2 18.000 | 14 - South Central Oklahoma | ALL | 320
GEN-2017-023 | 520948 | Bus: 511948 ID: 1 Name: KIOWA G3 18.000 | 14 - South Central Oklahoma | ALL | 177
GEN-2017-023 | 520948 | Bus: 511949 ID: 1 Name: KIOWA G4 18.000 | 14 - South Central Oklahoma | ALL | 177
GEN-2017-023 | 520948 | Bus: 515041 ID: 1 Name: SEMINL2G 17.100 | 14 - South Central Oklahoma | ALL | 502
GEN-2017-023 | 520948 | Bus: 515042 ID: 1 Name: SEMINL3G 20.900 | 14 - South Central Oklahoma | ALL | 500
GEN-2017-023 | 520948 | Bus: 520947 ID: 1 Name: HUGO1 23.400 | 14 - South Central Oklahoma | ALL | 465.07
GEN-2017-023 | 520948 | Bus: 587433 ID: 1 Name: G16-063-GEN10.6900 | 14 - South Central Oklahoma | ALL | 100
GEN-2017-023 | 520948 | Bus: 587436 ID: 1 Name: G16-063-GEN20.6900 | 14 - South Central Oklahoma | ALL | 100
GEN-2017-027 | 515561 | Bus: 515040 ID: 1 Name: SEMINL1G 20.900 | 14 - South Central Oklahoma | ALL | 521
GEN-2017-027 | 515561 | Bus: 599143 ID: 1 Name: G1140G1204G10.6900 | 14 - South Central Oklahoma | ALL | 74
GEN-2017-027 | 515561 | Bus: 599144 ID: 1 Name: G1140G1204G20.6901 | 14 - South Central Oklahoma | ALL | 76
GEN-2017-075 | 560088 | Bus: 505606 ID: 1 Name: DEN #1 1 13.800 | 14 - South Central Oklahoma | ALL | 40
GEN-2017-075 | 560088 | Bus: 505608 ID: 2 Name: DEN #2 1 13.800 | 14 - South Central Oklahoma | ALL | 40
GEN-2017-075 | 560088 | Bus: 511944 ID: 1 Name: KIOWA G1 18.000 | 14 - South Central Oklahoma | ALL | 177
GEN-2017-075 | 560088 | Bus: 511945 ID: 1 Name: KIOWA G2 18.000 | 14 - South Central Oklahoma | ALL | 177
GEN-2017-075 | 560088 | Bus: 511946 ID: 1 Name: KIOWA S1 18.000 | 14 - South Central Oklahoma | ALL | 320
GEN-2017-075 | 560088 | Bus: 511947 ID: 1 Name: KIOWA S2 18.000 | 14 - South Central Oklahoma | ALL | 320
GEN-2017-075 | 560088 | Bus: 511948 ID: 1 Name: KIOWA G3 18.000 | 14 - South Central Oklahoma | ALL | 177
GEN-2017-075 | 560088 | Bus: 511949 ID: 1 Name: KIOWA G4 18.000 | 14 - South Central Oklahoma | ALL | 177
GEN-2017-075 | 560088 | Bus: 515041 ID: 1 Name: SEMINL2G 17.100 | 14 - South Central Oklahoma | ALL | 502
GEN-2017-075 | 560088 | Bus: 515042 ID: 1 Name: SEMINL3G 20.900 | 14 - South Central Oklahoma | ALL | 500
GEN-2017-075 | 560088 | Bus: 520947 ID: 1 Name: HUGO1 23.400 | 14 - South Central Oklahoma | ALL | 465.07
GEN-2017-075 | 560088 | Bus: 587433 ID: 1 Name: G16-063-GEN10.6900 | 14 - South Central Oklahoma | ALL | 100
GEN-2017-075 | 560088 | Bus: 587436 ID: 1 Name: G16-063-GEN20.6900 | 14 - South Central Oklahoma | ALL | 100

## Short Circuit Analysis
Gen Number | Region | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 28SP Fault Current 3-Phase (kA) | Request In Service 28SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2017-011 | Central | 01 - Woodward | 526337 | JONES 6 | 230 | 19.271 | 19.271 | 0
GEN-2017-011 | Central | 01 - Woodward | 524296 | SPNSPUR_WND7 | 345 | 4.5325 | 4.5325 | 0
GEN-2017-011 | Central | 01 - Woodward | 523961 | POTTER_CO 7 | 345 | 7.4527 | 7.4527 | 0
GEN-2017-011 | Central | 01 - Woodward | 590001 | OKLEHV24 | 138 | 4.7903 | 4.7903 | 0
GEN-2017-011 | Central | 01 - Woodward | 590003 | OKLEHV14 | 138 | 4.8014 | 4.8014 | 0
GEN-2017-011 | Central | 01 - Woodward | 583370 | GEN-2012-024 | 345 | 11.3148 | 11.3148 | 0
GEN-2017-011 | Central | 01 - Woodward | 520430 | NOELSW 4 | 138 | 11.3345 | 11.3345 | 0
GEN-2017-011 | Central | 01 - Woodward | 520436 | ROSEVLY4 | 138 | 12.6971 | 12.6971 | 0
GEN-2017-011 | Central | 01 - Woodward | 532782 | BUFFALO7 | 345 | 20.7023 | 20.7023 | 0
GEN-2017-011 | Central | 01 - Woodward | 532783 | KINGMAN7 | 345 | 6.8327 | 6.8327 | 0
GEN-2017-011 | Central | 01 - Woodward | 532784 | NINN1WF7 | 345 | 5.6893 | 5.6893 | 0
GEN-2017-011 | Central | 01 - Woodward | 532796 | WICHITA7 | 345 | 24.3835 | 24.3835 | 0
GEN-2017-011 | Central | 01 - Woodward | 520529 | RSVLYSW4 | 138 | 13.677 | 13.677 | 0
GEN-2017-011 | Central | 01 - Woodward | 582008 | GEN-2011-008 | 345 | 10.5174 | 10.5174 | 0
GEN-2017-011 | Central | 01 - Woodward | 584060 | GEN-2015-057 | 345 | 9.1364 | 9.1364 | 0
GEN-2017-011 | Central | 01 - Woodward | 520601 | AVARD 4 | 138 | 6.9924 | 6.9924 | 0
GEN-2017-011 | Central | 01 - Woodward | 588190 | GEN-2016-128 | 345 | 7.9545 | 7.9545 | 0
GEN-2017-011 | Central | 01 - Woodward | 526935 | YOAKUM 6 | 230 | 16.8151 | 16.8151 | 0
GEN-2017-011 | Central | 01 - Woodward | 526936 | YOAKUM_345 | 345 | 8.5075 | 8.5075 | 0
GEN-2017-011 | Central | 01 - Woodward | 514715 | WOODRNG7 | 345 | 19.1426 | 19.1426 | 0
GEN-2017-011 | Central | 01 - Woodward | 515786 | FPLWIND4 | 138 | 6.8223 | 6.8223 | 0
GEN-2017-011 | Central | 01 - Woodward | 514771 | TANGIER2 | 69 | 3.6773 | 3.6773 | 0
GEN-2017-011 | Central | 01 - Woodward | 514773 | NEWMAN 2 | 69 | 1.5468 | 1.5468 | 0
GEN-2017-011 | Central | 01 - Woodward | 514775 | TANGRTP2 | 69 | 4.7834 | 4.7834 | 0
GEN-2017-011 | Central | 01 - Woodward | 514776 | NEWGRTP2 | 69 | 5.4632 | 5.4632 | 0
GEN-2017-011 | Central | 01 - Woodward | 514779 | WDNITRO2 | 69 | 4.7713 | 4.7713 | 0
GEN-2017-011 | Central | 01 - Woodward | 514781 | CEDARAV2 | 69 | 5.7047 | 5.7047 | 0
GEN-2017-011 | Central | 01 - Woodward | 514782 | WODWRD 2 | 69 | 10.9471 | 10.9471 | 0
GEN-2017-011 | Central | 01 - Woodward | 514785 | WOODWRD4 | 138 | 13.1308 | 13.1308 | 0
GEN-2017-011 | Central | 01 - Woodward | 514787 | DEWEY 4 | 138 | 7.7536 | 7.7536 | 0
GEN-2017-011 | Central | 01 - Woodward | 514794 | KNOBHIL2 | 69 | 9.1065 | 9.1065 | 0
GEN-2017-011 | Central | 01 - Woodward | 514795 | KNOBHIL4 | 138 | 11.3932 | 11.3932 | 0
GEN-2017-011 | Central | 01 - Woodward | 514796 | IODINE-4 | 138 | 7.3853 | 7.3853 | 0
GEN-2017-011 | Central | 01 - Woodward | 514801 | MINCO 7 | 345 | 18.2091 | 18.2091 | 0
GEN-2017-011 | Central | 01 - Woodward | 579370 | G06-044-MV1A | 115 | 8.2373 | 8.2373 | 0
GEN-2017-011 | Central | 01 - Woodward | 588560 | GEN-2017-011 | 345 | 12.2639 | 12.2639 | 0
GEN-2017-011 | Central | 01 - Woodward | 520999 | MOORLND4 | 138 | 20.5768 | 20.5768 | 0
GEN-2017-011 | Central | 01 - Woodward | 514879 | NORTWST4 | 138 | 44.4108 | 44.4108 | 0
GEN-2017-011 | Central | 01 - Woodward | 514880 | NORTWST7 | 345 | 33.063 | 33.063 | 0
GEN-2017-011 | Central | 01 - Woodward | 514881 | SPRNGCK7 | 345 | 23.857 | 23.857 | 0
GEN-2017-011 | Central | 01 - Woodward | 514898 | CIMARON4 | 138 | 43.3374 | 43.3374 | 0
GEN-2017-011 | Central | 01 - Woodward | 514901 | CIMARON7 | 345 | 34.6112 | 34.6112 | 0
GEN-2017-011 | Central | 01 - Woodward | 523097 | HITCHLAND 7 | 345 | 15.1013 | 15.1013 | 0
GEN-2017-011 | Central | 01 - Woodward | 514908 | ARCADIA7 | 345 | 30.6277 | 30.6277 | 0
GEN-2017-011 | Central | 01 - Woodward | 523103 | NOBLE_WND 3 | 115 | 10.6735 | 10.6735 | 0
GEN-2017-011 | Central | 01 - Woodward | 523111 | NOVUS1 3 | 115 | 19.4188 | 19.4188 | 0
GEN-2017-011 | Central | 01 - Woodward | 523112 | NOVUS1 7 | 345 | 14.8323 | 14.8323 | 0
GEN-2017-011 | Central | 01 - Woodward | 523118 | BUFF_DUNES 7 | 345 | 6.0476 | 6.0476 | 0
GEN-2017-011 | Central | 01 - Woodward | 514934 | DRAPER 7 | 345 | 21.066 | 21.066 | 0
GEN-2017-011 | Central | 01 - Woodward | 523130 | NBLWND-HV2 3 | 115 | 5.1334 | 5.1334 | 0
GEN-2017-011 | Central | 01 - Woodward | 523131 | NBLWND-HV3 3 | 115 | 8.0198 | 8.0198 | 0
GEN-2017-011 | Central | 01 - Woodward | 521096 | WOODWRD2 | 69 | 9.9388 | 9.9388 | 0
GEN-2017-011 | Central | 01 - Woodward | 576395 | GEN-2010-014 | 345 | 11.1504 | 11.1504 | 0
GEN-2017-011 | Central | 01 - Woodward | 576396 | G10-014-XFMR | 115 | 13.2853 | 13.2853 | 0
GEN-2017-011 | Central | 01 - Woodward | 576397 | G10-014-XF-1 | 115 | 9.2449 | 9.2449 | 0
GEN-2017-011 | Central | 01 - Woodward | 523155 | OCHILTREE 6 | 230 | 4.2744 | 4.2744 | 0
GEN-2017-011 | Central | 01 - Woodward | 576407 | G10-014-XF-2 | 115 | 12.512 | 12.512 | 0
GEN-2017-011 | Central | 01 - Woodward | 525213 | SWISHER 6 | 230 | 10.3091 | 10.3091 | 0
GEN-2017-011 | Central | 01 - Woodward | 900001 | TRAVERSE1 | 345 | 7.3845 | 7.3845 | 0
GEN-2017-011 | Central | 01 - Woodward | 900002 | TRAVERSE2 | 345 | 5.7168 | 5.7168 | 0
GEN-2017-011 | Central | 01 - Woodward | 900003 | TRAVERSE3 | 345 | 5.1975 | 5.1975 | 0
GEN-2017-011 | Central | 01 - Woodward | 523174 | GOODWELLWND3 | 115 | 6.6033 | 6.6033 | 0
GEN-2017-011 | Central | 01 - Woodward | 560071 | G16-003-TAP | 345 | 15.2408 | 15.2408 | 0
GEN-2017-011 | Central | 01 - Woodward | 588750 | GEN-2017-032 | 345 | 3.2299 | 3.2299 | 0
GEN-2017-011 | Central | 01 - Woodward | 523215 | FREWHELCOL17 | 345 | 9.1713 | 9.1713 | 0
GEN-2017-011 | Central | 01 - Woodward | 560080 | G16-046-TAP | 345 | 11.4323 | 11.4323 | 0
GEN-2017-011 | Central | 01 - Woodward | 588754 | G17-032-TAP | 345 | 3.2299 | 3.2299 | 0
GEN-2017-011 | Central | 01 - Woodward | 588760 | GEN-2017-033 | 345 | 4.0304 | 4.0304 | 0
GEN-2017-011 | Central | 01 - Woodward | 526161 | CARLISLE 6 | 230 | 13.2714 | 13.2714 | 0
GEN-2017-011 | Central | 01 - Woodward | 539631 | FLATRWD4 | 138 | 10.3664 | 10.3664 | 0
GEN-2017-011 | Central | 01 - Woodward | 539638 | FLATRDG4 | 138 | 15.5308 | 15.5308 | 0
GEN-2017-011 | Central | 01 - Woodward | 523093 | HITCHLAND 3 | 115 | 17.775 | 17.775 | 0
GEN-2017-011 | Central | 01 - Woodward | 588630 | GEN-2017-018 | 345 | 16.4054 | 16.4054 | 0
GEN-2017-011 | Central | 01 - Woodward | 523095 | HITCHLAND 6 | 230 | 14.7393 | 14.7393 | 0
GEN-2017-011 | Central | 01 - Woodward | 531469 | SPERVIL7 | 345 | 13.739 | 13.739 | 0
GEN-2017-011 | Central | 01 - Woodward | 525828 | TUCO_INT 3 | 115 | 19.3193 | 19.3193 | 0
GEN-2017-011 | Central | 01 - Woodward | 525830 | TUCO_INT 6 | 230 | 21.2069 | 21.2069 | 0
GEN-2017-011 | Central | 01 - Woodward | 523309 | MOORE_CNTY 6 | 230 | 6.8187 | 6.8187 | 0
GEN-2017-011 | Central | 01 - Woodward | 525832 | TUCO_INT 7 | 345 | 11.9885 | 11.9885 | 0
GEN-2017-011 | Central | 01 - Woodward | 582708 | G-2011-008-1 | 345 | 8.564 | 8.564 | 0
GEN-2017-011 | Central | 01 - Woodward | 531512 | HARBNGR7 | 345 | 6.5528 | 6.5528 | 0
GEN-2017-011 | Central | 01 - Woodward | 515600 | KNGFSHR7 | 345 | 11.9002 | 11.9002 | 0
GEN-2017-011 | Central | 01 - Woodward | 525826 | TUCO_INT 2 | 69 | 7.85 | 7.85 | 0
GEN-2017-011 | Central | 01 - Woodward | 515605 | CANADN7 | 345 | 12.9579 | 12.9579 | 0
GEN-2017-011 | Central | 01 - Woodward | 539800 | CLARKCOUNTY7 | 345 | 13.2652 | 13.2652 | 0
GEN-2017-011 | Central | 01 - Woodward | 539801 | THISTLE7 | 345 | 16.4054 | 16.4054 | 0
GEN-2017-011 | Central | 01 - Woodward | 539804 | THISTLE4 | 138 | 17.502 | 17.502 | 0
GEN-2017-011 | Central | 01 - Woodward | 525850 | ELK_CT1 | 345 | 11.8972 | 11.8972 | 0
GEN-2017-011 | Central | 01 - Woodward | 588970 | GEN-2017-059 | 230 | 8.547 | 8.547 | 0
GEN-2017-011 | Central | 01 - Woodward | 539852 | P1 MPT PRI | 345 | 10.7708 | 10.7708 | 0
GEN-2017-011 | Central | 01 - Woodward | 585250 | GEN-2015-090 | 345 | 5.0829 | 5.0829 | 0
GEN-2017-011 | Central | 01 - Woodward | 539857 | P2 MPT PRI | 345 | 9.1323 | 9.1323 | 0
GEN-2017-011 | Central | 01 - Woodward | 525524 | TOLK_EAST 6 | 230 | 26.995 | 26.995 | 0
GEN-2017-011 | Central | 01 - Woodward | 525860 | SP-BECTON +2 | 69 | 2.254 | 2.254 | 0
GEN-2017-011 | Central | 01 - Woodward | 589030 | GEN-2017-065 | 345 | 5.0163 | 5.0163 | 0
GEN-2017-011 | Central | 01 - Woodward | 582908 | G-2011-008-2 | 345 | 8.4371 | 8.4371 | 0
GEN-2017-011 | Central | 01 - Woodward | 589060 | GEN-2017-068 | 345 | 20.2698 | 20.2698 | 0
GEN-2017-011 | Central | 01 - Woodward | 587020 | GEN-2016-003 | 345 | 15.2408 | 15.2408 | 0
GEN-2017-011 | Central | 01 - Woodward | 515363 | CENT 4 | 138 | 3.1164 | 3.1164 | 0
GEN-2017-011 | Central | 01 - Woodward | 515375 | WWRDEHV7 | 345 | 19.8203 | 19.8204 | 5.0453e-06
GEN-2017-011 | Central | 01 - Woodward | 515376 | WWRDEHV4 | 138 | 24.1765 | 24.1765 | 0
GEN-2017-011 | Central | 01 - Woodward | 515390 | TLGAWND4 | 138 | 4.0402 | 4.0402 | 0
GEN-2017-011 | Central | 01 - Woodward | 515394 | KEENAN 4 | 138 | 8.9124 | 8.9124 | 0
GEN-2017-011 | Central | 01 - Woodward | 515398 | OUSPRT 4 | 138 | 9.4842 | 9.4842 | 0
GEN-2017-011 | Central | 01 - Woodward | 515407 | TATONGA7 | 345 | 16.7261 | 16.7261 | 0
GEN-2017-011 | Central | 01 - Woodward | 515425 | WWDPST 4 | 138 | 17.5451 | 17.5451 | 0
GEN-2017-011 | Central | 01 - Woodward | 515444 | MCNOWND7 | 345 | 18.1528 | 18.1528 | 0
GEN-2017-011 | Central | 01 - Woodward | 515448 | CRSRDSW7 | 345 | 11.7432 | 11.7432 | 0
GEN-2017-011 | Central | 01 - Woodward | 515458 | BORDER 7 | 345 | 4.496 | 4.496 | 0
GEN-2017-011 | Central | 01 - Woodward | 587140 | GEN-2016-020 | 138 | 7.483 | 7.483 | 0
GEN-2017-011 | Central | 01 - Woodward | 525723 | CNTYLINE_TP2 | 69 | 2.2011 | 2.2011 | 0
GEN-2017-011 | Central | 01 - Woodward | 525724 | COUNTYLINE 2 | 69 | 1.9277 | 1.9277 | 0
GEN-2017-011 | Central | 01 - Woodward | 525731 | SP-ABERNTHY2 | 69 | 3.0086 | 3.0086 | 0
GEN-2017-011 | Central | 01 - Woodward | 515497 | MATHWSN7 | 345 | 33.254 | 33.254 | 0
GEN-2017-011 | Central | 01 - Woodward | 525738 | HALECENTER 2 | 69 | 2.456 | 2.456 | 0
GEN-2017-011 | Central | 01 - Woodward | 525745 | LH-HALECTR 2 | 69 | 2.4284 | 2.4284 | 0
GEN-2017-011 | Central | 01 - Woodward | 525899 | SP-SHALLWTR2 | 69 | 2.0997 | 2.0997 | 0
GEN-2017-011 | Central | 01 - Woodward | 515533 | REDCLFT4 | 138 | 6.7371 | 6.7371 | 0
GEN-2017-011 | Central | 01 - Woodward | 523853 | FINNEY 7 | 345 | 9.8902 | 9.8902 | 0
GEN-2017-011 | Central | 01 - Woodward | 515549 | MNCWND37 | 345 | 12.468 | 12.468 | 0
GEN-2017-011 | Central | 01 - Woodward | 511456 | O.K.U.-7 | 345 | 5.4913 | 5.4913 | 0
GEN-2017-011 | Central | 01 - Woodward | 515554 | BVRCNTY7 | 345 | 14.759 | 14.759 | 0
GEN-2017-011 | Central | 01 - Woodward | 585190 | GEN-2015-082 | 345 | 7.1443 | 7.1443 | 0
GEN-2017-011 | Central | 01 - Woodward | 511468 | L.E.S.-7 | 345 | 13.2765 | 13.2765 | 0
GEN-2017-011 | Central | 01 - Woodward | 525816 | TUCO_INT2 2 | 69 | 4.6511 | 4.6511 | 0
GEN-2017-011 | Central | 01 - Woodward | 515582 | SLNGWND7 | 345 | 7.3463 | 7.3463 | 0
GEN-2017-011 | Central | 01 - Woodward | 515585 | MAMTHPW7 | 345 | 13.2801 | 13.2801 | 0
GEN-2017-011 | Central | 01 - Woodward | 515590 | PALDR2W7 | 345 | 12.8458 | 12.8458 | 0
GEN-2017-011 | Central | 01 - Woodward | 515599 | G07621119-20 | 345 | 13.2036 | 13.2036 | 0
GEN-2017-011 | Central | 01 - Woodward | 525840 | ANTELOPE_1 6 | 230 | 21.0433 | 21.0433 | 0
GEN-2017-011 | Central | 01 - Woodward | 527896 | HOBBS_INT 7 | 345 | 7.7348 | 7.7348 | 0
GEN-2017-011 | Central | 01 - Woodward | 515610 | FSHRTAP7 | 345 | 17.7292 | 17.7292 | 0
GEN-2017-011 | Central | 01 - Woodward | 525853 | LH-WIL&ELN+2 | 69 | 2.5398 | 2.5398 | 0
GEN-2017-011 | Central | 01 - Woodward | 515618 | BALKOW 7 | 345 | 12.2581 | 12.2581 | 0
GEN-2017-011 | Central | 01 - Woodward | 587310 | GEN-2016-046 | 345 | 9.8441 | 9.8441 | 0
GEN-2017-011 | Central | 01 - Woodward | 523823 | CARPENTER 7 | 345 | 6.5732 | 6.5732 | 0
GEN-2017-011 | Central | 01 - Woodward | 515634 | PALDR1W7 | 345 | 11.2735 | 11.2735 | 0
GEN-2017-011 | Central | 01 - Woodward | 525885 | SP-NEWDEAL 2 | 69 | 3.3064 | 3.3064 | 0
GEN-2017-011 | Central | 01 - Woodward | 525891 | WHITEHEAD 2 | 69 | 2.551 | 2.551 | 0
GEN-2017-011 | Central | 01 - Woodward | 525892 | MONROE 2 | 69 | 2.6469 | 2.6469 | 0
GEN-2017-011 | Central | 01 - Woodward | 511565 | OKLAUN HVDC7 | 345 | 5.4749 | 5.4749 | 0
GEN-2017-011 | Central | 01 - Woodward | 585300 | GEN-2015-095 | 138 | 11.314 | 11.314 | 0
GEN-2017-011 | Central | 01 - Woodward | 515677 | BADGER 7 | 345 | 14.1624 | 14.1624 | 0
GEN-2017-011 | Central | 01 - Woodward | 515686 | GEN-2011-014 | 345 | 12.7624 | 12.7624 | 0
GEN-2017-011 | Central | 01 - Woodward | 583340 | GEN-2012-020 | 230 | 9.8745 | 9.8745 | 0
GEN-2017-011 | Central | 01 - Woodward | 523959 | POTTER_CO 6 | 230 | 20.0753 | 20.0753 | 0
GEN-2017-011 | Central | 01 - Woodward | 585410 | GREAT_WESTRN | 345 | 9.9473 | 9.9473 | 0
GEN-2017-011 | Central | 01 - Woodward | 587460 | GEN-2016-068 | 345 | 6.5319 | 6.5319 | 0
GEN-2017-011 | Central | 01 - Woodward | 515785 | WINDFRM4 | 138 | 20.1178 | 20.1178 | 0
GEN-2017-011 | Central | 01 - Woodward | 585420 | COWBOY_RIDGE | 345 | 7.6727 | 7.6727 | 0
GEN-2017-011 | Central | 01 - Woodward | 585430 | PRSIMN_CRK1 | 345 | 11.6188 | 11.6188 | 0
GEN-2017-011 | Central | 01 - Woodward | 585440 | PRSIMN_CRK2 | 345 | 10.6096 | 10.6096 | 0
GEN-2017-011 | Central | 01 - Woodward | 587500 | GEN-2016-073 | 345 | 15.1939 | 15.1939 | 0
GEN-2017-011 | Central | 01 - Woodward | 526073 | STANTON_N 2 | 69 | 1.6642 | 1.6642 | 0
GEN-2017-011 | Central | 01 - Woodward | 515852 | DGRASSE7 | 345 | 14.5578 | 14.5578 | 0
GEN-2017-011 | Central | 01 - Woodward | 515853 | DGRASSE4 | 138 | 15.3923 | 15.3923 | 0
GEN-2017-011 | Central | 01 - Woodward | 515863 | REDCLF 4 | 138 | 6.7225 | 6.7225 | 0
GEN-2017-011 | Central | 01 - Woodward | 515875 | REDNGTN7 | 345 | 18.0758 | 18.0758 | 0
GEN-2017-011 | Central | 01 - Woodward | 515877 | REDDIRT7 | 345 | 18.0716 | 18.0716 | 0
GEN-2017-011 | Central | 01 - Woodward | 579377 | G06-044-MV2B | 115 | 10.2533 | 10.2533 | 0
GEN-2017-011 | Central | 01 - Woodward | 599891 | OKLAUN 7 | 345 | 4.0421 | 4.0421 | 0
GEN-2017-011 | Central | 01 - Woodward | 515939 | MNCWND47 | 345 | 6.8069 | 6.8069 | 0
GEN-2017-011 | Central | 01 - Woodward | 599950 | LAMAR7 | 345 | 2.5722 | 2.5722 | 0
GEN-2017-047 | South | 02 - Hitchland | 515554 | BVRCNTY7 | 345 | 19.13 | 19.18 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 522898 | BEARD-T 2 | 69 | 2.01 | 2.07 | 0.06
GEN-2017-047 | South | 02 - Hitchland | 522910 | ADAMS 2 | 69 | 1.49 | 1.52 | 0.03
GEN-2017-047 | South | 02 - Hitchland | 522912 | Y TAP 3 | 115 | 5.26 | 5.35 | 0.09
GEN-2017-047 | South | 02 - Hitchland | 522917 | ADAMS-T 2 | 69 | 2.05 | 2.1 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 522918 | COLE 2 | 69 | 3.03 | 3.2 | 0.17
GEN-2017-047 | South | 02 - Hitchland | 522927 | JEFFERSON 2 | 69 | 2.25 | 2.3 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 522934 | TURPIN-T 2 | 69 | 2.03 | 2.11 | 0.08
GEN-2017-047 | South | 02 - Hitchland | 522943 | BEARD 2 | 69 | 1.79 | 1.84 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 522957 | POWELL CNR 3 | 115 | 4.41 | 4.47 | 0.06
GEN-2017-047 | South | 02 - Hitchland | 523012 | TC-ANTHY_TP3 | 115 | 2.14 | 2.3 | 0.16
GEN-2017-047 | South | 02 - Hitchland | 523024 | TC-BEAVER 3 | 115 | 1.66 | 1.76 | 0.1
GEN-2017-047 | South | 02 - Hitchland | 523072 | TC-SEABOARD2 | 69 | 6.77 | 6.87 | 0.1
GEN-2017-047 | South | 02 - Hitchland | 523079 | TC-GUYMON_N2 | 69 | 7.18 | 7.28 | 0.1
GEN-2017-047 | South | 02 - Hitchland | 523089 | TC-TXCOUNTY2 | 69 | 9.2 | 9.35 | 0.15
GEN-2017-047 | South | 02 - Hitchland | 523090 | TEXAS_CNTY 3 | 115 | 9.12 | 9.34 | 0.22
GEN-2017-047 | South | 02 - Hitchland | 523093 | HITCHLAND 3 | 115 | 19.11 | 19.35 | 0.24
GEN-2017-047 | South | 02 - Hitchland | 523095 | HITCHLAND 6 | 230 | 16.26 | 16.42 | 0.16
GEN-2017-047 | South | 02 - Hitchland | 523097 | HITCHLAND 7 | 345 | 17.64 | 17.73 | 0.09
GEN-2017-047 | South | 02 - Hitchland | 523103 | NOBLE_WND 3 | 115 | 11.74 | 11.76 | 0.02
GEN-2017-047 | South | 02 - Hitchland | 523106 | TXPHSF 3 | 115 | 4.55 | 4.6 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 523112 | NOVUS1 7 | 345 | 17.28 | 17.37 | 0.09
GEN-2017-047 | South | 02 - Hitchland | 523113 | TC-MCMURRY 3 | 115 | 6.97 | 7.19 | 0.22
GEN-2017-047 | South | 02 - Hitchland | 523120 | COLE 3 | 115 | 4.49 | 5.16 | 0.67
GEN-2017-047 | South | 02 - Hitchland | 523135 | LIPSCOMB 3 | 115 | 2.87 | 2.96 | 0.09
GEN-2017-047 | South | 02 - Hitchland | 523140 | TXFARMS 3 | 115 | 5.52 | 5.71 | 0.19
GEN-2017-047 | South | 02 - Hitchland | 523142 | TC-AGGIE 3 | 115 | 4.35 | 4.91 | 0.56
GEN-2017-047 | South | 02 - Hitchland | 523147 | WADE 3 | 115 | 3.67 | 3.8 | 0.13
GEN-2017-047 | South | 02 - Hitchland | 523154 | OCHILTREE 3 | 115 | 6.47 | 6.83 | 0.36
GEN-2017-047 | South | 02 - Hitchland | 523155 | OCHILTREE 6 | 230 | 4.51 | 4.61 | 0.1
GEN-2017-047 | South | 02 - Hitchland | 523157 | PERRYTON 2 | 69 | 2.52 | 2.57 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 523158 | PERRYTON 3 | 115 | 6.16 | 6.49 | 0.33
GEN-2017-047 | South | 02 - Hitchland | 523160 | FRISCO_WND 3 | 115 | 7.5 | 7.53 | 0.03
GEN-2017-047 | South | 02 - Hitchland | 523174 | GOODWELLWND3 | 115 | 7.09 | 7.12 | 0.03
GEN-2017-047 | South | 02 - Hitchland | 523185 | SPEARMAN 2 | 69 | 4.41 | 4.43 | 0.02
GEN-2017-047 | South | 02 - Hitchland | 523186 | SPEARMAN 3 | 115 | 9.37 | 9.46 | 0.09
GEN-2017-047 | South | 02 - Hitchland | 523195 | HANSFORD 3 | 115 | 10.98 | 11.07 | 0.09
GEN-2017-047 | South | 02 - Hitchland | 523203 | SPEARMNSUB 3 | 115 | 6.51 | 6.61 | 0.1
GEN-2017-047 | South | 02 - Hitchland | 523215 | FREWHELCOL17 | 345 | 10.3 | 10.33 | 0.03
GEN-2017-047 | South | 02 - Hitchland | 523266 | PRINGLE 3 | 115 | 11.73 | 11.78 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 523308 | MOORE_E 3 | 115 | 12.2 | 12.21 | 0.01
GEN-2017-047 | South | 02 - Hitchland | 523309 | MOORE_CNTY 6 | 230 | 7.23 | 7.24 | 0.01
GEN-2017-047 | South | 02 - Hitchland | 523823 | CARPENTER 7 | 345 | 6.94 | 6.95 | 0.01
GEN-2017-047 | South | 02 - Hitchland | 523959 | POTTER_CO 6 | 230 | 22.46 | 22.48 | 0.02
GEN-2017-047 | South | 02 - Hitchland | 523961 | POTTER_CO 7 | 345 | 10.22 | 10.24 | 0.02
GEN-2017-047 | South | 02 - Hitchland | 539672 | E-LIBER3 | 115 | 4.76 | 4.77 | 0.01
GEN-2017-047 | South | 02 - Hitchland | 576395 | GEN-2010-014 | 345 | 12.69 | 12.74 | 0.05
GEN-2017-047 | South | 02 - Hitchland | 588860 | GEN-2017-047 | 115 | 4.39 | 5.06 | 0.67
GEN-2017-047 | South | 02 - Hitchland | 589380 | GEN-2017-100 | 115 | 5.44 | 5.53 | 0.09
GEN-2017-100 | South | 02 - Hitchland | 515554 | BVRCNTY7 | 345 | 19.16 | 19.18 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 515590 | PALDR2W7 | 345 | 16.03 | 16.05 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 515618 | BALKOW 7 | 345 | 15.28 | 15.3 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 515677 | BADGER 7 | 345 | 16.85 | 16.87 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 522905 | STURGIS 2 | 69 | 1.93 | 1.98 | 0.05
GEN-2017-100 | South | 02 - Hitchland | 522912 | Y TAP 3 | 115 | 5.21 | 5.35 | 0.14
GEN-2017-100 | South | 02 - Hitchland | 522918 | COLE 2 | 69 | 3.16 | 3.2 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 522921 | THRASH 2 | 69 | 3.91 | 4.01 | 0.1
GEN-2017-100 | South | 02 - Hitchland | 522927 | JEFFERSON 2 | 69 | 2.25 | 2.3 | 0.05
GEN-2017-100 | South | 02 - Hitchland | 522929 | POWELL CNR 2 | 69 | 4.27 | 4.38 | 0.11
GEN-2017-100 | South | 02 - Hitchland | 522934 | TURPIN-T 2 | 69 | 2.07 | 2.11 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 522944 | STURGIS-T 2 | 69 | 3.61 | 3.7 | 0.09
GEN-2017-100 | South | 02 - Hitchland | 522948 | WEST_TIE 2 | 69 | 4.04 | 4.14 | 0.1
GEN-2017-100 | South | 02 - Hitchland | 522950 | THRALL 2 | 69 | 1.7 | 1.74 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 522954 | HOVEY 3 | 115 | 3.76 | 3.85 | 0.09
GEN-2017-100 | South | 02 - Hitchland | 522957 | POWELL CNR 3 | 115 | 4.36 | 4.47 | 0.11
GEN-2017-100 | South | 02 - Hitchland | 522960 | WEST-TIE 3 | 115 | 3.01 | 3.08 | 0.07
GEN-2017-100 | South | 02 - Hitchland | 523001 | TC-HOVEY 2 | 69 | 6.68 | 6.86 | 0.18
GEN-2017-100 | South | 02 - Hitchland | 523012 | TC-ANTHY_TP3 | 115 | 2.27 | 2.3 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 523024 | TC-BEAVER 3 | 115 | 1.74 | 1.76 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523044 | TC-ELKHRT_T2 | 69 | 3.2 | 3.28 | 0.08
GEN-2017-100 | South | 02 - Hitchland | 523051 | TC-EVAREG 2 | 69 | 2.9 | 2.97 | 0.07
GEN-2017-100 | South | 02 - Hitchland | 523065 | TC-THOMPSON2 | 69 | 7.15 | 7.35 | 0.2
GEN-2017-100 | South | 02 - Hitchland | 523072 | TC-SEABOARD2 | 69 | 6.69 | 6.87 | 0.18
GEN-2017-100 | South | 02 - Hitchland | 523079 | TC-GUYMON_N2 | 69 | 7.09 | 7.28 | 0.19
GEN-2017-100 | South | 02 - Hitchland | 523089 | TC-TXCOUNTY2 | 69 | 9.1 | 9.35 | 0.25
GEN-2017-100 | South | 02 - Hitchland | 523090 | TEXAS_CNTY 3 | 115 | 9.09 | 9.34 | 0.25
GEN-2017-100 | South | 02 - Hitchland | 523093 | HITCHLAND 3 | 115 | 19.19 | 19.35 | 0.16
GEN-2017-100 | South | 02 - Hitchland | 523095 | HITCHLAND 6 | 230 | 16.36 | 16.42 | 0.06
GEN-2017-100 | South | 02 - Hitchland | 523097 | HITCHLAND 7 | 345 | 17.69 | 17.73 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 523099 | TC-WHITING 3 | 115 | 2.75 | 2.83 | 0.08
GEN-2017-100 | South | 02 - Hitchland | 523103 | NOBLE_WND 3 | 115 | 11.73 | 11.76 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 523106 | TXPHSF 3 | 115 | 4.49 | 4.6 | 0.11
GEN-2017-100 | South | 02 - Hitchland | 523111 | NOVUS1 3 | 115 | 21.03 | 21.06 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 523112 | NOVUS1 7 | 345 | 17.33 | 17.37 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 523113 | TC-MCMURRY 3 | 115 | 7 | 7.19 | 0.19
GEN-2017-100 | South | 02 - Hitchland | 523120 | COLE 3 | 115 | 5.09 | 5.16 | 0.07
GEN-2017-100 | South | 02 - Hitchland | 523130 | NBLWND-HV2 3 | 115 | 5.65 | 5.66 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523131 | NBLWND-HV3 3 | 115 | 8.81 | 8.83 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523140 | TXFARMS 3 | 115 | 5.67 | 5.71 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 523142 | TC-AGGIE 3 | 115 | 4.84 | 4.91 | 0.07
GEN-2017-100 | South | 02 - Hitchland | 523147 | WADE 3 | 115 | 3.77 | 3.8 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 523154 | OCHILTREE 3 | 115 | 6.78 | 6.83 | 0.05
GEN-2017-100 | South | 02 - Hitchland | 523155 | OCHILTREE 6 | 230 | 4.59 | 4.61 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523158 | PERRYTON 3 | 115 | 6.44 | 6.49 | 0.05
GEN-2017-100 | South | 02 - Hitchland | 523160 | FRISCO_WND 3 | 115 | 7.49 | 7.53 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 523161 | RB-CLDWTRTP3 | 115 | 4.25 | 4.26 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523168 | SHERMAN 3 | 115 | 4.69 | 4.7 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523174 | GOODWELLWND3 | 115 | 7.07 | 7.12 | 0.05
GEN-2017-100 | South | 02 - Hitchland | 523175 | LASLEY 3 | 115 | 6.15 | 6.17 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523176 | RB-ELKS 3 | 115 | 6.07 | 6.09 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523177 | RB-SPURLCK+3 | 115 | 6.12 | 6.13 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523185 | SPEARMAN 2 | 69 | 4.41 | 4.43 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523186 | SPEARMAN 3 | 115 | 9.42 | 9.46 | 0.04
GEN-2017-100 | South | 02 - Hitchland | 523195 | HANSFORD 3 | 115 | 11 | 11.07 | 0.07
GEN-2017-100 | South | 02 - Hitchland | 523197 | EXCELN4-HV23 | 115 | 5.03 | 5.05 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523198 | EXCELN4-HV13 | 115 | 4.46 | 4.48 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523203 | SPEARMNSUB 3 | 115 | 6.58 | 6.61 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 523215 | FREWHELCOL17 | 345 | 10.31 | 10.33 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523216 | RB-HOGUE 3 | 115 | 4.31 | 4.32 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523256 | ETTER 3 | 115 | 6.33 | 6.34 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523266 | PRINGLE 3 | 115 | 11.76 | 11.78 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523267 | PRINGLE 6 | 230 | 4.5 | 4.51 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523277 | VALERO 3 | 115 | 11.03 | 11.04 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523304 | MOORE_W 3 | 115 | 12.19 | 12.21 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523308 | MOORE_E 3 | 115 | 12.19 | 12.21 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523309 | MOORE_CNTY 6 | 230 | 7.23 | 7.24 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523377 | RIVERVIEW 3 | 115 | 13.59 | 13.6 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523478 | Q_RYTON_TP 3 | 115 | 11.63 | 11.63 | 0
GEN-2017-100 | South | 02 - Hitchland | 523823 | CARPENTER 7 | 345 | 6.94 | 6.95 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523853 | FINNEY 7 | 345 | 10.13 | 10.14 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523869 | CHAN+TASCOS6 | 230 | 4.53 | 4.53 | 0
GEN-2017-100 | South | 02 - Hitchland | 523959 | POTTER_CO 6 | 230 | 22.47 | 22.48 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 523961 | POTTER_CO 7 | 345 | 10.22 | 10.24 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 523979 | HARRNG_EST 6 | 230 | 26.36 | 26.37 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 524010 | ROLLHILLS 6 | 230 | 20.17 | 20.19 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 524267 | BUSHLAND 6 | 230 | 11.71 | 11.71 | 0
GEN-2017-100 | South | 02 - Hitchland | 524296 | SPNSPUR_WND7 | 345 | 5.54 | 5.54 | 0
GEN-2017-100 | South | 02 - Hitchland | 525230 | NEWPOT_SS 6 | 230 | 7.31 | 7.31 | 0
GEN-2017-100 | South | 02 - Hitchland | 531405 | WALKMYR3 | 115 | 9.61 | 9.63 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 531512 | HARBNGR7 | 345 | 6.92 | 6.93 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 539640 | HAYNE3 | 115 | 5.14 | 5.16 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 539646 | KISMET 3 | 115 | 4.98 | 5 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 539652 | CMRIVTP3 | 115 | 5.51 | 5.54 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 539654 | CIM-PLT3 | 115 | 6.04 | 6.07 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 539659 | CUDAHY 3 | 115 | 4 | 4.01 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 539672 | E-LIBER3 | 115 | 4.74 | 4.77 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 539690 | E-PINE 3 | 115 | 4.08 | 4.11 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 539700 | W-LIBER3 | 115 | 3.75 | 3.77 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 539737 | NLIB 3 | 115 | 4.56 | 4.59 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 539749 | N-CIMRN3 | 115 | 5.99 | 6.01 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 539751 | NATBEEF3 | 115 | 4.67 | 4.7 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 539800 | CLARKCOUNTY7 | 345 | 15.65 | 15.66 | 0.01
GEN-2017-100 | South | 02 - Hitchland | 560035 | GRAPEVINE | 345 | 8.57 | 8.57 | 0
GEN-2017-100 | South | 02 - Hitchland | 576395 | GEN-2010-014 | 345 | 12.71 | 12.74 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 576396 | G10-014-XFMR | 115 | 14.61 | 14.64 | 0.03
GEN-2017-100 | South | 02 - Hitchland | 588480 | A16-010_SUB | 345 | 0.67 | 0.69 | 0.02
GEN-2017-100 | South | 02 - Hitchland | 588486 | ASGI2016-010 | 115 | 2.72 | 2.78 | 0.06
GEN-2017-100 | South | 02 - Hitchland | 588860 | GEN-2017-047 | 115 | 5 | 5.06 | 0.06
GEN-2017-100 | South | 02 - Hitchland | 589380 | GEN-2017-100 | 115 | 5.27 | 5.53 | 0.26
GEN-2017-018 | Central | 03 - Spearville | 588750 | GEN-2017-032 | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-018 | Central | 03 - Spearville | 588754 | G17-032-TAP | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-018 | Central | 03 - Spearville | 588650 | GEN-2017-021 | 345 | 8.859 | 9.6649 | 0.09097
GEN-2017-018 | Central | 03 - Spearville | 588654 | G17-021-TAP | 345 | 9.2902 | 10.1312 | 0.090525
GEN-2017-018 | Central | 03 - Spearville | 589370 | GEN-2017-099 | 345 | 8.859 | 9.6568 | 0.090055
GEN-2017-018 | Central | 03 - Spearville | 599950 | LAMAR7 | 345 | 2.3728 | 2.5722 | 0.084036
GEN-2017-018 | Central | 03 - Spearville | 531469 | SPERVIL7 | 345 | 13.1153 | 13.739 | 0.047555
GEN-2017-018 | Central | 03 - Spearville | 539803 | IRONWOOD7 | 345 | 12.5911 | 13.1405 | 0.043634
GEN-2017-018 | Central | 03 - Spearville | 579480 | GEN-2008-124 | 345 | 12.1777 | 12.6897 | 0.042044
GEN-2017-018 | Central | 03 - Spearville | 523853 | FINNEY 7 | 345 | 9.544 | 9.8902 | 0.036274
GEN-2017-018 | Central | 03 - Spearville | 531449 | HOLCOMB7 | 345 | 9.6562 | 10.0016 | 0.03577
GEN-2017-018 | Central | 03 - Spearville | 589484 | G16-049-TAP | 345 | 8.6792 | 8.9146 | 0.027122
GEN-2017-018 | Central | 03 - Spearville | 531501 | BUCKNER7 | 345 | 8.8014 | 9.0375 | 0.026825
GEN-2017-018 | Central | 03 - Spearville | 560080 | G16-046-TAP | 345 | 11.1556 | 11.4323 | 0.024804
GEN-2017-018 | Central | 03 - Spearville | 539800 | CLARKCOUNTY7 | 345 | 12.9764 | 13.2652 | 0.022256
GEN-2017-018 | Central | 03 - Spearville | 539695 | SPEARVL6 | 230 | 12.2036 | 12.4729 | 0.022067
GEN-2017-018 | Central | 03 - Spearville | 539117 | SPRVILL-EHVB | 230 | 11.8903 | 12.1451 | 0.021429
GEN-2017-018 | Central | 03 - Spearville | 531502 | CIMRRN 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-018 | Central | 03 - Spearville | 531504 | CIMWD2 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-018 | Central | 03 - Spearville | 587310 | GEN-2016-046 | 345 | 9.641 | 9.8441 | 0.021066
GEN-2017-018 | Central | 03 - Spearville | 523118 | BUFF_DUNES 7 | 345 | 5.9244 | 6.0476 | 0.020795
GEN-2017-018 | Central | 03 - Spearville | 530583 | POSTROCK7 | 345 | 9.5651 | 9.7633 | 0.020721
GEN-2017-018 | Central | 03 - Spearville | 583370 | GEN-2012-024 | 345 | 11.1056 | 11.3148 | 0.018837
GEN-2017-018 | Central | 03 - Spearville | 539852 | P1 MPT PRI | 345 | 10.5849 | 10.7708 | 0.017563
GEN-2017-018 | Central | 03 - Spearville | 582008 | GEN-2011-008 | 345 | 10.3495 | 10.5174 | 0.016223
GEN-2017-018 | Central | 03 - Spearville | 531465 | SETAB 7 | 345 | 7.0502 | 7.1573 | 0.015191
GEN-2017-018 | Central | 03 - Spearville | 539857 | P2 MPT PRI | 345 | 9.0022 | 9.1323 | 0.014452
GEN-2017-018 | Central | 03 - Spearville | 582908 | G-2011-008-2 | 345 | 8.3279 | 8.4371 | 0.013113
GEN-2017-018 | Central | 03 - Spearville | 582708 | G-2011-008-1 | 345 | 8.457 | 8.564 | 0.012652
GEN-2017-018 | Central | 03 - Spearville | 539759 | SPRVL 3 | 115 | 11.4523 | 11.5615 | 0.0095352
GEN-2017-018 | Central | 03 - Spearville | 531448 | HOLCOMB3 | 115 | 21.3888 | 21.5721 | 0.0085699
GEN-2017-018 | Central | 03 - Spearville | 539694 | SPEARVL3 | 115 | 10.2986 | 10.3686 | 0.006797
GEN-2017-018 | Central | 03 - Spearville | 530582 | S HAYS6 | 230 | 9.7644 | 9.8282 | 0.0065339
GEN-2017-018 | Central | 03 - Spearville | 588630 | GEN-2017-018 | 345 | 16.3278 | 16.4054 | 0.0047526
GEN-2017-018 | Central | 03 - Spearville | 539801 | THISTLE7 | 345 | 16.3278 | 16.4054 | 0.0047526
GEN-2017-018 | Central | 03 - Spearville | 539679 | GRTBEND6 | 230 | 8.4778 | 8.513 | 0.004152
GEN-2017-018 | Central | 03 - Spearville | 530680 | HEIZER 6 | 230 | 8.4277 | 8.4625 | 0.0041292
GEN-2017-018 | Central | 03 - Spearville | 539771 | NFTDODG3 | 115 | 12.214 | 12.2642 | 0.00411
GEN-2017-018 | Central | 03 - Spearville | 539671 | FTDODGE3 | 115 | 12.1733 | 12.2228 | 0.0040663
GEN-2017-018 | Central | 03 - Spearville | 539645 | DCBEEF3 | 115 | 8.1294 | 8.1515 | 0.0027185
GEN-2017-018 | Central | 03 - Spearville | 539688 | S-DODGE3 | 115 | 8.1466 | 8.1667 | 0.0024673
GEN-2017-018 | Central | 03 - Spearville | 539740 | EDODGE 3 | 115 | 7.2953 | 7.3131 | 0.0024399
GEN-2017-018 | Central | 03 - Spearville | 539678 | GRTBEND3 | 115 | 12.9225 | 12.9518 | 0.0022674
GEN-2017-018 | Central | 03 - Spearville | 539804 | THISTLE4 | 138 | 17.4711 | 17.502 | 0.0017686
GEN-2017-018 | Central | 03 - Spearville | 515852 | DGRASSE7 | 345 | 14.5329 | 14.5578 | 0.0017134
GEN-2017-018 | Central | 03 - Spearville | 539680 | N-DODGE3 | 115 | 5.1229 | 5.1316 | 0.0016983
GEN-2017-018 | Central | 03 - Spearville | 530610 | SHAYS_230 | 230 | 4.2554 | 4.2625 | 0.0016685
GEN-2017-018 | Central | 03 - Spearville | 539638 | FLATRDG4 | 138 | 15.5075 | 15.5308 | 0.0015025
GEN-2017-018 | Central | 03 - Spearville | 539758 | FORD 3 | 115 | 5.5694 | 5.5777 | 0.0014903
GEN-2017-018 | Central | 03 - Spearville | 539681 | N-GBEND3 | 115 | 8.3462 | 8.3584 | 0.0014617
GEN-2017-018 | Central | 03 - Spearville | 539641 | NW-DODG3 | 115 | 3.8709 | 3.8759 | 0.0012917
GEN-2017-018 | Central | 03 - Spearville | 539699 | W-DODGE3 | 115 | 5.2105 | 5.2171 | 0.0012667
GEN-2017-018 | Central | 03 - Spearville | 532782 | BUFFALO7 | 345 | 20.6769 | 20.7023 | 0.0012284
GEN-2017-018 | Central | 03 - Spearville | 539661 | 24-FREY3 | 115 | 5.6199 | 5.6255 | 0.00099646
GEN-2017-018 | Central | 03 - Spearville | 539628 | NW-DGTP3 | 115 | 4.063 | 4.067 | 0.00098449
GEN-2017-018 | Central | 03 - Spearville | 539631 | FLATRWD4 | 138 | 10.3564 | 10.3664 | 0.00096559
GEN-2017-018 | Central | 03 - Spearville | 532796 | WICHITA7 | 345 | 24.3601 | 24.3835 | 0.00096059
GEN-2017-018 | Central | 03 - Spearville | 539689 | 2ND-KS 3 | 115 | 5.0444 | 5.0489 | 0.00089208
GEN-2017-018 | Central | 03 - Spearville | 539944 | LOCHS | 115 | 3.6994 | 3.7027 | 0.00089204
GEN-2017-018 | Central | 03 - Spearville | 587500 | GEN-2016-073 | 345 | 15.1804 | 15.1939 | 0.0008893
GEN-2017-018 | Central | 03 - Spearville | 539674 | BARBER 4 | 138 | 8.2161 | 8.2231 | 0.00085199
GEN-2017-018 | Central | 03 - Spearville | 515554 | BVRCNTY7 | 345 | 14.7467 | 14.759 | 0.00083408
GEN-2017-018 | Central | 03 - Spearville | 589060 | GEN-2017-068 | 345 | 20.2535 | 20.2698 | 0.0008048
GEN-2017-018 | Central | 03 - Spearville | 515375 | WWRDEHV7 | 345 | 19.805 | 19.8204 | 0.00077758
GEN-2017-018 | Central | 03 - Spearville | 539760 | BARBER 3 | 115 | 8.0545 | 8.0604 | 0.00073251
GEN-2017-018 | Central | 03 - Spearville | 539673 | MED-LDG3 | 115 | 7.8793 | 7.8849 | 0.00071072
GEN-2017-018 | Central | 03 - Spearville | 515590 | PALDR2W7 | 345 | 12.8368 | 12.8458 | 0.00070111
GEN-2017-018 | Central | 03 - Spearville | 515677 | BADGER 7 | 345 | 14.1527 | 14.1624 | 0.00068538
GEN-2017-018 | Central | 03 - Spearville | 515618 | BALKOW 7 | 345 | 12.2498 | 12.2581 | 0.00067756
GEN-2017-018 | Central | 03 - Spearville | 560071 | G16-003-TAP | 345 | 15.2315 | 15.2408 | 0.00061058
GEN-2017-018 | Central | 03 - Spearville | 587020 | GEN-2016-003 | 345 | 15.2315 | 15.2408 | 0.00061058
GEN-2017-018 | Central | 03 - Spearville | 532871 | CIRCLE 6 | 230 | 10.0517 | 10.0578 | 0.00060686
GEN-2017-018 | Central | 03 - Spearville | 515686 | GEN-2011-014 | 345 | 12.7547 | 12.7624 | 0.0006037
GEN-2017-018 | Central | 03 - Spearville | 515634 | PALDR1W7 | 345 | 11.2669 | 11.2735 | 0.00058579
GEN-2017-018 | Central | 03 - Spearville | 539684 | OTISSUB3 | 115 | 2.9576 | 2.9591 | 0.00050717
GEN-2017-018 | Central | 03 - Spearville | 588560 | GEN-2017-011 | 345 | 12.2579 | 12.2639 | 0.00048948
GEN-2017-018 | Central | 03 - Spearville | 515599 | G07621119-20 | 345 | 13.1976 | 13.2036 | 0.00045463
GEN-2017-018 | Central | 03 - Spearville | 539779 | GRAY CO3 | 115 | 3.5101 | 3.5116 | 0.00042734
GEN-2017-018 | Central | 03 - Spearville | 539667 | HAGGARD3 | 115 | 3.5101 | 3.5116 | 0.00042734
GEN-2017-018 | Central | 03 - Spearville | 539778 | GYCOTAP3 | 115 | 3.5101 | 3.5116 | 0.00042734
GEN-2017-018 | Central | 03 - Spearville | 515853 | DGRASSE4 | 138 | 15.3859 | 15.3923 | 0.00041597
GEN-2017-018 | Central | 03 - Spearville | 532771 | RENO 7 | 345 | 12.6407 | 12.6459 | 0.00041137
GEN-2017-018 | Central | 03 - Spearville | 533413 | CIRCLE 3 | 115 | 23.6141 | 23.6235 | 0.00039807
GEN-2017-018 | Central | 03 - Spearville | 585430 | PRSIMN_CRK1 | 345 | 11.6142 | 11.6188 | 0.00039607
GEN-2017-018 | Central | 03 - Spearville | 539649 | SAWYER 3 | 115 | 4.5887 | 4.5905 | 0.00039227
GEN-2017-018 | Central | 03 - Spearville | 533416 | RENO 3 | 115 | 26.7924 | 26.8023 | 0.00036951
GEN-2017-018 | Central | 03 - Spearville | 585440 | PRSIMN_CRK2 | 345 | 10.6058 | 10.6096 | 0.00035829
GEN-2017-018 | Central | 03 - Spearville | 532791 | BENTON 7 | 345 | 19.74 | 19.7468 | 0.00034448
GEN-2017-018 | Central | 03 - Spearville | 533040 | EVANS N4 | 138 | 33.521 | 33.5322 | 0.00033412
GEN-2017-018 | Central | 03 - Spearville | 533041 | EVANS S4 | 138 | 33.521 | 33.5322 | 0.00033412
GEN-2017-018 | Central | 03 - Spearville | 585190 | GEN-2015-082 | 345 | 7.142 | 7.1443 | 0.00032204
GEN-2017-018 | Central | 03 - Spearville | 520529 | RSVLYSW4 | 138 | 13.6726 | 13.677 | 0.00032181
GEN-2017-018 | Central | 03 - Spearville | 585410 | GREAT_WESTRN | 345 | 9.9442 | 9.9473 | 0.00031174
GEN-2017-018 | Central | 03 - Spearville | 532783 | KINGMAN7 | 345 | 6.8306 | 6.8327 | 0.00030744
GEN-2017-018 | Central | 03 - Spearville | 539668 | HARPER 4 | 138 | 7.2222 | 7.2244 | 0.00030462
GEN-2017-018 | Central | 03 - Spearville | 520436 | ROSEVLY4 | 138 | 12.6934 | 12.6971 | 0.00029149
GEN-2017-018 | Central | 03 - Spearville | 587884 | G16-111-TAP | 345 | 11.3842 | 11.3875 | 0.00028988
GEN-2017-018 | Central | 03 - Spearville | 532798 | VIOLA 7 | 345 | 14.4584 | 14.4624 | 0.00027666
GEN-2017-018 | Central | 03 - Spearville | 515376 | WWRDEHV4 | 138 | 24.17 | 24.1765 | 0.00026893
GEN-2017-018 | Central | 03 - Spearville | 587894 | G16-112-TAP | 345 | 11.182 | 11.1849 | 0.00025935
GEN-2017-018 | Central | 03 - Spearville | 587910 | GEN-2016-114 | 345 | 10.1524 | 10.155 | 0.0002561
GEN-2017-018 | Central | 03 - Spearville | 532784 | NINN1WF7 | 345 | 5.6879 | 5.6893 | 0.00024614
GEN-2017-018 | Central | 03 - Spearville | 533074 | 45TH ST4 | 138 | 24.2551 | 24.2608 | 0.000235
GEN-2017-018 | Central | 03 - Spearville | 585420 | COWBOY_RIDGE | 345 | 7.6709 | 7.6727 | 0.00023465
GEN-2017-018 | Central | 03 - Spearville | 533075 | VIOLA 4 | 138 | 24.4694 | 24.4751 | 0.00023294
GEN-2017-018 | Central | 03 - Spearville | 515407 | TATONGA7 | 345 | 16.7223 | 16.7261 | 0.00022724
GEN-2017-018 | Central | 03 - Spearville | 585250 | GEN-2015-090 | 345 | 5.0818 | 5.0829 | 0.00021646
GEN-2017-018 | Central | 03 - Spearville | 562476 | G14-001-TAP | 345 | 10.626 | 10.6282 | 0.00020704
GEN-2017-018 | Central | 03 - Spearville | 520430 | NOELSW 4 | 138 | 11.3322 | 11.3345 | 0.00020296
GEN-2017-018 | Central | 03 - Spearville | 514795 | KNOBHIL4 | 138 | 11.3909 | 11.3932 | 0.00020192
GEN-2017-018 | Central | 03 - Spearville | 532794 | ROSEHIL7 | 345 | 19.0627 | 19.0665 | 0.00019934
GEN-2017-018 | Central | 03 - Spearville | 589240 | GEN-2017-086 | 345 | 10.5531 | 10.5552 | 0.00019899
GEN-2017-018 | Central | 03 - Spearville | 533065 | SG12COL4 | 138 | 19.7802 | 19.7841 | 0.00019717
GEN-2017-018 | Central | 03 - Spearville | 585300 | GEN-2015-095 | 138 | 11.3118 | 11.314 | 0.00019449
GEN-2017-018 | Central | 03 - Spearville | 532986 | BENTON 4 | 138 | 27.9826 | 27.9879 | 0.0001894
GEN-2017-018 | Central | 03 - Spearville | 533054 | MAIZE 4 | 138 | 21.1222 | 21.1262 | 0.00018937
GEN-2017-018 | Central | 03 - Spearville | 515585 | MAMTHPW7 | 345 | 13.2777 | 13.2801 | 0.00018075
GEN-2017-018 | Central | 03 - Spearville | 539001 | ANTHONY4 | 138 | 5.0259 | 5.0268 | 0.00017907
GEN-2017-018 | Central | 03 - Spearville | 533047 | GILL 4 | 138 | 22.0305 | 22.0344 | 0.00017703
GEN-2017-018 | Central | 03 - Spearville | 533438 | WMCPHER3 | 115 | 15.7546 | 15.7573 | 0.00017138
GEN-2017-018 | Central | 03 - Spearville | 587880 | GEN-2016-111 | 345 | 7.1269 | 7.1281 | 0.00016838
GEN-2017-018 | Central | 03 - Spearville | 515425 | WWDPST 4 | 138 | 17.5422 | 17.5451 | 0.00016532
GEN-2017-018 | Central | 03 - Spearville | 533035 | CHISHLM4 | 138 | 21.3532 | 21.3567 | 0.00016391
GEN-2017-018 | Central | 03 - Spearville | 520601 | AVARD 4 | 138 | 6.9913 | 6.9924 | 0.00015734
GEN-2017-018 | Central | 03 - Spearville | 539009 | CONWAY | 138 | 12.7335 | 12.7355 | 0.00015707
GEN-2017-018 | Central | 03 - Spearville | 533053 | LAKERDG4 | 138 | 17.3481 | 17.3508 | 0.00015564
GEN-2017-018 | Central | 03 - Spearville | 533052 | PARKCTY4 | 138 | 20.1237 | 20.1268 | 0.00015405
GEN-2017-018 | Central | 03 - Spearville | 588320 | GEN-2016-162 | 345 | 9.7753 | 9.7768 | 0.00015345
GEN-2017-018 | Central | 03 - Spearville | 515448 | CRSRDSW7 | 345 | 11.7414 | 11.7432 | 0.0001533
GEN-2017-018 | Central | 03 - Spearville | 539000 | RAGO 4 | 138 | 3.95 | 3.9506 | 0.0001519
GEN-2017-018 | Central | 03 - Spearville | 533062 | ROSEHIL4 | 138 | 31.0086 | 31.0133 | 0.00015157
GEN-2017-018 | Central | 03 - Spearville | 539675 | MILANTP4 | 138 | 9.9211 | 9.9226 | 0.00015119
GEN-2017-018 | Central | 03 - Spearville | 588330 | GEN-2016-163 | 345 | 8.6372 | 8.6384 | 0.00013893
GEN-2017-018 | Central | 03 - Spearville | 539008 | MILAN_GOAB | 138 | 11.9456 | 11.9472 | 0.00013394
GEN-2017-018 | Central | 03 - Spearville | 533024 | 29TH 4 | 138 | 19.423 | 19.4255 | 0.00012871
GEN-2017-018 | Central | 03 - Spearville | 583850 | GEN-2014-001 | 345 | 7.0897 | 7.0906 | 0.00012694
GEN-2017-018 | Central | 03 - Spearville | 533415 | DAVIS 3 | 115 | 8.7135 | 8.7146 | 0.00012624
GEN-2017-018 | Central | 03 - Spearville | 532988 | BELAIRE4 | 138 | 18.7913 | 18.7936 | 0.0001224
GEN-2017-018 | Central | 03 - Spearville | 533036 | CLEARWT4 | 138 | 14.1688 | 14.1705 | 0.00011998
GEN-2017-018 | Central | 03 - Spearville | 539676 | MILAN 4 | 138 | 10.5417 | 10.5429 | 0.00011383
GEN-2017-018 | Central | 03 - Spearville | 515543 | RENFROW7 | 345 | 12.5417 | 12.5431 | 0.00011163
GEN-2017-018 | Central | 03 - Spearville | 533015 | BENTLEY4 | 138 | 10.8174 | 10.8186 | 0.00011093
GEN-2017-018 | Central | 03 - Spearville | 588360 | GEN-2016-153 | 345 | 7.2616 | 7.2624 | 0.00011017
GEN-2017-018 | Central | 03 - Spearville | 539002 | BLF-CRK4 | 138 | 4.7102 | 4.7107 | 0.00010615
GEN-2017-018 | Central | 03 - Spearville | 588364 | G16-153-TAP | 345 | 7.5916 | 7.5924 | 0.00010538
GEN-2017-018 | Central | 03 - Spearville | 532792 | FR2EAST7 | 345 | 6.8423 | 6.843 | 0.0001023
GEN-2017-018 | Central | 03 - Spearville | 587980 | GEN-2016-122 | 345 | 5.2094 | 5.2099 | 9.598e-05
GEN-2017-018 | Central | 03 - Spearville | 515582 | SLNGWND7 | 345 | 7.3456 | 7.3463 | 9.5295e-05
GEN-2017-018 | Central | 03 - Spearville | 515398 | OUSPRT 4 | 138 | 9.4833 | 9.4842 | 9.4904e-05
GEN-2017-018 | Central | 03 - Spearville | 520437 | SALTPLN4 | 138 | 6.5467 | 6.5473 | 9.1649e-05
GEN-2017-018 | Central | 03 - Spearville | 515646 | GRNTWD 7 | 345 | 11.0032 | 11.0042 | 9.0883e-05
GEN-2017-018 | Central | 03 - Spearville | 515394 | KEENAN 4 | 138 | 8.9116 | 8.9124 | 8.9771e-05
GEN-2017-018 | Central | 03 - Spearville | 515458 | BORDER 7 | 345 | 4.4956 | 4.496 | 8.8976e-05
GEN-2017-018 | Central | 03 - Spearville | 533016 | WWUPLNT4 | 138 | 8.1589 | 8.1596 | 8.5796e-05
GEN-2017-018 | Central | 03 - Spearville | 587890 | GEN-2016-112 | 345 | 4.6689 | 4.6693 | 8.5673e-05
GEN-2017-018 | Central | 03 - Spearville | 533429 | MOUNDRG3 | 115 | 8.6504 | 8.6511 | 8.0921e-05
GEN-2017-018 | Central | 03 - Spearville | 578530 | FR3HV | 345 | 4.9911 | 4.9915 | 8.0143e-05
GEN-2017-018 | Central | 03 - Spearville | 514785 | WOODWRD4 | 138 | 13.1298 | 13.1308 | 7.6163e-05
GEN-2017-018 | Central | 03 - Spearville | 532795 | FR2WEST7 | 345 | 5.4502 | 5.4506 | 7.3392e-05
GEN-2017-018 | Central | 03 - Spearville | 584900 | GEN-2015-052 | 345 | 13.0806 | 13.0815 | 6.8804e-05
GEN-2017-018 | Central | 03 - Spearville | 560053 | G15-052T | 345 | 13.1309 | 13.1318 | 6.8541e-05
GEN-2017-018 | Central | 03 - Spearville | 515477 | CHSHLMV7 | 345 | 13.5537 | 13.5546 | 6.6403e-05
GEN-2017-018 | Central | 03 - Spearville | 515476 | HUNTERS7 | 345 | 13.5721 | 13.573 | 6.6313e-05
GEN-2017-018 | Central | 03 - Spearville | 532768 | EMPEC 7 | 345 | 17.6048 | 17.6059 | 6.2483e-05
GEN-2017-018 | Central | 03 - Spearville | 515497 | MATHWSN7 | 345 | 33.252 | 33.254 | 6.0147e-05
GEN-2017-018 | Central | 03 - Spearville | 532769 | LANG 7 | 345 | 17.3857 | 17.3867 | 5.7519e-05
GEN-2017-018 | Central | 03 - Spearville | 532800 | LATHAMS7 | 345 | 10.5077 | 10.5083 | 5.7101e-05
GEN-2017-018 | Central | 03 - Spearville | 532990 | MIDIAN 4 | 138 | 10.5583 | 10.5589 | 5.6827e-05
GEN-2017-018 | Central | 03 - Spearville | 515544 | RENFROW4 | 138 | 14.4233 | 14.4241 | 5.5466e-05
GEN-2017-018 | Central | 03 - Spearville | 514794 | KNOBHIL2 | 69 | 9.106 | 9.1065 | 5.4909e-05
GEN-2017-018 | Central | 03 - Spearville | 532801 | ELKRVR17 | 345 | 9.264 | 9.2645 | 5.3972e-05
GEN-2017-018 | Central | 03 - Spearville | 514792 | ALVAOGE2 | 69 | 7.6425 | 7.6429 | 5.2339e-05
GEN-2017-018 | Central | 03 - Spearville | 532984 | SUMNER 4 | 138 | 10.2472 | 10.2477 | 4.8794e-05
GEN-2017-018 | Central | 03 - Spearville | 520462 | ASPEN 4 | 138 | 19.8344 | 19.8353 | 4.5376e-05
GEN-2017-018 | Central | 03 - Spearville | 585100 | GEN-2015-073 | 345 | 13.3996 | 13.4002 | 4.4777e-05
GEN-2017-018 | Central | 03 - Spearville | 515785 | WINDFRM4 | 138 | 20.1169 | 20.1178 | 4.4739e-05
GEN-2017-018 | Central | 03 - Spearville | 515863 | REDCLF 4 | 138 | 6.7222 | 6.7225 | 4.4628e-05
GEN-2017-018 | Central | 03 - Spearville | 520999 | MOORLND4 | 138 | 20.5759 | 20.5768 | 4.374e-05
GEN-2017-018 | Central | 03 - Spearville | 514796 | IODINE-4 | 138 | 7.385 | 7.3853 | 4.0623e-05
GEN-2017-018 | Central | 03 - Spearville | 532770 | MORRIS 7 | 345 | 12.8684 | 12.8689 | 3.8855e-05
GEN-2017-018 | Central | 03 - Spearville | 532797 | WOLFCRK7 | 345 | 18.1147 | 18.1154 | 3.8643e-05
GEN-2017-018 | Central | 03 - Spearville | 514901 | CIMARON7 | 345 | 34.6099 | 34.6112 | 3.7562e-05
GEN-2017-018 | Central | 03 - Spearville | 515877 | REDDIRT7 | 345 | 18.071 | 18.0716 | 3.3202e-05
GEN-2017-018 | Central | 03 - Spearville | 515875 | REDNGTN7 | 345 | 18.0752 | 18.0758 | 3.3195e-05
GEN-2017-018 | Central | 03 - Spearville | 515363 | CENT 4 | 138 | 3.1163 | 3.1164 | 3.2089e-05
GEN-2017-018 | Central | 03 - Spearville | 532799 | WAVERLY7 | 345 | 16.0603 | 16.0608 | 3.1133e-05
GEN-2017-018 | Central | 03 - Spearville | 515560 | CZYCRVT2 | 69 | 3.2561 | 3.2562 | 3.0712e-05
GEN-2017-018 | Central | 03 - Spearville | 514880 | NORTWST7 | 345 | 33.062 | 33.063 | 3.0246e-05
GEN-2017-018 | Central | 03 - Spearville | 515533 | REDCLFT4 | 138 | 6.7369 | 6.7371 | 2.9687e-05
GEN-2017-018 | Central | 03 - Spearville | 514782 | WODWRD 2 | 69 | 10.9468 | 10.9471 | 2.7405e-05
GEN-2017-018 | Central | 03 - Spearville | 532802 | WAVERTX7 | 345 | 13.4367 | 13.437 | 2.2327e-05
GEN-2017-018 | Central | 03 - Spearville | 514779 | WDNITRO2 | 69 | 4.7712 | 4.7713 | 2.0959e-05
GEN-2017-018 | Central | 03 - Spearville | 514775 | TANGRTP2 | 69 | 4.7833 | 4.7834 | 2.0906e-05
GEN-2017-018 | Central | 03 - Spearville | 514788 | GLASMTN4 | 138 | 5.1336 | 5.1337 | 1.948e-05
GEN-2017-018 | Central | 03 - Spearville | 532774 | SWISVAL7 | 345 | 16.1666 | 16.1669 | 1.8557e-05
GEN-2017-018 | Central | 03 - Spearville | 514776 | NEWGRTP2 | 69 | 5.4631 | 5.4632 | 1.8305e-05
GEN-2017-018 | Central | 03 - Spearville | 514781 | CEDARAV2 | 69 | 5.7046 | 5.7047 | 1.753e-05
GEN-2017-018 | Central | 03 - Spearville | 515610 | FSHRTAP7 | 345 | 17.7289 | 17.7292 | 1.6922e-05
GEN-2017-018 | Central | 03 - Spearville | 515786 | FPLWIND4 | 138 | 6.8222 | 6.8223 | 1.4658e-05
GEN-2017-018 | Central | 03 - Spearville | 900001 | TRAVERSE1 | 345 | 7.3844 | 7.3845 | 1.3542e-05
GEN-2017-018 | Central | 03 - Spearville | 521065 | TALOGA 4 | 138 | 7.4782 | 7.4783 | 1.3372e-05
GEN-2017-018 | Central | 03 - Spearville | 587140 | GEN-2016-020 | 138 | 7.4829 | 7.483 | 1.3364e-05
GEN-2017-018 | Central | 03 - Spearville | 520425 | PIC4 | 138 | 7.8452 | 7.8453 | 1.2747e-05
GEN-2017-018 | Central | 03 - Spearville | 520957 | IODINE 4 | 138 | 7.8901 | 7.8902 | 1.2674e-05
GEN-2017-018 | Central | 03 - Spearville | 520995 | MOORLND2 | 69 | 8.5665 | 8.5666 | 1.1673e-05
GEN-2017-018 | Central | 03 - Spearville | 583340 | GEN-2012-020 | 230 | 9.8744 | 9.8745 | 1.0127e-05
GEN-2017-018 | Central | 03 - Spearville | 525850 | ELK_CT1 | 345 | 11.8971 | 11.8972 | 8.4054e-06
GEN-2017-018 | Central | 03 - Spearville | 515600 | KNGFSHR7 | 345 | 11.9001 | 11.9002 | 8.4033e-06
GEN-2017-018 | Central | 03 - Spearville | 525832 | TUCO_INT 7 | 345 | 11.9884 | 11.9885 | 8.3414e-06
GEN-2017-018 | Central | 03 - Spearville | 515605 | CANADN7 | 345 | 12.9578 | 12.9579 | 7.7174e-06
GEN-2017-018 | Central | 03 - Spearville | 525840 | ANTELOPE_1 6 | 230 | 21.0432 | 21.0433 | 4.7521e-06
GEN-2017-018 | Central | 03 - Spearville | 525830 | TUCO_INT 6 | 230 | 21.2068 | 21.2069 | 4.7155e-06
GEN-2017-018 | Central | 03 - Spearville | 526936 | YOAKUM_345 | 345 | 8.5075 | 8.5075 | 0
GEN-2017-018 | Central | 03 - Spearville | 514771 | TANGIER2 | 69 | 3.6773 | 3.6773 | 0
GEN-2017-018 | Central | 03 - Spearville | 514773 | NEWMAN 2 | 69 | 1.5468 | 1.5468 | 0
GEN-2017-018 | Central | 03 - Spearville | 533629 | CC2SHAR2 | 69 | 4.5461 | 4.5461 | 0
GEN-2017-018 | Central | 03 - Spearville | 900002 | TRAVERSE2 | 345 | 5.7168 | 5.7168 | 0
GEN-2017-018 | Central | 03 - Spearville | 900003 | TRAVERSE3 | 345 | 5.1975 | 5.1975 | 0
GEN-2017-018 | Central | 03 - Spearville | 588760 | GEN-2017-033 | 345 | 4.0304 | 4.0304 | 0
GEN-2017-018 | Central | 03 - Spearville | 533653 | WOLFCRK2 | 69 | 5.8601 | 5.8601 | 0
GEN-2017-018 | Central | 03 - Spearville | 588970 | GEN-2017-059 | 230 | 8.547 | 8.547 | 0
GEN-2017-018 | Central | 03 - Spearville | 589030 | GEN-2017-065 | 345 | 5.0163 | 5.0163 | 0
GEN-2017-018 | Central | 03 - Spearville | 511565 | OKLAUN HVDC7 | 345 | 5.4749 | 5.4749 | 0
GEN-2017-018 | Central | 03 - Spearville | 511456 | O.K.U.-7 | 345 | 5.4913 | 5.4913 | 0
GEN-2017-021 | Central | 03 - Spearville | 588750 | GEN-2017-032 | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-021 | Central | 03 - Spearville | 588754 | G17-032-TAP | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-021 | Central | 03 - Spearville | 588650 | GEN-2017-021 | 345 | 8.859 | 9.6649 | 0.09097
GEN-2017-021 | Central | 03 - Spearville | 588654 | G17-021-TAP | 345 | 9.2902 | 10.1312 | 0.090525
GEN-2017-021 | Central | 03 - Spearville | 589370 | GEN-2017-099 | 345 | 8.859 | 9.6568 | 0.090055
GEN-2017-021 | Central | 03 - Spearville | 599950 | LAMAR7 | 345 | 2.3728 | 2.5722 | 0.084036
GEN-2017-021 | Central | 03 - Spearville | 531469 | SPERVIL7 | 345 | 13.1153 | 13.739 | 0.047555
GEN-2017-021 | Central | 03 - Spearville | 539803 | IRONWOOD7 | 345 | 12.5911 | 13.1405 | 0.043634
GEN-2017-021 | Central | 03 - Spearville | 579480 | GEN-2008-124 | 345 | 12.1777 | 12.6897 | 0.042044
GEN-2017-021 | Central | 03 - Spearville | 523853 | FINNEY 7 | 345 | 9.544 | 9.8902 | 0.036274
GEN-2017-021 | Central | 03 - Spearville | 531449 | HOLCOMB7 | 345 | 9.6562 | 10.0016 | 0.03577
GEN-2017-021 | Central | 03 - Spearville | 589484 | G16-049-TAP | 345 | 8.6792 | 8.9146 | 0.027122
GEN-2017-021 | Central | 03 - Spearville | 531501 | BUCKNER7 | 345 | 8.8014 | 9.0375 | 0.026825
GEN-2017-021 | Central | 03 - Spearville | 560080 | G16-046-TAP | 345 | 11.1556 | 11.4323 | 0.024804
GEN-2017-021 | Central | 03 - Spearville | 539800 | CLARKCOUNTY7 | 345 | 12.9764 | 13.2652 | 0.022256
GEN-2017-021 | Central | 03 - Spearville | 539695 | SPEARVL6 | 230 | 12.2036 | 12.4729 | 0.022067
GEN-2017-021 | Central | 03 - Spearville | 539117 | SPRVILL-EHVB | 230 | 11.8903 | 12.1451 | 0.021429
GEN-2017-021 | Central | 03 - Spearville | 531502 | CIMRRN 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-021 | Central | 03 - Spearville | 531504 | CIMWD2 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-021 | Central | 03 - Spearville | 587310 | GEN-2016-046 | 345 | 9.641 | 9.8441 | 0.021066
GEN-2017-021 | Central | 03 - Spearville | 523118 | BUFF_DUNES 7 | 345 | 5.9244 | 6.0476 | 0.020795
GEN-2017-021 | Central | 03 - Spearville | 530583 | POSTROCK7 | 345 | 9.5651 | 9.7633 | 0.020721
GEN-2017-021 | Central | 03 - Spearville | 583370 | GEN-2012-024 | 345 | 11.1056 | 11.3148 | 0.018837
GEN-2017-021 | Central | 03 - Spearville | 539852 | P1 MPT PRI | 345 | 10.5849 | 10.7708 | 0.017563
GEN-2017-021 | Central | 03 - Spearville | 582008 | GEN-2011-008 | 345 | 10.3495 | 10.5174 | 0.016223
GEN-2017-021 | Central | 03 - Spearville | 531465 | SETAB 7 | 345 | 7.0502 | 7.1573 | 0.015191
GEN-2017-021 | Central | 03 - Spearville | 539857 | P2 MPT PRI | 345 | 9.0022 | 9.1323 | 0.014452
GEN-2017-021 | Central | 03 - Spearville | 582908 | G-2011-008-2 | 345 | 8.3279 | 8.4371 | 0.013113
GEN-2017-021 | Central | 03 - Spearville | 582708 | G-2011-008-1 | 345 | 8.457 | 8.564 | 0.012652
GEN-2017-021 | Central | 03 - Spearville | 530584 | POSTROCK6 | 230 | 12.8772 | 13.0179 | 0.010926
GEN-2017-021 | Central | 03 - Spearville | 530558 | KNOLL 6 | 230 | 12.7371 | 12.8736 | 0.010717
GEN-2017-021 | Central | 03 - Spearville | 539759 | SPRVL 3 | 115 | 11.4523 | 11.5615 | 0.0095352
GEN-2017-021 | Central | 03 - Spearville | 531448 | HOLCOMB3 | 115 | 21.3888 | 21.5721 | 0.0085699
GEN-2017-021 | Central | 03 - Spearville | 530702 | BUCKEYE_230 | 230 | 9.2881 | 9.3543 | 0.0071274
GEN-2017-021 | Central | 03 - Spearville | 539694 | SPEARVL3 | 115 | 10.2986 | 10.3686 | 0.006797
GEN-2017-021 | Central | 03 - Spearville | 530582 | S HAYS6 | 230 | 9.7644 | 9.8282 | 0.0065339
GEN-2017-021 | Central | 03 - Spearville | 531451 | MINGO 7 | 345 | 6.8482 | 6.8898 | 0.0060746
GEN-2017-021 | Central | 03 - Spearville | 531632 | GEN-2016-067 | 345 | 6.8482 | 6.8898 | 0.0060746
GEN-2017-021 | Central | 03 - Spearville | 588580 | GEN-2017-013 | 345 | 6.7841 | 6.8249 | 0.0060141
GEN-2017-021 | Central | 03 - Spearville | 523823 | CARPENTER 7 | 345 | 6.5344 | 6.5732 | 0.0059378
GEN-2017-021 | Central | 03 - Spearville | 531464 | SETAB 3 | 115 | 10.2918 | 10.3483 | 0.0054898
GEN-2017-021 | Central | 03 - Spearville | 585030 | GEN-2015-065 | 345 | 6.1591 | 6.1922 | 0.0053742
GEN-2017-021 | Central | 03 - Spearville | 588630 | GEN-2017-018 | 345 | 16.3278 | 16.4054 | 0.0047526
GEN-2017-021 | Central | 03 - Spearville | 539801 | THISTLE7 | 345 | 16.3278 | 16.4054 | 0.0047526
GEN-2017-021 | Central | 03 - Spearville | 539679 | GRTBEND6 | 230 | 8.4778 | 8.513 | 0.004152
GEN-2017-021 | Central | 03 - Spearville | 530680 | HEIZER 6 | 230 | 8.4277 | 8.4625 | 0.0041292
GEN-2017-021 | Central | 03 - Spearville | 539771 | NFTDODG3 | 115 | 12.214 | 12.2642 | 0.00411
GEN-2017-021 | Central | 03 - Spearville | 539671 | FTDODGE3 | 115 | 12.1733 | 12.2228 | 0.0040663
GEN-2017-021 | Central | 03 - Spearville | 531379 | JONES3 | 115 | 10.8669 | 10.9085 | 0.0038281
GEN-2017-021 | Central | 03 - Spearville | 531445 | GRDNCTY3 | 115 | 14.0365 | 14.0881 | 0.0036761
GEN-2017-021 | Central | 03 - Spearville | 530561 | KNOLL 3 | 115 | 12.1272 | 12.168 | 0.0033643
GEN-2017-021 | Central | 03 - Spearville | 531429 | MINGO 3 | 115 | 12.9898 | 13.033 | 0.0033257
GEN-2017-021 | Central | 03 - Spearville | 530676 | GMEC 3 | 115 | 11.5228 | 11.5588 | 0.0031242
GEN-2017-021 | Central | 03 - Spearville | 640325 | REDWILO3 | 345 | 9.3783 | 9.4068 | 0.0030389
GEN-2017-021 | Central | 03 - Spearville | 560082 | G16-050-TAP | 345 | 7.1649 | 7.1859 | 0.002931
GEN-2017-021 | Central | 03 - Spearville | 530553 | S HAYS 3 | 115 | 9.13 | 9.1552 | 0.0027601
GEN-2017-021 | Central | 03 - Spearville | 539645 | DCBEEF3 | 115 | 8.1294 | 8.1515 | 0.0027185
GEN-2017-021 | Central | 03 - Spearville | 587350 | GEN-2016-050 | 345 | 6.4203 | 6.4369 | 0.0025855
GEN-2017-021 | Central | 03 - Spearville | 539688 | S-DODGE3 | 115 | 8.1466 | 8.1667 | 0.0024673
GEN-2017-021 | Central | 03 - Spearville | 539740 | EDODGE 3 | 115 | 7.2953 | 7.3131 | 0.0024399
GEN-2017-021 | Central | 03 - Spearville | 585020 | GEN-2015-064 | 115 | 10.1386 | 10.1633 | 0.0024362
GEN-2017-021 | Central | 03 - Spearville | 531393 | PLYMELL3 | 115 | 7.569 | 7.5869 | 0.0023649
GEN-2017-021 | Central | 03 - Spearville | 531420 | FLETCHR3 | 115 | 6.7413 | 6.7567 | 0.0022844
GEN-2017-021 | Central | 03 - Spearville | 530601 | HEIZER 3 | 115 | 12.7456 | 12.7746 | 0.0022753
GEN-2017-021 | Central | 03 - Spearville | 539678 | GRTBEND3 | 115 | 12.9225 | 12.9518 | 0.0022674
GEN-2017-021 | Central | 03 - Spearville | 539804 | THISTLE4 | 138 | 17.4711 | 17.502 | 0.0017686
GEN-2017-021 | Central | 03 - Spearville | 515852 | DGRASSE7 | 345 | 14.5329 | 14.5578 | 0.0017134
GEN-2017-021 | Central | 03 - Spearville | 539680 | N-DODGE3 | 115 | 5.1229 | 5.1316 | 0.0016983
GEN-2017-021 | Central | 03 - Spearville | 530610 | SHAYS_230 | 230 | 4.2554 | 4.2625 | 0.0016685
GEN-2017-021 | Central | 03 - Spearville | 640065 | AXTELL 3 | 345 | 9.6103 | 9.6255 | 0.0015816
GEN-2017-021 | Central | 03 - Spearville | 539638 | FLATRDG4 | 138 | 15.5075 | 15.5308 | 0.0015025
GEN-2017-021 | Central | 03 - Spearville | 539758 | FORD 3 | 115 | 5.5694 | 5.5777 | 0.0014903
GEN-2017-021 | Central | 03 - Spearville | 539681 | N-GBEND3 | 115 | 8.3462 | 8.3584 | 0.0014617
GEN-2017-021 | Central | 03 - Spearville | 530609 | HZRNGPL3 | 115 | 8.0052 | 8.0167 | 0.0014366
GEN-2017-021 | Central | 03 - Spearville | 539641 | NW-DODG3 | 115 | 3.8709 | 3.8759 | 0.0012917
GEN-2017-021 | Central | 03 - Spearville | 539699 | W-DODGE3 | 115 | 5.2105 | 5.2171 | 0.0012667
GEN-2017-021 | Central | 03 - Spearville | 532782 | BUFFALO7 | 345 | 20.6769 | 20.7023 | 0.0012284
GEN-2017-021 | Central | 03 - Spearville | 539666 | GBENDTP3 | 115 | 7.6967 | 7.7061 | 0.0012213
GEN-2017-021 | Central | 03 - Spearville | 531408 | PIERCVL3 | 115 | 3.8381 | 3.8427 | 0.0011985
GEN-2017-021 | Central | 03 - Spearville | 539783 | CRKCK 3 | 115 | 4.1956 | 4.2001 | 0.0010726
GEN-2017-021 | Central | 03 - Spearville | 539661 | 24-FREY3 | 115 | 5.6199 | 5.6255 | 0.00099646
GEN-2017-021 | Central | 03 - Spearville | 539628 | NW-DGTP3 | 115 | 4.063 | 4.067 | 0.00098449
GEN-2017-021 | Central | 03 - Spearville | 530552 | GORHAM 3 | 115 | 3.171 | 3.1741 | 0.00097761
GEN-2017-021 | Central | 03 - Spearville | 539631 | FLATRWD4 | 138 | 10.3564 | 10.3664 | 0.00096559
GEN-2017-021 | Central | 03 - Spearville | 532796 | WICHITA7 | 345 | 24.3601 | 24.3835 | 0.00096059
GEN-2017-021 | Central | 03 - Spearville | 530592 | SMOKYHL6 | 230 | 7.1343 | 7.1409 | 0.00092511
GEN-2017-021 | Central | 03 - Spearville | 539689 | 2ND-KS 3 | 115 | 5.0444 | 5.0489 | 0.00089208
GEN-2017-021 | Central | 03 - Spearville | 539944 | LOCHS | 115 | 3.6994 | 3.7027 | 0.00089204
GEN-2017-021 | Central | 03 - Spearville | 587500 | GEN-2016-073 | 345 | 15.1804 | 15.1939 | 0.0008893
GEN-2017-021 | Central | 03 - Spearville | 640326 | REDWILO7 | 115 | 12.6507 | 12.6619 | 0.00088533
GEN-2017-021 | Central | 03 - Spearville | 640183 | GENTLMN3 | 345 | 18.2387 | 18.2548 | 0.00088274
GEN-2017-021 | Central | 03 - Spearville | 531407 | INGALLS3 | 115 | 2.6792 | 2.6814 | 0.00082114
GEN-2017-021 | Central | 03 - Spearville | 531213 | SANTAFE3 | 115 | 2.6806 | 2.6828 | 0.00082071
GEN-2017-021 | Central | 03 - Spearville | 530599 | SMKYP2 6 | 230 | 6.6055 | 6.6109 | 0.0008175
GEN-2017-021 | Central | 03 - Spearville | 589060 | GEN-2017-068 | 345 | 20.2535 | 20.2698 | 0.0008048
GEN-2017-021 | Central | 03 - Spearville | 515375 | WWRDEHV7 | 345 | 19.805 | 19.8204 | 0.00077758
GEN-2017-021 | Central | 03 - Spearville | 530593 | SMKYP1 6 | 230 | 6.1703 | 6.175 | 0.00076171
GEN-2017-021 | Central | 03 - Spearville | 640252 | KEYSTON3 | 345 | 12.7746 | 12.7842 | 0.00075149
GEN-2017-021 | Central | 03 - Spearville | 530677 | OGALATP3 | 115 | 2.6344 | 2.6363 | 0.00072123
GEN-2017-021 | Central | 03 - Spearville | 539763 | SSTARTP3 | 115 | 4.0724 | 4.0753 | 0.00071211
GEN-2017-021 | Central | 03 - Spearville | 640374 | SWEET W3 | 345 | 10.9794 | 10.9872 | 0.00071042
GEN-2017-021 | Central | 03 - Spearville | 539784 | ENSNGW 3 | 115 | 2.8424 | 2.8444 | 0.00070363
GEN-2017-021 | Central | 03 - Spearville | 531211 | CHRLSTN3 | 115 | 2.2297 | 2.2312 | 0.00067274
GEN-2017-021 | Central | 03 - Spearville | 531210 | BLUEJAY3 | 115 | 2.1032 | 2.1046 | 0.00066565
GEN-2017-021 | Central | 03 - Spearville | 530684 | RUSLPMP3 | 115 | 2.0504 | 2.0517 | 0.00063402
GEN-2017-021 | Central | 03 - Spearville | 531492 | OG ONEOK | 115 | 2.1303 | 2.1316 | 0.00061024
GEN-2017-021 | Central | 03 - Spearville | 532871 | CIRCLE 6 | 230 | 10.0517 | 10.0578 | 0.00060686
GEN-2017-021 | Central | 03 - Spearville | 530560 | WKNNY 3 | 115 | 2.2105 | 2.2118 | 0.0005881
GEN-2017-021 | Central | 03 - Spearville | 531423 | GARDNCY2 | 69 | 3.6434 | 3.6455 | 0.00057638
GEN-2017-021 | Central | 03 - Spearville | 539761 | SSTARW 3 | 115 | 3.4163 | 3.4182 | 0.00055616
GEN-2017-021 | Central | 03 - Spearville | 640269 | MCCOOK 7 | 115 | 9.3182 | 9.3232 | 0.00053658
GEN-2017-021 | Central | 03 - Spearville | 539684 | OTISSUB3 | 115 | 2.9576 | 2.9591 | 0.00050717
GEN-2017-021 | Central | 03 - Spearville | 640312 | PAULINE3 | 345 | 8.4521 | 8.4562 | 0.00048509
GEN-2017-021 | Central | 03 - Spearville | 531212 | TWNSPRG3 | 115 | 1.6677 | 1.6685 | 0.0004797
GEN-2017-021 | Central | 03 - Spearville | 640066 | AXTELL 7 | 115 | 14.2198 | 14.2265 | 0.00047117
GEN-2017-021 | Central | 03 - Spearville | 515599 | G07621119-20 | 345 | 13.1976 | 13.2036 | 0.00045463
GEN-2017-021 | Central | 03 - Spearville | 588530 | GEN-2017-008 | 345 | 7.853 | 7.8565 | 0.00044569
GEN-2017-021 | Central | 03 - Spearville | 539779 | GRAY CO3 | 115 | 3.5101 | 3.5116 | 0.00042734
GEN-2017-021 | Central | 03 - Spearville | 539667 | HAGGARD3 | 115 | 3.5101 | 3.5116 | 0.00042734
GEN-2017-021 | Central | 03 - Spearville | 539778 | GYCOTAP3 | 115 | 3.5101 | 3.5116 | 0.00042734
GEN-2017-021 | Central | 03 - Spearville | 515853 | DGRASSE4 | 138 | 15.3859 | 15.3923 | 0.00041597
GEN-2017-021 | Central | 03 - Spearville | 640184 | GENTLMN4 | 230 | 20.0055 | 20.0136 | 0.00040489
GEN-2017-021 | Central | 03 - Spearville | 533413 | CIRCLE 3 | 115 | 23.6141 | 23.6235 | 0.00039807
GEN-2017-021 | Central | 03 - Spearville | 585430 | PRSIMN_CRK1 | 345 | 11.6142 | 11.6188 | 0.00039607
GEN-2017-021 | Central | 03 - Spearville | 587680 | GEN-2016-074 | 345 | 6.4721 | 6.4745 | 0.00037082
GEN-2017-021 | Central | 03 - Spearville | 585440 | PRSIMN_CRK2 | 345 | 10.6058 | 10.6096 | 0.00035829
GEN-2017-021 | Central | 03 - Spearville | 539642 | ELLSWTP3 | 115 | 3.9821 | 3.9835 | 0.00035157
GEN-2017-021 | Central | 03 - Spearville | 532872 | EMCPHER6 | 230 | 9.3729 | 9.3761 | 0.00034141
GEN-2017-021 | Central | 03 - Spearville | 587850 | GEN-2016-106 | 345 | 8.8132 | 8.8161 | 0.00032905
GEN-2017-021 | Central | 03 - Spearville | 585410 | GREAT_WESTRN | 345 | 9.9442 | 9.9473 | 0.00031174
GEN-2017-021 | Central | 03 - Spearville | 532783 | KINGMAN7 | 345 | 6.8306 | 6.8327 | 0.00030744
GEN-2017-021 | Central | 03 - Spearville | 640082 | BEVERLY7 | 115 | 4.8655 | 4.8669 | 0.00028774
GEN-2017-021 | Central | 03 - Spearville | 659425 | SD.LS-KS-MB3 | 345 | 7.6812 | 7.6833 | 0.00027339
GEN-2017-021 | Central | 03 - Spearville | 659426 | SD.LS-LR-MB3 | 345 | 7.6812 | 7.6833 | 0.00027339
GEN-2017-021 | Central | 03 - Spearville | 640253 | KEYSTON7 | 115 | 15.6225 | 15.6265 | 0.00025604
GEN-2017-021 | Central | 03 - Spearville | 532784 | NINN1WF7 | 345 | 5.6879 | 5.6893 | 0.00024614
GEN-2017-021 | Central | 03 - Spearville | 585420 | COWBOY_RIDGE | 345 | 7.6709 | 7.6727 | 0.00023465
GEN-2017-021 | Central | 03 - Spearville | 585250 | GEN-2015-090 | 345 | 5.0818 | 5.0829 | 0.00021646
GEN-2017-021 | Central | 03 - Spearville | 530686 | RICE 6 | 230 | 4.9172 | 4.9182 | 0.00020337
GEN-2017-021 | Central | 03 - Spearville | 640365 | STOCKVL7 | 115 | 4.5853 | 4.5862 | 0.00019628
GEN-2017-021 | Central | 03 - Spearville | 640083 | BEVERLY8 | 69 | 4.356 | 4.3567 | 0.0001607
GEN-2017-021 | Central | 03 - Spearville | 640270 | MCCOOK 8 | 69 | 4.5246 | 4.5253 | 0.00015471
GEN-2017-021 | Central | 03 - Spearville | 640255 | KINGSLY7 | 115 | 9.3401 | 9.3414 | 0.00013918
GEN-2017-021 | Central | 03 - Spearville | 640500 | THEDFRD3 | 345 | 5.2771 | 5.2777 | 0.0001137
GEN-2017-021 | Central | 03 - Spearville | 640366 | STOCKVL8 | 69 | 3.2872 | 3.2875 | 9.1263e-05
GEN-2017-021 | Central | 03 - Spearville | 530688 | BUFLOCRK6 | 230 | 3.6479 | 3.6482 | 8.2239e-05
GEN-2017-032 | Central | 03 - Spearville | 588750 | GEN-2017-032 | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-032 | Central | 03 - Spearville | 588754 | G17-032-TAP | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-032 | Central | 03 - Spearville | 588650 | GEN-2017-021 | 345 | 8.859 | 9.6649 | 0.09097
GEN-2017-032 | Central | 03 - Spearville | 588654 | G17-021-TAP | 345 | 9.2902 | 10.1312 | 0.090525
GEN-2017-032 | Central | 03 - Spearville | 589370 | GEN-2017-099 | 345 | 8.859 | 9.6568 | 0.090055
GEN-2017-032 | Central | 03 - Spearville | 599950 | LAMAR7 | 345 | 2.3728 | 2.5722 | 0.084036
GEN-2017-032 | Central | 03 - Spearville | 531469 | SPERVIL7 | 345 | 13.1153 | 13.739 | 0.047555
GEN-2017-032 | Central | 03 - Spearville | 539803 | IRONWOOD7 | 345 | 12.5911 | 13.1405 | 0.043634
GEN-2017-032 | Central | 03 - Spearville | 579480 | GEN-2008-124 | 345 | 12.1777 | 12.6897 | 0.042044
GEN-2017-032 | Central | 03 - Spearville | 523853 | FINNEY 7 | 345 | 9.544 | 9.8902 | 0.036274
GEN-2017-032 | Central | 03 - Spearville | 531449 | HOLCOMB7 | 345 | 9.6562 | 10.0016 | 0.03577
GEN-2017-032 | Central | 03 - Spearville | 531501 | BUCKNER7 | 345 | 8.8014 | 9.0375 | 0.026825
GEN-2017-032 | Central | 03 - Spearville | 539800 | CLARKCOUNTY7 | 345 | 12.9764 | 13.2652 | 0.022256
GEN-2017-032 | Central | 03 - Spearville | 539695 | SPEARVL6 | 230 | 12.2036 | 12.4729 | 0.022067
GEN-2017-032 | Central | 03 - Spearville | 539117 | SPRVILL-EHVB | 230 | 11.8903 | 12.1451 | 0.021429
GEN-2017-032 | Central | 03 - Spearville | 531502 | CIMRRN 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-032 | Central | 03 - Spearville | 531504 | CIMWD2 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-032 | Central | 03 - Spearville | 523118 | BUFF_DUNES 7 | 345 | 5.9244 | 6.0476 | 0.020795
GEN-2017-032 | Central | 03 - Spearville | 583370 | GEN-2012-024 | 345 | 11.1056 | 11.3148 | 0.018837
GEN-2017-032 | Central | 03 - Spearville | 539852 | P1 MPT PRI | 345 | 10.5849 | 10.7708 | 0.017563
GEN-2017-032 | Central | 03 - Spearville | 582008 | GEN-2011-008 | 345 | 10.3495 | 10.5174 | 0.016223
GEN-2017-032 | Central | 03 - Spearville | 531465 | SETAB 7 | 345 | 7.0502 | 7.1573 | 0.015191
GEN-2017-032 | Central | 03 - Spearville | 539857 | P2 MPT PRI | 345 | 9.0022 | 9.1323 | 0.014452
GEN-2017-032 | Central | 03 - Spearville | 582908 | G-2011-008-2 | 345 | 8.3279 | 8.4371 | 0.013113
GEN-2017-032 | Central | 03 - Spearville | 582708 | G-2011-008-1 | 345 | 8.457 | 8.564 | 0.012652
GEN-2017-032 | Central | 03 - Spearville | 539759 | SPRVL 3 | 115 | 11.4523 | 11.5615 | 0.0095352
GEN-2017-032 | Central | 03 - Spearville | 531448 | HOLCOMB3 | 115 | 21.3888 | 21.5721 | 0.0085699
GEN-2017-032 | Central | 03 - Spearville | 531632 | GEN-2016-067 | 345 | 6.8482 | 6.8898 | 0.0060746
GEN-2017-032 | Central | 03 - Spearville | 531451 | MINGO 7 | 345 | 6.8482 | 6.8898 | 0.0060746
GEN-2017-032 | Central | 03 - Spearville | 588580 | GEN-2017-013 | 345 | 6.7841 | 6.8249 | 0.0060141
GEN-2017-032 | Central | 03 - Spearville | 523823 | CARPENTER 7 | 345 | 6.5344 | 6.5732 | 0.0059378
GEN-2017-032 | Central | 03 - Spearville | 531512 | HARBNGR7 | 345 | 6.5143 | 6.5528 | 0.0059101
GEN-2017-032 | Central | 03 - Spearville | 531464 | SETAB 3 | 115 | 10.2918 | 10.3483 | 0.0054898
GEN-2017-032 | Central | 03 - Spearville | 585030 | GEN-2015-065 | 345 | 6.1591 | 6.1922 | 0.0053742
GEN-2017-032 | Central | 03 - Spearville | 531433 | SCOTCTY3 | 115 | 8.7819 | 8.82 | 0.0043385
GEN-2017-032 | Central | 03 - Spearville | 531379 | JONES3 | 115 | 10.8669 | 10.9085 | 0.0038281
GEN-2017-032 | Central | 03 - Spearville | 531445 | GRDNCTY3 | 115 | 14.0365 | 14.0881 | 0.0036761
GEN-2017-032 | Central | 03 - Spearville | 531480 | KSAVWTP3 | 115 | 13.5136 | 13.5621 | 0.003589
GEN-2017-032 | Central | 03 - Spearville | 531426 | JAMESON3 | 115 | 10.363 | 10.3994 | 0.0035125
GEN-2017-032 | Central | 03 - Spearville | 531429 | MINGO 3 | 115 | 12.9898 | 13.033 | 0.0033257
GEN-2017-032 | Central | 03 - Spearville | 640325 | REDWILO3 | 345 | 9.3783 | 9.4068 | 0.0030389
GEN-2017-032 | Central | 03 - Spearville | 531510 | HARBNGR3 | 115 | 9.5207 | 9.5445 | 0.0024998
GEN-2017-032 | Central | 03 - Spearville | 531485 | CNTRLPL3 | 115 | 5.5886 | 5.6025 | 0.0024872
GEN-2017-032 | Central | 03 - Spearville | 585020 | GEN-2015-064 | 115 | 10.1386 | 10.1633 | 0.0024362
GEN-2017-032 | Central | 03 - Spearville | 531405 | WALKMYR3 | 115 | 9.1635 | 9.1852 | 0.0023681
GEN-2017-032 | Central | 03 - Spearville | 531393 | PLYMELL3 | 115 | 7.569 | 7.5869 | 0.0023649
GEN-2017-032 | Central | 03 - Spearville | 531420 | FLETCHR3 | 115 | 6.7413 | 6.7567 | 0.0022844
GEN-2017-032 | Central | 03 - Spearville | 531476 | SWNDTAP3 | 115 | 7.603 | 7.6182 | 0.0019992
GEN-2017-032 | Central | 03 - Spearville | 531477 | S. WIND3 | 115 | 6.9695 | 6.9823 | 0.0018366
GEN-2017-032 | Central | 03 - Spearville | 531392 | PIONTAP3 | 115 | 6.4742 | 6.4831 | 0.0013747
GEN-2017-032 | Central | 03 - Spearville | 531400 | PK_GOAB3 | 115 | 4.8387 | 4.8451 | 0.0013227
GEN-2017-032 | Central | 03 - Spearville | 531375 | PUCKET 3 | 115 | 4.8253 | 4.8316 | 0.0013056
GEN-2017-032 | Central | 03 - Spearville | 523097 | HITCHLAND 7 | 345 | 15.0825 | 15.1013 | 0.0012465
GEN-2017-032 | Central | 03 - Spearville | 531398 | SUBLETE3 | 115 | 5.7966 | 5.8038 | 0.0012421
GEN-2017-032 | Central | 03 - Spearville | 531404 | WALKMYR2 | 69 | 8.0166 | 8.0265 | 0.0012349
GEN-2017-032 | Central | 03 - Spearville | 531440 | WILLIAM3 | 115 | 3.7332 | 3.7378 | 0.0012322
GEN-2017-032 | Central | 03 - Spearville | 523112 | NOVUS1 7 | 345 | 14.8143 | 14.8323 | 0.001215
GEN-2017-032 | Central | 03 - Spearville | 531408 | PIERCVL3 | 115 | 3.8381 | 3.8427 | 0.0011985
GEN-2017-032 | Central | 03 - Spearville | 531406 | WOODS 2 | 69 | 5.9432 | 5.9487 | 0.00092543
GEN-2017-032 | Central | 03 - Spearville | 576395 | GEN-2010-014 | 345 | 11.1406 | 11.1504 | 0.00087967
GEN-2017-032 | Central | 03 - Spearville | 515554 | BVRCNTY7 | 345 | 14.7467 | 14.759 | 0.00083408
GEN-2017-032 | Central | 03 - Spearville | 531407 | INGALLS3 | 115 | 2.6792 | 2.6814 | 0.00082114
GEN-2017-032 | Central | 03 - Spearville | 531213 | SANTAFE3 | 115 | 2.6806 | 2.6828 | 0.00082071
GEN-2017-032 | Central | 03 - Spearville | 523215 | FREWHELCOL17 | 345 | 9.1648 | 9.1713 | 0.00070924
GEN-2017-032 | Central | 03 - Spearville | 515590 | PALDR2W7 | 345 | 12.8368 | 12.8458 | 0.00070111
GEN-2017-032 | Central | 03 - Spearville | 515677 | BADGER 7 | 345 | 14.1527 | 14.1624 | 0.00068538
GEN-2017-032 | Central | 03 - Spearville | 515618 | BALKOW 7 | 345 | 12.2498 | 12.2581 | 0.00067756
GEN-2017-032 | Central | 03 - Spearville | 531211 | CHRLSTN3 | 115 | 2.2297 | 2.2312 | 0.00067274
GEN-2017-032 | Central | 03 - Spearville | 531210 | BLUEJAY3 | 115 | 2.1032 | 2.1046 | 0.00066565
GEN-2017-032 | Central | 03 - Spearville | 523095 | HITCHLAND 6 | 230 | 14.7297 | 14.7393 | 0.00065174
GEN-2017-032 | Central | 03 - Spearville | 515686 | GEN-2011-014 | 345 | 12.7547 | 12.7624 | 0.0006037
GEN-2017-032 | Central | 03 - Spearville | 515634 | PALDR1W7 | 345 | 11.2669 | 11.2735 | 0.00058579
GEN-2017-032 | Central | 03 - Spearville | 531423 | GARDNCY2 | 69 | 3.6434 | 3.6455 | 0.00057638
GEN-2017-032 | Central | 03 - Spearville | 531212 | TWNSPRG3 | 115 | 1.6677 | 1.6685 | 0.0004797
GEN-2017-032 | Central | 03 - Spearville | 531389 | NORTH6T2 | 69 | 2.9234 | 2.9247 | 0.00044469
GEN-2017-032 | Central | 03 - Spearville | 531388 | NORTH6 2 | 69 | 2.5026 | 2.5035 | 0.00035963
GEN-2017-032 | Central | 03 - Spearville | 531384 | MOSCOW 2 | 69 | 2.1181 | 2.1188 | 0.00033048
GEN-2017-032 | Central | 03 - Spearville | 523111 | NOVUS1 3 | 115 | 19.4124 | 19.4188 | 0.00032969
GEN-2017-032 | Central | 03 - Spearville | 585190 | GEN-2015-082 | 345 | 7.142 | 7.1443 | 0.00032204
GEN-2017-032 | Central | 03 - Spearville | 531385 | MOSCOWT2 | 69 | 2.2272 | 2.2279 | 0.0003143
GEN-2017-032 | Central | 03 - Spearville | 523093 | HITCHLAND 3 | 115 | 17.7697 | 17.775 | 0.00029826
GEN-2017-032 | Central | 03 - Spearville | 576396 | G10-014-XFMR | 115 | 13.2816 | 13.2853 | 0.00027858
GEN-2017-032 | Central | 03 - Spearville | 576407 | G10-014-XF-2 | 115 | 12.5088 | 12.512 | 0.00025582
GEN-2017-032 | Central | 03 - Spearville | 523103 | NOBLE_WND 3 | 115 | 10.6709 | 10.6735 | 0.00024365
GEN-2017-032 | Central | 03 - Spearville | 523131 | NBLWND-HV3 3 | 115 | 8.0184 | 8.0198 | 0.0001746
GEN-2017-032 | Central | 03 - Spearville | 576397 | G10-014-XF-1 | 115 | 9.2433 | 9.2449 | 0.0001731
GEN-2017-032 | Central | 03 - Spearville | 523155 | OCHILTREE 6 | 230 | 4.2738 | 4.2744 | 0.00014039
GEN-2017-032 | Central | 03 - Spearville | 579377 | G06-044-MV2B | 115 | 10.2519 | 10.2533 | 0.00013656
GEN-2017-032 | Central | 03 - Spearville | 523961 | POTTER_CO 7 | 345 | 7.4518 | 7.4527 | 0.00012078
GEN-2017-032 | Central | 03 - Spearville | 523130 | NBLWND-HV2 3 | 115 | 5.1328 | 5.1334 | 0.0001169
GEN-2017-032 | Central | 03 - Spearville | 579370 | G06-044-MV1A | 115 | 8.2364 | 8.2373 | 0.00010927
GEN-2017-032 | Central | 03 - Spearville | 523309 | MOORE_CNTY 6 | 230 | 6.8181 | 6.8187 | 8.8001e-05
GEN-2017-032 | Central | 03 - Spearville | 523174 | GOODWELLWND3 | 115 | 6.6028 | 6.6033 | 7.5725e-05
GEN-2017-032 | Central | 03 - Spearville | 523959 | POTTER_CO 6 | 230 | 20.0739 | 20.0753 | 6.9742e-05
GEN-2017-032 | Central | 03 - Spearville | 524296 | SPNSPUR_WND7 | 345 | 4.5322 | 4.5325 | 6.6193e-05
GEN-2017-032 | Central | 03 - Spearville | 524909 | ROSEVELT_N 6 | 230 | 9.3752 | 9.3752 | 0
GEN-2017-032 | Central | 03 - Spearville | 599955 | PNM-DC6 | 230 | 9.3752 | 9.3752 | 0
GEN-2017-032 | Central | 03 - Spearville | 599951 | LAMAR 6 | 345 | 57.859 | 57.859 | 0
GEN-2017-032 | Central | 03 - Spearville | 599960 | EPTNP-D6 | 230 | 7.7768 | 7.7768 | 0
GEN-2017-099 | Central | 03 - Spearville | 588750 | GEN-2017-032 | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-099 | Central | 03 - Spearville | 588754 | G17-032-TAP | 345 | 2.9216 | 3.2299 | 0.10552
GEN-2017-099 | Central | 03 - Spearville | 588650 | GEN-2017-021 | 345 | 8.859 | 9.6649 | 0.09097
GEN-2017-099 | Central | 03 - Spearville | 588654 | G17-021-TAP | 345 | 9.2902 | 10.1312 | 0.090525
GEN-2017-099 | Central | 03 - Spearville | 589370 | GEN-2017-099 | 345 | 8.859 | 9.6568 | 0.090055
GEN-2017-099 | Central | 03 - Spearville | 599950 | LAMAR7 | 345 | 2.3728 | 2.5722 | 0.084036
GEN-2017-099 | Central | 03 - Spearville | 531469 | SPERVIL7 | 345 | 13.1153 | 13.739 | 0.047555
GEN-2017-099 | Central | 03 - Spearville | 539803 | IRONWOOD7 | 345 | 12.5911 | 13.1405 | 0.043634
GEN-2017-099 | Central | 03 - Spearville | 579480 | GEN-2008-124 | 345 | 12.1777 | 12.6897 | 0.042044
GEN-2017-099 | Central | 03 - Spearville | 523853 | FINNEY 7 | 345 | 9.544 | 9.8902 | 0.036274
GEN-2017-099 | Central | 03 - Spearville | 531449 | HOLCOMB7 | 345 | 9.6562 | 10.0016 | 0.03577
GEN-2017-099 | Central | 03 - Spearville | 531501 | BUCKNER7 | 345 | 8.8014 | 9.0375 | 0.026825
GEN-2017-099 | Central | 03 - Spearville | 539800 | CLARKCOUNTY7 | 345 | 12.9764 | 13.2652 | 0.022256
GEN-2017-099 | Central | 03 - Spearville | 539695 | SPEARVL6 | 230 | 12.2036 | 12.4729 | 0.022067
GEN-2017-099 | Central | 03 - Spearville | 539117 | SPRVILL-EHVB | 230 | 11.8903 | 12.1451 | 0.021429
GEN-2017-099 | Central | 03 - Spearville | 531502 | CIMRRN 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-099 | Central | 03 - Spearville | 531504 | CIMWD2 7 | 345 | 7.0225 | 7.172 | 0.021289
GEN-2017-099 | Central | 03 - Spearville | 523118 | BUFF_DUNES 7 | 345 | 5.9244 | 6.0476 | 0.020795
GEN-2017-099 | Central | 03 - Spearville | 583370 | GEN-2012-024 | 345 | 11.1056 | 11.3148 | 0.018837
GEN-2017-099 | Central | 03 - Spearville | 539852 | P1 MPT PRI | 345 | 10.5849 | 10.7708 | 0.017563
GEN-2017-099 | Central | 03 - Spearville | 582008 | GEN-2011-008 | 345 | 10.3495 | 10.5174 | 0.016223
GEN-2017-099 | Central | 03 - Spearville | 531465 | SETAB 7 | 345 | 7.0502 | 7.1573 | 0.015191
GEN-2017-099 | Central | 03 - Spearville | 539857 | P2 MPT PRI | 345 | 9.0022 | 9.1323 | 0.014452
GEN-2017-099 | Central | 03 - Spearville | 582908 | G-2011-008-2 | 345 | 8.3279 | 8.4371 | 0.013113
GEN-2017-099 | Central | 03 - Spearville | 582708 | G-2011-008-1 | 345 | 8.457 | 8.564 | 0.012652
GEN-2017-099 | Central | 03 - Spearville | 539759 | SPRVL 3 | 115 | 11.4523 | 11.5615 | 0.0095352
GEN-2017-099 | Central | 03 - Spearville | 531448 | HOLCOMB3 | 115 | 21.3888 | 21.5721 | 0.0085699
GEN-2017-099 | Central | 03 - Spearville | 531632 | GEN-2016-067 | 345 | 6.8482 | 6.8898 | 0.0060746
GEN-2017-099 | Central | 03 - Spearville | 531451 | MINGO 7 | 345 | 6.8482 | 6.8898 | 0.0060746
GEN-2017-099 | Central | 03 - Spearville | 588580 | GEN-2017-013 | 345 | 6.7841 | 6.8249 | 0.0060141
GEN-2017-099 | Central | 03 - Spearville | 523823 | CARPENTER 7 | 345 | 6.5344 | 6.5732 | 0.0059378
GEN-2017-099 | Central | 03 - Spearville | 531512 | HARBNGR7 | 345 | 6.5143 | 6.5528 | 0.0059101
GEN-2017-099 | Central | 03 - Spearville | 531464 | SETAB 3 | 115 | 10.2918 | 10.3483 | 0.0054898
GEN-2017-099 | Central | 03 - Spearville | 585030 | GEN-2015-065 | 345 | 6.1591 | 6.1922 | 0.0053742
GEN-2017-099 | Central | 03 - Spearville | 531433 | SCOTCTY3 | 115 | 8.7819 | 8.82 | 0.0043385
GEN-2017-099 | Central | 03 - Spearville | 531379 | JONES3 | 115 | 10.8669 | 10.9085 | 0.0038281
GEN-2017-099 | Central | 03 - Spearville | 531445 | GRDNCTY3 | 115 | 14.0365 | 14.0881 | 0.0036761
GEN-2017-099 | Central | 03 - Spearville | 531480 | KSAVWTP3 | 115 | 13.5136 | 13.5621 | 0.003589
GEN-2017-099 | Central | 03 - Spearville | 531426 | JAMESON3 | 115 | 10.363 | 10.3994 | 0.0035125
GEN-2017-099 | Central | 03 - Spearville | 531429 | MINGO 3 | 115 | 12.9898 | 13.033 | 0.0033257
GEN-2017-099 | Central | 03 - Spearville | 640325 | REDWILO3 | 345 | 9.3783 | 9.4068 | 0.0030389
GEN-2017-099 | Central | 03 - Spearville | 531510 | HARBNGR3 | 115 | 9.5207 | 9.5445 | 0.0024998
GEN-2017-099 | Central | 03 - Spearville | 531485 | CNTRLPL3 | 115 | 5.5886 | 5.6025 | 0.0024872
GEN-2017-099 | Central | 03 - Spearville | 585020 | GEN-2015-064 | 115 | 10.1386 | 10.1633 | 0.0024362
GEN-2017-099 | Central | 03 - Spearville | 531405 | WALKMYR3 | 115 | 9.1635 | 9.1852 | 0.0023681
GEN-2017-099 | Central | 03 - Spearville | 531393 | PLYMELL3 | 115 | 7.569 | 7.5869 | 0.0023649
GEN-2017-099 | Central | 03 - Spearville | 531420 | FLETCHR3 | 115 | 6.7413 | 6.7567 | 0.0022844
GEN-2017-099 | Central | 03 - Spearville | 531476 | SWNDTAP3 | 115 | 7.603 | 7.6182 | 0.0019992
GEN-2017-099 | Central | 03 - Spearville | 531477 | S. WIND3 | 115 | 6.9695 | 6.9823 | 0.0018366
GEN-2017-099 | Central | 03 - Spearville | 531392 | PIONTAP3 | 115 | 6.4742 | 6.4831 | 0.0013747
GEN-2017-099 | Central | 03 - Spearville | 531400 | PK_GOAB3 | 115 | 4.8387 | 4.8451 | 0.0013227
GEN-2017-099 | Central | 03 - Spearville | 531375 | PUCKET 3 | 115 | 4.8253 | 4.8316 | 0.0013056
GEN-2017-099 | Central | 03 - Spearville | 523097 | HITCHLAND 7 | 345 | 15.0825 | 15.1013 | 0.0012465
GEN-2017-099 | Central | 03 - Spearville | 531398 | SUBLETE3 | 115 | 5.7966 | 5.8038 | 0.0012421
GEN-2017-099 | Central | 03 - Spearville | 531404 | WALKMYR2 | 69 | 8.0166 | 8.0265 | 0.0012349
GEN-2017-099 | Central | 03 - Spearville | 531440 | WILLIAM3 | 115 | 3.7332 | 3.7378 | 0.0012322
GEN-2017-099 | Central | 03 - Spearville | 523112 | NOVUS1 7 | 345 | 14.8143 | 14.8323 | 0.001215
GEN-2017-099 | Central | 03 - Spearville | 531408 | PIERCVL3 | 115 | 3.8381 | 3.8427 | 0.0011985
GEN-2017-099 | Central | 03 - Spearville | 531406 | WOODS 2 | 69 | 5.9432 | 5.9487 | 0.00092543
GEN-2017-099 | Central | 03 - Spearville | 576395 | GEN-2010-014 | 345 | 11.1406 | 11.1504 | 0.00087967
GEN-2017-099 | Central | 03 - Spearville | 515554 | BVRCNTY7 | 345 | 14.7467 | 14.759 | 0.00083408
GEN-2017-099 | Central | 03 - Spearville | 531407 | INGALLS3 | 115 | 2.6792 | 2.6814 | 0.00082114
GEN-2017-099 | Central | 03 - Spearville | 531213 | SANTAFE3 | 115 | 2.6806 | 2.6828 | 0.00082071
GEN-2017-099 | Central | 03 - Spearville | 523215 | FREWHELCOL17 | 345 | 9.1648 | 9.1713 | 0.00070924
GEN-2017-099 | Central | 03 - Spearville | 515590 | PALDR2W7 | 345 | 12.8368 | 12.8458 | 0.00070111
GEN-2017-099 | Central | 03 - Spearville | 515677 | BADGER 7 | 345 | 14.1527 | 14.1624 | 0.00068538
GEN-2017-099 | Central | 03 - Spearville | 515618 | BALKOW 7 | 345 | 12.2498 | 12.2581 | 0.00067756
GEN-2017-099 | Central | 03 - Spearville | 531211 | CHRLSTN3 | 115 | 2.2297 | 2.2312 | 0.00067274
GEN-2017-099 | Central | 03 - Spearville | 531210 | BLUEJAY3 | 115 | 2.1032 | 2.1046 | 0.00066565
GEN-2017-099 | Central | 03 - Spearville | 523095 | HITCHLAND 6 | 230 | 14.7297 | 14.7393 | 0.00065174
GEN-2017-099 | Central | 03 - Spearville | 515686 | GEN-2011-014 | 345 | 12.7547 | 12.7624 | 0.0006037
GEN-2017-099 | Central | 03 - Spearville | 515634 | PALDR1W7 | 345 | 11.2669 | 11.2735 | 0.00058579
GEN-2017-099 | Central | 03 - Spearville | 531423 | GARDNCY2 | 69 | 3.6434 | 3.6455 | 0.00057638
GEN-2017-099 | Central | 03 - Spearville | 531212 | TWNSPRG3 | 115 | 1.6677 | 1.6685 | 0.0004797
GEN-2017-099 | Central | 03 - Spearville | 531389 | NORTH6T2 | 69 | 2.9234 | 2.9247 | 0.00044469
GEN-2017-099 | Central | 03 - Spearville | 531388 | NORTH6 2 | 69 | 2.5026 | 2.5035 | 0.00035963
GEN-2017-099 | Central | 03 - Spearville | 531384 | MOSCOW 2 | 69 | 2.1181 | 2.1188 | 0.00033048
GEN-2017-099 | Central | 03 - Spearville | 523111 | NOVUS1 3 | 115 | 19.4124 | 19.4188 | 0.00032969
GEN-2017-099 | Central | 03 - Spearville | 585190 | GEN-2015-082 | 345 | 7.142 | 7.1443 | 0.00032204
GEN-2017-099 | Central | 03 - Spearville | 531385 | MOSCOWT2 | 69 | 2.2272 | 2.2279 | 0.0003143
GEN-2017-099 | Central | 03 - Spearville | 523093 | HITCHLAND 3 | 115 | 17.7697 | 17.775 | 0.00029826
GEN-2017-099 | Central | 03 - Spearville | 576396 | G10-014-XFMR | 115 | 13.2816 | 13.2853 | 0.00027858
GEN-2017-099 | Central | 03 - Spearville | 576407 | G10-014-XF-2 | 115 | 12.5088 | 12.512 | 0.00025582
GEN-2017-099 | Central | 03 - Spearville | 523103 | NOBLE_WND 3 | 115 | 10.6709 | 10.6735 | 0.00024365
GEN-2017-099 | Central | 03 - Spearville | 523131 | NBLWND-HV3 3 | 115 | 8.0184 | 8.0198 | 0.0001746
GEN-2017-099 | Central | 03 - Spearville | 576397 | G10-014-XF-1 | 115 | 9.2433 | 9.2449 | 0.0001731
GEN-2017-099 | Central | 03 - Spearville | 523155 | OCHILTREE 6 | 230 | 4.2738 | 4.2744 | 0.00014039
GEN-2017-099 | Central | 03 - Spearville | 579377 | G06-044-MV2B | 115 | 10.2519 | 10.2533 | 0.00013656
GEN-2017-099 | Central | 03 - Spearville | 523961 | POTTER_CO 7 | 345 | 7.4518 | 7.4527 | 0.00012078
GEN-2017-099 | Central | 03 - Spearville | 523130 | NBLWND-HV2 3 | 115 | 5.1328 | 5.1334 | 0.0001169
GEN-2017-099 | Central | 03 - Spearville | 579370 | G06-044-MV1A | 115 | 8.2364 | 8.2373 | 0.00010927
GEN-2017-099 | Central | 03 - Spearville | 523309 | MOORE_CNTY 6 | 230 | 6.8181 | 6.8187 | 8.8001e-05
GEN-2017-099 | Central | 03 - Spearville | 523174 | GOODWELLWND3 | 115 | 6.6028 | 6.6033 | 7.5725e-05
GEN-2017-099 | Central | 03 - Spearville | 523959 | POTTER_CO 6 | 230 | 20.0739 | 20.0753 | 6.9742e-05
GEN-2017-099 | Central | 03 - Spearville | 524296 | SPNSPUR_WND7 | 345 | 4.5322 | 4.5325 | 6.6193e-05
GEN-2017-099 | Central | 03 - Spearville | 524909 | ROSEVELT_N 6 | 230 | 9.3752 | 9.3752 | 0
GEN-2017-099 | Central | 03 - Spearville | 599955 | PNM-DC6 | 230 | 9.3752 | 9.3752 | 0
GEN-2017-099 | Central | 03 - Spearville | 599951 | LAMAR 6 | 345 | 57.859 | 57.859 | 0
GEN-2017-099 | Central | 03 - Spearville | 599960 | EPTNP-D6 | 230 | 7.7768 | 7.7768 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 510907 | PITTSB-7 | 345 | 14.43 | 14.44 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511422 | FLETCHR4 | 138 | 8.32 | 8.34 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511423 | FLE TAP4 | 138 | 9.13 | 9.15 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511428 | LG-YEAR4 | 138 | 12.2 | 12.25 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511431 | LWS S4 | 138 | 11.35 | 11.4 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511436 | COMANC-2 | 69 | 10.11 | 10.13 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511437 | COMANC-4 | 138 | 18.69 | 18.79 | 0.1
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511439 | LWSTAP 4 | 138 | 11.84 | 11.89 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511451 | CYRIL--2 | 69 | 4.77 | 4.78 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511453 | DUNCAN-4 | 138 | 6.68 | 6.69 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511456 | O.K.U.-7 | 345 | 5.56 | 6 | 0.44
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511461 | FT.SILL2 | 69 | 6.1 | 6.12 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511466 | L.E.S.-2 | 69 | 17.11 | 17.17 | 0.06
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511467 | L.E.S.-4 | 138 | 25.39 | 25.58 | 0.19
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511468 | L.E.S.-7 | 345 | 13.53 | 13.76 | 0.23
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511469 | LGORE-N2 | 69 | 8.24 | 8.26 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511470 | LGORE-S2 | 69 | 7.15 | 7.17 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511471 | LWS-NTP4 | 138 | 11.97 | 12.02 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511473 | PO.HILL2 | 69 | 5.97 | 5.99 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511474 | SHERID4 | 138 | 12.65 | 12.7 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511477 | S.W.S.-4 | 138 | 36.36 | 36.4 | 0.04
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511486 | ELGINJT4 | 138 | 10.32 | 10.35 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511487 | ELGINJT2 | 69 | 8.74 | 8.76 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511488 | 112GORE4 | 138 | 13 | 13.06 | 0.06
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511494 | COMMTAP4 | 138 | 22.2 | 22.35 | 0.15
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511503 | LAW WC2 | 69 | 4.67 | 4.68 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511509 | 53CACHE4 | 138 | 12 | 12.06 | 0.06
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511510 | LAIRGST4 | 138 | 12.59 | 12.64 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511512 | RPPAPER4 | 138 | 12.26 | 12.31 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511524 | L-DISTP2 | 69 | 9.34 | 9.36 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511537 | ARTVLTP4 | 138 | 12.02 | 12.08 | 0.06
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511538 | ARTVILL4 | 138 | 8.71 | 8.74 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511553 | CHISHOLM7 | 345 | 5.81 | 5.82 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511563 | ELSWORTH 4 | 138 | 10.24 | 10.27 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511565 | OKLAUN HVDC7 | 345 | 5.54 | 5.98 | 0.44
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511568 | TERRYRD7 | 345 | 10.19 | 10.27 | 0.08
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 511571 | RUSHSPR7 | 345 | 6.53 | 6.57 | 0.04
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 514785 | WOODWRD4 | 138 | 13.28 | 13.28 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 514796 | IODINE-4 | 138 | 7.48 | 7.48 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 514801 | MINCO 7 | 345 | 18.52 | 18.55 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 514808 | JOHNCO 4 | 138 | 15.44 | 15.46 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 514809 | JOHNCO 7 | 345 | 10.14 | 10.15 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 514901 | CIMARON7 | 345 | 35.49 | 35.51 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515045 | SEMINOL7 | 345 | 33.65 | 33.68 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515135 | SUNNYSD4 | 138 | 18.99 | 19.02 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515136 | SUNNYSD7 | 345 | 11.36 | 11.39 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515137 | UNIROY 4 | 138 | 12.74 | 12.76 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515144 | LONEGRV4 | 138 | 13.7 | 13.72 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515164 | ROCKYPT4 | 138 | 10.63 | 10.64 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515375 | WWRDEHV7 | 345 | 20.17 | 20.17 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515376 | WWRDEHV4 | 138 | 24.55 | 24.55 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515394 | KEENAN 4 | 138 | 9.05 | 9.05 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515398 | OUSPRT 4 | 138 | 9.63 | 9.63 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515407 | TATONGA7 | 345 | 16.97 | 16.98 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515425 | WWDPST 4 | 138 | 17.79 | 17.79 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515444 | MCNOWND7 | 345 | 18.46 | 18.49 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515448 | CRSRDSW7 | 345 | 11.91 | 11.91 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515458 | BORDER 7 | 345 | 4.71 | 4.71 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515497 | MATHWSN7 | 345 | 33.94 | 33.96 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515549 | MNCWND37 | 345 | 12.66 | 12.68 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515561 | CARTRCO4 | 138 | 9.91 | 9.92 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515582 | SLNGWND7 | 345 | 7.45 | 7.45 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515585 | MAMTHPW7 | 345 | 13.48 | 13.48 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515599 | G07621119-20 | 345 | 13.41 | 13.42 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515677 | BADGER 7 | 345 | 14.39 | 14.39 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515800 | GRACMNT7 | 345 | 17.51 | 17.58 | 0.07
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515802 | GRACMNT4 | 138 | 30.3 | 30.35 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515852 | DGRASSE7 | 345 | 14.79 | 14.79 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 515853 | DGRASSE4 | 138 | 15.6 | 15.6 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 520814 | ANADARK4 | 138 | 32.75 | 32.78 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 521089 | WASHITA4 | 138 | 31.11 | 31.15 | 0.04
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 521157 | HUGO 7 | 345 | 11.54 | 11.54 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 522823 | LP-MCDONALD6 | 230 | 14.32 | 14.33 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 522870 | LP-HOLLY 6 | 230 | 16.99 | 17 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 524415 | AMA_SOUTH 6 | 230 | 13.83 | 13.83 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 524909 | ROSEVELT_N 6 | 230 | 10.67 | 10.67 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525212 | SWISHER 3 | 115 | 12.63 | 12.64 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525213 | SWISHER 6 | 230 | 11.31 | 11.31 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525454 | HALE_CNTY 3 | 115 | 11.08 | 11.09 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525461 | NEWHART 6 | 230 | 11.87 | 11.87 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525481 | PLANT_X 6 | 230 | 24.21 | 24.21 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525524 | TOLK_EAST 6 | 230 | 31.3 | 31.31 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525543 | TOLK_TAP 6 | 230 | 31.3 | 31.31 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525549 | TOLK 7 | 345 | 12.96 | 12.96 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525780 | FLOYD_CNTY 3 | 115 | 6.87 | 6.88 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525816 | TUCO_INT2 2 | 69 | 4.97 | 4.98 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525826 | TUCO_INT 2 | 69 | 8.45 | 8.45 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525828 | TUCO_INT 3 | 115 | 21.91 | 21.93 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525830 | TUCO_INT 6 | 230 | 28.97 | 29.02 | 0.05
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525832 | TUCO_INT 7 | 345 | 23.61 | 23.68 | 0.07
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525840 | ANTELOPE_1 6 | 230 | 28.67 | 28.71 | 0.04
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 525850 | ELK_CT1 | 345 | 23.22 | 23.29 | 0.07
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526013 | DEAN_INTG 6 | 230 | 8.72 | 8.73 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526076 | STANTON_W 3 | 115 | 9.7 | 9.7 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526160 | CARLISLE 3 | 115 | 14.09 | 14.1 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526161 | CARLISLE 6 | 230 | 14.7 | 14.71 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526269 | LUBBCK_STH 6 | 230 | 19.21 | 19.22 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526298 | LUBBCK_EST 3 | 115 | 16.19 | 16.2 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526299 | LUBBCK_EST 6 | 230 | 13.84 | 13.85 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526337 | JONES 6 | 230 | 21.13 | 21.14 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526460 | AMOCO_SS 6 | 230 | 10.37 | 10.37 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526525 | WOLFFORTH 6 | 230 | 14.34 | 14.34 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526677 | GRASSLAND 6 | 230 | 6.83 | 6.83 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526934 | YOAKUM 3 | 115 | 17.41 | 17.42 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526935 | YOAKUM 6 | 230 | 18.56 | 18.57 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 526936 | YOAKUM_345 | 345 | 9.69 | 9.7 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527009 | BRU_SUB 6 | 230 | 14.65 | 14.65 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527028 | INK_BASIN 6 | 230 | 11.13 | 11.13 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527149 | MUSTANG 6 | 230 | 16.15 | 16.15 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527655 | RSVLT_CC_E 7 | 345 | 13.93 | 13.94 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527656 | CROSSROADS 7 | 345 | 17.56 | 17.58 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527802 | EDDY_CNTY 7 | 345 | 7.71 | 7.72 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527894 | HOBBS_INT 6 | 230 | 17.05 | 17.06 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527896 | HOBBS_INT 7 | 345 | 9.33 | 9.34 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 527965 | KIOWA 7 | 345 | 8.15 | 8.16 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 529304 | OMDUNCN4 | 138 | 6.9 | 6.91 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 539801 | THISTLE7 | 345 | 16.68 | 16.68 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560022 | CRAWFISH_DR | 345 | 23.86 | 23.94 | 0.08
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560071 | G16-003-TAP | 345 | 15.51 | 15.51 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560078 | G16-037-TAP | 345 | 7.63 | 7.64 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560088 | G16-063-TAP | 345 | 8.06 | 8.07 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560100 | CRAWFISH765 | 765 | 11.14 | 11.17 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560101 | SEMINOLE765 | 765 | 11.92 | 11.93 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560102 | CROSSRDS765 | 765 | 8 | 8.01 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 560104 | CDSEMMID | 765 | 9.39 | 9.4 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 563259 | GEN-2015-092 | 345 | 6.34 | 6.37 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 563269 | GEN-2015-093 | 345 | 10.03 | 10.06 | 0.03
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 583340 | GEN-2012-020 | 230 | 11.69 | 11.7 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 584780 | GEN-2015-036 | 345 | 7.2 | 7.21 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 585410 | GREAT_WESTRN | 345 | 10.1 | 10.1 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 585430 | PRSIMN_CRK1 | 345 | 11.8 | 11.8 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587020 | GEN-2016-003 | 345 | 15.51 | 15.51 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587230 | GEN-2016-037 | 345 | 6.95 | 6.96 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587430 | GEN-2016-063 | 345 | 7.96 | 7.97 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587740 | GEN-2016-091 | 345 | 13.4 | 13.48 | 0.08
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587744 | G16-091-TAP | 345 | 15.1 | 15.19 | 0.09
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587770 | GEN-2016-095 | 345 | 11.1 | 11.16 | 0.06
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587790 | GEN-2016-097 | 138 | 9.83 | 9.84 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 587794 | G16-097-TAP | 138 | 12.05 | 12.06 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 588000 | GEN-2016-123 | 345 | 16.89 | 16.91 | 0.02
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 588560 | GEN-2017-011 | 345 | 12.48 | 12.48 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 588760 | GEN-2017-033 | 345 | 3.94 | 4.39 | 0.45
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 588970 | GEN-2017-059 | 230 | 10 | 10.01 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 589030 | GEN-2017-065 | 345 | 5.11 | 5.48 | 0.37
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 589130 | GEN-2017-075 | 345 | 8.05 | 8.06 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 589160 | GEN-2017-078 | 345 | 10.87 | 10.88 | 0.01
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 590001 | OKLEHV24 | 138 | 5.17 | 5.17 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 590003 | OKLEHV14 | 138 | 5.18 | 5.18 | 0
GEN-2017-033 | South | 06 - South Texas Panhandle/New Mexico | 599891 | OKLAUN 7 | 345 | 4.36 | 4.36 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511421 | VERDEN 4 | 138 | 10.28 | 10.29 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511423 | FLE TAP4 | 138 | 9.22 | 9.23 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511425 | TUTCONT4 | 138 | 10.55 | 10.55 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511437 | COMANC-4 | 138 | 18.75 | 18.8 | 0.05
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511439 | LWSTAP 4 | 138 | 11.95 | 11.98 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511445 | CARNEG-4 | 138 | 8.2 | 8.2 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511446 | CL-AFTP4 | 138 | 6.65 | 6.68 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511456 | O.K.U.-7 | 345 | 5.63 | 5.64 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511458 | ELKCTY-4 | 138 | 10.93 | 11.06 | 0.13
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511459 | ELKCTY-2 | 69 | 7.19 | 7.21 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511466 | L.E.S.-2 | 69 | 17.2 | 17.21 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511467 | L.E.S.-4 | 138 | 25.48 | 25.59 | 0.11
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511468 | L.E.S.-7 | 345 | 13.54 | 13.66 | 0.12
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511474 | SHERID4 | 138 | 12.73 | 12.76 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511476 | S.W.S.-2 | 69 | 4.38 | 4.38 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511477 | S.W.S.-4 | 138 | 36.79 | 36.92 | 0.13
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511483 | NORGE--4 | 138 | 11.82 | 11.83 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511485 | CLINTJC4 | 138 | 6.34 | 6.36 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511486 | ELGINJT4 | 138 | 10.4 | 10.41 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511490 | ELKCITY6 | 230 | 6.53 | 6.66 | 0.13
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511494 | COMMTAP4 | 138 | 22.28 | 22.36 | 0.08
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511511 | FALCNRD4 | 138 | 7.83 | 7.89 | 0.06
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511541 | SWEETWT6 | 230 | 7.9 | 8.14 | 0.24
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511542 | BUFFCK6 | 230 | 6.05 | 6.18 | 0.13
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511544 | DEMPSEY6 | 230 | 5.27 | 5.35 | 0.08
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511547 | ROARK6 | 230 | 4.88 | 4.95 | 0.07
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511553 | CHISHOLM7 | 345 | 5.49 | 5.94 | 0.45
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511557 | CHISHOLM6 | 230 | 8.56 | 8.97 | 0.41
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511563 | ELSWORTH 4 | 138 | 10.33 | 10.34 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511565 | OKLAUN HVDC7 | 345 | 5.61 | 5.62 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511568 | TERRYRD7 | 345 | 10.16 | 10.19 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 511571 | RUSHSPR7 | 345 | 6.5 | 6.52 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514801 | MINCO 7 | 345 | 18.29 | 18.54 | 0.25
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514819 | EL-RENO4 | 138 | 15.77 | 15.78 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514820 | JENSENT4 | 138 | 15.67 | 15.68 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514863 | HAYMAKR4 | 138 | 26.84 | 26.85 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514879 | NORTWST4 | 138 | 45.02 | 45.04 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514880 | NORTWST7 | 345 | 33.37 | 33.43 | 0.06
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514881 | SPRNGCK7 | 345 | 24.08 | 24.1 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514894 | CZECHAL4 | 138 | 28.4 | 28.41 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514895 | SARA 4 | 138 | 19.09 | 19.1 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514898 | CIMARON4 | 138 | 44.07 | 44.12 | 0.05
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514901 | CIMARON7 | 345 | 34.91 | 35.04 | 0.13
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514908 | ARCADIA7 | 345 | 30.93 | 30.94 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514933 | DRAPER 4 | 138 | 40.11 | 40.13 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 514934 | DRAPER 7 | 345 | 21.39 | 21.4 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515045 | SEMINOL7 | 345 | 27.13 | 27.14 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515136 | SUNNYSD7 | 345 | 11.25 | 11.26 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515407 | TATONGA7 | 345 | 16.81 | 16.81 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515444 | MCNOWND7 | 345 | 18.24 | 18.48 | 0.24
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515497 | MATHWSN7 | 345 | 33.51 | 33.58 | 0.07
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515549 | MNCWND37 | 345 | 12.58 | 12.68 | 0.1
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515600 | KNGFSHR7 | 345 | 12 | 12.01 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515605 | CANADN7 | 345 | 13.07 | 13.08 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515610 | FSHRTAP7 | 345 | 17.88 | 17.91 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515800 | GRACMNT7 | 345 | 17.02 | 17.68 | 0.66
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515802 | GRACMNT4 | 138 | 30.52 | 30.71 | 0.19
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515875 | REDNGTN7 | 345 | 18.2 | 18.21 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 515939 | MNCWND47 | 345 | 6.89 | 6.92 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520422 | SEQUOYAHJ4 | 138 | 24.62 | 24.66 | 0.04
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520440 | HARPER2 | 69 | 18.71 | 18.72 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520508 | CLVJCTN2 | 69 | 5.05 | 5.05 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520509 | CLVJCTS2 | 69 | 4.64 | 4.64 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520512 | BC SW 4 | 138 | 7.94 | 7.94 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520513 | BCV SW 4 | 138 | 6.12 | 6.12 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520514 | BCVI_HVB | 138 | 8.85 | 8.85 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520810 | ANADARK2 | 69 | 20.24 | 20.25 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520814 | ANADARK4 | 138 | 33.13 | 33.23 | 0.1
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520827 | BINGERJ4 | 138 | 8.11 | 8.12 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520838 | CADDO 2 | 69 | 14.01 | 14.02 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520867 | CORN TP4 | 138 | 14.57 | 14.58 | 0.01
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520912 | FLETCH-4 | 138 | 7.35 | 7.35 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 520923 | GEORGIA4 | 138 | 18.07 | 18.1 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521017 | ONEY 4 | 138 | 11.44 | 11.46 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521024 | PARADSE4 | 138 | 6.25 | 6.25 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521027 | PINERDG2 | 69 | 5.01 | 5.01 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521031 | POCASET4 | 138 | 7.91 | 7.91 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521072 | TUTLETP4 | 138 | 6.78 | 6.78 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521088 | WASHITA2 | 69 | 9.76 | 9.76 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521089 | WASHITA4 | 138 | 31.46 | 31.59 | 0.13
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521103 | SLKHILLS 4 | 138 | 8.88 | 8.88 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521116 | REDHLSW4 | 138 | 7.32 | 7.36 | 0.04
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 521129 | CHERRYRD 4 | 138 | 6.63 | 6.63 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 523771 | GRAPEVINE 6 | 230 | 5.77 | 5.8 | 0.03
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 523776 | WHEELER 3 | 115 | 6.58 | 6.62 | 0.04
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 523777 | WHEELER 6 | 230 | 5.98 | 6.06 | 0.08
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 525832 | TUCO_INT 7 | 345 | 12.33 | 12.33 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 560078 | G16-037-TAP | 345 | 6.52 | 7.76 | 1.24
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 563269 | GEN-2015-093 | 345 | 9.92 | 10.12 | 0.2
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 584060 | GEN-2015-057 | 345 | 9.24 | 9.29 | 0.05
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 587230 | GEN-2016-037 | 345 | 5.81 | 7.07 | 1.26
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 587740 | GEN-2016-091 | 345 | 13.28 | 13.56 | 0.28
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 587744 | G16-091-TAP | 345 | 14.9 | 15.26 | 0.36
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 587770 | GEN-2016-095 | 345 | 11.03 | 11.22 | 0.19
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 587794 | G16-097-TAP | 138 | 12.2 | 12.22 | 0.02
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 588760 | GEN-2017-033 | 345 | 4.13 | 4.13 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 589030 | GEN-2017-065 | 345 | 5.15 | 5.15 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 599891 | OKLAUN 7 | 345 | 4.36 | 4.36 | 0
GEN-2016-037 | South | 07 - Southwestern Oklahoma | 900001 | TRAVERSE1 | 345 | 7.38 | 7.38 | 0
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511428 | LG-YEAR4 | 138 | 12.28 | 12.37 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511429 | L AIRGS4 | 138 | 11.86 | 11.95 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511430 | LWS N4 | 138 | 10.73 | 10.79 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511432 | R-AMOCO2 | 69 | 3.88 | 3.94 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511435 | SNYDER-4 | 138 | 6.9 | 7.12 | 0.22
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511437 | COMANC-4 | 138 | 18.74 | 18.8 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511438 | DUKE---2 | 69 | 3.49 | 3.56 | 0.07
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511439 | LWSTAP 4 | 138 | 11.9 | 11.98 | 0.08
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511440 | ALTUSJT4 | 138 | 5 | 5.12 | 0.12
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511441 | ALTUSJT2 | 69 | 5.73 | 5.87 | 0.14
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511444 | ROSVTAP2 | 69 | 4.1 | 4.16 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511460 | FREDJC-2 | 69 | 2.89 | 2.98 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511462 | HEADRIK2 | 69 | 4.67 | 4.79 | 0.12
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511465 | HOBART-2 | 69 | 5.75 | 5.81 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511467 | L.E.S.-4 | 138 | 25.51 | 25.59 | 0.08
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511471 | LWS-NTP4 | 138 | 12.02 | 12.1 | 0.08
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511472 | TIPTE T2 | 69 | 3.78 | 3.89 | 0.11
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511475 | SNYDER-2 | 69 | 7.7 | 7.92 | 0.22
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511479 | TIPTCTY2 | 69 | 2.44 | 2.51 | 0.07
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511488 | 112GORE4 | 138 | 13.09 | 13.18 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511494 | COMMTAP4 | 138 | 22.29 | 22.36 | 0.07
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511495 | TOMSTEED2 | 69 | 4.33 | 4.42 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511500 | CACHE4 | 138 | 8.58 | 8.7 | 0.12
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511509 | 53CACHE4 | 138 | 12.06 | 12.13 | 0.07
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511510 | LAIRGST4 | 138 | 12.67 | 12.77 | 0.1
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511512 | RPPAPER4 | 138 | 12.33 | 12.42 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511520 | DAV TAP2 | 69 | 2.3 | 2.35 | 0.05
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511543 | TIPTN T2 | 69 | 4.66 | 4.79 | 0.13
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 511545 | TIPTON 2 | 69 | 2.6 | 2.67 | 0.07
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 512101 | CHILD4WT | 138 | 1.74 | 1.77 | 0.03
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 512110 | LAKEP4WT | 138 | 2.24 | 2.29 | 0.05
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 512111 | LAKEP2WT | 69 | 3.23 | 3.29 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520404 | MDCPRK4 | 138 | 5.81 | 5.87 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520410 | CACHE4 | 138 | 5 | 5.1 | 0.1
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520491 | NAVAJO 2 | 69 | 2.33 | 2.38 | 0.05
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520528 | ROSEVLT2 | 69 | 3.98 | 4.07 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520534 | DUKE 2 | 69 | 4.28 | 4.37 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520803 | ALTUS_ 2 | 69 | 3.49 | 3.58 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520805 | ALTUSSW2 | 69 | 3.52 | 3.61 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520914 | FREDRIK2 | 69 | 3.65 | 3.73 | 0.08
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 520954 | INDHOMA4 | 138 | 4.37 | 4.45 | 0.08
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521009 | NAVJOTP2 | 69 | 3.61 | 3.7 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521024 | PARADSE4 | 138 | 6.2 | 6.25 | 0.05
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521042 | RUSSELL2 | 69 | 4.28 | 4.37 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521043 | RUSSELL4 | 138 | 3.74 | 3.83 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521051 | SNYDER 2 | 69 | 7.08 | 7.29 | 0.21
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521052 | SNYDER 4 | 138 | 6.42 | 6.62 | 0.2
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521069 | TIPTON-2 | 69 | 1.5 | 1.54 | 0.04
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521070 | TIPTONJ2 | 69 | 4.13 | 4.23 | 0.1
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521081 | VERNON 2 | 69 | 2.48 | 2.54 | 0.06
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 521190 | CACHEJ4 | 138 | 5.4 | 5.51 | 0.11
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 529298 | OMPVET-4 | 138 | 4.65 | 4.75 | 0.1
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 529302 | OMALTUS4 | 138 | 4.56 | 4.65 | 0.09
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 529345 | OMPARK-4 | 138 | 4.82 | 4.93 | 0.11
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 584550 | GEN-2015-013 | 138 | 6.41 | 6.6 | 0.19
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 588780 | GEN-2017-036 | 138 | 6.65 | 6.87 | 0.22
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 588904 | G17-051-TAP | 69 | 3.2 | 3.25 | 0.05
GEN-2017-036 | South | 07 - Southwestern Oklahoma | 999600 | TAP_G17-036 | 138 | 6.86 | 7.09 | 0.23
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 588500 | GEN-2017-005 | 161 | 6.1239 | 6.7684 | 0.10524
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 588504 | G17-005-TAP | 161 | 6.2091 | 6.8529 | 0.10369
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 588540 | GEN-2017-009 | 345 | 9.9978 | 10.5633 | 0.056562
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 588544 | G17-009-TAP | 345 | 10.8451 | 11.4101 | 0.052097
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 532934 | MARMTNE5 | 161 | 8.0271 | 8.3996 | 0.046405
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 532935 | MARMTNW5 | 161 | 8.0271 | 8.3996 | 0.046405
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 532938 | FRANKLIN5 | 161 | 7.3574 | 7.6097 | 0.034292
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 532793 | NEOSHO 7 | 345 | 16.4472 | 16.8864 | 0.026704
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 532932 | LITCH 5 | 161 | 8.4404 | 8.6426 | 0.023956
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543650 | DAKOTA_5 | 161 | 7.5109 | 7.6868 | 0.023419
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543651 | PRQN_WIND5 | 161 | 6.4747 | 6.5832 | 0.016758
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547476 | ASB349 5 | 161 | 10.2736 | 10.4272 | 0.014951
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533876 | FRANKLIN2 | 69 | 10.8139 | 10.9702 | 0.014454
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533765 | LITCH N2 | 69 | 12.258 | 12.4335 | 0.014317
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533766 | LITCH S2 | 69 | 12.258 | 12.4335 | 0.014317
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533639 | MARMATN2 | 69 | 8.3602 | 8.4769 | 0.013959
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 532937 | NEOSHO 5 | 161 | 21.0898 | 21.3739 | 0.013471
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533769 | PITNAC 2 | 69 | 10.791 | 10.9282 | 0.012714
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533020 | NEOSHOS4 | 138 | 22.8316 | 23.1093 | 0.012163
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533021 | NEOSHO 4 | 138 | 22.8316 | 23.1093 | 0.012163
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533022 | NEOSHON4 | 138 | 22.8316 | 23.1093 | 0.012163
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533647 | UN1ELSM2 | 69 | 7.4596 | 7.5451 | 0.011462
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533771 | ROUSE 2 | 69 | 9.1923 | 9.2932 | 0.010977
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533759 | DEPAUL 2 | 69 | 9.0629 | 9.1617 | 0.010902
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533775 | FRONTEN2 | 69 | 8.3303 | 8.4155 | 0.010228
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533767 | MULBERY2 | 69 | 7.9288 | 8.0076 | 0.0099385
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533770 | PITTSBG2 | 69 | 8.2594 | 8.3412 | 0.0099039
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 589200 | GEN-2017-082 | 161 | 7.1442 | 7.2138 | 0.0097422
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533764 | HUDSJCT2 | 69 | 7.8793 | 7.9533 | 0.0093917
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533756 | AQUARS 2 | 69 | 7.837 | 7.9101 | 0.0093275
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543065 | CNTRVIL5 | 161 | 6.1989 | 6.2554 | 0.0091145
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 300739 | 7BLACKBERRY | 345 | 14.7665 | 14.8807 | 0.0077337
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533763 | HUDSON-2 | 69 | 6.2651 | 6.312 | 0.0074859
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547491 | PUR421 5 | 161 | 9.0186 | 9.0825 | 0.0070854
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547477 | CJ 366 5 | 161 | 11.7457 | 11.8216 | 0.0064619
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533640 | MCKEE 2 | 69 | 4.1424 | 4.1691 | 0.0064455
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533778 | NEOSHOS2 | 69 | 22.2897 | 22.4333 | 0.0064424
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533762 | GIR JCT2 | 69 | 6.3031 | 6.3413 | 0.0060605
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533774 | SHEFFLD2 | 69 | 4.4112 | 4.4364 | 0.0057127
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 510380 | DELWARE7 | 345 | 10.9307 | 10.9927 | 0.0056721
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547490 | FIR417 5 | 161 | 13.5186 | 13.595 | 0.0056515
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533645 | SE9HIAT2 | 69 | 3.7003 | 3.7211 | 0.0056212
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533654 | ZILAJCT2 | 69 | 5.6188 | 5.6478 | 0.0051612
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547467 | ORO110 5 | 161 | 18.3996 | 18.4918 | 0.005011
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533635 | FTSCOTT2 | 69 | 3.4075 | 3.4241 | 0.0048716
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533652 | WARE 2 | 69 | 3.4346 | 3.4512 | 0.0048332
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547485 | CAR395 5 | 161 | 11.5223 | 11.576 | 0.0046605
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533761 | GIRARD 2 | 69 | 4.4111 | 4.4296 | 0.004194
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533650 | UN8HUMB2 | 69 | 4.0623 | 4.0775 | 0.0037417
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547469 | RIV4525 | 161 | 23.1554 | 23.2407 | 0.0036838
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547503 | RIV452T 5 | 161 | 22.7618 | 22.8433 | 0.0035806
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547502 | RIV167 5 | 161 | 21.5053 | 21.578 | 0.0033806
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547501 | RIV453 5 | 161 | 21.9817 | 22.056 | 0.0033801
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 532926 | BAKER 2 | 69 | 4.8595 | 4.8748 | 0.0031485
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547498 | STL439 5 | 161 | 23.7884 | 23.8627 | 0.0031234
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533772 | SE1GREE2 | 69 | 5.9484 | 5.9667 | 0.0030765
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533758 | CRAWFOR2 | 69 | 7.108 | 7.129 | 0.0029544
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547459 | WWR477 | 161 | 21.7196 | 21.7815 | 0.00285
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543069 | PAOLA 5 | 161 | 10.4536 | 10.4773 | 0.0022672
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543112 | OSAWAT 5 | 161 | 10.3659 | 10.3892 | 0.0022478
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547487 | HOC404 5 | 161 | 12.8473 | 12.8753 | 0.0021794
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 533008 | TV1MNDV4 | 138 | 6.9074 | 6.9223 | 0.0021571
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543067 | CENTENL5 | 161 | 10.3128 | 10.3315 | 0.0018133
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 542981 | LACYGNE7 | 345 | 24.761 | 24.8029 | 0.0016922
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543629 | LACYGNE11_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543632 | LACYGNE22_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547541 | RIV167 2 | 69 | 18.4455 | 18.47 | 0.0013282
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543066 | S.OTTWA5 | 161 | 7.6022 | 7.6068 | 0.00060509
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 547690 | GLF339 2 | 69 | 9.0983 | 9.1038 | 0.00060451
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543659 | LACYGNE2 | 69 | 8.4733 | 8.4743 | 0.00011802
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543667 | LAC3_STAR7 | 345 | 0.6403 | 0.6403 | 0
GEN-2017-005 | Central | 08 - North Oklahoma/South Central Kansas | 543669 | LAC8_STAR7 | 345 | 0.6133 | 0.6133 | 0
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588500 | GEN-2017-005 | 161 | 6.1239 | 6.7684 | 0.10524
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588504 | G17-005-TAP | 161 | 6.2091 | 6.8529 | 0.10369
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588540 | GEN-2017-009 | 345 | 9.9978 | 10.5633 | 0.056562
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588544 | G17-009-TAP | 345 | 10.8451 | 11.4101 | 0.052097
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532934 | MARMTNE5 | 161 | 8.0271 | 8.3996 | 0.046405
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532935 | MARMTNW5 | 161 | 8.0271 | 8.3996 | 0.046405
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532793 | NEOSHO 7 | 345 | 16.4472 | 16.8864 | 0.026704
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543650 | DAKOTA_5 | 161 | 7.5109 | 7.6868 | 0.023419
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543651 | PRQN_WIND5 | 161 | 6.4747 | 6.5832 | 0.016758
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512656 | GRDA1 5 | 161 | 41.696 | 42.3541 | 0.015783
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533766 | LITCH S2 | 69 | 12.258 | 12.4335 | 0.014317
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533639 | MARMATN2 | 69 | 8.3602 | 8.4769 | 0.013959
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532937 | NEOSHO 5 | 161 | 21.0898 | 21.3739 | 0.013471
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533020 | NEOSHOS4 | 138 | 22.8316 | 23.1093 | 0.012163
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533021 | NEOSHO 4 | 138 | 22.8316 | 23.1093 | 0.012163
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533022 | NEOSHON4 | 138 | 22.8316 | 23.1093 | 0.012163
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533647 | UN1ELSM2 | 69 | 7.4596 | 7.5451 | 0.011462
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532780 | CANEYRV7 | 345 | 9.847 | 9.9559 | 0.011059
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532781 | CANEYWF7 | 345 | 9.5894 | 9.692 | 0.010699
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532796 | WICHITA7 | 345 | 24.1532 | 24.3835 | 0.009535
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532800 | LATHAMS7 | 345 | 10.4136 | 10.5083 | 0.0090939
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532801 | ELKRVR17 | 345 | 9.1912 | 9.2645 | 0.007975
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 589060 | GEN-2017-068 | 345 | 20.1103 | 20.2698 | 0.0079313
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300739 | 7BLACKBERRY | 345 | 14.7665 | 14.8807 | 0.0077337
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533640 | MCKEE 2 | 69 | 4.1424 | 4.1691 | 0.0064455
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533768 | NEOSHON2 | 69 | 22.2897 | 22.4333 | 0.0064424
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533778 | NEOSHOS2 | 69 | 22.2897 | 22.4333 | 0.0064424
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512650 | GRDA1 7 | 345 | 25.9865 | 26.1539 | 0.0064418
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512865 | GREC TAP5 | 345 | 24.9005 | 25.0478 | 0.0059155
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532794 | ROSEHIL7 | 345 | 18.9572 | 19.0665 | 0.0057656
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300740 | 7SPORTSMAN | 345 | 23.6136 | 23.749 | 0.005734
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 510380 | DELWARE7 | 345 | 10.9307 | 10.9927 | 0.0056721
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547490 | FIR417 5 | 161 | 13.5186 | 13.595 | 0.0056515
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532791 | BENTON 7 | 345 | 19.6359 | 19.7468 | 0.0056478
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533005 | NEPARSN4 | 138 | 11.9276 | 11.9931 | 0.0054915
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547467 | ORO110 5 | 161 | 18.3996 | 18.4918 | 0.005011
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547494 | OAK432 5 | 161 | 16.7249 | 16.8003 | 0.0045082
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300949 | 7JASPER | 345 | 12.0507 | 12.1045 | 0.0044645
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 301348 | 5CHOTEAU2 | 161 | 40.4609 | 40.6388 | 0.0043968
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300741 | 5SPORTSMAN | 161 | 38.9761 | 39.1423 | 0.0042642
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533062 | ROSEHIL4 | 138 | 30.8868 | 31.0133 | 0.0040956
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509745 | CLARKSV7 | 345 | 19.5998 | 19.6788 | 0.0040307
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533039 | ELPASO 4 | 138 | 24.1926 | 24.2863 | 0.0038731
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547469 | RIV4525 | 161 | 23.1554 | 23.2407 | 0.0036838
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547503 | RIV452T 5 | 161 | 22.7618 | 22.8433 | 0.0035806
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532986 | BENTON 4 | 138 | 27.8896 | 27.9879 | 0.0035246
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547502 | RIV167 5 | 161 | 21.5053 | 21.578 | 0.0033806
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547501 | RIV453 5 | 161 | 21.9817 | 22.056 | 0.0033801
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509782 | R.S.S.-7 | 345 | 28.8139 | 28.9088 | 0.0032935
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509807 | ONETA--7 | 345 | 26.6084 | 26.6954 | 0.0032696
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547470 | JOP145 5 | 161 | 16.9579 | 17.0133 | 0.0032669
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 510406 | N.E.S.-7 | 345 | 15.8275 | 15.8785 | 0.0032222
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509852 | T.NO.--7 | 345 | 22.5867 | 22.6594 | 0.0032187
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509836 | OEC 7 | 345 | 26.3545 | 26.4393 | 0.0032177
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532926 | BAKER 2 | 69 | 4.8595 | 4.8748 | 0.0031485
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547498 | STL439 5 | 161 | 23.7884 | 23.8627 | 0.0031234
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533772 | SE1GREE2 | 69 | 5.9484 | 5.9667 | 0.0030765
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509834 | COGENT 7 | 345 | 26.6803 | 26.7611 | 0.0030285
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532991 | WEAVER 4 | 138 | 21.7367 | 21.8021 | 0.0030087
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533758 | CRAWFOR2 | 69 | 7.108 | 7.129 | 0.0029544
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547459 | WWR477 | 161 | 21.7196 | 21.7815 | 0.00285
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533068 | STEARMN4 | 138 | 19.1751 | 19.2296 | 0.0028422
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509895 | T.NO.2-4 | 138 | 33.6374 | 33.7265 | 0.0026488
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509806 | ONETA--4 | 138 | 47.2399 | 47.3648 | 0.002644
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588664 | G17-022-TAP | 138 | 8.0166 | 8.0375 | 0.0026071
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547483 | JOP389 5 | 161 | 19.3374 | 19.3878 | 0.0026063
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588660 | GEN-2017-022 | 138 | 7.7289 | 7.7484 | 0.002523
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588320 | GEN-2016-162 | 345 | 9.7523 | 9.7768 | 0.0025122
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 509755 | WEKIWA-7 | 345 | 18.6818 | 18.7267 | 0.0024034
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533703 | ORDNJCT2 | 69 | 8.2682 | 8.2867 | 0.0022375
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512750 | TONECE7 | 345 | 14.5005 | 14.5329 | 0.0022344
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588330 | GEN-2016-163 | 345 | 8.6195 | 8.6384 | 0.0021927
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547487 | HOC404 5 | 161 | 12.8473 | 12.8753 | 0.0021794
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 560053 | G15-052T | 345 | 13.1034 | 13.1318 | 0.0021674
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533008 | TV1MNDV4 | 138 | 6.9074 | 6.9223 | 0.0021571
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 584900 | GEN-2015-052 | 345 | 13.0534 | 13.0815 | 0.0021527
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512631 | MIAMI 5 | 161 | 9.1774 | 9.196 | 0.0020267
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 510379 | DELWARE4 | 138 | 10.8834 | 10.905 | 0.0019847
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532797 | WOLFCRK7 | 345 | 18.0814 | 18.1154 | 0.0018804
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533003 | LIBERTY4 | 138 | 7.3341 | 7.3476 | 0.0018407
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300950 | 5JASPER | 161 | 12.2916 | 12.3134 | 0.0017736
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542981 | LACYGNE7 | 345 | 24.761 | 24.8029 | 0.0016922
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543629 | LACYGNE11_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543632 | LACYGNE22_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533702 | ORDNCE 2 | 69 | 5.9863 | 5.9958 | 0.001587
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532799 | WAVERLY7 | 345 | 16.0356 | 16.0608 | 0.0015715
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533696 | LABETTS2 | 69 | 6.0496 | 6.0591 | 0.0015704
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547534 | ORO110 2 | 69 | 17.4344 | 17.4606 | 0.0015028
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300045 | 7MORGAN | 345 | 12.7058 | 12.7243 | 0.001456
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547525 | JOP 59 2 | 69 | 18.9342 | 18.9602 | 0.0013732
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512694 | CLEVLND7 | 345 | 14.9069 | 14.9267 | 0.0013282
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547541 | RIV167 2 | 69 | 18.4455 | 18.47 | 0.0013282
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532802 | WAVERTX7 | 345 | 13.4196 | 13.437 | 0.0012966
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 510378 | SCOFCTY4 | 138 | 8.6339 | 8.6447 | 0.0012509
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533704 | PARSONS2 | 69 | 4.8191 | 4.8251 | 0.001245
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547555 | GAL278 2 | 69 | 15.7673 | 15.7857 | 0.001167
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 514825 | KAYWIND7 | 345 | 12.6052 | 12.6199 | 0.0011662
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 515621 | OPENSKY7 | 345 | 12.64 | 12.6547 | 0.001163
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547602 | RIV406 2 | 69 | 16.1759 | 16.1946 | 0.001156
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512734 | FARML 4 | 138 | 8.4258 | 8.4353 | 0.0011275
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533695 | LABETTE2 | 69 | 3.9998 | 4.004 | 0.0010501
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547486 | HOC404 4 | 138 | 6.4258 | 6.4319 | 0.0009493
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 549984 | BROOKLINE 7 | 345 | 11.278 | 11.2881 | 0.00089555
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300794 | 5LAMAR | 161 | 8.3936 | 8.4008 | 0.0008578
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300101 | 5MORGAN | 161 | 17.7718 | 17.7855 | 0.00077088
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547601 | HOC404 2 | 69 | 9.4214 | 9.4278 | 0.0006793
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542968 | STILWEL7 | 345 | 23.1239 | 23.1391 | 0.00065733
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547690 | GLF339 2 | 69 | 9.0983 | 9.1038 | 0.00060451
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543057 | BUCYRUS5 | 161 | 19.4621 | 19.4734 | 0.00058062
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542965 | W.GRDNR7 | 345 | 24.8262 | 24.8406 | 0.00058003
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542969 | STILWEL5 | 161 | 36.7533 | 36.773 | 0.00053601
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547530 | COL 94 2 | 69 | 6.3506 | 6.3532 | 0.00040941
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532768 | EMPEC 7 | 345 | 17.5987 | 17.6059 | 0.00040912
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 541198 | PECULR 7 | 345 | 18.8625 | 18.8701 | 0.00040292
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300042 | 7HUBEN | 345 | 9.9412 | 9.9451 | 0.00039231
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 512735 | COFCTY2 | 69 | 10.0966 | 10.1003 | 0.00036646
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533653 | WOLFCRK2 | 69 | 5.8582 | 5.8601 | 0.00032433
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542977 | CRAIG 7 | 345 | 21.4243 | 21.4312 | 0.00032206
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542966 | WGARDNR5 | 161 | 23.42 | 23.4273 | 0.0003117
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547411 | COL282 2 | 69 | 4.5155 | 4.5169 | 0.00031004
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 585100 | GEN-2015-073 | 345 | 13.3961 | 13.4002 | 0.00030606
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543077 | PLSTVAL5 | 161 | 14.6788 | 14.6832 | 0.00029975
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543105 | BULLCRK5 | 161 | 22.4616 | 22.4683 | 0.00029829
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547455 | SCM66T 2 | 69 | 4.3392 | 4.3404 | 0.00027655
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542978 | CRAIG 5 | 161 | 38.4477 | 38.4581 | 0.0002705
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543053 | REDEL 5 | 161 | 22.9474 | 22.9535 | 0.00026583
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543050 | ANTIOCH5 | 161 | 21.2541 | 21.2597 | 0.00026348
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543058 | NLOUISB5 | 161 | 8.7738 | 8.7761 | 0.00026214
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 541200 | PHILL 7 | 345 | 17.2763 | 17.2807 | 0.00025468
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532775 | 87TH 7 | 345 | 20.0723 | 20.0774 | 0.00025408
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 533629 | CC2SHAR2 | 69 | 4.545 | 4.5461 | 0.00024202
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532774 | SWISVAL7 | 345 | 16.163 | 16.1669 | 0.00024129
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543132 | BNSF 5 | 161 | 18.2748 | 18.2791 | 0.0002353
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547412 | SEK225T2 | 69 | 3.4688 | 3.4696 | 0.00023063
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 541342 | PECULR 5 | 161 | 21.2998 | 21.3042 | 0.00020657
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543049 | CEDRCRK5 | 161 | 27.3304 | 27.336 | 0.0002049
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547413 | SEK225 2 | 69 | 3.423 | 3.4237 | 0.0002045
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 541341 | S.HARP 5 | 161 | 19.2739 | 19.2777 | 0.00019716
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543126 | LACKMAN5 | 161 | 12.9686 | 12.9708 | 0.00016964
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 532856 | SWISVAL6 | 230 | 20.9983 | 21.0016 | 0.00015716
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547415 | SHR444 2 | 69 | 2.686 | 2.6864 | 0.00014892
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 542994 | HICKMAN5 | 161 | 18.3162 | 18.3189 | 0.00014741
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547409 | SCAM66 2 | 69 | 2.44 | 2.4403 | 0.00012295
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543054 | CEDARNL5 | 161 | 8.9661 | 8.9672 | 0.00012268
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543659 | LACYGNE2 | 69 | 8.4733 | 8.4743 | 0.00011802
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 547414 | SMN425 2 | 69 | 1.946 | 1.9462 | 0.00010277
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 300071 | 5CLINTN | 161 | 11.477 | 11.478 | 8.7131e-05
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588310 | GEN-2016-158 | 345 | 4.6245 | 4.6249 | 8.6496e-05
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 588300 | GEN-2016-157 | 345 | 4.8983 | 4.8987 | 8.1661e-05
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543667 | LAC3_STAR7 | 345 | 0.6403 | 0.6403 | 0
GEN-2017-009 | Central | 08 - North Oklahoma/South Central Kansas | 543669 | LAC8_STAR7 | 345 | 0.6133 | 0.6133 | 0
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 588540 | GEN-2017-009 | 345 | 9.9978 | 10.5633 | 0.056562
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 588544 | G17-009-TAP | 345 | 10.8451 | 11.4101 | 0.052097
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532935 | MARMTNW5 | 161 | 8.0271 | 8.3996 | 0.046405
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532793 | NEOSHO 7 | 345 | 16.4472 | 16.8864 | 0.026704
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532937 | NEOSHO 5 | 161 | 21.0898 | 21.3739 | 0.013471
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533020 | NEOSHOS4 | 138 | 22.8316 | 23.1093 | 0.012163
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533021 | NEOSHO 4 | 138 | 22.8316 | 23.1093 | 0.012163
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533022 | NEOSHON4 | 138 | 22.8316 | 23.1093 | 0.012163
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 300739 | 7BLACKBERRY | 345 | 14.7665 | 14.8807 | 0.0077337
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533768 | NEOSHON2 | 69 | 22.2897 | 22.4333 | 0.0064424
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533778 | NEOSHOS2 | 69 | 22.2897 | 22.4333 | 0.0064424
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 510380 | DELWARE7 | 345 | 10.9307 | 10.9927 | 0.0056721
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532791 | BENTON 7 | 345 | 19.6359 | 19.7468 | 0.0056478
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533005 | NEPARSN4 | 138 | 11.9276 | 11.9931 | 0.0054915
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 547469 | RIV4525 | 161 | 23.1554 | 23.2407 | 0.0036838
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 547503 | RIV452T 5 | 161 | 22.7618 | 22.8433 | 0.0035806
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532986 | BENTON 4 | 138 | 27.8896 | 27.9879 | 0.0035246
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 547502 | RIV167 5 | 161 | 21.5053 | 21.578 | 0.0033806
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 547501 | RIV453 5 | 161 | 21.9817 | 22.056 | 0.0033801
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532926 | BAKER 2 | 69 | 4.8595 | 4.8748 | 0.0031485
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532991 | WEAVER 4 | 138 | 21.7367 | 21.8021 | 0.0030087
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533758 | CRAWFOR2 | 69 | 7.108 | 7.129 | 0.0029544
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533052 | PARKCTY4 | 138 | 20.1019 | 20.1569 | 0.0027361
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533634 | ENA 2 | 69 | 5.2712 | 5.2854 | 0.0026939
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 588664 | G17-022-TAP | 138 | 8.0166 | 8.0375 | 0.0026071
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533001 | ALTOONA4 | 138 | 8.0292 | 8.0501 | 0.002603
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 588660 | GEN-2017-022 | 138 | 7.7289 | 7.7484 | 0.002523
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 588320 | GEN-2016-162 | 345 | 9.7523 | 9.7768 | 0.0025122
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533024 | 29TH 4 | 138 | 19.377 | 19.4255 | 0.002503
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533633 | COALCRK2 | 69 | 5.2439 | 5.2569 | 0.0024791
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532988 | BELAIRE4 | 138 | 18.7482 | 18.7936 | 0.0024216
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533703 | ORDNJCT2 | 69 | 8.2682 | 8.2867 | 0.0022375
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 588330 | GEN-2016-163 | 345 | 8.6195 | 8.6384 | 0.0021927
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533008 | TV1MNDV4 | 138 | 6.9074 | 6.9223 | 0.0021571
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533003 | LIBERTY4 | 138 | 7.3341 | 7.3476 | 0.0018407
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533646 | TIOGA 2 | 69 | 6.9097 | 6.9223 | 0.0018235
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533002 | DEARING4 | 138 | 9.2078 | 9.2238 | 0.0017377
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 542981 | LACYGNE7 | 345 | 24.761 | 24.8029 | 0.0016922
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532996 | TIOGA 4 | 138 | 4.3732 | 4.3806 | 0.0016921
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 543629 | LACYGNE11_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 543632 | LACYGNE22_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533702 | ORDNCE 2 | 69 | 5.9863 | 5.9958 | 0.001587
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533696 | LABETTS2 | 69 | 6.0496 | 6.0591 | 0.0015704
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533004 | MONTGOM4 | 138 | 6.7466 | 6.7571 | 0.0015563
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533006 | TAYLOR 4 | 138 | 6.5449 | 6.555 | 0.0015432
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533660 | ASHGRJ22 | 69 | 5.9685 | 5.9776 | 0.0015247
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 510422 | COFFEYT4 | 138 | 9.8765 | 9.8915 | 0.0015188
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533662 | CGENSUB2 | 69 | 5.8632 | 5.8719 | 0.0014838
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533658 | ASHGRV22 | 69 | 5.7386 | 5.747 | 0.0014638
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533666 | CHANTAP2 | 69 | 5.8503 | 5.8588 | 0.0014529
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533661 | CGENTAP2 | 69 | 5.5336 | 5.5414 | 0.0014096
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533659 | ASHGRJ12 | 69 | 5.4588 | 5.4663 | 0.0013739
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532990 | MIDIAN 4 | 138 | 10.5446 | 10.5589 | 0.0013561
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532993 | TALLGRS4 | 138 | 10.1282 | 10.1418 | 0.0013428
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532987 | BUTLER 4 | 138 | 10.362 | 10.3759 | 0.0013414
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 532989 | BUTLERS4 | 138 | 10.362 | 10.3759 | 0.0013414
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533657 | ASHGRV12 | 69 | 5.2652 | 5.2722 | 0.0013295
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533663 | CHANP1 2 | 69 | 5.1713 | 5.1781 | 0.0013149
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533664 | CHANP2 2 | 69 | 5.1713 | 5.1781 | 0.0013149
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533665 | CHANP3 2 | 69 | 5.1071 | 5.1137 | 0.0012923
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533649 | UN7ROSE2 | 69 | 4.4513 | 4.4568 | 0.0012356
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533643 | ORCHARD2 | 69 | 3.8504 | 3.8548 | 0.0011427
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533695 | LABETTE2 | 69 | 3.9998 | 4.004 | 0.0010501
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533672 | ALTAMNS2 | 69 | 3.9875 | 3.9915 | 0.0010031
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533698 | MONTGOM2 | 69 | 7.6649 | 7.6718 | 0.00090021
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533597 | MIDIANW2 | 69 | 13.8298 | 13.8422 | 0.00089661
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533610 | MIDIANE2 | 69 | 13.8298 | 13.8422 | 0.00089661
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533583 | BUTLERN2 | 69 | 13.54 | 13.5517 | 0.00086411
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533609 | BUTLERS2 | 69 | 13.54 | 13.5517 | 0.00086411
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533713 | WILLJCT2 | 69 | 7.1968 | 7.2029 | 0.0008476
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533673 | ALTOO E2 | 69 | 5.4371 | 5.4416 | 0.00082765
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533694 | INDEPEN2 | 69 | 6.8515 | 6.8571 | 0.00081734
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533706 | RA5HIPR2 | 69 | 5.4019 | 5.4063 | 0.00081453
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533688 | DEARING2 | 69 | 7.8716 | 7.878 | 0.00081305
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533712 | WILLMS 2 | 69 | 6.8016 | 6.807 | 0.00079393
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533602 | SKELLY 2 | 69 | 12.2841 | 12.2937 | 0.0007815
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533700 | NEODJCT2 | 69 | 5.0391 | 5.0429 | 0.0007541
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533593 | FRNTR N2 | 69 | 11.8169 | 11.8258 | 0.00075316
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533592 | GETTY E2 | 69 | 11.6564 | 11.665 | 0.00073779
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533679 | CHERRYV2 | 69 | 5.3711 | 5.3748 | 0.00068887
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533671 | ALTAMNT2 | 69 | 2.7854 | 2.7873 | 0.00068213
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533587 | CHASJCT2 | 69 | 10.3806 | 10.3876 | 0.00067433
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533707 | RA6BROO2 | 69 | 4.613 | 4.6161 | 0.00067201
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533648 | UN6URBA2 | 69 | 3.469 | 3.4712 | 0.00063419
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533589 | CHESNEY2 | 69 | 8.9552 | 8.9604 | 0.00058067
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533675 | ARGO 2 | 69 | 3.8423 | 3.8445 | 0.00057257
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533603 | THUNBRD2 | 69 | 8.1334 | 8.1378 | 0.00054098
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533590 | ELDORAD2 | 69 | 8.4415 | 8.446 | 0.00053308
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533588 | CHASE 2 | 69 | 7.6935 | 7.6974 | 0.00050692
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533699 | NEODESH2 | 69 | 3.336 | 3.3376 | 0.00047962
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533674 | ALTOO W2 | 69 | 2.9702 | 2.9716 | 0.00047135
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533760 | ERIE 2 | 69 | 2.8041 | 2.8052 | 0.00039228
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533705 | STUDBKR2 | 69 | 1.7767 | 1.7772 | 0.00028142
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533601 | POTWIN 2 | 69 | 3.528 | 3.5288 | 0.00022676
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533692 | YELLOWJ2 | 69 | 1.3845 | 1.3848 | 0.00021668
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533701 | NEW ALB2 | 69 | 1.4684 | 1.4687 | 0.0002043
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533584 | BU6DEGR2 | 69 | 2.4872 | 2.4876 | 0.00016082
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 543659 | LACYGNE2 | 69 | 8.4733 | 8.4743 | 0.00011802
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533599 | PEABODY2 | 69 | 1.7306 | 1.7307 | 5.7783e-05
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 533183 | WM BROS3 | 115 | 11.0007 | 11.0009 | 1.8181e-05
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 543667 | LAC3_STAR7 | 345 | 0.6403 | 0.6403 | 0
GEN-2017-022 | Central | 08 - North Oklahoma/South Central Kansas | 543669 | LAC8_STAR7 | 345 | 0.6133 | 0.6133 | 0
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 589300 | GEN-2017-092 | 345 | 9.3838 | 9.9032 | 0.055351
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588810 | GEN-2017-040 | 345 | 10.5528 | 11.1329 | 0.054971
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588839 | FIREWHL-TAP | 345 | 10.7008 | 11.2888 | 0.054949
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588834 | FWL-WND-SWYD | 345 | 10.7008 | 11.2888 | 0.054949
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588838 | G17-092-SWYD | 345 | 10.7008 | 11.2888 | 0.054949
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515422 | C-RIVER7 | 345 | 9.8234 | 9.9892 | 0.016878
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515224 | MUSKOGE7 | 345 | 28.6169 | 28.9683 | 0.012279
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515249 | BEGGS 4 | 138 | 5.4729 | 5.5141 | 0.007528
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515235 | PECANCK7 | 345 | 21.3829 | 21.5268 | 0.0067297
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510946 | C-RIVER4 | 138 | 12.8883 | 12.9719 | 0.0064865
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510907 | PITTSB-7 | 345 | 13.6566 | 13.7363 | 0.005836
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510925 | KIOWA 7 | 345 | 13.4158 | 13.4927 | 0.005732
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510380 | DELWARE7 | 345 | 10.9307 | 10.9927 | 0.0056721
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509745 | CLARKSV7 | 345 | 19.5998 | 19.6788 | 0.0040307
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588039 | G16133G16146 | 345 | 28.8139 | 28.9088 | 0.0032935
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509782 | R.S.S.-7 | 345 | 28.8139 | 28.9088 | 0.0032935
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509807 | ONETA--7 | 345 | 26.6084 | 26.6954 | 0.0032696
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510406 | N.E.S.-7 | 345 | 15.8275 | 15.8785 | 0.0032222
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509852 | T.NO.--7 | 345 | 22.5867 | 22.6594 | 0.0032187
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509836 | OEC 7 | 345 | 26.3545 | 26.4393 | 0.0032177
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509834 | COGENT 7 | 345 | 26.6803 | 26.7611 | 0.0030285
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515234 | PECANCK5 | 161 | 20.9267 | 20.9845 | 0.002762
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509783 | R.S.S.-4 | 138 | 59.4345 | 59.5979 | 0.0027492
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510951 | TALAWANDA 4 | 138 | 9.6276 | 9.6531 | 0.0026486
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509806 | ONETA--4 | 138 | 47.2399 | 47.3648 | 0.002644
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509870 | SAPLPRD7 | 345 | 22.2177 | 22.2751 | 0.0025835
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509755 | WEKIWA-7 | 345 | 18.6818 | 18.7267 | 0.0024034
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509875 | RSS T2 4 | 138 | 50.2851 | 50.4013 | 0.0023108
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509773 | RSS T1 4 | 138 | 49.413 | 49.5251 | 0.0022686
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509786 | BA.N-ST4 | 138 | 23.2255 | 23.2754 | 0.0021485
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588040 | G16133_345GS | 345 | 19.6751 | 19.7156 | 0.0020584
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510908 | MCALEST4 | 138 | 9.8253 | 9.844 | 0.0019032
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515233 | PECANCK4 | 138 | 9.5555 | 9.5735 | 0.0018837
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515228 | 5TRIBES5 | 161 | 15.4215 | 15.4503 | 0.0018675
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509871 | SAPLPRD4 | 138 | 32.0377 | 32.0936 | 0.0017448
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515230 | AGENCY 5 | 161 | 14.0106 | 14.0335 | 0.0016345
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515250 | HANCOK-5 | 161 | 14.1046 | 14.1276 | 0.0016307
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 506948 | SILOAM 5 | 161 | 21.0049 | 21.039 | 0.0016234
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515045 | SEMINOL7 | 345 | 26.7023 | 26.7438 | 0.0015542
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510909 | MCALESTIND 4 | 138 | 5.5912 | 5.5998 | 0.0015381
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515251 | EUCLID 5 | 161 | 13.7075 | 13.7284 | 0.0015247
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510906 | SMCALTP4 | 138 | 8.4625 | 8.4751 | 0.0014889
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 506944 | CHAMSPR5 | 161 | 21.9263 | 21.9572 | 0.0014093
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588041 | G16133_765GS | 765 | 6.6077 | 6.6167 | 0.001362
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 506945 | CHAMSPR7 | 345 | 9.5419 | 9.5542 | 0.0012891
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509891 | BA_71ST4 | 138 | 22.592 | 22.621 | 0.0012836
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514803 | SOONER 7 | 345 | 27.048 | 27.0822 | 0.0012644
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 589140 | GEN-2017-076 | 161 | 19.6452 | 19.67 | 0.0012624
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514809 | JOHNCO 7 | 345 | 9.7918 | 9.8039 | 0.0012357
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 504202 | SILOAMSP 5 | 161 | 18.7584 | 18.7808 | 0.0011941
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 506957 | TONTITN5 | 161 | 19.6592 | 19.6826 | 0.0011903
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 506978 | MATTISN5 | 161 | 19.1954 | 19.2178 | 0.0011669
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 506959 | TONTITN7 | 345 | 8.4933 | 8.5029 | 0.0011303
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510897 | LONEOAK4 | 138 | 8.7091 | 8.7189 | 0.0011253
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509721 | BA.NO-S4 | 138 | 12.0065 | 12.0198 | 0.0011077
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509769 | BA101-N4 | 138 | 19.1268 | 19.1477 | 0.0010927
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510865 | S-MCALT4 | 138 | 5.8211 | 5.8271 | 0.0010307
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509869 | 121LYNN4 | 138 | 17.2637 | 17.2807 | 0.00098473
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509768 | BA101ST4 | 138 | 18.3048 | 18.3223 | 0.00095603
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 509737 | BA101 S4 | 138 | 17.6486 | 17.6648 | 0.00091792
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 584780 | GEN-2015-036 | 345 | 6.9686 | 6.9744 | 0.0008323
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510911 | VALIANT7 | 345 | 13.1354 | 13.1462 | 0.00082221
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514934 | DRAPER 7 | 345 | 21.0498 | 21.066 | 0.0007696
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 504020 | FARMNGTN 5 | 161 | 12.1769 | 12.1858 | 0.00073089
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515497 | MATHWSN7 | 345 | 33.2303 | 33.254 | 0.0007132
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515302 | FTSMITH7 | 345 | 10.0478 | 10.0548 | 0.00069667
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515136 | SUNNYSD7 | 345 | 11.0206 | 11.0282 | 0.00068962
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514908 | ARCADIA7 | 345 | 30.6072 | 30.6277 | 0.00066978
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514880 | NORTWST7 | 345 | 33.0413 | 33.063 | 0.00065675
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514827 | CTNWOOD4 | 138 | 18.1397 | 18.1516 | 0.00065602
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515229 | AGENCY 2 | 69 | 12.9096 | 12.918 | 0.00065068
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515044 | SEMINOL4 | 138 | 40.0654 | 40.091 | 0.00063896
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515227 | 5TRIBES2 | 69 | 12.6248 | 12.6328 | 0.00063367
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514901 | CIMARON7 | 345 | 34.5896 | 34.6112 | 0.00062447
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514907 | ARCADIA4 | 138 | 43.807 | 43.8341 | 0.00061862
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 521157 | HUGO 7 | 345 | 11.1023 | 11.1089 | 0.00059447
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515461 | RNDBARN4 | 138 | 41.4854 | 41.5097 | 0.00058575
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514909 | REDBUD 7 | 345 | 28.9155 | 28.9324 | 0.00058446
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588043 | G16133_765MP | 765 | 4.0542 | 4.0565 | 0.00056731
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515075 | FRSTHIL4 | 138 | 13.8188 | 13.8266 | 0.00056445
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510921 | DUSTIN-4 | 138 | 9.3147 | 9.3198 | 0.00054752
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514933 | DRAPER 4 | 138 | 39.3786 | 39.3998 | 0.00053836
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514808 | JOHNCO 4 | 138 | 14.931 | 14.9389 | 0.0005291
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 587804 | G16-100-TAP | 345 | 21.9166 | 21.9281 | 0.00052472
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514906 | JNSKAMO4 | 138 | 20.6591 | 20.6695 | 0.00050341
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515894 | THUNDER7 | 345 | 11.3237 | 11.329 | 0.00046804
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514881 | SPRNGCK7 | 345 | 23.8462 | 23.857 | 0.0004529
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515305 | FTSMITH8 | 500 | 8.3973 | 8.4011 | 0.00045253
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515055 | MAUD 4 | 138 | 19.9584 | 19.9671 | 0.00043591
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515301 | FTSMTHW5 | 161 | 22.898 | 22.9076 | 0.00041925
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515300 | FTSMTHE5 | 161 | 23.0236 | 23.0332 | 0.00041696
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514879 | NORTWST4 | 138 | 44.3924 | 44.4108 | 0.00041449
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514946 | MIDWEST4 | 138 | 30.6139 | 30.6262 | 0.00040178
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515135 | SUNNYSD4 | 138 | 18.4585 | 18.4657 | 0.00039006
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 560088 | G16-063-TAP | 345 | 7.8302 | 7.8332 | 0.00038313
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 587430 | GEN-2016-063 | 345 | 7.7314 | 7.7343 | 0.00037509
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510899 | MCALEST2 | 69 | 4.8017 | 4.8035 | 0.00037487
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 589130 | GEN-2017-075 | 345 | 7.8196 | 7.8225 | 0.00037086
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515299 | BEVYTAP5 | 161 | 20.3431 | 20.3504 | 0.00035884
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515465 | LGARBER4 | 138 | 21.4859 | 21.4934 | 0.00034907
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 587800 | GEN-2016-100 | 345 | 14.9185 | 14.9237 | 0.00034856
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 504182 | BEVERLY5 | 161 | 19.5597 | 19.5664 | 0.00034254
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515345 | COLONY 5 | 161 | 18.2162 | 18.2223 | 0.00033487
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 520948 | HUGO PP4 | 138 | 22.1004 | 22.1078 | 0.00033484
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515122 | SXMLCKT4 | 138 | 10.9444 | 10.948 | 0.00032894
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515120 | RUSSET-4 | 138 | 11.1342 | 11.1378 | 0.00032333
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 521122 | HOWE 4 | 138 | 10.8417 | 10.8452 | 0.00032283
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515310 | QUANXTP5 | 161 | 17.5041 | 17.5096 | 0.00031421
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510918 | VALIANT4 | 138 | 14.7574 | 14.762 | 0.00031171
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515474 | QUANEXS5 | 161 | 16.5843 | 16.5893 | 0.00030149
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515178 | PARKLN 4 | 138 | 16.2138 | 16.2186 | 0.00029604
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515117 | ARBUCKL4 | 138 | 15.5845 | 15.5891 | 0.00029517
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515306 | ARKOMA 5 | 161 | 16.0234 | 16.0281 | 0.00029332
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514898 | CIMARON4 | 138 | 43.3248 | 43.3374 | 0.00029083
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515308 | 3RDST 5 | 161 | 15.4222 | 15.4265 | 0.00027882
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588670 | GEN-2017-023 | 138 | 18.3072 | 18.3123 | 0.00027858
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515003 | BARNES 4 | 138 | 15.8287 | 15.833 | 0.00027166
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515610 | FSHRTAP7 | 345 | 17.7246 | 17.7292 | 0.00025953
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588045 | G16133_765CS | 765 | 3.5157 | 3.5166 | 0.00025599
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 508298 | LYDIA 7 | 345 | 12.5635 | 12.5666 | 0.00024675
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588180 | GEN-2016-126 | 138 | 12.9061 | 12.9092 | 0.0002402
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515174 | VANOSS 4 | 138 | 13.1499 | 13.153 | 0.00023574
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514961 | GM 4 | 138 | 19.1936 | 19.1981 | 0.00023445
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515531 | VANOSTP4 | 138 | 13.2751 | 13.2782 | 0.00023352
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514949 | SOONRTP4 | 138 | 20.3707 | 20.3754 | 0.00023072
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 587950 | GEN-2016-119 | 345 | 11.7707 | 11.7734 | 0.00022938
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515150 | CANEYCK4 | 138 | 8.4199 | 8.4218 | 0.00022566
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515318 | SOTHADA4 | 138 | 11.2764 | 11.2789 | 0.0002217
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 511568 | TERRYRD7 | 345 | 9.9356 | 9.9378 | 0.00022143
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510866 | V-WEYCO4 | 138 | 9.6578 | 9.6598 | 0.00020709
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510948 | EARLSBORO 4 | 138 | 8.0011 | 8.0027 | 0.00019997
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 508072 | NWTXARK7 | 345 | 13.0046 | 13.0072 | 0.00019993
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588080 | ZONE-4 SUB | 345 | 7.8057 | 7.8072 | 0.00019217
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588046 | G16133_345CS | 345 | 7.9204 | 7.9219 | 0.00018938
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 514801 | MINCO 7 | 345 | 18.2057 | 18.2091 | 0.00018675
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515133 | BLUERIV4 | 138 | 10.4405 | 10.4424 | 0.00018198
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 587955 | GEN2016-119B | 345 | 9.8967 | 9.8985 | 0.00018188
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515444 | MCNOWND7 | 345 | 18.1495 | 18.1528 | 0.00018182
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515605 | CANADN7 | 345 | 12.9556 | 12.9579 | 0.00017753
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588100 | ZONE-6 SUB | 345 | 7.0415 | 7.0427 | 0.00017042
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 504021 | FARM_1 2 | 69 | 8.0603 | 8.0616 | 0.00016128
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588050 | ZONE-1 SUB | 345 | 6.3025 | 6.3035 | 0.00015867
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 587820 | GEN-2016-102 | 138 | 9.5679 | 9.5694 | 0.00015677
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588090 | ZONE-5 SUB | 345 | 6.5065 | 6.5075 | 0.00015369
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588070 | ZONE-3 SUB | 345 | 6.5318 | 6.5328 | 0.0001531
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515600 | KNGFSHR7 | 345 | 11.8984 | 11.9002 | 0.00015128
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515100 | PAOLI- 4 | 138 | 10.2996 | 10.3011 | 0.00014564
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 588060 | ZONE-2 SUB | 345 | 6.3129 | 6.3138 | 0.00014257
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515054 | MAUD 2 | 69 | 11.755 | 11.7566 | 0.00013611
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515114 | CHIGLEY4 | 138 | 8.0822 | 8.0833 | 0.0001361
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515177 | PARKLN 2 | 69 | 14.1839 | 14.1858 | 0.00013395
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510886 | IDABEL-4 | 138 | 6.7374 | 6.7383 | 0.00013358
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 508071 | NWTXARK4 | 138 | 24.3065 | 24.3096 | 0.00012754
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 511571 | RUSHSPR7 | 345 | 6.3575 | 6.3583 | 0.00012584
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515549 | MNCWND37 | 345 | 12.4665 | 12.468 | 0.00012032
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 563259 | GEN-2015-092 | 345 | 6.1634 | 6.1641 | 0.00011357
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515175 | IDEAL 2 | 69 | 11.8437 | 11.845 | 0.00010976
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 900001 | TRAVERSE1 | 345 | 7.3837 | 7.3845 | 0.00010835
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515097 | WLNUTCK4 | 138 | 9.2421 | 9.2431 | 0.0001082
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 507455 | TURK 7 | 345 | 8.7928 | 8.7937 | 0.00010236
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510901 | HUGO---4 | 138 | 3.4725 | 3.4728 | 8.6393e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 508359 | WELSH 7 | 345 | 20.8377 | 20.8395 | 8.6382e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 337909 | 8ANO% | 500 | 17.5426 | 17.5441 | 8.5506e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515124 | MAYSVIL4 | 138 | 6.2202 | 6.2207 | 8.0383e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 584060 | GEN-2015-057 | 345 | 9.1357 | 9.1364 | 7.6622e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 900002 | TRAVERSE2 | 345 | 5.7164 | 5.7168 | 6.9974e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510910 | VALIANT2 | 69 | 7.2552 | 7.2557 | 6.8916e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510870 | WCITYTP2 | 69 | 6.3166 | 6.317 | 6.3325e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515099 | PALIOGE2 | 69 | 8.0639 | 8.0644 | 6.2005e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515939 | MNCWND47 | 345 | 6.8065 | 6.8069 | 5.8767e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 900003 | TRAVERSE3 | 345 | 5.1972 | 5.1975 | 5.7723e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 337922 | 8P.HILL% | 500 | 15.1307 | 15.1314 | 4.6264e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515053 | PEARSNT2 | 69 | 4.4506 | 4.4508 | 4.4938e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510868 | GA PAC 2 | 69 | 2.4741 | 2.4742 | 4.0419e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515052 | TRIBBEY2 | 69 | 2.6015 | 2.6016 | 3.8439e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515637 | SRVCPLT2 | 69 | 2.6089 | 2.609 | 3.833e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515067 | PEARSON2 | 69 | 2.9482 | 2.9483 | 3.3919e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510867 | KI PMPS2 | 69 | 3.0643 | 3.0644 | 3.2634e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 511508 | BLANCHD4 | 138 | 6.5665 | 6.5667 | 3.0458e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 337912 | 5ANO% | 161 | 17.7035 | 17.704 | 2.8243e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 337811 | 8HAPPYVALY% | 500 | 24.9494 | 24.9501 | 2.8057e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 510869 | W CITY 2 | 69 | 3.8276 | 3.8277 | 2.6126e-05
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515095 | SRVCEPL2 | 69 | 2.3711 | 2.3711 | 0
GEN-2017-040 | Central | 08 - North Oklahoma/South Central Kansas | 515636 | TRIBYTP2 | 69 | 2.6045 | 2.6045 | 0
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509752 | INOLATP4 | 138 | 8.7677 | 9.0163 | 0.028354
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 532793 | NEOSHO 7 | 345 | 16.4472 | 16.8864 | 0.026704
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509736 | INOLA 4 | 138 | 7.5297 | 7.7124 | 0.024264
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 589110 | GEN-2017-073 | 161 | 13.8689 | 14.1649 | 0.021343
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 588990 | GEN-2017-061 | 161 | 21.0425 | 21.4795 | 0.020767
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512629 | DRYGULCH5 | 161 | 14.9318 | 15.2351 | 0.020312
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512742 | WMAIN ST5 | 161 | 26.1139 | 26.5974 | 0.018515
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512757 | NWMAID5 | 161 | 25.7016 | 26.1342 | 0.016832
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512648 | MAID 5 | 161 | 42.0337 | 42.7216 | 0.016365
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512656 | GRDA1 5 | 161 | 41.696 | 42.3541 | 0.015783
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512760 | GERALDGAY5 | 161 | 26.7603 | 27.1519 | 0.014634
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512635 | KERR GR5 | 161 | 27.3021 | 27.58 | 0.010179
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512770 | KERR BRK1 5 | 161 | 27.3021 | 27.58 | 0.010179
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512771 | KERR BRK4 5 | 161 | 27.3021 | 27.58 | 0.010179
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509790 | CATOOSA4 | 138 | 34.4428 | 34.7238 | 0.0081585
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512639 | PRY0RC22 | 69 | 9.9798 | 10.06 | 0.0080362
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300739 | 7BLACKBERRY | 345 | 14.7665 | 14.8807 | 0.0077337
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512654 | PENSA 5 | 161 | 12.632 | 12.729 | 0.0076789
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512671 | HUNT 2 | 69 | 13.2212 | 13.3129 | 0.0069358
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512634 | KERR GR3 | 115 | 16.4433 | 16.551 | 0.0065498
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512650 | GRDA1 7 | 345 | 25.9865 | 26.1539 | 0.0064418
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512638 | CATSAGR5 | 161 | 23.1122 | 23.2493 | 0.0059319
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512805 | SALNCRK5 | 161 | 17.8109 | 17.9164 | 0.0059233
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512865 | GREC TAP5 | 345 | 24.9005 | 25.0478 | 0.0059155
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 510416 | HUNTAP-2 | 69 | 8.9456 | 8.9978 | 0.0058353
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300740 | 7SPORTSMAN | 345 | 23.6136 | 23.749 | 0.005734
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512812 | ARMIN 2 | 69 | 10.8395 | 10.9011 | 0.0056829
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512686 | SALINA 5 | 161 | 17.2179 | 17.3153 | 0.0056569
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512687 | AIRPROD2 | 69 | 12.5676 | 12.6381 | 0.0056097
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512669 | KETCHUM5 | 161 | 10.2578 | 10.3142 | 0.0054983
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509804 | LLANETP4 | 138 | 26.3863 | 26.5258 | 0.0052868
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512661 | CPPTAP 2 | 69 | 12.6182 | 12.6789 | 0.0048105
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512681 | AMERCAST S2 | 69 | 12.934 | 12.9919 | 0.0044766
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300949 | 7JASPER | 345 | 12.0507 | 12.1045 | 0.0044645
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512625 | MAIDTP2 | 69 | 11.6454 | 11.697 | 0.0044309
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300069 | 5CHOTEAU1 | 161 | 40.4609 | 40.6388 | 0.0043968
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 301348 | 5CHOTEAU2 | 161 | 40.4609 | 40.6388 | 0.0043968
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509771 | LLAN ET4 | 138 | 23.6336 | 23.7353 | 0.0043032
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300741 | 5SPORTSMAN | 161 | 38.9761 | 39.1423 | 0.0042642
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512626 | MAID 2 | 69 | 14.1113 | 14.1698 | 0.0041456
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509892 | 141PINE4 | 138 | 19.8285 | 19.9044 | 0.0038278
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512727 | GRDA1 2 | 69 | 12.0314 | 12.0774 | 0.0038233
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300274 | 5LOCSTGV | 161 | 13.111 | 13.1594 | 0.0036916
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509728 | LLANE-E4 | 138 | 19.325 | 19.3929 | 0.0035136
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509841 | PCATSAT4 | 138 | 17.472 | 17.5299 | 0.0033139
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 510406 | N.E.S.-7 | 345 | 15.8275 | 15.8785 | 0.0032222
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509852 | T.NO.--7 | 345 | 22.5867 | 22.6594 | 0.0032187
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509899 | BIRDCREE-4 | 138 | 16.9241 | 16.9784 | 0.0032084
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512698 | REDDEN 2 | 69 | 10.3792 | 10.4108 | 0.0030446
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300993 | 5ELMCRK | 161 | 12.8554 | 12.8914 | 0.0028004
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512637 | 412SUB 5 | 161 | 11.4637 | 11.4954 | 0.0027653
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509835 | TERNITP4 | 138 | 15.6551 | 15.6979 | 0.0027339
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512685 | CASTING TAP2 | 69 | 9.091 | 9.1152 | 0.002662
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509895 | T.NO.2-4 | 138 | 33.6374 | 33.7265 | 0.0026488
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509755 | WEKIWA-7 | 345 | 18.6818 | 18.7267 | 0.0024034
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512683 | AMERCAST N2 | 69 | 8.1658 | 8.1853 | 0.002388
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 301344 | 5CDRCRST | 161 | 10.4498 | 10.4741 | 0.0023254
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512651 | CLARMR 5 | 161 | 12.51 | 12.5388 | 0.0023022
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509723 | TER-NIT4 | 138 | 12.9515 | 12.9807 | 0.0022546
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512750 | TONECE7 | 345 | 14.5005 | 14.5329 | 0.0022344
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512627 | COLINS 5 | 161 | 11.7421 | 11.7681 | 0.0022143
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 506935 | FLINTCR7 | 345 | 14.6814 | 14.7134 | 0.0021796
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512628 | PENSA 2 | 69 | 13.0379 | 13.0661 | 0.0021629
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509725 | PCATOSA4 | 138 | 11.2036 | 11.2273 | 0.0021154
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509887 | OWAS88_4 | 138 | 16.3829 | 16.4174 | 0.0021059
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 506934 | FLINTCR5 | 161 | 31.8761 | 31.9414 | 0.0020486
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 510396 | N.E.S.-4 | 138 | 35.2821 | 35.3504 | 0.0019358
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300997 | 5KETONVL | 161 | 10.4336 | 10.4537 | 0.0019265
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512714 | KANSATP5 | 161 | 11.3325 | 11.3539 | 0.0018884
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512700 | WAGNOR 5 | 161 | 9.4446 | 9.4607 | 0.0017047
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512643 | SILMCTY5 | 161 | 19.0667 | 19.0979 | 0.0016364
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 506979 | SHIPERD7 | 345 | 9.9081 | 9.9224 | 0.0014433
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300795 | 4OOLOGAH | 138 | 20.3525 | 20.3801 | 0.0013561
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512707 | CLARMR 4 | 138 | 13.1884 | 13.2061 | 0.0013421
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 505558 | MUSKTAP5 | 161 | 13.9439 | 13.9626 | 0.0013411
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512694 | CLEVLND7 | 345 | 14.9069 | 14.9267 | 0.0013282
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512640 | OKAYGR 5 | 161 | 9.5822 | 9.5949 | 0.0013254
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512655 | TAHLQH 5 | 161 | 10.1269 | 10.1399 | 0.0012837
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512751 | TONECE5 | 161 | 14.7089 | 14.7264 | 0.0011898
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 505560 | FT GIB 5 | 161 | 10.332 | 10.3442 | 0.0011808
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 301307 | 5PARK | 161 | 9.0106 | 9.0209 | 0.0011431
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512705 | COLLINS4 | 138 | 8.3164 | 8.3258 | 0.0011303
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 509799 | CATOOSA2 | 69 | 10.4127 | 10.4244 | 0.0011236
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512679 | CLARMR 2 | 69 | 12.3636 | 12.3762 | 0.0010191
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512624 | CENTLFT2 | 69 | 11.0777 | 11.0879 | 0.00092077
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 549984 | BROOKLINE 7 | 345 | 11.278 | 11.2881 | 0.00089555
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512870 | COLNSGR2 | 69 | 9.9201 | 9.9272 | 0.00071572
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300992 | 2COLINS | 69 | 9.92 | 9.927 | 0.00070565
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 301345 | 2CDRCRST | 69 | 8.0233 | 8.0285 | 0.00064811
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 301002 | 2SEQUOYA | 69 | 6.7757 | 6.7799 | 0.00061986
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512646 | OKAYGR 2 | 69 | 9.5995 | 9.6045 | 0.00052086
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512725 | CHELSGR2 | 69 | 4.4584 | 4.4606 | 0.00049345
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512820 | SILMCTY2 | 69 | 13.0474 | 13.0536 | 0.00047519
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512737 | SSSWTP2 | 69 | 12.1751 | 12.1805 | 0.00044353
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512697 | WAGNOR 2 | 69 | 6.773 | 6.7759 | 0.00042817
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300970 | 2SWAGONR | 69 | 7.0338 | 7.0368 | 0.00042651
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512828 | UNARCO 2 | 69 | 6.8025 | 6.8054 | 0.00042631
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300956 | 2FTGIBSN | 69 | 7.4162 | 7.4193 | 0.000418
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512690 | WAGNRTP2 | 69 | 6.795 | 6.7978 | 0.00041207
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512730 | SSSWES2 | 69 | 11.1406 | 11.1451 | 0.00040393
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300973 | 2WHITETP | 69 | 6.427 | 6.4295 | 0.00038898
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512759 | WAGCTY22 | 69 | 6.229 | 6.2314 | 0.00038529
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512801 | WAGCTY12 | 69 | 6.2904 | 6.2928 | 0.00038153
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512744 | SSMOSS2 | 69 | 10.0523 | 10.056 | 0.00036807
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300972 | 2WAGNERW | 69 | 4.4124 | 4.4136 | 0.00027196
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 301464 | 2PYRCRNR | 69 | 0.9905 | 0.9907 | 0.00020192
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300905 | 2MUSK-SW | 69 | 5.8004 | 5.8015 | 0.00018964
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300974 | 2WHITHRN | 69 | 3.1751 | 3.1757 | 0.00018897
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512765 | PYRCRNRTP2 | 69 | 1.6063 | 1.6066 | 0.00018676
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300955 | 2COWETA | 69 | 2.3983 | 2.3987 | 0.00016678
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512753 | TONNEC2 | 69 | 4.7099 | 4.7106 | 0.00014862
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300991 | 2CHILDRS | 69 | 1.38 | 1.3802 | 0.00014493
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512723 | CHILDRS2 | 69 | 1.3802 | 1.3804 | 0.00014491
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512728 | ARKLIN2 | 69 | 3.6464 | 3.6469 | 0.00013712
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512756 | TONECESTR2 | 69 | 3.7544 | 3.7549 | 0.00013318
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512745 | SSLINC2 | 69 | 2.7443 | 2.7446 | 0.00010932
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 300958 | 2HIGHLND | 69 | 1.8441 | 1.8443 | 0.00010845
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 301001 | 2SCOFEYV | 69 | 0.9648 | 0.9649 | 0.00010365
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512747 | SSNEWN2 | 69 | 3.034 | 3.0343 | 9.8879e-05
GEN-2017-061 | Central | 08 - North Oklahoma/South Central Kansas | 512746 | SSNORT2 | 69 | 2.7976 | 2.7978 | 7.149e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 589240 | GEN-2017-086 | 345 | 9.9635 | 10.5552 | 0.059387
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588540 | GEN-2017-009 | 345 | 9.9978 | 10.5633 | 0.056562
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588544 | G17-009-TAP | 345 | 10.8451 | 11.4101 | 0.052097
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532798 | VIOLA 7 | 345 | 13.8783 | 14.4624 | 0.042087
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532793 | NEOSHO 7 | 345 | 16.4472 | 16.8864 | 0.026704
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533075 | VIOLA 4 | 138 | 24.0364 | 24.4751 | 0.018251
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588364 | G16-153-TAP | 345 | 7.4618 | 7.5924 | 0.017502
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588360 | GEN-2016-153 | 345 | 7.1436 | 7.2624 | 0.01663
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532792 | FR2EAST7 | 345 | 6.7405 | 6.843 | 0.015207
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515543 | RENFROW7 | 345 | 12.3872 | 12.5431 | 0.012586
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532795 | FR2WEST7 | 345 | 5.3886 | 5.4506 | 0.011506
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532780 | CANEYRV7 | 345 | 9.847 | 9.9559 | 0.011059
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515646 | GRNTWD 7 | 345 | 10.8855 | 11.0042 | 0.010904
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532781 | CANEYWF7 | 345 | 9.5894 | 9.692 | 0.010699
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 578530 | FR3HV | 345 | 4.9398 | 4.9915 | 0.010466
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532796 | WICHITA7 | 345 | 24.1532 | 24.3835 | 0.009535
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532800 | LATHAMS7 | 345 | 10.4136 | 10.5083 | 0.0090939
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539009 | CONWAY | 138 | 12.6276 | 12.7355 | 0.0085448
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539008 | MILAN_GOAB | 138 | 11.8476 | 11.9472 | 0.0084068
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532801 | ELKRVR17 | 345 | 9.1912 | 9.2645 | 0.007975
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 589060 | GEN-2017-068 | 345 | 20.1103 | 20.2698 | 0.0079313
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539676 | MILAN 4 | 138 | 10.4656 | 10.5429 | 0.0073861
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532782 | BUFFALO7 | 345 | 20.5614 | 20.7023 | 0.0068526
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539675 | MILANTP4 | 138 | 9.8621 | 9.9226 | 0.0061346
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515476 | HUNTERS7 | 345 | 13.4924 | 13.573 | 0.0059737
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515477 | CHSHLMV7 | 345 | 13.4742 | 13.5546 | 0.005967
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533044 | GILL E 4 | 138 | 21.9045 | 22.0344 | 0.0059303
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533045 | GILL W 4 | 138 | 21.9045 | 22.0344 | 0.0059303
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533046 | GILL S 4 | 138 | 21.9045 | 22.0344 | 0.0059303
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533047 | GILL 4 | 138 | 21.9045 | 22.0344 | 0.0059303
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532794 | ROSEHIL7 | 345 | 18.9572 | 19.0665 | 0.0057656
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532791 | BENTON 7 | 345 | 19.6359 | 19.7468 | 0.0056478
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533036 | CLEARWT4 | 138 | 14.0937 | 14.1705 | 0.0054492
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533071 | WACO S 4 | 138 | 19.1512 | 19.2466 | 0.0049814
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587500 | GEN-2016-073 | 345 | 15.119 | 15.1939 | 0.004954
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533040 | EVANS N4 | 138 | 33.3755 | 33.5322 | 0.0046951
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533041 | EVANS S4 | 138 | 33.3755 | 33.5322 | 0.0046951
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533062 | ROSEHIL4 | 138 | 30.8868 | 31.0133 | 0.0040956
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533039 | ELPASO 4 | 138 | 24.1926 | 24.2863 | 0.0038731
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533059 | ELPASOE4 | 138 | 24.1926 | 24.2863 | 0.0038731
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515544 | RENFROW4 | 138 | 14.3714 | 14.4241 | 0.003667
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533074 | 45TH ST4 | 138 | 24.1728 | 24.2608 | 0.0036405
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533029 | 59TH ST4 | 138 | 17.0897 | 17.1516 | 0.0036221
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532986 | BENTON 4 | 138 | 27.8896 | 27.9879 | 0.0035246
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533795 | GILL E 2 | 69 | 29.2006 | 29.301 | 0.0034383
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533796 | GILL W 2 | 69 | 29.2006 | 29.301 | 0.0034383
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533049 | HOOVERN4 | 138 | 17.1453 | 17.2018 | 0.0032954
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533050 | HOOVERS4 | 138 | 17.1453 | 17.2018 | 0.0032954
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539003 | CLDWELL4 | 138 | 5.5937 | 5.6121 | 0.0032894
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533038 | COWSKIN4 | 138 | 17.5293 | 17.5823 | 0.0030235
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532991 | WEAVER 4 | 138 | 21.7367 | 21.8021 | 0.0030087
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533035 | CHISHLM4 | 138 | 21.2936 | 21.3567 | 0.0029633
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533053 | LAKERDG4 | 138 | 17.2997 | 17.3508 | 0.0029538
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533054 | MAIZE 4 | 138 | 21.0644 | 21.1262 | 0.0029339
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533068 | STEARMN4 | 138 | 19.1751 | 19.2296 | 0.0028422
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533034 | CENTENN4 | 138 | 14.7464 | 14.7883 | 0.0028414
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 514715 | WOODRNG7 | 345 | 19.0903 | 19.1426 | 0.0027396
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533052 | PARKCTY4 | 138 | 20.1019 | 20.1569 | 0.0027361
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533805 | HOOVERN2 | 69 | 30.449 | 30.5323 | 0.0027357
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533060 | NOEASTE4 | 138 | 20.2888 | 20.3433 | 0.0026862
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533061 | NOEASTW4 | 138 | 20.2888 | 20.3433 | 0.0026862
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533065 | SG12COL4 | 138 | 19.7318 | 19.7841 | 0.0026505
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533042 | FARBER 4 | 138 | 15.7644 | 15.806 | 0.0026389
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515569 | MDFRDTP4 | 138 | 11.4762 | 11.5063 | 0.0026228
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533001 | ALTOONA4 | 138 | 8.0292 | 8.0501 | 0.002603
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533064 | 17TH 4 | 138 | 17.2325 | 17.2761 | 0.0025301
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588320 | GEN-2016-162 | 345 | 9.7523 | 9.7768 | 0.0025122
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533024 | 29TH 4 | 138 | 19.377 | 19.4255 | 0.002503
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533030 | BOEINGE4 | 138 | 16.6198 | 16.661 | 0.002479
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 520409 | WFEC_RNFRO4 | 138 | 10.6021 | 10.628 | 0.0024429
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532988 | BELAIRE4 | 138 | 18.7482 | 18.7936 | 0.0024216
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533037 | COMOTAR4 | 138 | 18.4588 | 18.5033 | 0.0024108
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533026 | ANDOVER4 | 138 | 17.5952 | 17.6373 | 0.0023927
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533043 | FOWLER 4 | 138 | 15.8625 | 15.9002 | 0.0023767
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539668 | HARPER 4 | 138 | 7.2078 | 7.2244 | 0.0023031
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539002 | BLF-CRK4 | 138 | 4.6999 | 4.7107 | 0.0022979
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532984 | SUMNER 4 | 138 | 10.2243 | 10.2477 | 0.0022887
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533850 | VULCAN 2 | 69 | 18.7158 | 18.757 | 0.0022013
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588330 | GEN-2016-163 | 345 | 8.6195 | 8.6384 | 0.0021927
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 560053 | G15-052T | 345 | 13.1034 | 13.1318 | 0.0021674
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533032 | BU11PON4 | 138 | 14.8177 | 14.8496 | 0.0021528
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 584900 | GEN-2015-052 | 345 | 13.0534 | 13.0815 | 0.0021527
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533840 | 17TH 2 | 69 | 26.6243 | 26.6814 | 0.0021447
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588630 | GEN-2017-018 | 345 | 16.3709 | 16.4054 | 0.0021074
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539801 | THISTLE7 | 345 | 16.3709 | 16.4054 | 0.0021074
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533067 | SPRNGDL4 | 138 | 14.2305 | 14.2594 | 0.0020308
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532982 | OXFORD 4 | 138 | 9.3635 | 9.3817 | 0.0019437
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 562476 | G14-001-TAP | 345 | 10.6079 | 10.6282 | 0.0019137
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533063 | SC10BEL4 | 138 | 9.6835 | 9.702 | 0.0019105
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532797 | WOLFCRK7 | 345 | 18.0814 | 18.1154 | 0.0018804
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533823 | NOEASTE2 | 69 | 25.1631 | 25.2079 | 0.0017804
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532783 | KINGMAN7 | 345 | 6.821 | 6.8327 | 0.0017153
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 522397 | MEDFORD4 | 138 | 7.4872 | 7.5 | 0.0017096
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 542981 | LACYGNE7 | 345 | 24.761 | 24.8029 | 0.0016922
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533859 | RIPLEYE2 | 69 | 22.2574 | 22.2948 | 0.0016803
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532771 | RENO 7 | 345 | 12.6248 | 12.6459 | 0.0016713
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 543629 | LACYGNE11_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 543632 | LACYGNE22_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532799 | WAVERLY7 | 345 | 16.0356 | 16.0608 | 0.0015715
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515546 | GRANTCO4 | 138 | 6.4548 | 6.4642 | 0.0014563
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533786 | CHISHLM2 | 69 | 19.7124 | 19.7409 | 0.0014458
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533788 | COWSKIN2 | 69 | 15.8589 | 15.8814 | 0.0014188
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 560084 | G16-061-TAP | 345 | 16.1024 | 16.125 | 0.0014035
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587410 | GEN-2016-061 | 345 | 16.1024 | 16.125 | 0.0014035
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533874 | SG9STMK2 | 69 | 15.5648 | 15.5864 | 0.0013877
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532990 | MIDIAN 4 | 138 | 10.5446 | 10.5589 | 0.0013561
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532784 | NINN1WF7 | 345 | 5.6816 | 5.6893 | 0.0013553
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532993 | TALLGRS4 | 138 | 10.1282 | 10.1418 | 0.0013428
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532987 | BUTLER 4 | 138 | 10.362 | 10.3759 | 0.0013414
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532989 | BUTLERS4 | 138 | 10.362 | 10.3759 | 0.0013414
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532802 | WAVERTX7 | 345 | 13.4196 | 13.437 | 0.0012966
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533015 | BENTLEY4 | 138 | 10.8046 | 10.8186 | 0.0012957
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539000 | RAGO 4 | 138 | 3.9456 | 3.9506 | 0.0012672
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539804 | THISTLE4 | 138 | 17.4802 | 17.502 | 0.0012471
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 583850 | GEN-2014-001 | 345 | 7.0819 | 7.0906 | 0.0012285
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532992 | TIMBJCT4 | 138 | 5.8655 | 5.8727 | 0.0012275
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539638 | FLATRDG4 | 138 | 15.5121 | 15.5308 | 0.0012055
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 585250 | GEN-2015-090 | 345 | 5.0769 | 5.0829 | 0.0011818
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 514825 | KAYWIND7 | 345 | 12.6052 | 12.6199 | 0.0011662
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515621 | OPENSKY7 | 345 | 12.64 | 12.6547 | 0.001163
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 522398 | PONDCRK4 | 138 | 5.091 | 5.0969 | 0.0011589
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515877 | REDDIRT7 | 345 | 18.0507 | 18.0716 | 0.0011578
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515875 | REDNGTN7 | 345 | 18.0549 | 18.0758 | 0.0011576
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515426 | RDRUNNR4 | 138 | 8.4138 | 8.4234 | 0.001141
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532985 | TCROCK 4 | 138 | 5.4745 | 5.4807 | 0.0011325
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588190 | GEN-2016-128 | 345 | 7.9459 | 7.9545 | 0.0010823
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533016 | WWUPLNT4 | 138 | 8.1516 | 8.1596 | 0.0009814
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 529200 | OMCDLEC7 | 345 | 13.8474 | 13.8608 | 0.00096769
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515576 | RANCHRD7 | 345 | 13.8732 | 13.8866 | 0.00096589
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532981 | CRESWLN4 | 138 | 9.1264 | 9.1352 | 0.00096424
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533597 | MIDIANW2 | 69 | 13.8298 | 13.8422 | 0.00089661
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533610 | MIDIANE2 | 69 | 13.8298 | 13.8422 | 0.00089661
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587884 | G16-111-TAP | 345 | 11.3773 | 11.3875 | 0.00089652
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533011 | HALSTD 4 | 138 | 8.3248 | 8.3322 | 0.00088891
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533799 | GRANT 2 | 69 | 12.2628 | 12.2736 | 0.00088071
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 520434 | WAKTASW4 | 138 | 6.3232 | 6.3287 | 0.00086981
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515852 | DGRASSE7 | 345 | 14.5452 | 14.5578 | 0.00086627
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533583 | BUTLERN2 | 69 | 13.54 | 13.5517 | 0.00086411
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587460 | GEN-2016-068 | 345 | 6.5264 | 6.5319 | 0.00084273
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533604 | WEAVER 2 | 69 | 11.6633 | 11.6729 | 0.00082309
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 584770 | GEN-2015-034 | 345 | 11.7376 | 11.747 | 0.00080085
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587160 | GEN-2016-022 | 345 | 11.7376 | 11.747 | 0.00080085
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587910 | GEN-2016-114 | 345 | 10.1469 | 10.155 | 0.00079827
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539631 | FLATRWD4 | 138 | 10.3583 | 10.3664 | 0.00078198
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533416 | RENO 3 | 115 | 26.7821 | 26.8023 | 0.00075424
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515688 | FRNTWND7 | 345 | 11.1998 | 11.2082 | 0.00075001
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 584570 | GEN-2015-015 | 138 | 5.8242 | 5.8284 | 0.00072113
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533558 | TIMBJCT2 | 69 | 8.1517 | 8.1575 | 0.00071151
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 542968 | STILWEL7 | 345 | 23.1239 | 23.1391 | 0.00065733
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515547 | GRANTCO2 | 69 | 7.4693 | 7.4742 | 0.00065602
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 514714 | WOODRNG4 | 138 | 20.0668 | 20.0796 | 0.00063787
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587894 | G16-112-TAP | 345 | 11.1782 | 11.1849 | 0.00059938
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533541 | AKRON 2 | 69 | 6.7266 | 6.7306 | 0.00059465
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533589 | CHESNEY2 | 69 | 8.9552 | 8.9604 | 0.00058067
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 542965 | W.GRDNR7 | 345 | 24.8262 | 24.8406 | 0.00058003
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533013 | MOUND 4 | 138 | 6.9434 | 6.9474 | 0.00057609
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533070 | SLATECRK4 | 138 | 6.7318 | 6.7356 | 0.00056448
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533603 | THUNBRD2 | 69 | 8.1334 | 8.1378 | 0.00054098
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587880 | GEN-2016-111 | 345 | 7.1243 | 7.1281 | 0.00053339
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539674 | BARBER 4 | 138 | 8.2188 | 8.2231 | 0.00052319
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533413 | CIRCLE 3 | 115 | 23.6123 | 23.6235 | 0.00047433
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533674 | ALTOO W2 | 69 | 2.9702 | 2.9716 | 0.00047135
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533421 | HEC GT 3 | 115 | 22.9426 | 22.953 | 0.00045331
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539800 | CLARKCOUNTY7 | 345 | 13.2594 | 13.2652 | 0.00043743
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533419 | HEC 3 | 115 | 21.8737 | 21.8832 | 0.00043431
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533630 | CC3WEST2 | 69 | 4.4272 | 4.4291 | 0.00042917
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533429 | MOUNDRG3 | 115 | 8.6474 | 8.6511 | 0.00042787
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532768 | EMPEC 7 | 345 | 17.5987 | 17.6059 | 0.00040912
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532769 | LANG 7 | 345 | 17.3797 | 17.3867 | 0.00040277
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533736 | HALSTED2 | 69 | 7.2751 | 7.278 | 0.00039862
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532773 | SUMMIT 7 | 345 | 12.1324 | 12.1372 | 0.00039563
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515375 | WWRDEHV7 | 345 | 19.8126 | 19.8204 | 0.00039369
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533626 | BURLJCT2 | 69 | 4.8155 | 4.8173 | 0.00037379
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 583370 | GEN-2012-024 | 345 | 11.3107 | 11.3148 | 0.00036249
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515853 | DGRASSE4 | 138 | 15.3869 | 15.3923 | 0.00035095
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539852 | P1 MPT PRI | 345 | 10.7671 | 10.7708 | 0.00034364
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533653 | WOLFCRK2 | 69 | 5.8582 | 5.8601 | 0.00032433
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 582008 | GEN-2011-008 | 345 | 10.514 | 10.5174 | 0.00032338
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 542977 | CRAIG 7 | 345 | 21.4243 | 21.4312 | 0.00032206
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533742 | MOUND 2 | 69 | 7.0573 | 7.0595 | 0.00031173
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 542966 | WGARDNR5 | 161 | 23.42 | 23.4273 | 0.0003117
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588494 | G17-004-TAP | 345 | 10.1178 | 10.1209 | 0.00030639
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 585100 | GEN-2015-073 | 345 | 13.3961 | 13.4002 | 0.00030606
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 520529 | RSVLYSW4 | 138 | 13.6729 | 13.677 | 0.00029986
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 543105 | BULLCRK5 | 161 | 22.4616 | 22.4683 | 0.00029829
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533440 | 43LORAN | 115 | 14.4364 | 14.4407 | 0.00029786
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 560080 | G16-046-TAP | 345 | 11.4289 | 11.4323 | 0.00029749
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 514795 | KNOBHIL4 | 138 | 11.3899 | 11.3932 | 0.00028973
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539857 | P2 MPT PRI | 345 | 9.1297 | 9.1323 | 0.00028478
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 585300 | GEN-2015-095 | 138 | 11.3108 | 11.314 | 0.00028292
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533705 | STUDBKR2 | 69 | 1.7767 | 1.7772 | 0.00028142
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515407 | TATONGA7 | 345 | 16.7215 | 16.7261 | 0.00027509
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533551 | SC1KING2 | 69 | 3.2879 | 3.2888 | 0.00027373
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533628 | CC1BURL2 | 69 | 3.3205 | 3.3214 | 0.00027104
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533624 | BURLING2 | 69 | 3.3336 | 3.3345 | 0.00026998
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 582908 | G-2011-008-2 | 345 | 8.4349 | 8.4371 | 0.00026082
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 582708 | G-2011-008-1 | 345 | 8.5619 | 8.564 | 0.00024527
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587310 | GEN-2016-046 | 345 | 9.8417 | 9.8441 | 0.00024386
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533629 | CC2SHAR2 | 69 | 4.545 | 4.5461 | 0.00024202
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532774 | SWISVAL7 | 345 | 16.163 | 16.1669 | 0.00024129
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 531469 | SPERVIL7 | 345 | 13.7357 | 13.739 | 0.00024025
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588490 | GEN-2017-004 | 345 | 8.0601 | 8.062 | 0.00023573
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533625 | BURLIND2 | 69 | 2.9763 | 2.977 | 0.00023519
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587980 | GEN-2016-122 | 345 | 5.2087 | 5.2099 | 0.00023038
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532871 | CIRCLE 6 | 230 | 10.0555 | 10.0578 | 0.00022873
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 579480 | GEN-2008-124 | 345 | 12.6868 | 12.6897 | 0.00022858
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539803 | IRONWOOD7 | 345 | 13.1375 | 13.1405 | 0.00022835
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515599 | G07621119-20 | 345 | 13.2006 | 13.2036 | 0.00022726
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533601 | POTWIN 2 | 69 | 3.528 | 3.5288 | 0.00022676
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533546 | FLORALJ2 | 69 | 2.7316 | 2.7322 | 0.00021965
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515585 | MAMTHPW7 | 345 | 13.2772 | 13.2801 | 0.00021842
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533692 | YELLOWJ2 | 69 | 1.3845 | 1.3848 | 0.00021668
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532873 | SUMMIT 6 | 230 | 14.5337 | 14.5368 | 0.0002133
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533412 | ARKVALJ3 | 115 | 10.8426 | 10.8449 | 0.00021213
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 560071 | G16-003-TAP | 345 | 15.2376 | 15.2408 | 0.00021001
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587020 | GEN-2016-003 | 345 | 15.2376 | 15.2408 | 0.00021001
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533411 | ARKVAL 3 | 115 | 10.6123 | 10.6145 | 0.00020731
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 585430 | PRSIMN_CRK1 | 345 | 11.6164 | 11.6188 | 0.0002066
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533415 | DAVIS 3 | 115 | 8.7128 | 8.7146 | 0.00020659
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533557 | TIMBER 2 | 69 | 2.4233 | 2.4238 | 0.00020633
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533701 | NEW ALB2 | 69 | 1.4684 | 1.4687 | 0.0002043
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533434 | SALTCRK3 | 115 | 9.0473 | 9.0491 | 0.00019895
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 587890 | GEN-2016-112 | 345 | 4.6684 | 4.6693 | 0.00019279
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515448 | CRSRDSW7 | 345 | 11.741 | 11.7432 | 0.00018738
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532770 | MORRIS 7 | 345 | 12.8665 | 12.8689 | 0.00018653
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533414 | CITIES 3 | 115 | 8.5877 | 8.5893 | 0.00018631
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 585440 | PRSIMN_CRK2 | 345 | 10.6077 | 10.6096 | 0.00017912
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533732 | BURRTON2 | 69 | 3.4761 | 3.4767 | 0.00017261
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588560 | GEN-2017-011 | 345 | 12.2618 | 12.2639 | 0.00017126
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532872 | EMCPHER6 | 230 | 9.3745 | 9.3761 | 0.00017068
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533545 | FLORAL 2 | 69 | 2.4109 | 2.4113 | 0.00016591
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 585410 | GREAT_WESTRN | 345 | 9.9457 | 9.9473 | 0.00016087
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533584 | BU6DEGR2 | 69 | 2.4872 | 2.4876 | 0.00016082
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532856 | SWISVAL6 | 230 | 20.9983 | 21.0016 | 0.00015716
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515376 | WWRDEHV4 | 138 | 24.1729 | 24.1765 | 0.00014893
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532767 | GEARY 7 | 345 | 10.3222 | 10.3237 | 0.00014532
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533380 | SPRGCRK3 | 115 | 3.8099 | 3.8104 | 0.00013124
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532863 | MORRIS 6 | 230 | 13.9585 | 13.9603 | 0.00012895
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588654 | G17-021-TAP | 345 | 10.1299 | 10.1312 | 0.00012833
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539695 | SPEARVL6 | 230 | 12.4713 | 12.4729 | 0.00012829
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539117 | SPRVILL-EHVB | 230 | 12.1436 | 12.1451 | 0.00012352
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 543054 | CEDARNL5 | 161 | 8.9661 | 8.9672 | 0.00012268
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 543659 | LACYGNE2 | 69 | 8.4733 | 8.4743 | 0.00011802
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533369 | HILSBOR3 | 115 | 2.5456 | 2.5459 | 0.00011785
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 585420 | COWBOY_RIDGE | 345 | 7.6718 | 7.6727 | 0.00011731
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533438 | WMCPHER3 | 115 | 15.7555 | 15.7573 | 0.00011425
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 589370 | GEN-2017-099 | 345 | 9.6557 | 9.6568 | 0.00011392
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588650 | GEN-2017-021 | 345 | 9.6638 | 9.6649 | 0.00011383
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533417 | EMCPHER3 | 115 | 15.2137 | 15.2154 | 0.00011174
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533304 | LANG 3 | 115 | 14.5028 | 14.5044 | 0.00011032
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515582 | SLNGWND7 | 345 | 7.3455 | 7.3463 | 0.00010891
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533428 | MCPHER 3 | 115 | 15.7273 | 15.729 | 0.00010809
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533506 | DAVIS 2 | 69 | 7.4951 | 7.4959 | 0.00010674
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533427 | REFINRY3 | 115 | 14.6512 | 14.6527 | 0.00010238
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532766 | JEC N 7 | 345 | 23.7584 | 23.7608 | 0.00010102
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533520 | 2ND ELM2 | 69 | 6.1435 | 6.1441 | 9.7664e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533516 | MAPLE J2 | 69 | 7.1953 | 7.196 | 9.7286e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533372 | PHILIPS3 | 115 | 12.8586 | 12.8598 | 9.3323e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533529 | MWIRNJ22 | 69 | 6.5493 | 6.5499 | 9.1613e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533366 | FLORENC3 | 115 | 3.3362 | 3.3365 | 8.9923e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 531501 | BUCKNER7 | 345 | 9.0367 | 9.0375 | 8.8528e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588310 | GEN-2016-158 | 345 | 4.6245 | 4.6249 | 8.6496e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 588300 | GEN-2016-157 | 345 | 4.8983 | 4.8987 | 8.1661e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533519 | MWIRONJ2 | 69 | 6.1417 | 6.1422 | 8.1411e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533513 | HEC 2 | 69 | 11.1813 | 11.1822 | 8.0492e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533518 | MWIRON 2 | 69 | 6.3596 | 6.3601 | 7.8621e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532874 | UNIONRG6 | 230 | 8.9642 | 8.9649 | 7.8088e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533426 | MANVILE3 | 115 | 11.7012 | 11.7021 | 7.6915e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533505 | NCTYSVC2 | 69 | 3.9782 | 3.9785 | 7.5411e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533307 | PRAIRIE3 | 115 | 9.2854 | 9.2861 | 7.5387e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532862 | MCDOWEL6 | 230 | 7.005 | 7.0055 | 7.1378e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539679 | GRTBEND6 | 230 | 8.5124 | 8.513 | 7.0485e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 531502 | CIMRRN 7 | 345 | 7.1715 | 7.172 | 6.972e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 531504 | CIMWD2 7 | 345 | 7.1715 | 7.172 | 6.972e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532765 | HOYT 7 | 345 | 15.8447 | 15.8458 | 6.9424e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532851 | AUBURN 6 | 230 | 13.1378 | 13.1387 | 6.8505e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532857 | TECHILL6 | 230 | 10.7002 | 10.7009 | 6.5419e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533301 | EAST ST3 | 115 | 9.236 | 9.2366 | 6.4963e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532852 | JEC 6 | 230 | 24.7674 | 24.769 | 6.4601e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533305 | MORRIS 3 | 115 | 12.4747 | 12.4755 | 6.413e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 530686 | RICE 6 | 230 | 4.9179 | 4.9182 | 6.1002e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 539759 | SPRVL 3 | 115 | 11.5608 | 11.5615 | 6.0549e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533599 | PEABODY2 | 69 | 1.7306 | 1.7307 | 5.7783e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533522 | 17HUXMN2 | 69 | 7.0441 | 7.0445 | 5.6785e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533509 | 11HALST2 | 69 | 7.3924 | 7.3928 | 5.411e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515398 | OUSPRT 4 | 138 | 9.4837 | 9.4842 | 5.2722e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533394 | CORONAD3 | 115 | 7.6677 | 7.6681 | 5.2167e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533504 | CITYSVC2 | 69 | 3.9513 | 3.9515 | 5.0616e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533439 | WHEATLD3 | 115 | 7.9438 | 7.9442 | 5.0354e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533503 | CESSNAJ2 | 69 | 5.9718 | 5.9721 | 5.0236e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533521 | 17HALST2 | 69 | 8.1271 | 8.1275 | 4.9218e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 530618 | HUNTSVL3 | 115 | 4.0986 | 4.0988 | 4.8797e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533523 | 17 PLUM2 | 69 | 6.2554 | 6.2557 | 4.7959e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533306 | READING3 | 115 | 6.3868 | 6.3871 | 4.6972e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532854 | LEC U5 6 | 230 | 12.9986 | 12.9992 | 4.6159e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532875 | GEN-2015-069 | 230 | 6.5502 | 6.5505 | 4.58e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 532853 | LAWHILL6 | 230 | 13.1179 | 13.1185 | 4.5739e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515394 | KEENAN 4 | 138 | 8.912 | 8.9124 | 4.4883e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 515458 | BORDER 7 | 345 | 4.4958 | 4.496 | 4.4486e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533511 | 14LORAN2 | 69 | 6.7624 | 6.7627 | 4.4363e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 530620 | LYONS 3 | 115 | 5.6298 | 5.63 | 3.5525e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533502 | CESSNA 2 | 69 | 5.8605 | 5.8607 | 3.4127e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533507 | 18&PLUM2 | 69 | 6.166 | 6.1662 | 3.2436e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 530688 | BUFLOCRK6 | 230 | 3.6481 | 3.6482 | 2.7412e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533359 | UNIONRG3 | 115 | 3.8029 | 3.803 | 2.6296e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 530711 | SAXMAN 3 | 115 | 4.3857 | 4.3858 | 2.2801e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533183 | WM BROS3 | 115 | 11.0007 | 11.0009 | 1.8181e-05
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 543669 | LAC8_STAR7 | 345 | 0.6133 | 0.6133 | 0
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 533360 | TCHOPE 3 | 115 | 3.3791 | 3.3791 | 0
GEN-2017-068 | Central | 08 - North Oklahoma/South Central Kansas | 543667 | LAC3_STAR7 | 345 | 0.6403 | 0.6403 | 0
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 589090 | GEN-2017-071 | 138 | 7.5805 | 8.2795 | 0.09221
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515417 | GRNWOOD4 | 138 | 7.845 | 8.5572 | 0.090784
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 589100 | GEN-2017-072 | 138 | 7.5805 | 8.2587 | 0.089466
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515033 | CUSHING4 | 138 | 7.0346 | 7.4039 | 0.052498
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515043 | GRTPLNS4 | 138 | 6.779 | 7.133 | 0.05222
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515453 | LNWOODT4 | 138 | 6.7539 | 7.0913 | 0.049956
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515401 | LINWOOD4 | 138 | 6.7099 | 7.0428 | 0.049613
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515416 | GRNWOOD2 | 69 | 8.1669 | 8.4418 | 0.03366
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515032 | CUSHING2 | 69 | 8.1882 | 8.433 | 0.029897
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515019 | HY99TAP2 | 69 | 7.048 | 7.2515 | 0.028873
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515021 | OAKGROV2 | 69 | 7.2682 | 7.4632 | 0.026829
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515035 | BRISTOW4 | 138 | 9.8092 | 10.0533 | 0.024885
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515026 | DRMRITE2 | 69 | 7.2387 | 7.4166 | 0.024576
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515675 | TRYON 4 | 138 | 9.1552 | 9.3776 | 0.024292
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515413 | CUSHOIL2 | 69 | 6.0365 | 6.1823 | 0.024153
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515039 | PAYNESB4 | 138 | 8.8061 | 9.0107 | 0.023234
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515020 | PLCNTRT2 | 69 | 5.7889 | 5.9212 | 0.022854
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515508 | SHLCSHT2 | 69 | 5.901 | 6.0358 | 0.022844
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515119 | SEAWAYS2 | 69 | 5.7749 | 5.906 | 0.022702
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515018 | ARCO PL2 | 69 | 5.7757 | 5.9066 | 0.022664
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515022 | PIPELIN2 | 69 | 5.7827 | 5.9136 | 0.022636
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515023 | SHELCSH2 | 69 | 5.8499 | 5.9823 | 0.022633
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515025 | EUCHEE 2 | 69 | 6.436 | 6.5805 | 0.022452
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515470 | SKPLCSH2 | 69 | 5.6759 | 5.8031 | 0.022411
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515027 | TIGERCK2 | 69 | 6.5632 | 6.6966 | 0.020325
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515574 | SPGVLLY4 | 138 | 10.491 | 10.7029 | 0.020198
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515028 | SVCPLTP2 | 69 | 6.4951 | 6.624 | 0.019846
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515016 | CHDRTAP2 | 69 | 4.6561 | 4.7452 | 0.019136
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515514 | KNIPE 4 | 138 | 7.9445 | 8.0833 | 0.017471
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515031 | SVCPLDR2 | 69 | 5.5167 | 5.6102 | 0.016949
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515047 | WARWICK4 | 138 | 10.3846 | 10.5483 | 0.015764
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515015 | SINDRUM2 | 69 | 3.5173 | 3.5684 | 0.014528
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515048 | KEYWEST4 | 138 | 5.7324 | 5.8006 | 0.011897
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515414 | ANTIOCH2 | 69 | 3.3865 | 3.4258 | 0.011605
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515369 | BELLCOW4 | 138 | 6.5038 | 6.5768 | 0.011224
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515011 | STILWTR4 | 138 | 13.9315 | 14.0722 | 0.010099
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515037 | PRNCVLT2 | 69 | 6.5286 | 6.5866 | 0.008884
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515030 | PRINCEV2 | 69 | 6.4068 | 6.4627 | 0.0087251
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515366 | WFROSST4 | 138 | 12.2847 | 12.3868 | 0.0083112
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 521107 | RSSVILE4 | 138 | 12.2847 | 12.3868 | 0.0083112
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515009 | MCELROY4 | 138 | 13.6114 | 13.7211 | 0.0080594
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515249 | BEGGS 4 | 138 | 5.4729 | 5.5141 | 0.007528
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515034 | BRISTOW2 | 69 | 5.7114 | 5.7533 | 0.0073362
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515235 | PECANCK7 | 345 | 21.3829 | 21.5268 | 0.0067297
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515242 | BLUEBEL4 | 138 | 16.6445 | 16.7529 | 0.0065127
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515200 | KELLYVL4 | 138 | 13.2901 | 13.3446 | 0.0041008
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515241 | BLUEBEL2 | 69 | 11.2247 | 11.2673 | 0.0037952
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515447 | MORISNT4 | 138 | 13.8859 | 13.9311 | 0.0032551
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515245 | LONESTR4 | 138 | 13.0189 | 13.0567 | 0.0029035
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509758 | PRATTV-4 | 138 | 19.8477 | 19.9027 | 0.0027711
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515234 | PECANCK5 | 161 | 20.9267 | 20.9845 | 0.002762
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515247 | BEELINE4 | 138 | 21.592 | 21.6509 | 0.0027279
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515243 | BOWDEN 4 | 138 | 11.9167 | 11.9484 | 0.0026601
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509815 | S.S.---4 | 138 | 27.7211 | 27.7896 | 0.002471
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515244 | HICKORY4 | 138 | 12.9855 | 13.0171 | 0.0024335
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509896 | DENV_WTAP4 | 138 | 27.0461 | 27.1109 | 0.0023959
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515218 | POLECTP4 | 138 | 14.9557 | 14.9915 | 0.0023937
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509812 | SHEFFD-4 | 138 | 25.0803 | 25.1346 | 0.002165
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515219 | POLECAT4 | 138 | 12.3767 | 12.4012 | 0.0019795
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515233 | PECANCK4 | 138 | 9.5555 | 9.5735 | 0.0018837
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515228 | 5TRIBES5 | 161 | 15.4215 | 15.4503 | 0.0018675
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509739 | CARSN-T4 | 138 | 31.4964 | 31.5511 | 0.0017367
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515230 | AGENCY 5 | 161 | 14.0106 | 14.0335 | 0.0016345
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509823 | WED-TAP4 | 138 | 18.6485 | 18.6767 | 0.0015122
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515236 | SAPULPA2 | 69 | 7.7468 | 7.7575 | 0.0013812
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515246 | BEELINE2 | 69 | 11.7156 | 11.729 | 0.0011438
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509740 | UNIONAV4 | 138 | 20.4392 | 20.4622 | 0.0011253
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509865 | CARSONT4 | 138 | 11.7252 | 11.7363 | 0.00094668
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509749 | CARSN-C4 | 138 | 16.7592 | 16.7746 | 0.0009189
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509832 | W.ED.-W4 | 138 | 11.3239 | 11.3342 | 0.00090958
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509748 | DENVR-W4 | 138 | 9.4088 | 9.4166 | 0.00082901
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509741 | CARSN-N4 | 138 | 9.1335 | 9.1403 | 0.00074451
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509754 | WHORSE-4 | 138 | 3.8711 | 3.8724 | 0.00033582
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509897 | WILDCT_TP4 | 138 | 3.8719 | 3.8732 | 0.00033575
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509821 | HWY20-T4 | 138 | 3.8796 | 3.8809 | 0.00033509
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509898 | WILDCAT_4 | 138 | 3.866 | 3.8672 | 0.0003104
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509816 | S.S.---2 | 69 | 6.2283 | 6.23 | 0.00027295
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509798 | HWY20--4 | 138 | 2.9668 | 2.9676 | 0.00026965
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 529306 | OMHOMNY4 | 138 | 2.49 | 2.4906 | 0.00024096
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 514927 | HSLEAST2 | 69 | 11.1732 | 11.175 | 0.0001611
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 509796 | DX----W2 | 69 | 3.745 | 3.7456 | 0.00016021
GEN-2017-071 | Central | 08 - North Oklahoma/South Central Kansas | 515017 | CHANDLR2 | 69 | 1.7237 | 1.7237 | 0
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 589090 | GEN-2017-071 | 138 | 7.5805 | 8.2795 | 0.09221
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515417 | GRNWOOD4 | 138 | 7.845 | 8.5572 | 0.090784
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 589100 | GEN-2017-072 | 138 | 7.5805 | 8.2587 | 0.089466
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515033 | CUSHING4 | 138 | 7.0346 | 7.4039 | 0.052498
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515043 | GRTPLNS4 | 138 | 6.779 | 7.133 | 0.05222
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515453 | LNWOODT4 | 138 | 6.7539 | 7.0913 | 0.049956
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515401 | LINWOOD4 | 138 | 6.7099 | 7.0428 | 0.049613
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515416 | GRNWOOD2 | 69 | 8.1669 | 8.4418 | 0.03366
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515032 | CUSHING2 | 69 | 8.1882 | 8.433 | 0.029897
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515019 | HY99TAP2 | 69 | 7.048 | 7.2515 | 0.028873
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515021 | OAKGROV2 | 69 | 7.2682 | 7.4632 | 0.026829
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515035 | BRISTOW4 | 138 | 9.8092 | 10.0533 | 0.024885
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515026 | DRMRITE2 | 69 | 7.2387 | 7.4166 | 0.024576
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515675 | TRYON 4 | 138 | 9.1552 | 9.3776 | 0.024292
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515413 | CUSHOIL2 | 69 | 6.0365 | 6.1823 | 0.024153
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515039 | PAYNESB4 | 138 | 8.8061 | 9.0107 | 0.023234
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515020 | PLCNTRT2 | 69 | 5.7889 | 5.9212 | 0.022854
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515508 | SHLCSHT2 | 69 | 5.901 | 6.0358 | 0.022844
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515119 | SEAWAYS2 | 69 | 5.7749 | 5.906 | 0.022702
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515018 | ARCO PL2 | 69 | 5.7757 | 5.9066 | 0.022664
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515022 | PIPELIN2 | 69 | 5.7827 | 5.9136 | 0.022636
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515023 | SHELCSH2 | 69 | 5.8499 | 5.9823 | 0.022633
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515025 | EUCHEE 2 | 69 | 6.436 | 6.5805 | 0.022452
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515470 | SKPLCSH2 | 69 | 5.6759 | 5.8031 | 0.022411
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515027 | TIGERCK2 | 69 | 6.5632 | 6.6966 | 0.020325
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515574 | SPGVLLY4 | 138 | 10.491 | 10.7029 | 0.020198
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515028 | SVCPLTP2 | 69 | 6.4951 | 6.624 | 0.019846
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515016 | CHDRTAP2 | 69 | 4.6561 | 4.7452 | 0.019136
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515514 | KNIPE 4 | 138 | 7.9445 | 8.0833 | 0.017471
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515031 | SVCPLDR2 | 69 | 5.5167 | 5.6102 | 0.016949
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515047 | WARWICK4 | 138 | 10.3846 | 10.5483 | 0.015764
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515015 | SINDRUM2 | 69 | 3.5173 | 3.5684 | 0.014528
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515048 | KEYWEST4 | 138 | 5.7324 | 5.8006 | 0.011897
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515414 | ANTIOCH2 | 69 | 3.3865 | 3.4258 | 0.011605
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515369 | BELLCOW4 | 138 | 6.5038 | 6.5768 | 0.011224
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515011 | STILWTR4 | 138 | 13.9315 | 14.0722 | 0.010099
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515037 | PRNCVLT2 | 69 | 6.5286 | 6.5866 | 0.008884
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515030 | PRINCEV2 | 69 | 6.4068 | 6.4627 | 0.0087251
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515366 | WFROSST4 | 138 | 12.2847 | 12.3868 | 0.0083112
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 521107 | RSSVILE4 | 138 | 12.2847 | 12.3868 | 0.0083112
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515009 | MCELROY4 | 138 | 13.6114 | 13.7211 | 0.0080594
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515249 | BEGGS 4 | 138 | 5.4729 | 5.5141 | 0.007528
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515034 | BRISTOW2 | 69 | 5.7114 | 5.7533 | 0.0073362
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515235 | PECANCK7 | 345 | 21.3829 | 21.5268 | 0.0067297
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515242 | BLUEBEL4 | 138 | 16.6445 | 16.7529 | 0.0065127
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515200 | KELLYVL4 | 138 | 13.2901 | 13.3446 | 0.0041008
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515241 | BLUEBEL2 | 69 | 11.2247 | 11.2673 | 0.0037952
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515447 | MORISNT4 | 138 | 13.8859 | 13.9311 | 0.0032551
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515245 | LONESTR4 | 138 | 13.0189 | 13.0567 | 0.0029035
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509758 | PRATTV-4 | 138 | 19.8477 | 19.9027 | 0.0027711
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515234 | PECANCK5 | 161 | 20.9267 | 20.9845 | 0.002762
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515247 | BEELINE4 | 138 | 21.592 | 21.6509 | 0.0027279
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515243 | BOWDEN 4 | 138 | 11.9167 | 11.9484 | 0.0026601
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509815 | S.S.---4 | 138 | 27.7211 | 27.7896 | 0.002471
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515244 | HICKORY4 | 138 | 12.9855 | 13.0171 | 0.0024335
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509896 | DENV_WTAP4 | 138 | 27.0461 | 27.1109 | 0.0023959
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515218 | POLECTP4 | 138 | 14.9557 | 14.9915 | 0.0023937
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509812 | SHEFFD-4 | 138 | 25.0803 | 25.1346 | 0.002165
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515219 | POLECAT4 | 138 | 12.3767 | 12.4012 | 0.0019795
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515233 | PECANCK4 | 138 | 9.5555 | 9.5735 | 0.0018837
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515228 | 5TRIBES5 | 161 | 15.4215 | 15.4503 | 0.0018675
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509739 | CARSN-T4 | 138 | 31.4964 | 31.5511 | 0.0017367
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515230 | AGENCY 5 | 161 | 14.0106 | 14.0335 | 0.0016345
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509823 | WED-TAP4 | 138 | 18.6485 | 18.6767 | 0.0015122
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515236 | SAPULPA2 | 69 | 7.7468 | 7.7575 | 0.0013812
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515246 | BEELINE2 | 69 | 11.7156 | 11.729 | 0.0011438
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509740 | UNIONAV4 | 138 | 20.4392 | 20.4622 | 0.0011253
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509865 | CARSONT4 | 138 | 11.7252 | 11.7363 | 0.00094668
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509749 | CARSN-C4 | 138 | 16.7592 | 16.7746 | 0.0009189
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509832 | W.ED.-W4 | 138 | 11.3239 | 11.3342 | 0.00090958
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509748 | DENVR-W4 | 138 | 9.4088 | 9.4166 | 0.00082901
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509741 | CARSN-N4 | 138 | 9.1335 | 9.1403 | 0.00074451
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509754 | WHORSE-4 | 138 | 3.8711 | 3.8724 | 0.00033582
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509897 | WILDCT_TP4 | 138 | 3.8719 | 3.8732 | 0.00033575
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509821 | HWY20-T4 | 138 | 3.8796 | 3.8809 | 0.00033509
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509898 | WILDCAT_4 | 138 | 3.866 | 3.8672 | 0.0003104
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509816 | S.S.---2 | 69 | 6.2283 | 6.23 | 0.00027295
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509798 | HWY20--4 | 138 | 2.9668 | 2.9676 | 0.00026965
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 529306 | OMHOMNY4 | 138 | 2.49 | 2.4906 | 0.00024096
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 514927 | HSLEAST2 | 69 | 11.1732 | 11.175 | 0.0001611
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 509796 | DX----W2 | 69 | 3.745 | 3.7456 | 0.00016021
GEN-2017-072 | Central | 08 - North Oklahoma/South Central Kansas | 515017 | CHANDLR2 | 69 | 1.7237 | 1.7237 | 0
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 510437 | ROCKPT-4 | 138 | 6.5227 | 6.8527 | 0.050593
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509752 | INOLATP4 | 138 | 8.7677 | 9.0163 | 0.028354
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509736 | INOLA 4 | 138 | 7.5297 | 7.7124 | 0.024264
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 589110 | GEN-2017-073 | 161 | 13.8689 | 14.1649 | 0.021343
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 588990 | GEN-2017-061 | 161 | 21.0425 | 21.4795 | 0.020767
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512629 | DRYGULCH5 | 161 | 14.9318 | 15.2351 | 0.020312
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512742 | WMAIN ST5 | 161 | 26.1139 | 26.5974 | 0.018515
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512757 | NWMAID5 | 161 | 25.7016 | 26.1342 | 0.016832
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512648 | MAID 5 | 161 | 42.0337 | 42.7216 | 0.016365
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512656 | GRDA1 5 | 161 | 41.696 | 42.3541 | 0.015783
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512760 | GERALDGAY5 | 161 | 26.7603 | 27.1519 | 0.014634
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512635 | KERR GR5 | 161 | 27.3021 | 27.58 | 0.010179
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512770 | KERR BRK1 5 | 161 | 27.3021 | 27.58 | 0.010179
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512771 | KERR BRK4 5 | 161 | 27.3021 | 27.58 | 0.010179
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509790 | CATOOSA4 | 138 | 34.4428 | 34.7238 | 0.0081585
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300739 | 7BLACKBERRY | 345 | 14.7665 | 14.8807 | 0.0077337
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512654 | PENSA 5 | 161 | 12.632 | 12.729 | 0.0076789
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512671 | HUNT 2 | 69 | 13.2212 | 13.3129 | 0.0069358
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512634 | KERR GR3 | 115 | 16.4433 | 16.551 | 0.0065498
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 510423 | L GROVE3 | 115 | 15.3902 | 15.4904 | 0.0065106
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512650 | GRDA1 7 | 345 | 25.9865 | 26.1539 | 0.0064418
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512638 | CATSAGR5 | 161 | 23.1122 | 23.2493 | 0.0059319
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512805 | SALNCRK5 | 161 | 17.8109 | 17.9164 | 0.0059233
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512865 | GREC TAP5 | 345 | 24.9005 | 25.0478 | 0.0059155
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300740 | 7SPORTSMAN | 345 | 23.6136 | 23.749 | 0.005734
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512812 | ARMIN 2 | 69 | 10.8395 | 10.9011 | 0.0056829
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512686 | SALINA 5 | 161 | 17.2179 | 17.3153 | 0.0056569
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512669 | KETCHUM5 | 161 | 10.2578 | 10.3142 | 0.0054983
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509804 | LLANETP4 | 138 | 26.3863 | 26.5258 | 0.0052868
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512699 | PRYORCHEM2 | 69 | 12.5184 | 12.5832 | 0.0051764
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512661 | CPPTAP 2 | 69 | 12.6182 | 12.6789 | 0.0048105
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509770 | LLAN WT4 | 138 | 23.6891 | 23.8015 | 0.0047448
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512681 | AMERCAST S2 | 69 | 12.934 | 12.9919 | 0.0044766
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512625 | MAIDTP2 | 69 | 11.6454 | 11.697 | 0.0044309
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300069 | 5CHOTEAU1 | 161 | 40.4609 | 40.6388 | 0.0043968
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301348 | 5CHOTEAU2 | 161 | 40.4609 | 40.6388 | 0.0043968
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509771 | LLAN ET4 | 138 | 23.6336 | 23.7353 | 0.0043032
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300741 | 5SPORTSMAN | 161 | 38.9761 | 39.1423 | 0.0042642
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512626 | MAID 2 | 69 | 14.1113 | 14.1698 | 0.0041456
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509720 | LLANE-W4 | 138 | 19.2616 | 19.3358 | 0.0038522
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509892 | 141PINE4 | 138 | 19.8285 | 19.9044 | 0.0038278
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512727 | GRDA1 2 | 69 | 12.0314 | 12.0774 | 0.0038233
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300274 | 5LOCSTGV | 161 | 13.111 | 13.1594 | 0.0036916
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509728 | LLANE-E4 | 138 | 19.325 | 19.3929 | 0.0035136
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509841 | PCATSAT4 | 138 | 17.472 | 17.5299 | 0.0033139
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509852 | T.NO.--7 | 345 | 22.5867 | 22.6594 | 0.0032187
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509899 | BIRDCREE-4 | 138 | 16.9241 | 16.9784 | 0.0032084
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512698 | REDDEN 2 | 69 | 10.3792 | 10.4108 | 0.0030446
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509787 | DAWSN-N4 | 138 | 17.2228 | 17.2727 | 0.0028973
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300993 | 5ELMCRK | 161 | 12.8554 | 12.8914 | 0.0028004
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512637 | 412SUB 5 | 161 | 11.4637 | 11.4954 | 0.0027653
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512632 | AFTON 5 | 161 | 8.1359 | 8.1583 | 0.0027532
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509835 | TERNITP4 | 138 | 15.6551 | 15.6979 | 0.0027339
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509886 | E41ST_W4 | 138 | 20.9176 | 20.9735 | 0.0026724
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512685 | CASTING TAP2 | 69 | 9.091 | 9.1152 | 0.002662
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512683 | AMERCAST N2 | 69 | 8.1658 | 8.1853 | 0.002388
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301344 | 5CDRCRST | 161 | 10.4498 | 10.4741 | 0.0023254
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512651 | CLARMR 5 | 161 | 12.51 | 12.5388 | 0.0023022
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509723 | TER-NIT4 | 138 | 12.9515 | 12.9807 | 0.0022546
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512750 | TONECE7 | 345 | 14.5005 | 14.5329 | 0.0022344
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512627 | COLINS 5 | 161 | 11.7421 | 11.7681 | 0.0022143
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 506935 | FLINTCR7 | 345 | 14.6814 | 14.7134 | 0.0021796
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 547487 | HOC404 5 | 161 | 12.8473 | 12.8753 | 0.0021794
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512628 | PENSA 2 | 69 | 13.0379 | 13.0661 | 0.0021629
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509786 | BA.N-ST4 | 138 | 23.2255 | 23.2754 | 0.0021485
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509725 | PCATOSA4 | 138 | 11.2036 | 11.2273 | 0.0021154
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509887 | OWAS88_4 | 138 | 16.3829 | 16.4174 | 0.0021059
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512631 | MIAMI 5 | 161 | 9.1774 | 9.196 | 0.0020267
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509843 | OWASO2_4 | 138 | 13.8307 | 13.8582 | 0.0019883
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509839 | CDC-ET 4 | 138 | 18.3658 | 18.4023 | 0.0019874
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300997 | 5KETONVL | 161 | 10.4336 | 10.4537 | 0.0019265
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512714 | KANSATP5 | 161 | 11.3325 | 11.3539 | 0.0018884
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512716 | KANSAS 5 | 161 | 10.7727 | 10.7921 | 0.0018008
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509854 | VERDIGS4 | 138 | 13.5268 | 13.5511 | 0.0017964
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512700 | WAGNOR 5 | 161 | 9.4446 | 9.4607 | 0.0017047
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512642 | SILSPWW5 | 161 | 14.2884 | 14.3105 | 0.0015467
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512633 | AFTON 2 | 69 | 10.147 | 10.1618 | 0.0014586
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509715 | CDC 4 | 138 | 13.2464 | 13.2654 | 0.0014344
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509714 | CIP 4 | 138 | 13.2554 | 13.2744 | 0.0014334
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 515252 | ROSSLAK5 | 161 | 13.2325 | 13.251 | 0.0013981
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512708 | FAIRTAP2 | 69 | 9.8061 | 9.8195 | 0.0013665
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300795 | 4OOLOGAH | 138 | 20.3525 | 20.3801 | 0.0013561
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512707 | CLARMR 4 | 138 | 13.1884 | 13.2061 | 0.0013421
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512672 | EXPL TP2 | 69 | 8.2196 | 8.2305 | 0.0013261
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512640 | OKAYGR 5 | 161 | 9.5822 | 9.5949 | 0.0013254
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512655 | TAHLQH 5 | 161 | 10.1269 | 10.1399 | 0.0012837
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512751 | TONECE5 | 161 | 14.7089 | 14.7264 | 0.0011898
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 505560 | FT GIB 5 | 161 | 10.332 | 10.3442 | 0.0011808
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512630 | MIAMI 2 | 69 | 11.8766 | 11.8906 | 0.0011788
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301455 | 2JAY (AECI) | 69 | 5.8661 | 5.873 | 0.0011762
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301307 | 5PARK | 161 | 9.0106 | 9.0209 | 0.0011431
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512705 | COLLINS4 | 138 | 8.3164 | 8.3258 | 0.0011303
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509799 | CATOOSA2 | 69 | 10.4127 | 10.4244 | 0.0011236
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512692 | CLEORTP2 | 69 | 7.3058 | 7.314 | 0.0011224
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301451 | 2GRAY TP | 69 | 6.8768 | 6.8845 | 0.0011197
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509721 | BA.NO-S4 | 138 | 12.0065 | 12.0198 | 0.0011077
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300766 | 5BRIGGSTP | 161 | 8.2541 | 8.2627 | 0.0010419
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 510415 | AFTONTP2 | 69 | 6.4472 | 6.4539 | 0.0010392
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512679 | CLARMR 2 | 69 | 12.3636 | 12.3762 | 0.0010191
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 509794 | BCIRCLE2 | 69 | 9.147 | 9.1557 | 0.00095113
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301453 | 2ZENA TP | 69 | 5.4709 | 5.476 | 0.0009322
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301452 | 2GRAY | 69 | 5.7002 | 5.7055 | 0.00092979
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512624 | CENTLFT2 | 69 | 11.0777 | 11.0879 | 0.00092077
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300767 | 5BRIGGS | 161 | 7.1793 | 7.1858 | 0.00090538
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 510427 | A-CONT 2 | 69 | 5.5085 | 5.5133 | 0.00087138
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301462 | 2COMMNEO | 69 | 8.2757 | 8.2825 | 0.00082168
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 510428 | AFTN-EX2 | 69 | 5.1862 | 5.1904 | 0.00080984
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512870 | COLNSGR2 | 69 | 9.9201 | 9.9272 | 0.00071572
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300992 | 2COLINS | 69 | 9.92 | 9.927 | 0.00070565
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301345 | 2CDRCRST | 69 | 8.0233 | 8.0285 | 0.00064811
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301454 | 2ZENA | 69 | 3.7395 | 3.7419 | 0.0006418
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301002 | 2SEQUOYA | 69 | 6.7757 | 6.7799 | 0.00061986
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512695 | ADARNEO2 | 69 | 4.7363 | 4.7392 | 0.00061229
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512647 | TAHLQH 2 | 69 | 10.9979 | 11.0046 | 0.00060921
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301460 | 2CLEORA | 69 | 3.8107 | 3.8129 | 0.00057732
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512696 | PARKER 2 | 69 | 4.4129 | 4.4152 | 0.0005212
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512646 | OKAYGR 2 | 69 | 9.5995 | 9.6045 | 0.00052086
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512725 | CHELSGR2 | 69 | 4.4584 | 4.4606 | 0.00049345
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512804 | RDFRNTP2 | 69 | 8.6747 | 8.6789 | 0.00048417
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 510409 | SAILBOA2 | 69 | 3.5802 | 3.5819 | 0.00047483
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 515014 | REDFERN2 | 69 | 8.3502 | 8.3541 | 0.00046705
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300962 | 2PEGGS | 69 | 6.1001 | 6.1029 | 0.00045901
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301472 | 2PARK | 69 | 8.171 | 8.1747 | 0.00045282
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512697 | WAGNOR 2 | 69 | 6.773 | 6.7759 | 0.00042817
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512690 | WAGNRTP2 | 69 | 6.795 | 6.7978 | 0.00041207
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512759 | WAGCTY22 | 69 | 6.229 | 6.2314 | 0.00038529
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512823 | TAH33CT2 | 69 | 7.0182 | 7.0209 | 0.00038471
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301467 | 2NEWPORT | 69 | 2.6209 | 2.6219 | 0.00038155
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301465 | 2MONKEY | 69 | 2.3385 | 2.3393 | 0.0003421
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300960 | 2LOWERY | 69 | 4.7054 | 4.707 | 0.00034003
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 515527 | HWY59TP5 | 161 | 15.6992 | 15.7041 | 0.00031212
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 504191 | HWY59 5 | 161 | 15.5028 | 15.5075 | 0.00030317
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300972 | 2WAGNERW | 69 | 4.4124 | 4.4136 | 0.00027196
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301464 | 2PYRCRNR | 69 | 0.9905 | 0.9907 | 0.00020192
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512765 | PYRCRNRTP2 | 69 | 1.6063 | 1.6066 | 0.00018676
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300955 | 2COWETA | 69 | 2.3983 | 2.3987 | 0.00016678
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512753 | TONNEC2 | 69 | 4.7099 | 4.7106 | 0.00014862
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300991 | 2CHILDRS | 69 | 1.38 | 1.3802 | 0.00014493
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512723 | CHILDRS2 | 69 | 1.3802 | 1.3804 | 0.00014491
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512728 | ARKLIN2 | 69 | 3.6464 | 3.6469 | 0.00013712
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512756 | TONECESTR2 | 69 | 3.7544 | 3.7549 | 0.00013318
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512745 | SSLINC2 | 69 | 2.7443 | 2.7446 | 0.00010932
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 300958 | 2HIGHLND | 69 | 1.8441 | 1.8443 | 0.00010845
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 301001 | 2SCOFEYV | 69 | 0.9648 | 0.9649 | 0.00010365
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512747 | SSNEWN2 | 69 | 3.034 | 3.0343 | 9.8879e-05
GEN-2017-073 | Central | 08 - North Oklahoma/South Central Kansas | 512746 | SSNORT2 | 69 | 2.7976 | 2.7978 | 7.149e-05
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 589150 | GEN-2017-077 | 138 | 5.192 | 5.8373 | 0.12429
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 589154 | G17-077-TAP | 138 | 5.5749 | 6.2387 | 0.11907
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510431 | PRY_CRK4 | 138 | 5.5867 | 6.2236 | 0.114
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510366 | MCARBDE4 | 138 | 5.7078 | 6.3044 | 0.10452
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510401 | EXCLART4 | 138 | 5.5966 | 6.1696 | 0.10238
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510419 | PRY-JCT4 | 138 | 6.0208 | 6.6262 | 0.10055
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 589120 | GEN-2017-074 | 138 | 5.9969 | 6.5998 | 0.10054
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510373 | CHOUTEA4 | 138 | 5.7192 | 6.1945 | 0.083106
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510405 | EXPCLAR4 | 138 | 4.221 | 4.5404 | 0.075669
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510398 | BIRDHOL4 | 138 | 4.2813 | 4.4412 | 0.037348
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510400 | PRY-JCT2 | 69 | 13.2696 | 13.7242 | 0.034259
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510421 | JAY 4 | 138 | 4.2956 | 4.3849 | 0.020789
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512810 | PRYORC12 | 69 | 10.4784 | 10.6227 | 0.013771
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510402 | GROVE 4 | 138 | 5.0487 | 5.1106 | 0.012261
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510387 | ADAIR--2 | 69 | 6.1071 | 6.1706 | 0.010398
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512719 | COWSKIN 4 | 138 | 4.3016 | 4.3445 | 0.009973
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510407 | PRY-JCT3 | 115 | 7.8619 | 7.9375 | 0.009616
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512622 | PRYORC32 | 69 | 9.6682 | 9.7576 | 0.0092468
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512639 | PRY0RC22 | 69 | 9.9798 | 10.06 | 0.0080362
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510408 | PCP-TAP2 | 69 | 8.091 | 8.1527 | 0.0076258
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510399 | LSTAR--3 | 115 | 9.6373 | 9.7099 | 0.0075332
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512671 | HUNT 2 | 69 | 13.2212 | 13.3129 | 0.0069358
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512634 | KERR GR3 | 115 | 16.4433 | 16.551 | 0.0065498
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510423 | L GROVE3 | 115 | 15.3902 | 15.4904 | 0.0065106
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510411 | GROVE 5 | 161 | 5.6048 | 5.6409 | 0.0064409
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510416 | HUNTAP-2 | 69 | 8.9456 | 8.9978 | 0.0058353
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512812 | ARMIN 2 | 69 | 10.8395 | 10.9011 | 0.0056829
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510425 | NEOHOME2 | 69 | 5.7529 | 5.7837 | 0.0053538
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510426 | PCPIPE 2 | 69 | 4.3118 | 4.3289 | 0.0039659
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 547496 | NOL435 5 | 161 | 9.6195 | 9.6542 | 0.0036073
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510393 | CHOUTEA2 | 69 | 5.5605 | 5.5774 | 0.0030393
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510404 | VINITA-2 | 69 | 6.7204 | 6.7351 | 0.0021874
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512717 | COWSKIN2 | 69 | 3.8702 | 3.8778 | 0.0019637
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512680 | ESH TP 2 | 69 | 6.4458 | 6.458 | 0.0018927
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 300983 | 2VINITAHQ | 69 | 5.6053 | 5.6146 | 0.0016591
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 301468 | 2ESHOSP | 69 | 5.5826 | 5.5918 | 0.001648
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510418 | VINTAJC2 | 69 | 6.3726 | 6.3831 | 0.0016477
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512673 | VINEOTP2 | 69 | 6.3038 | 6.3139 | 0.0016022
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 301463 | 2TURKEY | 69 | 3.1541 | 3.1591 | 0.0015852
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 512677 | VIN NEO2 | 69 | 5.6156 | 5.6235 | 0.0014068
GEN-2017-074 | Central | 08 - North Oklahoma/South Central Kansas | 510417 | VINTAJC4 | 138 | 4.9879 | 4.9924 | 0.00090218
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 589150 | GEN-2017-077 | 138 | 5.192 | 5.8373 | 0.12429
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 589154 | G17-077-TAP | 138 | 5.5749 | 6.2387 | 0.11907
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510431 | PRY_CRK4 | 138 | 5.5867 | 6.2236 | 0.114
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510366 | MCARBDE4 | 138 | 5.7078 | 6.3044 | 0.10452
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510401 | EXCLART4 | 138 | 5.5966 | 6.1696 | 0.10238
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510419 | PRY-JCT4 | 138 | 6.0208 | 6.6262 | 0.10055
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 589120 | GEN-2017-074 | 138 | 5.9969 | 6.5998 | 0.10054
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510373 | CHOUTEA4 | 138 | 5.7192 | 6.1945 | 0.083106
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510405 | EXPCLAR4 | 138 | 4.221 | 4.5404 | 0.075669
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510437 | ROCKPT-4 | 138 | 6.5227 | 6.8527 | 0.050593
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510398 | BIRDHOL4 | 138 | 4.2813 | 4.4412 | 0.037348
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510400 | PRY-JCT2 | 69 | 13.2696 | 13.7242 | 0.034259
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 509752 | INOLATP4 | 138 | 8.7677 | 9.0163 | 0.028354
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 509736 | INOLA 4 | 138 | 7.5297 | 7.7124 | 0.024264
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510421 | JAY 4 | 138 | 4.2956 | 4.3849 | 0.020789
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 512810 | PRYORC12 | 69 | 10.4784 | 10.6227 | 0.013771
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510387 | ADAIR--2 | 69 | 6.1071 | 6.1706 | 0.010398
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 510407 | PRY-JCT3 | 115 | 7.8619 | 7.9375 | 0.009616
GEN-2017-077 | Central | 08 - North Oklahoma/South Central Kansas | 509790 | CATOOSA4 | 138 | 34.4428 | 34.7238 | 0.0081585
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 589240 | GEN-2017-086 | 345 | 9.9635 | 10.5552 | 0.059387
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532798 | VIOLA 7 | 345 | 13.8783 | 14.4624 | 0.042087
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533075 | VIOLA 4 | 138 | 24.0364 | 24.4751 | 0.018251
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588364 | G16-153-TAP | 345 | 7.4618 | 7.5924 | 0.017502
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588360 | GEN-2016-153 | 345 | 7.1436 | 7.2624 | 0.01663
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532792 | FR2EAST7 | 345 | 6.7405 | 6.843 | 0.015207
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515543 | RENFROW7 | 345 | 12.3872 | 12.5431 | 0.012586
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532795 | FR2WEST7 | 345 | 5.3886 | 5.4506 | 0.011506
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532780 | CANEYRV7 | 345 | 9.847 | 9.9559 | 0.011059
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515646 | GRNTWD 7 | 345 | 10.8855 | 11.0042 | 0.010904
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532781 | CANEYWF7 | 345 | 9.5894 | 9.692 | 0.010699
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 578530 | FR3HV | 345 | 4.9398 | 4.9915 | 0.010466
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532796 | WICHITA7 | 345 | 24.1532 | 24.3835 | 0.009535
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532800 | LATHAMS7 | 345 | 10.4136 | 10.5083 | 0.0090939
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539009 | CONWAY | 138 | 12.6276 | 12.7355 | 0.0085448
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539008 | MILAN_GOAB | 138 | 11.8476 | 11.9472 | 0.0084068
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532801 | ELKRVR17 | 345 | 9.1912 | 9.2645 | 0.007975
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 589060 | GEN-2017-068 | 345 | 20.1103 | 20.2698 | 0.0079313
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539676 | MILAN 4 | 138 | 10.4656 | 10.5429 | 0.0073861
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532782 | BUFFALO7 | 345 | 20.5614 | 20.7023 | 0.0068526
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539675 | MILANTP4 | 138 | 9.8621 | 9.9226 | 0.0061346
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515476 | HUNTERS7 | 345 | 13.4924 | 13.573 | 0.0059737
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515477 | CHSHLMV7 | 345 | 13.4742 | 13.5546 | 0.005967
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533044 | GILL E 4 | 138 | 21.9045 | 22.0344 | 0.0059303
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533045 | GILL W 4 | 138 | 21.9045 | 22.0344 | 0.0059303
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533046 | GILL S 4 | 138 | 21.9045 | 22.0344 | 0.0059303
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533047 | GILL 4 | 138 | 21.9045 | 22.0344 | 0.0059303
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532794 | ROSEHIL7 | 345 | 18.9572 | 19.0665 | 0.0057656
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532791 | BENTON 7 | 345 | 19.6359 | 19.7468 | 0.0056478
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533036 | CLEARWT4 | 138 | 14.0937 | 14.1705 | 0.0054492
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533071 | WACO S 4 | 138 | 19.1512 | 19.2466 | 0.0049814
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533072 | WACO 4 | 138 | 19.1512 | 19.2466 | 0.0049814
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587500 | GEN-2016-073 | 345 | 15.119 | 15.1939 | 0.004954
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533040 | EVANS N4 | 138 | 33.3755 | 33.5322 | 0.0046951
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533041 | EVANS S4 | 138 | 33.3755 | 33.5322 | 0.0046951
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533062 | ROSEHIL4 | 138 | 30.8868 | 31.0133 | 0.0040956
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533039 | ELPASO 4 | 138 | 24.1926 | 24.2863 | 0.0038731
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533059 | ELPASOE4 | 138 | 24.1926 | 24.2863 | 0.0038731
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515544 | RENFROW4 | 138 | 14.3714 | 14.4241 | 0.003667
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533074 | 45TH ST4 | 138 | 24.1728 | 24.2608 | 0.0036405
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533029 | 59TH ST4 | 138 | 17.0897 | 17.1516 | 0.0036221
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532986 | BENTON 4 | 138 | 27.8896 | 27.9879 | 0.0035246
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533795 | GILL E 2 | 69 | 29.2006 | 29.301 | 0.0034383
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533796 | GILL W 2 | 69 | 29.2006 | 29.301 | 0.0034383
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533051 | INTERST4 | 138 | 15.7061 | 15.7592 | 0.0033809
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533049 | HOOVERN4 | 138 | 17.1453 | 17.2018 | 0.0032954
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539003 | CLDWELL4 | 138 | 5.5937 | 5.6121 | 0.0032894
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533038 | COWSKIN4 | 138 | 17.5293 | 17.5823 | 0.0030235
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532991 | WEAVER 4 | 138 | 21.7367 | 21.8021 | 0.0030087
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533035 | CHISHLM4 | 138 | 21.2936 | 21.3567 | 0.0029633
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533053 | LAKERDG4 | 138 | 17.2997 | 17.3508 | 0.0029538
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533054 | MAIZE 4 | 138 | 21.0644 | 21.1262 | 0.0029339
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533068 | STEARMN4 | 138 | 19.1751 | 19.2296 | 0.0028422
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514715 | WOODRNG7 | 345 | 19.0903 | 19.1426 | 0.0027396
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533052 | PARKCTY4 | 138 | 20.1019 | 20.1569 | 0.0027361
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533060 | NOEASTE4 | 138 | 20.2888 | 20.3433 | 0.0026862
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533065 | SG12COL4 | 138 | 19.7318 | 19.7841 | 0.0026505
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533042 | FARBER 4 | 138 | 15.7644 | 15.806 | 0.0026389
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515569 | MDFRDTP4 | 138 | 11.4762 | 11.5063 | 0.0026228
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533851 | VULCTP 2 | 69 | 22.0309 | 22.0878 | 0.0025827
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533064 | 17TH 4 | 138 | 17.2325 | 17.2761 | 0.0025301
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588320 | GEN-2016-162 | 345 | 9.7523 | 9.7768 | 0.0025122
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533024 | 29TH 4 | 138 | 19.377 | 19.4255 | 0.002503
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 520409 | WFEC_RNFRO4 | 138 | 10.6021 | 10.628 | 0.0024429
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532988 | BELAIRE4 | 138 | 18.7482 | 18.7936 | 0.0024216
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533037 | COMOTAR4 | 138 | 18.4588 | 18.5033 | 0.0024108
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539668 | HARPER 4 | 138 | 7.2078 | 7.2244 | 0.0023031
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539002 | BLF-CRK4 | 138 | 4.6999 | 4.7107 | 0.0022979
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532984 | SUMNER 4 | 138 | 10.2243 | 10.2477 | 0.0022887
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533850 | VULCAN 2 | 69 | 18.7158 | 18.757 | 0.0022013
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588330 | GEN-2016-163 | 345 | 8.6195 | 8.6384 | 0.0021927
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 560053 | G15-052T | 345 | 13.1034 | 13.1318 | 0.0021674
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 584900 | GEN-2015-052 | 345 | 13.0534 | 13.0815 | 0.0021527
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588630 | GEN-2017-018 | 345 | 16.3709 | 16.4054 | 0.0021074
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539801 | THISTLE7 | 345 | 16.3709 | 16.4054 | 0.0021074
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533798 | GILLJCT2 | 69 | 20.4559 | 20.4989 | 0.0021021
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533813 | MACARTH2 | 69 | 21.0946 | 21.1389 | 0.0021001
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539001 | ANTHONY4 | 138 | 5.0166 | 5.0268 | 0.0020332
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532982 | OXFORD 4 | 138 | 9.3635 | 9.3817 | 0.0019437
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 562476 | G14-001-TAP | 345 | 10.6079 | 10.6282 | 0.0019137
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533063 | SC10BEL4 | 138 | 9.6835 | 9.702 | 0.0019105
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532797 | WOLFCRK7 | 345 | 18.0814 | 18.1154 | 0.0018804
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532783 | KINGMAN7 | 345 | 6.821 | 6.8327 | 0.0017153
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 522397 | MEDFORD4 | 138 | 7.4872 | 7.5 | 0.0017096
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 542981 | LACYGNE7 | 345 | 24.761 | 24.8029 | 0.0016922
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532771 | RENO 7 | 345 | 12.6248 | 12.6459 | 0.0016713
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 543629 | LACYGNE11_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 543632 | LACYGNE22_7 | 345 | 24.1469 | 24.1868 | 0.0016524
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532799 | WAVERLY7 | 345 | 16.0356 | 16.0608 | 0.0015715
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533804 | HAYSVJN2 | 69 | 13.5493 | 13.5691 | 0.0014613
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515546 | GRANTCO4 | 138 | 6.4548 | 6.4642 | 0.0014563
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533786 | CHISHLM2 | 69 | 19.7124 | 19.7409 | 0.0014458
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 560084 | G16-061-TAP | 345 | 16.1024 | 16.125 | 0.0014035
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587410 | GEN-2016-061 | 345 | 16.1024 | 16.125 | 0.0014035
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532990 | MIDIAN 4 | 138 | 10.5446 | 10.5589 | 0.0013561
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532784 | NINN1WF7 | 345 | 5.6816 | 5.6893 | 0.0013553
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532987 | BUTLER 4 | 138 | 10.362 | 10.3759 | 0.0013414
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532802 | WAVERTX7 | 345 | 13.4196 | 13.437 | 0.0012966
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533015 | BENTLEY4 | 138 | 10.8046 | 10.8186 | 0.0012957
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539000 | RAGO 4 | 138 | 3.9456 | 3.9506 | 0.0012672
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514803 | SOONER 7 | 345 | 27.048 | 27.0822 | 0.0012644
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539804 | THISTLE4 | 138 | 17.4802 | 17.502 | 0.0012471
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 583850 | GEN-2014-001 | 345 | 7.0819 | 7.0906 | 0.0012285
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532992 | TIMBJCT4 | 138 | 5.8655 | 5.8727 | 0.0012275
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539638 | FLATRDG4 | 138 | 15.5121 | 15.5308 | 0.0012055
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 585250 | GEN-2015-090 | 345 | 5.0769 | 5.0829 | 0.0011818
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514825 | KAYWIND7 | 345 | 12.6052 | 12.6199 | 0.0011662
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515621 | OPENSKY7 | 345 | 12.64 | 12.6547 | 0.001163
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 522398 | PONDCRK4 | 138 | 5.091 | 5.0969 | 0.0011589
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515877 | REDDIRT7 | 345 | 18.0507 | 18.0716 | 0.0011578
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515875 | REDNGTN7 | 345 | 18.0549 | 18.0758 | 0.0011576
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515426 | RDRUNNR4 | 138 | 8.4138 | 8.4234 | 0.001141
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532985 | TCROCK 4 | 138 | 5.4745 | 5.4807 | 0.0011325
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588190 | GEN-2016-128 | 345 | 7.9459 | 7.9545 | 0.0010823
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533016 | WWUPLNT4 | 138 | 8.1516 | 8.1596 | 0.0009814
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532981 | CRESWLN4 | 138 | 9.1264 | 9.1352 | 0.00096424
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533803 | HAYSV 2 | 69 | 8.5824 | 8.5901 | 0.00089718
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533597 | MIDIANW2 | 69 | 13.8298 | 13.8422 | 0.00089661
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587884 | G16-111-TAP | 345 | 11.3773 | 11.3875 | 0.00089652
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533011 | HALSTD 4 | 138 | 8.3248 | 8.3322 | 0.00088891
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515581 | COYOTE 4 | 138 | 8.2619 | 8.2692 | 0.00088357
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 520434 | WAKTASW4 | 138 | 6.3232 | 6.3287 | 0.00086981
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515852 | DGRASSE7 | 345 | 14.5452 | 14.5578 | 0.00086627
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 520452 | WAKTASB4 | 138 | 6.2893 | 6.2947 | 0.0008586
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533802 | HAYSVJS2 | 69 | 7.9127 | 7.9194 | 0.00084674
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587460 | GEN-2016-068 | 345 | 6.5264 | 6.5319 | 0.00084273
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587910 | GEN-2016-114 | 345 | 10.1469 | 10.155 | 0.00079827
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539631 | FLATRWD4 | 138 | 10.3583 | 10.3664 | 0.00078198
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533416 | RENO 3 | 115 | 26.7821 | 26.8023 | 0.00075424
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533543 | CRESWLN2 | 69 | 12.9226 | 12.9321 | 0.00073515
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533573 | CRESWLS2 | 69 | 12.9226 | 12.9321 | 0.00073515
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533555 | SC7CRES2 | 69 | 12.7271 | 12.7363 | 0.00072287
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 584570 | GEN-2015-015 | 138 | 5.8242 | 5.8284 | 0.00072113
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515497 | MATHWSN7 | 345 | 33.2303 | 33.254 | 0.0007132
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533558 | TIMBJCT2 | 69 | 8.1517 | 8.1575 | 0.00071151
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514804 | MIDLTNT4 | 138 | 9.0073 | 9.0136 | 0.00069943
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515547 | GRANTCO2 | 69 | 7.4693 | 7.4742 | 0.00065602
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514714 | WOODRNG4 | 138 | 20.0668 | 20.0796 | 0.00063787
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587894 | G16-112-TAP | 345 | 11.1782 | 11.1849 | 0.00059938
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533559 | UDALL 2 | 69 | 7.0322 | 7.0364 | 0.00059725
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533541 | AKRON 2 | 69 | 6.7266 | 6.7306 | 0.00059465
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514709 | FRMNTAP4 | 138 | 18.7487 | 18.7597 | 0.00058671
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 542965 | W.GRDNR7 | 345 | 24.8262 | 24.8406 | 0.00058003
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533013 | MOUND 4 | 138 | 6.9434 | 6.9474 | 0.00057609
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533070 | SLATECRK4 | 138 | 6.7318 | 6.7356 | 0.00056448
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587480 | GEN-2016-071 | 138 | 7.4626 | 7.4667 | 0.00054941
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587880 | GEN-2016-111 | 345 | 7.1243 | 7.1281 | 0.00053339
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 521198 | CHILOCCO4 | 138 | 6.7544 | 6.758 | 0.00053299
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533413 | CIRCLE 3 | 115 | 23.6123 | 23.6235 | 0.00047433
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515894 | THUNDER7 | 345 | 11.3237 | 11.329 | 0.00046804
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514711 | WAUKOTP4 | 138 | 16.069 | 16.0765 | 0.00046674
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533421 | HEC GT 3 | 115 | 22.9426 | 22.953 | 0.00045331
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539800 | CLARKCOUNTY7 | 345 | 13.2594 | 13.2652 | 0.00043743
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533419 | HEC 3 | 115 | 21.8737 | 21.8832 | 0.00043431
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533429 | MOUNDRG3 | 115 | 8.6474 | 8.6511 | 0.00042787
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533561 | WINFLD 2 | 69 | 6.3557 | 6.3584 | 0.00042482
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514739 | MEDFORD2 | 69 | 5.4515 | 5.4538 | 0.0004219
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532768 | EMPEC 7 | 345 | 17.5987 | 17.6059 | 0.00040912
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532769 | LANG 7 | 345 | 17.3797 | 17.3867 | 0.00040277
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 520447 | BLUFCRK4 | 138 | 3.7612 | 3.7627 | 0.00039881
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532773 | SUMMIT 7 | 345 | 12.1324 | 12.1372 | 0.00039563
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515375 | WWRDEHV7 | 345 | 19.8126 | 19.8204 | 0.00039369
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533626 | BURLJCT2 | 69 | 4.8155 | 4.8173 | 0.00037379
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 584170 | GEN-2014-064 | 138 | 9.641 | 9.6446 | 0.00037341
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 583370 | GEN-2012-024 | 345 | 11.3107 | 11.3148 | 0.00036249
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514708 | OTTER 4 | 138 | 9.7166 | 9.7201 | 0.00036021
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515853 | DGRASSE4 | 138 | 15.3869 | 15.3923 | 0.00035095
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539852 | P1 MPT PRI | 345 | 10.7671 | 10.7708 | 0.00034364
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533653 | WOLFCRK2 | 69 | 5.8582 | 5.8601 | 0.00032433
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 582008 | GEN-2011-008 | 345 | 10.514 | 10.5174 | 0.00032338
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514719 | CLYDE 2 | 69 | 4.4044 | 4.4058 | 0.00031786
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 585100 | GEN-2015-073 | 345 | 13.3961 | 13.4002 | 0.00030606
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 560080 | G16-046-TAP | 345 | 11.4289 | 11.4323 | 0.00029749
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 521085 | WAKITA 2 | 69 | 5.1561 | 5.1576 | 0.00029092
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 539857 | P2 MPT PRI | 345 | 9.1297 | 9.1323 | 0.00028478
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533551 | SC1KING2 | 69 | 3.2879 | 3.2888 | 0.00027373
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533628 | CC1BURL2 | 69 | 3.3205 | 3.3214 | 0.00027104
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533624 | BURLING2 | 69 | 3.3336 | 3.3345 | 0.00026998
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 582908 | G-2011-008-2 | 345 | 8.4349 | 8.4371 | 0.00026082
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 582708 | G-2011-008-1 | 345 | 8.5619 | 8.564 | 0.00024527
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587310 | GEN-2016-046 | 345 | 9.8417 | 9.8441 | 0.00024386
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533629 | CC2SHAR2 | 69 | 4.545 | 4.5461 | 0.00024202
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532774 | SWISVAL7 | 345 | 16.163 | 16.1669 | 0.00024129
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 531469 | SPERVIL7 | 345 | 13.7357 | 13.739 | 0.00024025
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533625 | BURLIND2 | 69 | 2.9763 | 2.977 | 0.00023519
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587980 | GEN-2016-122 | 345 | 5.2087 | 5.2099 | 0.00023038
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532871 | CIRCLE 6 | 230 | 10.0555 | 10.0578 | 0.00022873
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 515599 | G07621119-20 | 345 | 13.2006 | 13.2036 | 0.00022726
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533546 | FLORALJ2 | 69 | 2.7316 | 2.7322 | 0.00021965
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 514733 | MARSHL 4 | 138 | 8.4007 | 8.4025 | 0.00021427
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 521006 | MARSHAL4 | 138 | 8.4007 | 8.4025 | 0.00021427
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533412 | ARKVALJ3 | 115 | 10.8426 | 10.8449 | 0.00021213
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533411 | ARKVAL 3 | 115 | 10.6123 | 10.6145 | 0.00020731
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 585430 | PRSIMN_CRK1 | 345 | 11.6164 | 11.6188 | 0.0002066
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533415 | DAVIS 3 | 115 | 8.7128 | 8.7146 | 0.00020659
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533557 | TIMBER 2 | 69 | 2.4233 | 2.4238 | 0.00020633
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 587890 | GEN-2016-112 | 345 | 4.6684 | 4.6693 | 0.00019279
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532770 | MORRIS 7 | 345 | 12.8665 | 12.8689 | 0.00018653
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533414 | CITIES 3 | 115 | 8.5877 | 8.5893 | 0.00018631
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 585440 | PRSIMN_CRK2 | 345 | 10.6077 | 10.6096 | 0.00017912
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533545 | FLORAL 2 | 69 | 2.4109 | 2.4113 | 0.00016591
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 585410 | GREAT_WESTRN | 345 | 9.9457 | 9.9473 | 0.00016087
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532856 | SWISVAL6 | 230 | 20.9983 | 21.0016 | 0.00015716
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533380 | SPRGCRK3 | 115 | 3.8099 | 3.8104 | 0.00013124
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532863 | MORRIS 6 | 230 | 13.9585 | 13.9603 | 0.00012895
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 543659 | LACYGNE2 | 69 | 8.4733 | 8.4743 | 0.00011802
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533369 | HILSBOR3 | 115 | 2.5456 | 2.5459 | 0.00011785
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 585420 | COWBOY_RIDGE | 345 | 7.6718 | 7.6727 | 0.00011731
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533438 | WMCPHER3 | 115 | 15.7555 | 15.7573 | 0.00011425
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533304 | LANG 3 | 115 | 14.5028 | 14.5044 | 0.00011032
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 900001 | TRAVERSE1 | 345 | 7.3837 | 7.3845 | 0.00010835
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533428 | MCPHER 3 | 115 | 15.7273 | 15.729 | 0.00010809
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533506 | DAVIS 2 | 69 | 7.4951 | 7.4959 | 0.00010674
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 532766 | JEC N 7 | 345 | 23.7584 | 23.7608 | 0.00010102
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533529 | MWIRNJ22 | 69 | 6.5493 | 6.5499 | 9.1613e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588310 | GEN-2016-158 | 345 | 4.6245 | 4.6249 | 8.6496e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 588300 | GEN-2016-157 | 345 | 4.8983 | 4.8987 | 8.1661e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533519 | MWIRONJ2 | 69 | 6.1417 | 6.1422 | 8.1411e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533518 | MWIRON 2 | 69 | 6.3596 | 6.3601 | 7.8621e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533426 | MANVILE3 | 115 | 11.7012 | 11.7021 | 7.6915e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533505 | NCTYSVC2 | 69 | 3.9782 | 3.9785 | 7.5411e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 900002 | TRAVERSE2 | 345 | 5.7164 | 5.7168 | 6.9974e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 900003 | TRAVERSE3 | 345 | 5.1972 | 5.1975 | 5.7723e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533394 | CORONAD3 | 115 | 7.6677 | 7.6681 | 5.2167e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533504 | CITYSVC2 | 69 | 3.9513 | 3.9515 | 5.0616e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 533439 | WHEATLD3 | 115 | 7.9438 | 7.9442 | 5.0354e-05
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 543669 | LAC8_STAR7 | 345 | 0.6133 | 0.6133 | 0
GEN-2017-086 | Central | 08 - North Oklahoma/South Central Kansas | 543667 | LAC3_STAR7 | 345 | 0.6403 | 0.6403 | 0
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 589300 | GEN-2017-092 | 345 | 9.3838 | 9.9032 | 0.055351
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588810 | GEN-2017-040 | 345 | 10.5528 | 11.1329 | 0.054971
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588839 | FIREWHL-TAP | 345 | 10.7008 | 11.2888 | 0.054949
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588834 | FWL-WND-SWYD | 345 | 10.7008 | 11.2888 | 0.054949
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588838 | G17-092-SWYD | 345 | 10.7008 | 11.2888 | 0.054949
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515422 | C-RIVER7 | 345 | 9.8234 | 9.9892 | 0.016878
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515224 | MUSKOGE7 | 345 | 28.6169 | 28.9683 | 0.012279
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515249 | BEGGS 4 | 138 | 5.4729 | 5.5141 | 0.007528
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515235 | PECANCK7 | 345 | 21.3829 | 21.5268 | 0.0067297
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510946 | C-RIVER4 | 138 | 12.8883 | 12.9719 | 0.0064865
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510907 | PITTSB-7 | 345 | 13.6566 | 13.7363 | 0.005836
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510925 | KIOWA 7 | 345 | 13.4158 | 13.4927 | 0.005732
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510380 | DELWARE7 | 345 | 10.9307 | 10.9927 | 0.0056721
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509745 | CLARKSV7 | 345 | 19.5998 | 19.6788 | 0.0040307
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588039 | G16133G16146 | 345 | 28.8139 | 28.9088 | 0.0032935
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509782 | R.S.S.-7 | 345 | 28.8139 | 28.9088 | 0.0032935
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509807 | ONETA--7 | 345 | 26.6084 | 26.6954 | 0.0032696
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510406 | N.E.S.-7 | 345 | 15.8275 | 15.8785 | 0.0032222
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509852 | T.NO.--7 | 345 | 22.5867 | 22.6594 | 0.0032187
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509836 | OEC 7 | 345 | 26.3545 | 26.4393 | 0.0032177
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509834 | COGENT 7 | 345 | 26.6803 | 26.7611 | 0.0030285
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515234 | PECANCK5 | 161 | 20.9267 | 20.9845 | 0.002762
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509783 | R.S.S.-4 | 138 | 59.4345 | 59.5979 | 0.0027492
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510951 | TALAWANDA 4 | 138 | 9.6276 | 9.6531 | 0.0026486
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509806 | ONETA--4 | 138 | 47.2399 | 47.3648 | 0.002644
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509870 | SAPLPRD7 | 345 | 22.2177 | 22.2751 | 0.0025835
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509755 | WEKIWA-7 | 345 | 18.6818 | 18.7267 | 0.0024034
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509875 | RSS T2 4 | 138 | 50.2851 | 50.4013 | 0.0023108
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509773 | RSS T1 4 | 138 | 49.413 | 49.5251 | 0.0022686
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509786 | BA.N-ST4 | 138 | 23.2255 | 23.2754 | 0.0021485
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588040 | G16133_345GS | 345 | 19.6751 | 19.7156 | 0.0020584
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510908 | MCALEST4 | 138 | 9.8253 | 9.844 | 0.0019032
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515233 | PECANCK4 | 138 | 9.5555 | 9.5735 | 0.0018837
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515228 | 5TRIBES5 | 161 | 15.4215 | 15.4503 | 0.0018675
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509871 | SAPLPRD4 | 138 | 32.0377 | 32.0936 | 0.0017448
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515230 | AGENCY 5 | 161 | 14.0106 | 14.0335 | 0.0016345
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515250 | HANCOK-5 | 161 | 14.1046 | 14.1276 | 0.0016307
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 506948 | SILOAM 5 | 161 | 21.0049 | 21.039 | 0.0016234
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515045 | SEMINOL7 | 345 | 26.7023 | 26.7438 | 0.0015542
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510909 | MCALESTIND 4 | 138 | 5.5912 | 5.5998 | 0.0015381
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515251 | EUCLID 5 | 161 | 13.7075 | 13.7284 | 0.0015247
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510906 | SMCALTP4 | 138 | 8.4625 | 8.4751 | 0.0014889
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 506944 | CHAMSPR5 | 161 | 21.9263 | 21.9572 | 0.0014093
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588041 | G16133_765GS | 765 | 6.6077 | 6.6167 | 0.001362
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 506945 | CHAMSPR7 | 345 | 9.5419 | 9.5542 | 0.0012891
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509891 | BA_71ST4 | 138 | 22.592 | 22.621 | 0.0012836
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514803 | SOONER 7 | 345 | 27.048 | 27.0822 | 0.0012644
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 589140 | GEN-2017-076 | 161 | 19.6452 | 19.67 | 0.0012624
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514809 | JOHNCO 7 | 345 | 9.7918 | 9.8039 | 0.0012357
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 504202 | SILOAMSP 5 | 161 | 18.7584 | 18.7808 | 0.0011941
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 506957 | TONTITN5 | 161 | 19.6592 | 19.6826 | 0.0011903
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 506978 | MATTISN5 | 161 | 19.1954 | 19.2178 | 0.0011669
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 506959 | TONTITN7 | 345 | 8.4933 | 8.5029 | 0.0011303
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510897 | LONEOAK4 | 138 | 8.7091 | 8.7189 | 0.0011253
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509721 | BA.NO-S4 | 138 | 12.0065 | 12.0198 | 0.0011077
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509769 | BA101-N4 | 138 | 19.1268 | 19.1477 | 0.0010927
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510865 | S-MCALT4 | 138 | 5.8211 | 5.8271 | 0.0010307
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509869 | 121LYNN4 | 138 | 17.2637 | 17.2807 | 0.00098473
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509768 | BA101ST4 | 138 | 18.3048 | 18.3223 | 0.00095603
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 509737 | BA101 S4 | 138 | 17.6486 | 17.6648 | 0.00091792
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 584780 | GEN-2015-036 | 345 | 6.9686 | 6.9744 | 0.0008323
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510911 | VALIANT7 | 345 | 13.1354 | 13.1462 | 0.00082221
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514934 | DRAPER 7 | 345 | 21.0498 | 21.066 | 0.0007696
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 504020 | FARMNGTN 5 | 161 | 12.1769 | 12.1858 | 0.00073089
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515497 | MATHWSN7 | 345 | 33.2303 | 33.254 | 0.0007132
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515302 | FTSMITH7 | 345 | 10.0478 | 10.0548 | 0.00069667
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515136 | SUNNYSD7 | 345 | 11.0206 | 11.0282 | 0.00068962
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514908 | ARCADIA7 | 345 | 30.6072 | 30.6277 | 0.00066978
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514880 | NORTWST7 | 345 | 33.0413 | 33.063 | 0.00065675
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514827 | CTNWOOD4 | 138 | 18.1397 | 18.1516 | 0.00065602
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515229 | AGENCY 2 | 69 | 12.9096 | 12.918 | 0.00065068
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515044 | SEMINOL4 | 138 | 40.0654 | 40.091 | 0.00063896
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515227 | 5TRIBES2 | 69 | 12.6248 | 12.6328 | 0.00063367
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514901 | CIMARON7 | 345 | 34.5896 | 34.6112 | 0.00062447
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514907 | ARCADIA4 | 138 | 43.807 | 43.8341 | 0.00061862
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 521157 | HUGO 7 | 345 | 11.1023 | 11.1089 | 0.00059447
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515461 | RNDBARN4 | 138 | 41.4854 | 41.5097 | 0.00058575
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514909 | REDBUD 7 | 345 | 28.9155 | 28.9324 | 0.00058446
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588043 | G16133_765MP | 765 | 4.0542 | 4.0565 | 0.00056731
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515075 | FRSTHIL4 | 138 | 13.8188 | 13.8266 | 0.00056445
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510921 | DUSTIN-4 | 138 | 9.3147 | 9.3198 | 0.00054752
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514933 | DRAPER 4 | 138 | 39.3786 | 39.3998 | 0.00053836
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514808 | JOHNCO 4 | 138 | 14.931 | 14.9389 | 0.0005291
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 587804 | G16-100-TAP | 345 | 21.9166 | 21.9281 | 0.00052472
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514906 | JNSKAMO4 | 138 | 20.6591 | 20.6695 | 0.00050341
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515894 | THUNDER7 | 345 | 11.3237 | 11.329 | 0.00046804
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514881 | SPRNGCK7 | 345 | 23.8462 | 23.857 | 0.0004529
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515305 | FTSMITH8 | 500 | 8.3973 | 8.4011 | 0.00045253
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515055 | MAUD 4 | 138 | 19.9584 | 19.9671 | 0.00043591
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515301 | FTSMTHW5 | 161 | 22.898 | 22.9076 | 0.00041925
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515300 | FTSMTHE5 | 161 | 23.0236 | 23.0332 | 0.00041696
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514879 | NORTWST4 | 138 | 44.3924 | 44.4108 | 0.00041449
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514946 | MIDWEST4 | 138 | 30.6139 | 30.6262 | 0.00040178
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515135 | SUNNYSD4 | 138 | 18.4585 | 18.4657 | 0.00039006
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 560088 | G16-063-TAP | 345 | 7.8302 | 7.8332 | 0.00038313
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 587430 | GEN-2016-063 | 345 | 7.7314 | 7.7343 | 0.00037509
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510899 | MCALEST2 | 69 | 4.8017 | 4.8035 | 0.00037487
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 589130 | GEN-2017-075 | 345 | 7.8196 | 7.8225 | 0.00037086
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515299 | BEVYTAP5 | 161 | 20.3431 | 20.3504 | 0.00035884
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515465 | LGARBER4 | 138 | 21.4859 | 21.4934 | 0.00034907
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 587800 | GEN-2016-100 | 345 | 14.9185 | 14.9237 | 0.00034856
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 504182 | BEVERLY5 | 161 | 19.5597 | 19.5664 | 0.00034254
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515345 | COLONY 5 | 161 | 18.2162 | 18.2223 | 0.00033487
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 520948 | HUGO PP4 | 138 | 22.1004 | 22.1078 | 0.00033484
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515122 | SXMLCKT4 | 138 | 10.9444 | 10.948 | 0.00032894
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515120 | RUSSET-4 | 138 | 11.1342 | 11.1378 | 0.00032333
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 521122 | HOWE 4 | 138 | 10.8417 | 10.8452 | 0.00032283
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515310 | QUANXTP5 | 161 | 17.5041 | 17.5096 | 0.00031421
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510918 | VALIANT4 | 138 | 14.7574 | 14.762 | 0.00031171
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515474 | QUANEXS5 | 161 | 16.5843 | 16.5893 | 0.00030149
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515178 | PARKLN 4 | 138 | 16.2138 | 16.2186 | 0.00029604
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515117 | ARBUCKL4 | 138 | 15.5845 | 15.5891 | 0.00029517
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515306 | ARKOMA 5 | 161 | 16.0234 | 16.0281 | 0.00029332
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514898 | CIMARON4 | 138 | 43.3248 | 43.3374 | 0.00029083
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515308 | 3RDST 5 | 161 | 15.4222 | 15.4265 | 0.00027882
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588670 | GEN-2017-023 | 138 | 18.3072 | 18.3123 | 0.00027858
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515003 | BARNES 4 | 138 | 15.8287 | 15.833 | 0.00027166
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515610 | FSHRTAP7 | 345 | 17.7246 | 17.7292 | 0.00025953
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588045 | G16133_765CS | 765 | 3.5157 | 3.5166 | 0.00025599
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 508298 | LYDIA 7 | 345 | 12.5635 | 12.5666 | 0.00024675
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588180 | GEN-2016-126 | 138 | 12.9061 | 12.9092 | 0.0002402
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515174 | VANOSS 4 | 138 | 13.1499 | 13.153 | 0.00023574
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514961 | GM 4 | 138 | 19.1936 | 19.1981 | 0.00023445
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515531 | VANOSTP4 | 138 | 13.2751 | 13.2782 | 0.00023352
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514949 | SOONRTP4 | 138 | 20.3707 | 20.3754 | 0.00023072
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 587950 | GEN-2016-119 | 345 | 11.7707 | 11.7734 | 0.00022938
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515150 | CANEYCK4 | 138 | 8.4199 | 8.4218 | 0.00022566
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515318 | SOTHADA4 | 138 | 11.2764 | 11.2789 | 0.0002217
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 511568 | TERRYRD7 | 345 | 9.9356 | 9.9378 | 0.00022143
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510866 | V-WEYCO4 | 138 | 9.6578 | 9.6598 | 0.00020709
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510948 | EARLSBORO 4 | 138 | 8.0011 | 8.0027 | 0.00019997
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 508072 | NWTXARK7 | 345 | 13.0046 | 13.0072 | 0.00019993
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588080 | ZONE-4 SUB | 345 | 7.8057 | 7.8072 | 0.00019217
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588046 | G16133_345CS | 345 | 7.9204 | 7.9219 | 0.00018938
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 514801 | MINCO 7 | 345 | 18.2057 | 18.2091 | 0.00018675
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515133 | BLUERIV4 | 138 | 10.4405 | 10.4424 | 0.00018198
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 587955 | GEN2016-119B | 345 | 9.8967 | 9.8985 | 0.00018188
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515444 | MCNOWND7 | 345 | 18.1495 | 18.1528 | 0.00018182
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515605 | CANADN7 | 345 | 12.9556 | 12.9579 | 0.00017753
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588100 | ZONE-6 SUB | 345 | 7.0415 | 7.0427 | 0.00017042
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 504021 | FARM_1 2 | 69 | 8.0603 | 8.0616 | 0.00016128
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588050 | ZONE-1 SUB | 345 | 6.3025 | 6.3035 | 0.00015867
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 587820 | GEN-2016-102 | 138 | 9.5679 | 9.5694 | 0.00015677
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588090 | ZONE-5 SUB | 345 | 6.5065 | 6.5075 | 0.00015369
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588070 | ZONE-3 SUB | 345 | 6.5318 | 6.5328 | 0.0001531
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515600 | KNGFSHR7 | 345 | 11.8984 | 11.9002 | 0.00015128
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515100 | PAOLI- 4 | 138 | 10.2996 | 10.3011 | 0.00014564
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 588060 | ZONE-2 SUB | 345 | 6.3129 | 6.3138 | 0.00014257
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515054 | MAUD 2 | 69 | 11.755 | 11.7566 | 0.00013611
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515114 | CHIGLEY4 | 138 | 8.0822 | 8.0833 | 0.0001361
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515177 | PARKLN 2 | 69 | 14.1839 | 14.1858 | 0.00013395
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510886 | IDABEL-4 | 138 | 6.7374 | 6.7383 | 0.00013358
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 508071 | NWTXARK4 | 138 | 24.3065 | 24.3096 | 0.00012754
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 511571 | RUSHSPR7 | 345 | 6.3575 | 6.3583 | 0.00012584
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515549 | MNCWND37 | 345 | 12.4665 | 12.468 | 0.00012032
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 563259 | GEN-2015-092 | 345 | 6.1634 | 6.1641 | 0.00011357
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515175 | IDEAL 2 | 69 | 11.8437 | 11.845 | 0.00010976
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 900001 | TRAVERSE1 | 345 | 7.3837 | 7.3845 | 0.00010835
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515097 | WLNUTCK4 | 138 | 9.2421 | 9.2431 | 0.0001082
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 507455 | TURK 7 | 345 | 8.7928 | 8.7937 | 0.00010236
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510901 | HUGO---4 | 138 | 3.4725 | 3.4728 | 8.6393e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 508359 | WELSH 7 | 345 | 20.8377 | 20.8395 | 8.6382e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 337909 | 8ANO% | 500 | 17.5426 | 17.5441 | 8.5506e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515124 | MAYSVIL4 | 138 | 6.2202 | 6.2207 | 8.0383e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 584060 | GEN-2015-057 | 345 | 9.1357 | 9.1364 | 7.6622e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 900002 | TRAVERSE2 | 345 | 5.7164 | 5.7168 | 6.9974e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510910 | VALIANT2 | 69 | 7.2552 | 7.2557 | 6.8916e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510870 | WCITYTP2 | 69 | 6.3166 | 6.317 | 6.3325e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515099 | PALIOGE2 | 69 | 8.0639 | 8.0644 | 6.2005e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515939 | MNCWND47 | 345 | 6.8065 | 6.8069 | 5.8767e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 900003 | TRAVERSE3 | 345 | 5.1972 | 5.1975 | 5.7723e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 337922 | 8P.HILL% | 500 | 15.1307 | 15.1314 | 4.6264e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515053 | PEARSNT2 | 69 | 4.4506 | 4.4508 | 4.4938e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510868 | GA PAC 2 | 69 | 2.4741 | 2.4742 | 4.0419e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515052 | TRIBBEY2 | 69 | 2.6015 | 2.6016 | 3.8439e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515637 | SRVCPLT2 | 69 | 2.6089 | 2.609 | 3.833e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515067 | PEARSON2 | 69 | 2.9482 | 2.9483 | 3.3919e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510867 | KI PMPS2 | 69 | 3.0643 | 3.0644 | 3.2634e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 511508 | BLANCHD4 | 138 | 6.5665 | 6.5667 | 3.0458e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 337912 | 5ANO% | 161 | 17.7035 | 17.704 | 2.8243e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 337811 | 8HAPPYVALY% | 500 | 24.9494 | 24.9501 | 2.8057e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 510869 | W CITY 2 | 69 | 3.8276 | 3.8277 | 2.6126e-05
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515095 | SRVCEPL2 | 69 | 2.3711 | 2.3711 | 0
GEN-2017-092 | Central | 08 - North Oklahoma/South Central Kansas | 515636 | TRIBYTP2 | 69 | 2.6045 | 2.6045 | 0
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508048 | PLEASHL2 | 69 | 7.06 | 7.08 | 0.02
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508052 | ATLANTA2 | 69 | 5.49 | 5.53 | 0.04
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508055 | BLOOMBG2 | 69 | 5.63 | 5.73 | 0.1
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508058 | IPC TAP2 | 69 | 5.61 | 5.64 | 0.03
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508089 | WATLANT2 | 69 | 8.29 | 8.31 | 0.02
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508092 | IPC 2 | 69 | 4.59 | 4.62 | 0.03
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508800 | BELCHER2 | 69 | 3.19 | 3.4 | 0.21
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508801 | BLANCH-2 | 69 | 6.8 | 6.86 | 0.06
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508803 | GILLIAM2 | 69 | 4.91 | 5.37 | 0.46
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508804 | HOSSTON2 | 69 | 5.55 | 6.3 | 0.75
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508805 | LIEBERM2 | 69 | 8.98 | 9.16 | 0.18
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508806 | LIEBERM4 | 138 | 16.85 | 16.95 | 0.1
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508807 | LINTNRD4 | 138 | 9 | 9.04 | 0.04
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508810 | NBENTON2 | 69 | 4.36 | 4.43 | 0.07
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508811 | NBENTON4 | 138 | 9.31 | 9.36 | 0.05
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508812 | OILCITY2 | 69 | 7.13 | 7.39 | 0.26
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508813 | PLAINDL2 | 69 | 3.71 | 3.88 | 0.17
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508814 | RODESSA2 | 69 | 4.3 | 4.54 | 0.24
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508815 | SUPEROR2 | 69 | 6.44 | 6.88 | 0.44
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508817 | VIVIAN 2 | 69 | 5.13 | 5.55 | 0.42
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508818 | MOTT TP2 | 69 | 3.71 | 3.86 | 0.15
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508828 | MOTT 2 | 69 | 3.29 | 3.42 | 0.13
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508830 | BALDWIN2 | 69 | 4.7 | 4.72 | 0.02
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508834 | JEFFRSN2 | 69 | 4.41 | 4.46 | 0.05
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508838 | NMARSHL2 | 69 | 9.9 | 9.91 | 0.01
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508842 | WOODLWN2 | 69 | 5.89 | 5.93 | 0.04
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 508846 | GODFREYRDTP2 | 69 | 4.31 | 4.56 | 0.25
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 588404 | G16-167-TAP | 138 | 10.01 | 10.07 | 0.06
GEN-2017-057 | South | 10 - Southeast Oklahoma/Northeast Texas | 588950 | GEN-2017-057 | 69 | 4.9 | 5.66 | 0.76
GEN-2017-060 | Central | 12 - Northwest Arkansas | 588980 | GEN-2017-060 | 161 | 5.1425 | 5.7501 | 0.11815
GEN-2017-060 | Central | 12 - Northwest Arkansas | 589200 | GEN-2017-082 | 161 | 6.5984 | 7.2138 | 0.093265
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547476 | ASB349 5 | 161 | 9.8099 | 10.4272 | 0.062926
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547479 | LAR382 5 | 161 | 12.5231 | 13.142 | 0.049421
GEN-2017-060 | Central | 12 - Northwest Arkansas | 532932 | LITCH 5 | 161 | 8.3258 | 8.6426 | 0.03805
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547491 | PUR421 5 | 161 | 8.8 | 9.0825 | 0.032102
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505488 | CARTHAG5 | 161 | 14.9914 | 15.4083 | 0.027809
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547477 | CJ 366 5 | 161 | 11.5152 | 11.8216 | 0.026608
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547485 | CAR395 5 | 161 | 11.2875 | 11.576 | 0.025559
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547490 | FIR417 5 | 161 | 13.2874 | 13.595 | 0.02315
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547467 | ORO110 5 | 161 | 18.1203 | 18.4918 | 0.020502
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547466 | ATL109 5 | 161 | 15.0356 | 15.3285 | 0.01948
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547494 | OAK432 5 | 161 | 16.4794 | 16.8003 | 0.019473
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547480 | MON383 5 | 161 | 10.9918 | 11.1548 | 0.014829
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547470 | JOP145 5 | 161 | 16.8006 | 17.0133 | 0.01266
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547498 | STL439 5 | 161 | 23.602 | 23.8627 | 0.011046
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547469 | RIV4525 | 161 | 22.9986 | 23.2407 | 0.010527
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547503 | RIV452T 5 | 161 | 22.6118 | 22.8433 | 0.010238
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547459 | WWR477 | 161 | 21.5641 | 21.7815 | 0.010082
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547483 | JOP389 5 | 161 | 19.1974 | 19.3878 | 0.009918
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547472 | TIP292 5 | 161 | 16.7605 | 16.9246 | 0.0097909
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547502 | RIV167 5 | 161 | 21.3713 | 21.578 | 0.0096718
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547501 | RIV453 5 | 161 | 21.8449 | 22.056 | 0.0096636
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505486 | NEO SPA5 | 161 | 14.7701 | 14.8979 | 0.0086526
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547500 | RNM393 5 | 161 | 13.7156 | 13.824 | 0.0079034
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505490 | CARTHG 2 | 69 | 13.1587 | 13.2582 | 0.0075615
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547471 | NEO184 5 | 161 | 13.648 | 13.7498 | 0.007459
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547462 | SVRCK469 5 | 161 | 13.7285 | 13.8296 | 0.0073642
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547593 | JOP391 5 | 161 | 12.9002 | 12.9942 | 0.0072867
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547533 | ATL109 2 | 69 | 19.9663 | 20.1099 | 0.0071921
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547607 | JOP422 5 | 161 | 12.75 | 12.8397 | 0.0070353
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547468 | AUR124 5 | 161 | 9.8562 | 9.9248 | 0.0069601
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547534 | ORO110 2 | 69 | 17.3555 | 17.4606 | 0.0060557
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547595 | RNM393 2 | 69 | 18.615 | 18.7164 | 0.0054472
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547556 | OAK280 2 | 69 | 15.3404 | 15.4233 | 0.005404
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547591 | MON383 2 | 69 | 11.8616 | 11.9195 | 0.0048813
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547588 | JOP372 2 | 69 | 14.7519 | 14.8184 | 0.0045079
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547581 | JOP360 2 | 69 | 13.6161 | 13.6768 | 0.004458
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547540 | MON152 2 | 69 | 10.3092 | 10.3513 | 0.0040837
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547608 | JOP430 2 | 69 | 15.2468 | 15.309 | 0.0040795
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547685 | PLB447 2 | 69 | 13.8559 | 13.9104 | 0.0039333
GEN-2017-060 | Central | 12 - Northwest Arkansas | 506934 | FLINTCR5 | 161 | 31.8219 | 31.9414 | 0.0037553
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547592 | JOP389 2 | 69 | 14.7987 | 14.8527 | 0.003649
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547564 | SOL315 2 | 69 | 9.9339 | 9.969 | 0.0035334
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547463 | KOD471 2 | 69 | 11.6008 | 11.6403 | 0.0034049
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547537 | AUR124 2 | 69 | 11.7987 | 11.8376 | 0.003297
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547499 | CPK446 5 | 161 | 8.1479 | 8.1745 | 0.0032646
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547405 | MON352J2 | 69 | 7.4624 | 7.4853 | 0.0030687
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547527 | WEB436 2 | 69 | 9.2188 | 9.246 | 0.0029505
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547406 | MON352 2 | 69 | 7.1717 | 7.1928 | 0.0029421
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300751 | 2REEDS | 69 | 6.2071 | 6.2235 | 0.0026421
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547407 | MON311J2 | 69 | 6.3976 | 6.4143 | 0.0026104
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547559 | TIP292 2 | 69 | 9.5721 | 9.5969 | 0.0025909
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505492 | SPRGFLD5 | 161 | 26.7935 | 26.8628 | 0.0025864
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547401 | MON376 2 | 69 | 6.3182 | 6.3345 | 0.0025798
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547408 | MON311 2 | 69 | 6.3182 | 6.3345 | 0.0025798
GEN-2017-060 | Central | 12 - Northwest Arkansas | 506935 | FLINTCR7 | 345 | 14.6762 | 14.7134 | 0.0025347
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547431 | WEB105 2 | 69 | 7.7177 | 7.7371 | 0.0025137
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547543 | NEO184 2 | 69 | 11.3621 | 11.3903 | 0.0024819
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549959 | BATTLEFIELD5 | 161 | 26.1754 | 26.2398 | 0.0024603
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300745 | 2DMNDTP | 69 | 5.2979 | 5.3106 | 0.0023972
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547578 | AUR355 2 | 69 | 9.0089 | 9.0302 | 0.0023643
GEN-2017-060 | Central | 12 - Northwest Arkansas | 512750 | TONECE7 | 345 | 14.499 | 14.5329 | 0.0023381
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549969 | BROOKLINE 5 | 161 | 27.9605 | 28.0243 | 0.0022818
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547532 | CAR108 2 | 69 | 8.0727 | 8.0903 | 0.0021802
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547563 | LIN314 2 | 69 | 9.6797 | 9.7001 | 0.0021075
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300748 | 2NEOSAC | 69 | 9.6525 | 9.6722 | 0.0020409
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547438 | EXP449T2 | 69 | 8.6558 | 8.6733 | 0.0020218
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549954 | JTEC 5 | 161 | 27.0836 | 27.1381 | 0.0020123
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547496 | NOL435 5 | 161 | 9.635 | 9.6542 | 0.0019927
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547449 | PRC460 2 | 69 | 5.4449 | 5.4557 | 0.0019835
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549960 | SW DISP PLT5 | 161 | 25.2728 | 25.3226 | 0.0019705
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547560 | ROC296 2 | 69 | 8.5408 | 8.5574 | 0.0019436
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547473 | RDS295 5 | 161 | 7.4227 | 7.4368 | 0.0018996
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300680 | 2VERONA | 69 | 6.2314 | 6.2431 | 0.0018776
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547484 | DEC392 5 | 161 | 14.8357 | 14.863 | 0.0018402
GEN-2017-060 | Central | 12 - Northwest Arkansas | 506979 | SHIPERD7 | 345 | 9.9042 | 9.9224 | 0.0018376
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300762 | 2WNTWRT | 69 | 4.5233 | 4.5314 | 0.0017907
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300678 | 5NIXA-1 | 161 | 18.8008 | 18.8338 | 0.0017552
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547492 | RDS424 5 | 161 | 7.9691 | 7.9827 | 0.0017066
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549955 | JUNCTION 5 | 161 | 20.368 | 20.4025 | 0.0016938
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547439 | EXP4492 | 69 | 7.1821 | 7.194 | 0.0016569
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549958 | MAIN STREET5 | 161 | 18.5062 | 18.5366 | 0.0016427
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300750 | 2NEOSHO | 69 | 8.2235 | 8.237 | 0.0016416
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300348 | 5BTLFD | 161 | 21.7694 | 21.805 | 0.0016353
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549956 | NICHOLS 5 | 161 | 18.5381 | 18.5682 | 0.0016237
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549957 | WEST BELT 5 | 161 | 18.2824 | 18.3119 | 0.0016136
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547400 | MON376J2 | 69 | 3.9084 | 3.9146 | 0.0015863
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547618 | CPK446 2 | 69 | 9.9027 | 9.9183 | 0.0015753
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300129 | 5WASHBRN | 161 | 7.7304 | 7.7425 | 0.0015652
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547478 | DAD368 5 | 161 | 16.7205 | 16.7465 | 0.001555
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300101 | 5MORGAN | 161 | 17.7579 | 17.7855 | 0.0015542
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547553 | ALB262 2 | 69 | 8.2888 | 8.301 | 0.0014719
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547544 | WEN205 2 | 69 | 4.3134 | 4.3196 | 0.0014374
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549984 | BROOKLINE 7 | 345 | 11.272 | 11.2881 | 0.0014283
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547606 | MTV420 2 | 69 | 6.7427 | 6.7522 | 0.0014089
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300089 | 5JAMESV | 161 | 15.5561 | 15.5778 | 0.001395
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547402 | MON416J2 | 69 | 3.4446 | 3.4493 | 0.0013645
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300677 | 2MTVRN | 69 | 8.5924 | 8.6041 | 0.0013617
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547582 | SAR362T2 | 69 | 4.1908 | 4.1965 | 0.0013601
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549971 | PIC WEST 5 | 161 | 16.6881 | 16.7106 | 0.0013483
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547403 | MON416 2 | 69 | 3.3555 | 3.36 | 0.0013411
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547488 | BRN412 5 | 161 | 9.4472 | 9.4598 | 0.0013337
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300045 | 7MORGAN | 345 | 12.7077 | 12.7243 | 0.0013063
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300754 | 2SPGCTP | 69 | 5.3641 | 5.371 | 0.0012863
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300659 | 2BOWRML | 69 | 5.8389 | 5.8464 | 0.0012845
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505472 | TABLE R5 | 161 | 13.931 | 13.9484 | 0.001249
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549970 | CLAY 5 | 161 | 17.9079 | 17.9302 | 0.0012453
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505480 | BEAVER 5 | 161 | 10.1705 | 10.1829 | 0.0012192
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547497 | RVS438 5 | 161 | 11.4408 | 11.4546 | 0.0012062
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300679 | 2PRDYTP | 69 | 4.8977 | 4.9035 | 0.0011842
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547489 | BRN413 5 | 161 | 9.9369 | 9.9485 | 0.0011674
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547546 | BIL221 2 | 69 | 9.5492 | 9.5601 | 0.0011415
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549925 | NICHOLS 2 | 69 | 23.032 | 23.0582 | 0.0011375
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505496 | NIXA 5 | 161 | 12.2079 | 12.2217 | 0.0011304
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547611 | MAR437 2 | 69 | 5.7004 | 5.7067 | 0.0011052
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300744 | 2DMNDGR | 69 | 2.474 | 2.4767 | 0.0010914
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300658 | 2BILLNG | 69 | 7.9793 | 7.9876 | 0.0010402
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547626 | HOL478_5 | 161 | 9.6843 | 9.6943 | 0.0010326
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549962 | MILL 5 | 161 | 15.3487 | 15.3644 | 0.0010229
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300726 | 5RIVRDL | 161 | 11.1603 | 11.1716 | 0.0010125
GEN-2017-060 | Central | 12 - Northwest Arkansas | 504000 | AVOCA 5 | 161 | 8.7039 | 8.7126 | 0.00099955
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549963 | MENTOR 5 | 161 | 14.592 | 14.6061 | 0.00096628
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300719 | 5COMPTN | 161 | 10.7659 | 10.7763 | 0.00096601
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300805 | 5RIVERSIDE | 161 | 10.563 | 10.5731 | 0.00095617
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549961 | JAMES RIVER5 | 161 | 15.8807 | 15.8957 | 0.00094454
GEN-2017-060 | Central | 12 - Northwest Arkansas | 510411 | GROVE 5 | 161 | 5.6356 | 5.6409 | 0.00094045
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300718 | 5CLEVCOV | 161 | 11.288 | 11.2986 | 0.00093905
GEN-2017-060 | Central | 12 - Northwest Arkansas | 506932 | EUREKA 5 | 161 | 9.1859 | 9.1945 | 0.00093622
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549966 | SUMMIT 5 | 161 | 12.8209 | 12.8328 | 0.00092817
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300681 | 2BUTRFLD | 69 | 4.901 | 4.9055 | 0.00091818
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301161 | 5LOGAN | 161 | 13.985 | 13.9978 | 0.00091527
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547450 | JAS344T2 | 69 | 4.8546 | 4.859 | 0.00090636
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549921 | MAIN STREET2 | 69 | 24.9345 | 24.957 | 0.00090236
GEN-2017-060 | Central | 12 - Northwest Arkansas | 338682 | 5OSAGE CRK#! | 161 | 8.9865 | 8.9946 | 0.00090135
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300649 | 2JASPER | 69 | 4.6934 | 4.6976 | 0.00089487
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300727 | 5ROARK | 161 | 9.5421 | 9.5503 | 0.00085935
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549968 | MC CARTNEY 5 | 161 | 14.3422 | 14.3543 | 0.00084366
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300670 | 2EPURDY | 69 | 3.4475 | 3.4504 | 0.00084119
GEN-2017-060 | Central | 12 - Northwest Arkansas | 338099 | 5GRANDVIEW% | 161 | 8.4811 | 8.4882 | 0.00083716
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300949 | 7JASPER | 345 | 12.0944 | 12.1045 | 0.0008351
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549979 | BATTLEFIELD2 | 69 | 19.8269 | 19.8425 | 0.00078681
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547451 | JAS344 | 69 | 4.2248 | 4.2281 | 0.0007811
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547610 | NOL435 2 | 69 | 8.1189 | 8.1252 | 0.00077597
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549911 | GOLDEN 2 | 69 | 19.4601 | 19.4752 | 0.00077595
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549924 | LAUREL 2 | 69 | 17.3873 | 17.4007 | 0.00077068
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547566 | AND322 2 | 69 | 5.5033 | 5.5075 | 0.00076318
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300758 | 2SWTWT | 69 | 4.1047 | 4.1078 | 0.00075523
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300763 | 2WASHBRN | 69 | 6.4293 | 6.4341 | 0.00074658
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300764 | 2SPURGNTP | 69 | 3.0369 | 3.0391 | 0.00072442
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549913 | DAYTON 2 | 69 | 18.522 | 18.5353 | 0.00071807
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300824 | 2SELIGM | 69 | 5.8556 | 5.8598 | 0.00071726
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300725 | 2REEDSP | 69 | 9.7864 | 9.7931 | 0.00068462
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549918 | MILL 2 | 69 | 21.5519 | 21.5665 | 0.00067743
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301368 | 5STRAFFORD | 161 | 12.1497 | 12.1579 | 0.00067491
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547424 | RES364 2 | 69 | 3.8646 | 3.8672 | 0.00067277
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549929 | WASHINGTON 2 | 69 | 18.6318 | 18.6443 | 0.0006709
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549922 | GRAND 2 | 69 | 18.4624 | 18.4744 | 0.00064997
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300765 | 2SPURGN | 69 | 2.7775 | 2.7793 | 0.00064806
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547404 | PUR390 2 | 69 | 1.7097 | 1.7108 | 0.00064339
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505494 | SPRGFLD2 | 69 | 15.4971 | 15.507 | 0.00063883
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300667 | 2CRANE | 69 | 3.1765 | 3.1785 | 0.00062962
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549903 | JRPS 69B-2 2 | 69 | 18.8201 | 18.8319 | 0.00062699
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547430 | SAR362 2 | 69 | 1.9304 | 1.9316 | 0.00062163
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300755 | 2SPGCTY | 69 | 2.6225 | 2.6241 | 0.0006101
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549914 | FORT 2 | 69 | 16.916 | 16.9263 | 0.00060889
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300651 | 2LAMR | 69 | 9.5732 | 9.579 | 0.00060586
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549920 | HARGISS 2 | 69 | 17.3849 | 17.3953 | 0.00059822
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300666 | 2CLRKSN | 69 | 2.7085 | 2.7101 | 0.00059073
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301395 | 2ROUNDGRVETP | 69 | 4.2478 | 4.2503 | 0.00058854
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505474 | TABLE R2 | 69 | 12.906 | 12.9135 | 0.00058113
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300660 | 2BRNSPG | 69 | 3.6463 | 3.6484 | 0.00057593
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301393 | 2ROUNDGROVE | 69 | 4.0712 | 4.0735 | 0.00056494
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301360 | 2T.ROCKSW | 69 | 11.9745 | 11.9811 | 0.00055117
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549916 | BLACKMAN 2 | 69 | 17.5578 | 17.5673 | 0.00054107
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547493 | BOL431 5 | 161 | 5.7418 | 5.7449 | 0.0005399
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300735 | 2T.ROCK | 69 | 11.7126 | 11.7188 | 0.00052934
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300656 | 2JACK ST | 69 | 7.1827 | 7.1864 | 0.00051513
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549917 | INGRAM 2 | 69 | 16.3806 | 16.3889 | 0.0005067
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300685 | 2LAMARPT | 69 | 8.0932 | 8.0973 | 0.0005066
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549910 | COX 2 | 69 | 13.4604 | 13.4672 | 0.00050519
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549919 | CHAD 2 | 69 | 15.2669 | 15.2746 | 0.00050436
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549905 | PLAINVIEW 2 | 69 | 13.7275 | 13.7341 | 0.00048079
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505498 | STOCKTN5 | 161 | 9.2958 | 9.3002 | 0.00047333
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547585 | DAD368 2 | 69 | 9.3451 | 9.3495 | 0.00047083
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300794 | 5LAMAR | 161 | 8.3969 | 8.4008 | 0.00046446
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549904 | JAMES RIVER2 | 69 | 15.4348 | 15.4419 | 0.00046
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505501 | NIXA 2 | 69 | 11.9887 | 11.9941 | 0.00045042
GEN-2017-060 | Central | 12 - Northwest Arkansas | 549932 | PACKER 2 | 69 | 13.8029 | 13.809 | 0.00044194
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300118 | 5STKAEC | 161 | 8.642 | 8.6458 | 0.00043971
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300673 | 2JAMESV | 69 | 11.6561 | 11.6612 | 0.00043754
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300042 | 7HUBEN | 345 | 9.9408 | 9.9451 | 0.00043256
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300653 | 2MEDOC | 69 | 2.3693 | 2.3703 | 0.00042207
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547604 | BHJ415 2 | 69 | 10.6802 | 10.6847 | 0.00042134
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505543 | NX ESPY2 | 69 | 10.9342 | 10.9386 | 0.00040241
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300753 | 2SIMS | 69 | 3.5189 | 3.5203 | 0.00039785
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505541 | NIXA DT2 | 69 | 10.5001 | 10.5041 | 0.00038095
GEN-2017-060 | Central | 12 - Northwest Arkansas | 547428 | SWC414 2 | 69 | 3.6366 | 3.6379 | 0.00035748
GEN-2017-060 | Central | 12 - Northwest Arkansas | 505545 | NIX_SLR_U1_2 | 69 | 8.4782 | 8.4809 | 0.00031846
GEN-2017-060 | Central | 12 - Northwest Arkansas | 504001 | AVOCA_1 2 | 69 | 6.3537 | 6.3557 | 0.00031478
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300668 | 2DADEVL | 69 | 5.4435 | 5.4451 | 0.00029393
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300782 | 2MORGAN | 69 | 6.5173 | 6.5192 | 0.00029153
GEN-2017-060 | Central | 12 - Northwest Arkansas | 338120 | 5S.LEAD HILL | 161 | 6.2137 | 6.2154 | 0.00027359
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300774 | 2EUDORA | 69 | 5.4601 | 5.4613 | 0.00021978
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301362 | 2LAMRLNDFL | 69 | 3.2081 | 3.2088 | 0.0002182
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300095 | 5MANSFD | 161 | 8.7665 | 8.7684 | 0.00021673
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300652 | 2LAMRCTS | 69 | 3.7463 | 3.7471 | 0.00021354
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300663 | 2CASSIDY | 69 | 6.6196 | 6.621 | 0.00021149
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300816 | 5COLLINS | 161 | 6.298 | 6.2993 | 0.00020641
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300723 | 2PARDIS | 69 | 4.8498 | 4.8508 | 0.00020619
GEN-2017-060 | Central | 12 - Northwest Arkansas | 338554 | 2OSAGE CRK-1 | 69 | 4.4225 | 4.4234 | 0.0002035
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300800 | 2BONA | 69 | 3.2784 | 3.279 | 0.00018302
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300647 | 2BLLMYTP | 69 | 4.9819 | 4.9828 | 0.00018065
GEN-2017-060 | Central | 12 - Northwest Arkansas | 338556 | 2OSAGE CRK-2 | 69 | 3.9872 | 3.9879 | 0.00017556
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300669 | 2ELWOOD | 69 | 5.1586 | 5.1595 | 0.00017447
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300788 | 2SLAGLE | 69 | 5.7331 | 5.7341 | 0.00017443
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300081 | 5GAINES | 161 | 5.6565 | 5.6572 | 0.00012375
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301057 | 5GRVSPG | 161 | 6.711 | 6.7118 | 0.00011921
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301168 | 2MANSFL | 69 | 9.9617 | 9.9628 | 0.00011042
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300657 | 2ASHGRV | 69 | 3.8347 | 3.8351 | 0.00010431
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301128 | 5MTNGRV | 161 | 5.9308 | 5.9314 | 0.00010117
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300664 | 2CAVESP | 69 | 2.2837 | 2.2839 | 8.7577e-05
GEN-2017-060 | Central | 12 - Northwest Arkansas | 300646 | 2BELLAMY | 69 | 2.5008 | 2.501 | 7.9974e-05
GEN-2017-060 | Central | 12 - Northwest Arkansas | 301058 | 2HARTVL | 69 | 3.2259 | 3.226 | 3.0999e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 589140 | GEN-2017-076 | 161 | 19.4844 | 19.67 | 0.0095256
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506944 | CHAMSPR5 | 161 | 21.7701 | 21.9572 | 0.0085944
GEN-2017-076 | Central | 12 - Northwest Arkansas | 547471 | NEO184 5 | 161 | 13.648 | 13.7498 | 0.007459
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506945 | CHAMSPR7 | 345 | 9.5126 | 9.5542 | 0.0043731
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506957 | TONTITN5 | 161 | 19.6004 | 19.6826 | 0.0041938
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506978 | MATTISN5 | 161 | 19.1394 | 19.2178 | 0.0040963
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504202 | SILOAMSP 5 | 161 | 18.7045 | 18.7808 | 0.0040792
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506959 | TONTITN7 | 345 | 8.4699 | 8.5029 | 0.0038961
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506948 | SILOAM 5 | 161 | 20.9588 | 21.039 | 0.0038266
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506934 | FLINTCR5 | 161 | 31.8219 | 31.9414 | 0.0037553
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504010 | ELMSPRGS 5 | 161 | 16.4507 | 16.5089 | 0.0035378
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504020 | FARMNGTN 5 | 161 | 12.143 | 12.1858 | 0.0035247
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506927 | DYESS 5 | 161 | 15.7448 | 15.7987 | 0.0034234
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506956 | FARMING5 | 161 | 11.907 | 11.9461 | 0.0032838
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506947 | SFAYTVL5 | 161 | 12.1293 | 12.1669 | 0.0030999
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504201 | GENTRY 5 | 161 | 25.4989 | 25.5755 | 0.0030041
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512643 | SILMCTY5 | 161 | 19.0409 | 19.0979 | 0.0029936
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506933 | FAYETVL5 | 161 | 11.648 | 11.6817 | 0.0028932
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504274 | CARLEYRD 5 | 161 | 12.3698 | 12.405 | 0.0028456
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506983 | GREGGST5 | 161 | 11.5396 | 11.5718 | 0.0027904
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506939 | VANASCH5 | 161 | 11.819 | 11.8519 | 0.0027837
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506943 | SEFAYTV5 | 161 | 10.878 | 10.9077 | 0.0027303
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506949 | SOSPRDL5 | 161 | 11.8548 | 11.8863 | 0.0026572
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506935 | FLINTCR7 | 345 | 14.6762 | 14.7134 | 0.0025347
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506937 | HYLAND 5 | 161 | 10.1967 | 10.2223 | 0.0025106
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506985 | OSBURN | 161 | 10.4862 | 10.5114 | 0.0024032
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512750 | TONECE7 | 345 | 14.499 | 14.5329 | 0.0023381
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504015 | EFAYETVL 5 | 161 | 9.8403 | 9.8632 | 0.0023272
GEN-2017-076 | Central | 12 - Northwest Arkansas | 549969 | BROOKLINE 5 | 161 | 27.9605 | 28.0243 | 0.0022818
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506991 | BRUSHCRK_5 | 161 | 12.3195 | 12.3474 | 0.0022647
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506931 | EROGERS5 | 161 | 14.2508 | 14.2797 | 0.002028
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506938 | LOWELL 5 | 161 | 11.6918 | 11.7152 | 0.0020014
GEN-2017-076 | Central | 12 - Northwest Arkansas | 547496 | NOL435 5 | 161 | 9.635 | 9.6542 | 0.0019927
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506942 | ROGERS 5 | 161 | 12.0679 | 12.0908 | 0.0018976
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512642 | SILSPWW5 | 161 | 14.2838 | 14.3105 | 0.0018693
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512751 | TONECE5 | 161 | 14.6993 | 14.7264 | 0.0018436
GEN-2017-076 | Central | 12 - Northwest Arkansas | 547484 | DEC392 5 | 161 | 14.8357 | 14.863 | 0.0018402
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506979 | SHIPERD7 | 345 | 9.9042 | 9.9224 | 0.0018376
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504200 | WROGERS 5 | 161 | 13.3408 | 13.3644 | 0.001769
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506955 | BENT ML5 | 161 | 13.4582 | 13.4813 | 0.0017164
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506990 | GREENHOUSE 5 | 161 | 14.4557 | 14.4804 | 0.0017087
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506960 | BEN279_5 | 161 | 12.6447 | 12.6636 | 0.0014947
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506980 | SHIPERD5 | 161 | 14.7688 | 14.7908 | 0.0014896
GEN-2017-076 | Central | 12 - Northwest Arkansas | 549984 | BROOKLINE 7 | 345 | 11.272 | 11.2881 | 0.0014283
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506926 | DYESS 2 | 69 | 14.9756 | 14.9964 | 0.0013889
GEN-2017-076 | Central | 12 - Northwest Arkansas | 300045 | 7MORGAN | 345 | 12.7077 | 12.7243 | 0.0013063
GEN-2017-076 | Central | 12 - Northwest Arkansas | 505480 | BEAVER 5 | 161 | 10.1705 | 10.1829 | 0.0012192
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506950 | SPRDALE2 | 69 | 11.2835 | 11.2954 | 0.0010546
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504000 | AVOCA 5 | 161 | 8.7039 | 8.7126 | 0.00099955
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506951 | SPRDALT2 | 69 | 10.5723 | 10.5827 | 0.0009837
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506946 | SFAYTVL2 | 69 | 10.2696 | 10.2796 | 0.00097375
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512714 | KANSATP5 | 161 | 11.3431 | 11.3539 | 0.00095212
GEN-2017-076 | Central | 12 - Northwest Arkansas | 510411 | GROVE 5 | 161 | 5.6356 | 5.6409 | 0.00094045
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512716 | KANSAS 5 | 161 | 10.7825 | 10.7921 | 0.00089033
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512820 | SILMCTY2 | 69 | 13.0422 | 13.0536 | 0.00087409
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506973 | SILOAM 2 | 69 | 10.8976 | 10.9069 | 0.0008534
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512737 | SSSWTP2 | 69 | 12.1706 | 12.1805 | 0.00081344
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504021 | FARM_1 2 | 69 | 8.0553 | 8.0616 | 0.00078209
GEN-2017-076 | Central | 12 - Northwest Arkansas | 547610 | NOL435 2 | 69 | 8.1189 | 8.1252 | 0.00077597
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512730 | SSSWES2 | 69 | 11.1368 | 11.1451 | 0.00074528
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512650 | GRDA1 7 | 345 | 26.1358 | 26.1539 | 0.00069254
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504013 | ELMSPG_2 2 | 69 | 7.4705 | 7.4755 | 0.0006693
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512744 | SSMOSS2 | 69 | 10.0493 | 10.056 | 0.00066671
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506930 | EROGERS2 | 69 | 11.5581 | 11.5658 | 0.0006662
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504016 | EFAYVL_1 2 | 69 | 6.5263 | 6.5306 | 0.00065887
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506940 | NROGERS2 | 69 | 10.5868 | 10.5932 | 0.00060453
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506936 | GREENLD2 | 69 | 7.1325 | 7.1366 | 0.00057483
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509745 | CLARKSV7 | 345 | 19.6676 | 19.6788 | 0.00056946
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512637 | 412SUB 5 | 161 | 11.4891 | 11.4954 | 0.00054835
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504018 | EFAYTVL2-2 | 69 | 4.9899 | 4.9924 | 0.00050101
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504011 | ELMSPG_1 2 | 69 | 5.3983 | 5.401 | 0.00050016
GEN-2017-076 | Central | 12 - Northwest Arkansas | 547594 | DEC392 2 | 69 | 8.1957 | 8.1996 | 0.00047586
GEN-2017-076 | Central | 12 - Northwest Arkansas | 547569 | DEC467 2 | 69 | 6.963 | 6.9659 | 0.00041649
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506941 | PRGROVE2 | 69 | 4.8692 | 4.8711 | 0.00039021
GEN-2017-076 | Central | 12 - Northwest Arkansas | 506972 | LINCOLN2 | 69 | 4.6958 | 4.6975 | 0.00036203
GEN-2017-076 | Central | 12 - Northwest Arkansas | 547428 | SWC414 2 | 69 | 3.6366 | 3.6379 | 0.00035748
GEN-2017-076 | Central | 12 - Northwest Arkansas | 510380 | DELWARE7 | 345 | 10.9891 | 10.9927 | 0.0003276
GEN-2017-076 | Central | 12 - Northwest Arkansas | 504001 | AVOCA_1 2 | 69 | 6.3537 | 6.3557 | 0.00031478
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509807 | ONETA--7 | 345 | 26.6882 | 26.6954 | 0.00026978
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509836 | OEC 7 | 345 | 26.4323 | 26.4393 | 0.00026483
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512753 | TONNEC2 | 69 | 4.7094 | 4.7106 | 0.00025481
GEN-2017-076 | Central | 12 - Northwest Arkansas | 510406 | N.E.S.-7 | 345 | 15.8748 | 15.8785 | 0.00023307
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509852 | T.NO.--7 | 345 | 22.6544 | 22.6594 | 0.00022071
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512756 | TONECESTR2 | 69 | 3.7541 | 3.7549 | 0.0002131
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512728 | ARKLIN2 | 69 | 3.6462 | 3.6469 | 0.00019198
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515224 | MUSKOGE7 | 345 | 28.963 | 28.9683 | 0.00018299
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509806 | ONETA--4 | 138 | 47.3567 | 47.3648 | 0.00017104
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512747 | SSNEWN2 | 69 | 3.0338 | 3.0343 | 0.00016481
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512745 | SSLINC2 | 69 | 2.7442 | 2.7446 | 0.00014576
GEN-2017-076 | Central | 12 - Northwest Arkansas | 588039 | G16133G16146 | 345 | 28.9046 | 28.9088 | 0.00014531
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509782 | R.S.S.-7 | 345 | 28.9046 | 28.9088 | 0.00014531
GEN-2017-076 | Central | 12 - Northwest Arkansas | 512746 | SSNORT2 | 69 | 2.7974 | 2.7978 | 0.00014299
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509834 | COGENT 7 | 345 | 26.7575 | 26.7611 | 0.00013454
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515235 | PECANCK7 | 345 | 21.524 | 21.5268 | 0.00013009
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509870 | SAPLPRD7 | 345 | 22.2724 | 22.2751 | 0.00012123
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509786 | BA.N-ST4 | 138 | 23.2733 | 23.2754 | 9.0232e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509875 | RSS T2 4 | 138 | 50.3973 | 50.4013 | 7.9369e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509773 | RSS T1 4 | 138 | 49.5212 | 49.5251 | 7.8754e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509891 | BA_71ST4 | 138 | 22.6193 | 22.621 | 7.5157e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509769 | BA101-N4 | 138 | 19.1465 | 19.1477 | 6.2675e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515234 | PECANCK5 | 161 | 20.9832 | 20.9845 | 6.1954e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509869 | 121LYNN4 | 138 | 17.2797 | 17.2807 | 5.7871e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509768 | BA101ST4 | 138 | 18.3213 | 18.3223 | 5.4581e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509737 | BA101 S4 | 138 | 17.6639 | 17.6648 | 5.0951e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 509721 | BA.NO-S4 | 138 | 12.0192 | 12.0198 | 4.992e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 588810 | GEN-2017-040 | 345 | 11.1324 | 11.1329 | 4.4914e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 588838 | G17-092-SWYD | 345 | 11.2884 | 11.2888 | 3.5435e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 588839 | FIREWHL-TAP | 345 | 11.2884 | 11.2888 | 3.5435e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 588834 | FWL-WND-SWYD | 345 | 11.2884 | 11.2888 | 3.5435e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 589300 | GEN-2017-092 | 345 | 9.9029 | 9.9032 | 3.0294e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515302 | FTSMITH7 | 345 | 10.0546 | 10.0548 | 1.9891e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515301 | FTSMTHW5 | 161 | 22.9073 | 22.9076 | 1.3096e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515305 | FTSMITH8 | 500 | 8.401 | 8.4011 | 1.1903e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515422 | C-RIVER7 | 345 | 9.9891 | 9.9892 | 1.0011e-05
GEN-2017-076 | Central | 12 - Northwest Arkansas | 514908 | ARCADIA7 | 345 | 30.6274 | 30.6277 | 9.7952e-06
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515045 | SEMINOL7 | 345 | 26.7436 | 26.7438 | 7.4784e-06
GEN-2017-076 | Central | 12 - Northwest Arkansas | 510925 | KIOWA 7 | 345 | 13.4926 | 13.4927 | 7.4115e-06
GEN-2017-076 | Central | 12 - Northwest Arkansas | 510907 | PITTSB-7 | 345 | 13.7362 | 13.7363 | 7.28e-06
GEN-2017-076 | Central | 12 - Northwest Arkansas | 514909 | REDBUD 7 | 345 | 28.9322 | 28.9324 | 6.9127e-06
GEN-2017-076 | Central | 12 - Northwest Arkansas | 514934 | DRAPER 7 | 345 | 21.0659 | 21.066 | 4.747e-06
GEN-2017-076 | Central | 12 - Northwest Arkansas | 515044 | SEMINOL4 | 138 | 40.0909 | 40.091 | 2.4943e-06
GEN-2017-082 | Central | 12 - Northwest Arkansas | 588980 | GEN-2017-060 | 161 | 5.1425 | 5.7501 | 0.11815
GEN-2017-082 | Central | 12 - Northwest Arkansas | 589200 | GEN-2017-082 | 161 | 6.5984 | 7.2138 | 0.093265
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547476 | ASB349 5 | 161 | 9.8099 | 10.4272 | 0.062926
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547479 | LAR382 5 | 161 | 12.5231 | 13.142 | 0.049421
GEN-2017-082 | Central | 12 - Northwest Arkansas | 532932 | LITCH 5 | 161 | 8.3258 | 8.6426 | 0.03805
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547491 | PUR421 5 | 161 | 8.8 | 9.0825 | 0.032102
GEN-2017-082 | Central | 12 - Northwest Arkansas | 505488 | CARTHAG5 | 161 | 14.9914 | 15.4083 | 0.027809
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547477 | CJ 366 5 | 161 | 11.5152 | 11.8216 | 0.026608
GEN-2017-082 | Central | 12 - Northwest Arkansas | 532938 | FRANKLIN5 | 161 | 7.4171 | 7.6097 | 0.025967
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547485 | CAR395 5 | 161 | 11.2875 | 11.576 | 0.025559
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547490 | FIR417 5 | 161 | 13.2874 | 13.595 | 0.02315
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547467 | ORO110 5 | 161 | 18.1203 | 18.4918 | 0.020502
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547466 | ATL109 5 | 161 | 15.0356 | 15.3285 | 0.01948
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547494 | OAK432 5 | 161 | 16.4794 | 16.8003 | 0.019473
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533765 | LITCH N2 | 69 | 12.206 | 12.4335 | 0.018638
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533766 | LITCH S2 | 69 | 12.206 | 12.4335 | 0.018638
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533769 | PITNAC 2 | 69 | 10.7546 | 10.9282 | 0.016142
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547480 | MON383 5 | 161 | 10.9918 | 11.1548 | 0.014829
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533771 | ROUSE 2 | 69 | 9.1703 | 9.2932 | 0.013402
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533876 | FRANKLIN2 | 69 | 10.8288 | 10.9702 | 0.013058
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533759 | DEPAUL 2 | 69 | 9.0438 | 9.1617 | 0.013037
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547470 | JOP145 5 | 161 | 16.8006 | 17.0133 | 0.01266
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533770 | PITTSBG2 | 69 | 8.2424 | 8.3412 | 0.011987
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533775 | FRONTEN2 | 69 | 8.3192 | 8.4155 | 0.011576
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533764 | HUDSJCT2 | 69 | 7.8627 | 7.9533 | 0.011523
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533756 | AQUARS 2 | 69 | 7.82 | 7.9101 | 0.011522
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547498 | STL439 5 | 161 | 23.602 | 23.8627 | 0.011046
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533767 | MULBERY2 | 69 | 7.9236 | 8.0076 | 0.010601
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547469 | RIV4525 | 161 | 22.9986 | 23.2407 | 0.010527
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547503 | RIV452T 5 | 161 | 22.6118 | 22.8433 | 0.010238
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547459 | WWR477 | 161 | 21.5641 | 21.7815 | 0.010082
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547472 | TIP292 5 | 161 | 16.7605 | 16.9246 | 0.0097909
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547502 | RIV167 5 | 161 | 21.3713 | 21.578 | 0.0096718
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547501 | RIV453 5 | 161 | 21.8449 | 22.056 | 0.0096636
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533763 | HUDSON-2 | 69 | 6.2554 | 6.312 | 0.0090482
GEN-2017-082 | Central | 12 - Northwest Arkansas | 588504 | G17-005-TAP | 161 | 6.7929 | 6.8529 | 0.0088328
GEN-2017-082 | Central | 12 - Northwest Arkansas | 588500 | GEN-2017-005 | 161 | 6.71 | 6.7684 | 0.0087034
GEN-2017-082 | Central | 12 - Northwest Arkansas | 505486 | NEO SPA5 | 161 | 14.7701 | 14.8979 | 0.0086526
GEN-2017-082 | Central | 12 - Northwest Arkansas | 505490 | CARTHG 2 | 69 | 13.1587 | 13.2582 | 0.0075615
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547471 | NEO184 5 | 161 | 13.648 | 13.7498 | 0.007459
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547533 | ATL109 2 | 69 | 19.9663 | 20.1099 | 0.0071921
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547539 | JOP145 2 | 69 | 20.9516 | 21.0841 | 0.0063241
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547534 | ORO110 2 | 69 | 17.3555 | 17.4606 | 0.0060557
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547574 | JOP341 2 | 69 | 17.8753 | 17.9753 | 0.0055943
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547556 | OAK280 2 | 69 | 15.3404 | 15.4233 | 0.005404
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533762 | GIR JCT2 | 69 | 6.3087 | 6.3413 | 0.0051675
GEN-2017-082 | Central | 12 - Northwest Arkansas | 532934 | MARMTNE5 | 161 | 8.3607 | 8.3996 | 0.0046527
GEN-2017-082 | Central | 12 - Northwest Arkansas | 532935 | MARMTNW5 | 161 | 8.3607 | 8.3996 | 0.0046527
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547541 | RIV167 2 | 69 | 18.3903 | 18.47 | 0.0043338
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547487 | HOC404 5 | 161 | 12.821 | 12.8753 | 0.0042352
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533774 | SHEFFLD2 | 69 | 4.4202 | 4.4364 | 0.003665
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533761 | GIRARD 2 | 69 | 4.4138 | 4.4296 | 0.0035797
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547564 | SOL315 2 | 69 | 9.9339 | 9.969 | 0.0035334
GEN-2017-082 | Central | 12 - Northwest Arkansas | 532926 | BAKER 2 | 69 | 4.8588 | 4.8748 | 0.003293
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547527 | WEB436 2 | 69 | 9.2188 | 9.246 | 0.0029505
GEN-2017-082 | Central | 12 - Northwest Arkansas | 300751 | 2REEDS | 69 | 6.2071 | 6.2235 | 0.0026421
GEN-2017-082 | Central | 12 - Northwest Arkansas | 505492 | SPRGFLD5 | 161 | 26.7935 | 26.8628 | 0.0025864
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547431 | WEB105 2 | 69 | 7.7177 | 7.7371 | 0.0025137
GEN-2017-082 | Central | 12 - Northwest Arkansas | 300745 | 2DMNDTP | 69 | 5.2979 | 5.3106 | 0.0023972
GEN-2017-082 | Central | 12 - Northwest Arkansas | 543650 | DAKOTA_5 | 161 | 7.6687 | 7.6868 | 0.0023602
GEN-2017-082 | Central | 12 - Northwest Arkansas | 532937 | NEOSHO 5 | 161 | 21.328 | 21.3739 | 0.0021521
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533652 | WARE 2 | 69 | 3.444 | 3.4512 | 0.0020906
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533772 | SE1GREE2 | 69 | 5.9545 | 5.9667 | 0.0020489
GEN-2017-082 | Central | 12 - Northwest Arkansas | 547690 | GLF339 2 | 69 | 9.0855 | 9.1038 | 0.0020142
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533021 | NEOSHO 4 | 138 | 23.0646 | 23.1093 | 0.001938
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533768 | NEOSHON2 | 69 | 22.3941 | 22.4333 | 0.0017505
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533778 | NEOSHOS2 | 69 | 22.3941 | 22.4333 | 0.0017505
GEN-2017-082 | Central | 12 - Northwest Arkansas | 543651 | PRQN_WIND5 | 161 | 6.5721 | 6.5832 | 0.001689
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533758 | CRAWFOR2 | 69 | 7.1173 | 7.129 | 0.0016439
GEN-2017-082 | Central | 12 - Northwest Arkansas | 300129 | 5WASHBRN | 161 | 7.7304 | 7.7425 | 0.0015652
GEN-2017-082 | Central | 12 - Northwest Arkansas | 300744 | 2DMNDGR | 69 | 2.474 | 2.4767 | 0.0010914
GEN-2017-082 | Central | 12 - Northwest Arkansas | 300649 | 2JASPER | 69 | 4.6934 | 4.6976 | 0.00089487
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533703 | ORDNJCT2 | 69 | 8.2819 | 8.2867 | 0.00057958
GEN-2017-082 | Central | 12 - Northwest Arkansas | 300653 | 2MEDOC | 69 | 2.3693 | 2.3703 | 0.00042207
GEN-2017-082 | Central | 12 - Northwest Arkansas | 533702 | ORDNCE 2 | 69 | 5.9934 | 5.9958 | 0.00040044
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 589280 | GEN-2017-090 | 161 | 5.0958 | 6.4026 | 0.25645
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541240 | ADRIAN 5 | 161 | 7.5635 | 8.771 | 0.15965
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 301342 | 5BUTLER | 161 | 6.278 | 6.8228 | 0.086779
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541207 | ARCHIE 5 | 161 | 13.3178 | 14.1155 | 0.059897
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541239 | HSNVL 5 | 161 | 13.4501 | 13.9403 | 0.036446
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541208 | NEVADA 5 | 161 | 5.6495 | 5.7821 | 0.023471
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541341 | S.HARP 5 | 161 | 18.9418 | 19.2777 | 0.017733
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300689 | 2BUTLER | 69 | 5.7195 | 5.8125 | 0.01626
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541344 | PECULRS5 | 161 | 19.6527 | 19.9154 | 0.013367
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300707 | 2PL GAP | 69 | 4.6323 | 4.6891 | 0.012262
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300070 | 5CLARK | 161 | 7.5209 | 7.6077 | 0.011541
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300690 | 2BUTLERE | 69 | 4.5861 | 4.639 | 0.011535
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541342 | PECULR 5 | 161 | 21.0636 | 21.3042 | 0.011423
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541225 | PHILL 5 | 161 | 30.7679 | 31.0587 | 0.0094514
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541340 | BELTONS5 | 161 | 17.945 | 18.0896 | 0.008058
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300697 | 2CRESTH | 69 | 3.1272 | 3.1498 | 0.0072269
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541243 | LKWINGB5 | 161 | 23.3724 | 23.524 | 0.0064863
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300709 | 2SHARSNV | 69 | 6.1058 | 6.1445 | 0.0063382
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541313 | HARRIS | 161 | 23.0849 | 23.2294 | 0.0062595
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541308 | NEVADA 2 | 69 | 4.3826 | 4.4099 | 0.0062292
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541198 | PECULR 7 | 345 | 18.7576 | 18.8701 | 0.0059976
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300699 | 2ELYNTP | 69 | 5.8335 | 5.8684 | 0.0059827
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541307 | NEVPLT 2 | 69 | 4.1244 | 4.1486 | 0.0058675
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 542969 | STILWEL5 | 161 | 36.5596 | 36.773 | 0.005837
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300708 | 2RICHHIL | 69 | 3.0706 | 3.0878 | 0.0056015
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541249 | HOOKRD 5 | 161 | 21.6409 | 21.7609 | 0.0055451
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541218 | GRNWD 5 | 161 | 21.0848 | 21.1972 | 0.0053309
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541200 | PHILL 7 | 345 | 17.1896 | 17.2807 | 0.0052997
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541295 | HSNVL 2 | 69 | 7.9986 | 8.0406 | 0.0052509
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 542968 | STILWEL7 | 345 | 23.0198 | 23.1391 | 0.0051825
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300704 | 2METZ | 69 | 2.9821 | 2.9965 | 0.0048288
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541309 | METZ 2 | 69 | 3.3616 | 3.3778 | 0.0048191
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300700 | 2FREEMN | 69 | 2.7946 | 2.808 | 0.004795
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541311 | NEVJCT 2 | 69 | 3.314 | 3.3298 | 0.0047677
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543002 | MARTCIT5 | 161 | 22.8469 | 22.952 | 0.0046002
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300705 | 2PECULR | 69 | 3.2162 | 3.2306 | 0.0044773
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541296 | HSNVLSW2 | 69 | 7.3327 | 7.3652 | 0.0044322
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541310 | 3M 2 | 69 | 3.0569 | 3.0703 | 0.0043835
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541294 | HSNVLS 2 | 69 | 6.8003 | 6.8301 | 0.0043822
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543053 | REDEL 5 | 161 | 22.8591 | 22.9535 | 0.0041296
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300794 | 5LAMAR | 161 | 8.3677 | 8.4008 | 0.0039557
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541293 | HSNVLW 2 | 69 | 6.1627 | 6.1868 | 0.0039106
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541292 | ANCONDA2 | 69 | 6.0642 | 6.0874 | 0.0038257
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300793 | 5HYDERHL | 161 | 7.9953 | 8.0249 | 0.0037022
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 542993 | STHTOWN5 | 161 | 32.8241 | 32.9439 | 0.0036498
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541297 | HSNVLN 2 | 69 | 6.733 | 6.7568 | 0.0035348
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300802 | 2CLARK | 69 | 6.1639 | 6.1844 | 0.0033258
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300698 | 2ELYNNE | 69 | 3.1551 | 3.1654 | 0.0032646
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541316 | LONEJACK | 161 | 12.4467 | 12.4857 | 0.0031334
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 542965 | W.GRDNR7 | 345 | 24.7636 | 24.8406 | 0.0031094
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541201 | SIBLEY 7 | 345 | 19.4936 | 19.5538 | 0.0030882
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300118 | 5STKAEC | 161 | 8.6192 | 8.6458 | 0.0030861
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300814 | 2WALKER | 69 | 4.5979 | 4.612 | 0.0030666
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300688 | 2AUSTIN | 69 | 4.1597 | 4.1719 | 0.0029329
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300706 | 2PIPER | 69 | 3.5543 | 3.5643 | 0.0028135
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543050 | ANTIOCH5 | 161 | 21.2006 | 21.2597 | 0.0027877
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541414 | SIB REA1 | 345 | 17.4648 | 17.5131 | 0.0027656
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543057 | BUCYRUS5 | 161 | 19.4208 | 19.4734 | 0.0027084
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541298 | GRDNCTY2 | 69 | 3.9319 | 3.9413 | 0.0023907
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541291 | FREEMAN2 | 69 | 4.2856 | 4.2957 | 0.0023567
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541299 | GUNNPS2 | 69 | 3.7633 | 3.7719 | 0.0022852
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541343 | S.HARP 2 | 69 | 4.3341 | 4.3439 | 0.0022611
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 542994 | HICKMAN5 | 161 | 18.2777 | 18.3189 | 0.0022541
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541499 | SHELDON_69 | 69 | 1.5534 | 1.5569 | 0.0022531
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541280 | PHILL 2 | 69 | 9.9311 | 9.9532 | 0.0022253
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541279 | RGREEN 2 | 69 | 9.2094 | 9.2298 | 0.0022151
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300654 | 2MILO | 69 | 5.0888 | 5.0999 | 0.0021813
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543046 | OXFORD 5 | 161 | 19.3743 | 19.4145 | 0.0020749
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543126 | LACKMAN5 | 161 | 12.947 | 12.9708 | 0.0018383
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300950 | 5JASPER | 161 | 12.2914 | 12.3134 | 0.0017899
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300071 | 5CLINTN | 161 | 11.4578 | 11.478 | 0.001763
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541242 | CLINTON5 | 161 | 11.4194 | 11.4394 | 0.0017514
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300692 | 2CLINTN | 69 | 12.7012 | 12.7219 | 0.0016298
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300651 | 2LAMR | 69 | 9.5635 | 9.579 | 0.0016207
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543068 | WAGSTAF5 | 161 | 13.5774 | 13.5991 | 0.0015982
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 542981 | LACYGNE7 | 345 | 24.7651 | 24.8029 | 0.0015263
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543629 | LACYGNE11_7 | 345 | 24.1508 | 24.1868 | 0.0014906
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543632 | LACYGNE22_7 | 345 | 24.1508 | 24.1868 | 0.0014906
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300798 | 2HYDERHL | 69 | 7.9428 | 7.9546 | 0.0014856
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541347 | RAYMORE | 69 | 7.926 | 7.9377 | 0.0014762
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 532914 | SPRGHL 5 | 161 | 10.4977 | 10.5125 | 0.0014098
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541312 | LAMAR 2 | 69 | 0.9984 | 0.9998 | 0.0014022
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300685 | 2LAMARPT | 69 | 8.0862 | 8.0973 | 0.0013727
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541306 | APCITY 2 | 69 | 2.3412 | 2.3443 | 0.0013241
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 301477 | 5OSCEOKC | 161 | 6.1508 | 6.1587 | 0.0012844
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543058 | NLOUISB5 | 161 | 8.7654 | 8.7761 | 0.0012207
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300645 | 2BRONA | 69 | 2.1295 | 2.1314 | 0.00089223
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541304 | URICHTP2 | 69 | 3.0174 | 3.02 | 0.00086167
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541217 | WINDSR 5 | 161 | 7.094 | 7.0996 | 0.0007894
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300652 | 2LAMRCTS | 69 | 3.7447 | 3.7471 | 0.00064091
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 541305 | URICH 2 | 69 | 2.1742 | 2.1755 | 0.00059792
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 300124 | 5HOLDEN | 161 | 10.5015 | 10.5067 | 0.00049517
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 588300 | GEN-2016-157 | 345 | 4.8966 | 4.8987 | 0.00042887
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 588310 | GEN-2016-158 | 345 | 4.623 | 4.6249 | 0.00041099
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 505502 | TRUMAN 5 | 161 | 7.0374 | 7.0401 | 0.00038366
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543659 | LACYGNE2 | 69 | 8.4734 | 8.4743 | 0.00010621
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543669 | LAC8_STAR7 | 345 | 0.6133 | 0.6133 | 0
GEN-2017-090 | Central | 13 - Northeast Kansas/Northwest Missouri | 543667 | LAC3_STAR7 | 345 | 0.6403 | 0.6403 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 504124 | ASHDWN_W 4 | 138 | 9.97 | 9.98 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 505614 | BRKN BW4 | 138 | 7.62 | 7.64 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 507419 | DEQUEEN4 | 138 | 4.25 | 4.26 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 507431 | PATTERS4 | 138 | 13.11 | 13.12 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 507454 | TURK 4 | 138 | 24.61 | 24.62 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 507455 | TURK 7 | 345 | 9.03 | 9.04 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 507461 | GORDON TAP 4 | 138 | 2.68 | 2.68 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 508049 | NASH 4 | 138 | 19.53 | 19.55 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 508070 | NWT-BNT4 | 138 | 24.01 | 24.03 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 508071 | NWTXARK4 | 138 | 25.01 | 25.03 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 508072 | NWTXARK7 | 345 | 13.38 | 13.4 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 508080 | SUGARHL4 | 138 | 12.14 | 12.15 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 508298 | LYDIA 7 | 345 | 12.94 | 12.96 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 508359 | WELSH 7 | 345 | 21.37 | 21.38 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 508832 | DIANA 7 | 345 | 19.23 | 19.24 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 508841 | WILKES 7 | 345 | 15.53 | 15.53 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 510864 | B.BOW 4 | 138 | 6.36 | 6.37 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510866 | V-WEYCO4 | 138 | 10.06 | 10.08 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 510867 | KI PMPS2 | 69 | 3.19 | 3.2 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510868 | GA PAC 2 | 69 | 2.58 | 2.58 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 510869 | W CITY 2 | 69 | 3.98 | 3.99 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510870 | WCITYTP2 | 69 | 6.57 | 6.59 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 510875 | KI PMPN2 | 69 | 3.49 | 3.5 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510876 | KIPUMPT2 | 69 | 4.89 | 4.91 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 510886 | IDABEL-4 | 138 | 7.03 | 7.04 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510888 | B.BOWTP4 | 138 | 7.39 | 7.4 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510890 | CRAIGJT4 | 138 | 8.89 | 8.91 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 510893 | HUGO---2 | 69 | 5.21 | 5.23 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 510894 | VALYTIM2 | 69 | 2.78 | 2.79 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510901 | HUGO---4 | 138 | 3.62 | 3.62 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 510907 | PITTSB-7 | 345 | 14.18 | 14.19 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510910 | VALIANT2 | 69 | 7.55 | 7.57 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 510911 | VALIANT7 | 345 | 13.64 | 13.67 | 0.03
GEN-2017-023 | South | 14 - South Central Oklahoma | 510915 | ANTLTAP2 | 69 | 2.57 | 2.58 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510917 | FTOWSON2 | 69 | 3.81 | 3.82 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510918 | VALIANT4 | 138 | 15.37 | 15.41 | 0.04
GEN-2017-023 | South | 14 - South Central Oklahoma | 510920 | SAWYER 2 | 69 | 3.74 | 3.75 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510925 | KIOWA 7 | 345 | 13.92 | 13.93 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 510946 | C-RIVER4 | 138 | 13.38 | 13.39 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 511468 | L.E.S.-7 | 345 | 13.59 | 13.59 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 511568 | TERRYRD7 | 345 | 10.33 | 10.33 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 511571 | RUSHSPR7 | 345 | 6.68 | 6.68 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 514808 | JOHNCO 4 | 138 | 15.71 | 15.73 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 514809 | JOHNCO 7 | 345 | 10.26 | 10.27 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 514908 | ARCADIA7 | 345 | 30.87 | 30.87 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 514934 | DRAPER 7 | 345 | 21.39 | 21.39 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 515044 | SEMINOL4 | 138 | 41.08 | 41.09 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515045 | SEMINOL7 | 345 | 27.22 | 27.23 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515135 | SUNNYSD4 | 138 | 19.3 | 19.31 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515136 | SUNNYSD7 | 345 | 11.52 | 11.53 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515137 | UNIROY 4 | 138 | 12.98 | 12.99 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515144 | LONEGRV4 | 138 | 13.92 | 13.93 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515164 | ROCKYPT4 | 138 | 10.82 | 10.83 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515224 | MUSKOGE7 | 345 | 29.64 | 29.64 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 515422 | C-RIVER7 | 345 | 10.29 | 10.3 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 515561 | CARTRCO4 | 138 | 10.1 | 10.1 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 520411 | SAWYER4 | 138 | 10.92 | 10.97 | 0.05
GEN-2017-023 | South | 14 - South Central Oklahoma | 520419 | GARVIN4 | 138 | 6.2 | 6.22 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 520466 | HAWORTH4 | 138 | 4.29 | 4.3 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 520497 | WSTBANK4 | 138 | 5.36 | 5.38 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 520826 | BENNGTN4 | 138 | 4.86 | 4.87 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 520834 | BROKNBW4 | 138 | 7.04 | 7.05 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 520874 | DARWIN 4 | 138 | 4.98 | 4.99 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 520884 | DURANTP4 | 138 | 5.67 | 5.68 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 520918 | FROGVIL4 | 138 | 11.09 | 11.14 | 0.05
GEN-2017-023 | South | 14 - South Central Oklahoma | 520946 | HOLYCRK4 | 138 | 6.52 | 6.53 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 520948 | HUGO PP4 | 138 | 23.23 | 23.33 | 0.1
GEN-2017-023 | South | 14 - South Central Oklahoma | 520953 | IDABEL 4 | 138 | 6.27 | 6.29 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 520968 | LANE 4 | 138 | 5.23 | 5.25 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 521004 | MTRIVER4 | 138 | 8.55 | 8.56 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 521036 | RATTAN 4 | 138 | 7.12 | 7.14 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 521077 | UNGER 4 | 138 | 5.18 | 5.2 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 521079 | VALLANT4 | 138 | 8.92 | 8.96 | 0.04
GEN-2017-023 | South | 14 - South Central Oklahoma | 521098 | WSBNKTP4 | 138 | 6.88 | 6.91 | 0.03
GEN-2017-023 | South | 14 - South Central Oklahoma | 521115 | BENNSUB4 | 138 | 4.58 | 4.59 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 521157 | HUGO 7 | 345 | 11.58 | 11.61 | 0.03
GEN-2017-023 | South | 14 - South Central Oklahoma | 521187 | ATKEAST4 | 138 | 5.45 | 5.46 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 560088 | G16-063-TAP | 345 | 8.18 | 8.2 | 0.02
GEN-2017-023 | South | 14 - South Central Oklahoma | 584780 | GEN-2015-036 | 345 | 7.33 | 7.33 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 587430 | GEN-2016-063 | 345 | 8.08 | 8.09 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 588670 | GEN-2017-023 | 138 | 19.23 | 19.35 | 0.12
GEN-2017-023 | South | 14 - South Central Oklahoma | 588680 | GEN-2017-024 | 138 | 10.68 | 10.72 | 0.04
GEN-2017-023 | South | 14 - South Central Oklahoma | 588839 | FIREWHL-TAP | 345 | 11.59 | 11.59 | 0
GEN-2017-023 | South | 14 - South Central Oklahoma | 589130 | GEN-2017-075 | 345 | 8.17 | 8.18 | 0.01
GEN-2017-023 | South | 14 - South Central Oklahoma | 599892 | EASTDC 7 | 345 | 6.29 | 6.29 | 0
GEN-2017-027 | South | 14 - South Central Oklahoma | 510907 | PITTSB-7 | 345 | 14.15 | 14.19 | 0.04
GEN-2017-027 | South | 14 - South Central Oklahoma | 510911 | VALIANT7 | 345 | 13.65 | 13.67 | 0.02
GEN-2017-027 | South | 14 - South Central Oklahoma | 510925 | KIOWA 7 | 345 | 13.9 | 13.93 | 0.03
GEN-2017-027 | South | 14 - South Central Oklahoma | 511456 | O.K.U.-7 | 345 | 5.61 | 5.62 | 0.01
GEN-2017-027 | South | 14 - South Central Oklahoma | 511467 | L.E.S.-4 | 138 | 25.26 | 25.28 | 0.02
GEN-2017-027 | South | 14 - South Central Oklahoma | 511468 | L.E.S.-7 | 345 | 13.57 | 13.59 | 0.02
GEN-2017-027 | South | 14 - South Central Oklahoma | 511566 | PERNELL4 | 138 | 4.59 | 4.77 | 0.18
GEN-2017-027 | South | 14 - South Central Oklahoma | 511568 | TERRYRD7 | 345 | 10.28 | 10.33 | 0.05
GEN-2017-027 | South | 14 - South Central Oklahoma | 511571 | RUSHSPR7 | 345 | 6.67 | 6.68 | 0.01
GEN-2017-027 | South | 14 - South Central Oklahoma | 514808 | JOHNCO 4 | 138 | 15.63 | 15.73 | 0.1
GEN-2017-027 | South | 14 - South Central Oklahoma | 514809 | JOHNCO 7 | 345 | 10.18 | 10.27 | 0.09
GEN-2017-027 | South | 14 - South Central Oklahoma | 515045 | SEMINOL7 | 345 | 27.19 | 27.23 | 0.04
GEN-2017-027 | South | 14 - South Central Oklahoma | 515100 | PAOLI- 4 | 138 | 10.52 | 10.61 | 0.09
GEN-2017-027 | South | 14 - South Central Oklahoma | 515120 | RUSSET-4 | 138 | 11.72 | 11.79 | 0.07
GEN-2017-027 | South | 14 - South Central Oklahoma | 515122 | SXMLCKT4 | 138 | 11.47 | 11.52 | 0.05
GEN-2017-027 | South | 14 - South Central Oklahoma | 515124 | MAYSVIL4 | 138 | 6.3 | 6.42 | 0.12
GEN-2017-027 | South | 14 - South Central Oklahoma | 515125 | WILDHRS2 | 69 | 3.57 | 3.64 | 0.07
GEN-2017-027 | South | 14 - South Central Oklahoma | 515126 | CONTYLN2 | 69 | 4.94 | 5.08 | 0.14
GEN-2017-027 | South | 14 - South Central Oklahoma | 515127 | WLDHRST2 | 69 | 5.11 | 5.26 | 0.15
GEN-2017-027 | South | 14 - South Central Oklahoma | 515128 | RATLIFF2 | 69 | 5.21 | 5.36 | 0.15
GEN-2017-027 | South | 14 - South Central Oklahoma | 515129 | RATLIFF4 | 138 | 6.68 | 7.28 | 0.6
GEN-2017-027 | South | 14 - South Central Oklahoma | 515130 | POOLVIL4 | 138 | 8.48 | 9.82 | 1.34
GEN-2017-027 | South | 14 - South Central Oklahoma | 515131 | FOX 4 | 138 | 6.96 | 7.67 | 0.71
GEN-2017-027 | South | 14 - South Central Oklahoma | 515132 | DUNDEE 4 | 138 | 6.44 | 6.82 | 0.38
GEN-2017-027 | South | 14 - South Central Oklahoma | 515134 | PRARPNT4 | 138 | 5.55 | 5.81 | 0.26
GEN-2017-027 | South | 14 - South Central Oklahoma | 515135 | SUNNYSD4 | 138 | 18.61 | 19.31 | 0.7
GEN-2017-027 | South | 14 - South Central Oklahoma | 515136 | SUNNYSD7 | 345 | 11.33 | 11.53 | 0.2
GEN-2017-027 | South | 14 - South Central Oklahoma | 515137 | UNIROY 4 | 138 | 12.74 | 12.99 | 0.25
GEN-2017-027 | South | 14 - South Central Oklahoma | 515138 | CARTER 4 | 138 | 12.7 | 12.89 | 0.19
GEN-2017-027 | South | 14 - South Central Oklahoma | 515139 | HEALDTN2 | 69 | 4.45 | 4.54 | 0.09
GEN-2017-027 | South | 14 - South Central Oklahoma | 515140 | HLTNTAP2 | 69 | 5.23 | 5.35 | 0.12
GEN-2017-027 | South | 14 - South Central Oklahoma | 515141 | HLTNTAP4 | 138 | 6.77 | 7.12 | 0.35
GEN-2017-027 | South | 14 - South Central Oklahoma | 515142 | DILLARD4 | 138 | 7.83 | 8.14 | 0.31
GEN-2017-027 | South | 14 - South Central Oklahoma | 515143 | WOLFCRK4 | 138 | 9.78 | 10.13 | 0.35
GEN-2017-027 | South | 14 - South Central Oklahoma | 515144 | LONEGRV4 | 138 | 13.47 | 13.93 | 0.46
GEN-2017-027 | South | 14 - South Central Oklahoma | 515148 | MOBILOL2 | 69 | 3.27 | 3.33 | 0.06
GEN-2017-027 | South | 14 - South Central Oklahoma | 515150 | CANEYCK4 | 138 | 8.89 | 8.91 | 0.02
GEN-2017-027 | South | 14 - South Central Oklahoma | 515160 | MRIETA 2 | 69 | 2.09 | 2.1 | 0.01
GEN-2017-027 | South | 14 - South Central Oklahoma | 515162 | FNDTION4 | 138 | 11.88 | 12.04 | 0.16
GEN-2017-027 | South | 14 - South Central Oklahoma | 515163 | ROCKYPT2 | 69 | 8.01 | 8.05 | 0.04
GEN-2017-027 | South | 14 - South Central Oklahoma | 515164 | ROCKYPT4 | 138 | 10.66 | 10.83 | 0.17
GEN-2017-027 | South | 14 - South Central Oklahoma | 515166 | ARDMORE2 | 69 | 9.97 | 10.03 | 0.06
GEN-2017-027 | South | 14 - South Central Oklahoma | 515171 | CHIKSAW4 | 138 | 12.49 | 12.66 | 0.17
GEN-2017-027 | South | 14 - South Central Oklahoma | 515172 | SPRNDAL4 | 138 | 11.73 | 11.88 | 0.15
GEN-2017-027 | South | 14 - South Central Oklahoma | 515372 | ARDWEST4 | 138 | 12.58 | 12.81 | 0.23
GEN-2017-027 | South | 14 - South Central Oklahoma | 515415 | CHEEKTP4 | 138 | 12.2 | 12.61 | 0.41
GEN-2017-027 | South | 14 - South Central Oklahoma | 515419 | COMMRCT2 | 69 | 9.3 | 9.35 | 0.05
GEN-2017-027 | South | 14 - South Central Oklahoma | 515420 | SCMMRCT2 | 69 | 9.26 | 9.31 | 0.05
GEN-2017-027 | South | 14 - South Central Oklahoma | 515422 | C-RIVER7 | 345 | 10.29 | 10.3 | 0.01
GEN-2017-027 | South | 14 - South Central Oklahoma | 515561 | CARTRCO4 | 138 | 8.67 | 10.1 | 1.43
GEN-2017-027 | South | 14 - South Central Oklahoma | 515563 | ORIGINW4 | 138 | 5.59 | 5.9 | 0.31
GEN-2017-027 | South | 14 - South Central Oklahoma | 515570 | MAYSVLT4 | 138 | 5.93 | 6.05 | 0.12
GEN-2017-027 | South | 14 - South Central Oklahoma | 515643 | HONEYCK4 | 138 | 8.89 | 8.95 | 0.06
GEN-2017-027 | South | 14 - South Central Oklahoma | 515676 | MRIETAT2 | 69 | 2.27 | 2.27 | 0
GEN-2017-027 | South | 14 - South Central Oklahoma | 515805 | COUTYTP2 | 69 | 4.95 | 5.09 | 0.14
GEN-2017-027 | South | 14 - South Central Oklahoma | 515873 | DRPSPRG4 | 138 | 10.99 | 11.12 | 0.13
GEN-2017-027 | South | 14 - South Central Oklahoma | 515932 | STIRLNG4 | 138 | 10.13 | 10.22 | 0.09
GEN-2017-027 | South | 14 - South Central Oklahoma | 520445 | MAYSVLL4 | 138 | 5.86 | 5.98 | 0.12
GEN-2017-027 | South | 14 - South Central Oklahoma | 520948 | HUGO PP4 | 138 | 23.31 | 23.33 | 0.02
GEN-2017-027 | South | 14 - South Central Oklahoma | 521125 | CHEEK_4 | 138 | 8.63 | 8.83 | 0.2
GEN-2017-027 | South | 14 - South Central Oklahoma | 521157 | HUGO 7 | 345 | 11.59 | 11.61 | 0.02
GEN-2017-027 | South | 14 - South Central Oklahoma | 560088 | G16-063-TAP | 345 | 8.15 | 8.2 | 0.05
GEN-2017-027 | South | 14 - South Central Oklahoma | 563259 | GEN-2015-092 | 345 | 6.47 | 6.48 | 0.01
GEN-2017-027 | South | 14 - South Central Oklahoma | 584780 | GEN-2015-036 | 345 | 7.29 | 7.33 | 0.04
GEN-2017-027 | South | 14 - South Central Oklahoma | 587430 | GEN-2016-063 | 345 | 8.05 | 8.09 | 0.04
GEN-2017-027 | South | 14 - South Central Oklahoma | 587744 | G16-091-TAP | 345 | 15.02 | 15.03 | 0.01
GEN-2017-027 | South | 14 - South Central Oklahoma | 588710 | GEN-2017-027 | 138 | 8.67 | 10.1 | 1.43
GEN-2017-027 | South | 14 - South Central Oklahoma | 589130 | GEN-2017-075 | 345 | 8.14 | 8.18 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 507431 | PATTERS4 | 138 | 13.11 | 13.12 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 507454 | TURK 4 | 138 | 24.61 | 24.62 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 507455 | TURK 7 | 345 | 9.03 | 9.04 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 508049 | NASH 4 | 138 | 19.53 | 19.55 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 508070 | NWT-BNT4 | 138 | 24.01 | 24.03 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 508071 | NWTXARK4 | 138 | 25 | 25.03 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 508072 | NWTXARK7 | 345 | 13.37 | 13.4 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 508080 | SUGARHL4 | 138 | 12.14 | 12.15 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 508298 | LYDIA 7 | 345 | 12.93 | 12.96 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 508359 | WELSH 7 | 345 | 21.36 | 21.38 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 508832 | DIANA 7 | 345 | 19.23 | 19.24 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 508841 | WILKES 7 | 345 | 15.53 | 15.53 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 510866 | V-WEYCO4 | 138 | 10.06 | 10.08 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 510870 | WCITYTP2 | 69 | 6.58 | 6.59 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 510876 | KIPUMPT2 | 69 | 4.9 | 4.91 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 510886 | IDABEL-4 | 138 | 7.03 | 7.04 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 510888 | B.BOWTP4 | 138 | 7.39 | 7.4 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 510893 | HUGO---2 | 69 | 5.22 | 5.23 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 510901 | HUGO---4 | 138 | 3.62 | 3.62 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 510907 | PITTSB-7 | 345 | 14.14 | 14.19 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 510910 | VALIANT2 | 69 | 7.56 | 7.57 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 510911 | VALIANT7 | 345 | 13.58 | 13.67 | 0.09
GEN-2017-075 | South | 14 - South Central Oklahoma | 510918 | VALIANT4 | 138 | 15.36 | 15.41 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 510925 | KIOWA 7 | 345 | 13.89 | 13.93 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 510946 | C-RIVER4 | 138 | 13.37 | 13.39 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 511423 | FLE TAP4 | 138 | 9.07 | 9.07 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 511437 | COMANC-4 | 138 | 18.52 | 18.54 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 511439 | LWSTAP 4 | 138 | 11.75 | 11.75 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 511456 | O.K.U.-7 | 345 | 5.61 | 5.62 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 511466 | L.E.S.-2 | 69 | 16.98 | 16.99 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 511467 | L.E.S.-4 | 138 | 25.26 | 25.28 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 511468 | L.E.S.-7 | 345 | 13.56 | 13.59 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 511474 | SHERID4 | 138 | 12.55 | 12.56 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 511486 | ELGINJT4 | 138 | 10.25 | 10.25 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 511494 | COMMTAP4 | 138 | 22.06 | 22.08 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 511565 | OKLAUN HVDC7 | 345 | 5.6 | 5.6 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 511568 | TERRYRD7 | 345 | 10.28 | 10.33 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 511571 | RUSHSPR7 | 345 | 6.66 | 6.68 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 514808 | JOHNCO 4 | 138 | 15.66 | 15.73 | 0.07
GEN-2017-075 | South | 14 - South Central Oklahoma | 514809 | JOHNCO 7 | 345 | 10.19 | 10.27 | 0.08
GEN-2017-075 | South | 14 - South Central Oklahoma | 514908 | ARCADIA7 | 345 | 30.87 | 30.87 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 514934 | DRAPER 7 | 345 | 21.38 | 21.39 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 515044 | SEMINOL4 | 138 | 41.06 | 41.09 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 515045 | SEMINOL7 | 345 | 27.21 | 27.23 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 515120 | RUSSET-4 | 138 | 11.75 | 11.79 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 515121 | MILLCKT4 | 138 | 11.34 | 11.37 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 515122 | SXMLCKT4 | 138 | 11.48 | 11.52 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 515128 | RATLIFF2 | 69 | 5.36 | 5.36 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 515129 | RATLIFF4 | 138 | 7.27 | 7.28 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 515130 | POOLVIL4 | 138 | 9.79 | 9.82 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 515131 | FOX 4 | 138 | 7.65 | 7.67 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 515134 | PRARPNT4 | 138 | 5.8 | 5.81 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 515135 | SUNNYSD4 | 138 | 19.15 | 19.31 | 0.16
GEN-2017-075 | South | 14 - South Central Oklahoma | 515136 | SUNNYSD7 | 345 | 11.35 | 11.53 | 0.18
GEN-2017-075 | South | 14 - South Central Oklahoma | 515137 | UNIROY 4 | 138 | 12.92 | 12.99 | 0.07
GEN-2017-075 | South | 14 - South Central Oklahoma | 515138 | CARTER 4 | 138 | 12.83 | 12.89 | 0.06
GEN-2017-075 | South | 14 - South Central Oklahoma | 515143 | WOLFCRK4 | 138 | 10.08 | 10.13 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 515144 | LONEGRV4 | 138 | 13.85 | 13.93 | 0.08
GEN-2017-075 | South | 14 - South Central Oklahoma | 515147 | GLASSES4 | 138 | 8.43 | 8.46 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 515149 | MADINDT4 | 138 | 8.42 | 8.45 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 515150 | CANEYCK4 | 138 | 8.89 | 8.91 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 515151 | LTLCITY4 | 138 | 7.46 | 7.47 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 515162 | FNDTION4 | 138 | 11.99 | 12.04 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 515163 | ROCKYPT2 | 69 | 8.03 | 8.05 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 515164 | ROCKYPT4 | 138 | 10.78 | 10.83 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 515172 | SPRNDAL4 | 138 | 11.83 | 11.88 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 515224 | MUSKOGE7 | 345 | 29.64 | 29.64 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 515372 | ARDWEST4 | 138 | 12.75 | 12.81 | 0.06
GEN-2017-075 | South | 14 - South Central Oklahoma | 515415 | CHEEKTP4 | 138 | 12.54 | 12.61 | 0.07
GEN-2017-075 | South | 14 - South Central Oklahoma | 515420 | SCMMRCT2 | 69 | 9.28 | 9.31 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 515422 | C-RIVER7 | 345 | 10.28 | 10.3 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 515561 | CARTRCO4 | 138 | 10.07 | 10.1 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 515563 | ORIGINW4 | 138 | 5.89 | 5.9 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 515676 | MRIETAT2 | 69 | 2.27 | 2.27 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 515800 | GRACMNT7 | 345 | 17.39 | 17.4 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 515873 | DRPSPRG4 | 138 | 11.07 | 11.12 | 0.05
GEN-2017-075 | South | 14 - South Central Oklahoma | 515932 | STIRLNG4 | 138 | 10.18 | 10.22 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 520411 | SAWYER4 | 138 | 10.94 | 10.97 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 520419 | GARVIN4 | 138 | 6.21 | 6.22 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 520497 | WSTBANK4 | 138 | 5.37 | 5.38 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 520874 | DARWIN 4 | 138 | 4.99 | 4.99 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 520918 | FROGVIL4 | 138 | 11.1 | 11.14 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 520948 | HUGO PP4 | 138 | 23.22 | 23.33 | 0.11
GEN-2017-075 | South | 14 - South Central Oklahoma | 520953 | IDABEL 4 | 138 | 6.28 | 6.29 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 521036 | RATTAN 4 | 138 | 7.13 | 7.14 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 521044 | RUSSETT4 | 138 | 11.67 | 11.71 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 521067 | TEXOMAJ4 | 138 | 8.79 | 8.81 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 521077 | UNGER 4 | 138 | 5.19 | 5.2 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 521079 | VALLANT4 | 138 | 8.94 | 8.96 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 521098 | WSBNKTP4 | 138 | 6.89 | 6.91 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 521122 | HOWE 4 | 138 | 11.38 | 11.41 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 521125 | CHEEK_4 | 138 | 8.79 | 8.83 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 521157 | HUGO 7 | 345 | 11.49 | 11.61 | 0.12
GEN-2017-075 | South | 14 - South Central Oklahoma | 525832 | TUCO_INT 7 | 345 | 12.31 | 12.31 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 560088 | G16-063-TAP | 345 | 7.8 | 8.2 | 0.4
GEN-2017-075 | South | 14 - South Central Oklahoma | 563259 | GEN-2015-092 | 345 | 6.46 | 6.48 | 0.02
GEN-2017-075 | South | 14 - South Central Oklahoma | 584780 | GEN-2015-036 | 345 | 7.29 | 7.33 | 0.04
GEN-2017-075 | South | 14 - South Central Oklahoma | 587430 | GEN-2016-063 | 345 | 7.71 | 8.09 | 0.38
GEN-2017-075 | South | 14 - South Central Oklahoma | 587740 | GEN-2016-091 | 345 | 13.33 | 13.34 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 587744 | G16-091-TAP | 345 | 15.02 | 15.03 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 587770 | GEN-2016-095 | 345 | 11.04 | 11.05 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 588670 | GEN-2017-023 | 138 | 19.27 | 19.35 | 0.08
GEN-2017-075 | South | 14 - South Central Oklahoma | 588680 | GEN-2017-024 | 138 | 10.69 | 10.72 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 588710 | GEN-2017-027 | 138 | 10.07 | 10.1 | 0.03
GEN-2017-075 | South | 14 - South Central Oklahoma | 588760 | GEN-2017-033 | 345 | 4.11 | 4.12 | 0.01
GEN-2017-075 | South | 14 - South Central Oklahoma | 588839 | FIREWHL-TAP | 345 | 11.59 | 11.59 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 589030 | GEN-2017-065 | 345 | 5.13 | 5.13 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 589130 | GEN-2017-075 | 345 | 7.79 | 8.18 | 0.39
GEN-2017-075 | South | 14 - South Central Oklahoma | 599891 | OKLAUN 7 | 345 | 4.36 | 4.36 | 0
GEN-2017-075 | South | 14 - South Central Oklahoma | 599892 | EASTDC 7 | 345 | 6.29 | 6.29 | 0
GEN-2017-010 | North | 16 - Western North Dakota | 588550 | GEN-2017-010 | 230 | 3.927 | 4.311 | 0.384
GEN-2017-010 | North | 16 - Western North Dakota | 652219 | MI CTYE8 | 60 | 3.669 | 3.67 | 0.001
GEN-2017-010 | North | 16 - Western North Dakota | 652395 | SHIRLEY TAP | 115 | 3.057 | 3.065 | 0.008
GEN-2017-010 | North | 16 - Western North Dakota | 652402 | MI CTYW4 | 230 | 14.135 | 14.135 | 0
GEN-2017-010 | North | 16 - Western North Dakota | 652403 | DAWSONC4 | 230 | 3.987 | 4.01 | 0.023
GEN-2017-010 | North | 16 - Western North Dakota | 652404 | DAWSONC7 | 115 | 7.49 | 7.528 | 0.038
GEN-2017-010 | North | 16 - Western North Dakota | 652405 | FTPECK 4 | 230 | 2.204 | 2.205 | 0.001
GEN-2017-010 | North | 16 - Western North Dakota | 652411 | MI CTYE4 | 230 | 2.683 | 2.699 | 0.016
GEN-2017-010 | North | 16 - Western North Dakota | 652412 | MI CTYE7 | 115 | 3.86 | 3.875 | 0.015
GEN-2017-010 | North | 16 - Western North Dakota | 652424 | BELFELD3 | 345 | 6.358 | 6.393 | 0.035
GEN-2017-010 | North | 16 - Western North Dakota | 652425 | BELFELD4 | 230 | 8.803 | 8.895 | 0.092
GEN-2017-010 | North | 16 - Western North Dakota | 652450 | MT WEST4 | 230 | 14.241 | 14.241 | 0
GEN-2017-010 | North | 16 - Western North Dakota | 652468 | HEBRON 4 | 230 | 5.223 | 5.202 | -0.021
GEN-2017-010 | North | 16 - Western North Dakota | 652480 | MAURINE7 | 115 | 4.137 | 4.093 | -0.044
GEN-2017-010 | North | 16 - Western North Dakota | 652497 | MAURINE4 | 230 | 2.894 | 2.862 | -0.032
GEN-2017-010 | North | 16 - Western North Dakota | 652616 | MINGUSVILLE4 | 230 | 3.662 | 3.676 | 0.014
GEN-2017-010 | North | 16 - Western North Dakota | 652884 | NUNDRWD-LNX3 | 230 | 3.97 | 3.945 | -0.025
GEN-2017-010 | North | 16 - Western North Dakota | 655730 | CENTIPED-UM7 | 115 | 2.972 | 2.955 | -0.017
GEN-2017-010 | North | 16 - Western North Dakota | 659101 | ANTELOPE-BE3 | 345 | 16.054 | 16.036 | -0.018
GEN-2017-010 | North | 16 - Western North Dakota | 659124 | DICKINSN-BE4 | 230 | 6.689 | 6.703 | 0.014
GEN-2017-010 | North | 16 - Western North Dakota | 659125 | DICKINSON 7 | 115 | 7.997 | 7.979 | -0.018
GEN-2017-010 | North | 16 - Western North Dakota | 659182 | CHARL_CK-BE7 | 115 | 13.584 | 13.559 | -0.025
GEN-2017-010 | North | 16 - Western North Dakota | 659183 | CHARL_CK-BE3 | 345 | 9.96 | 9.972 | 0.012
GEN-2017-010 | North | 16 - Western North Dakota | 659247 | MEDORA__-UM4 | 230 | 4.944 | 4.963 | 0.019
GEN-2017-010 | North | 16 - Western North Dakota | 659249 | MILES_DC-BED | 230 | 14.135 | 14.135 | 0
GEN-2017-010 | North | 16 - Western North Dakota | 659263 | LITTL_MS-BE7 | 115 | 1.9 | 1.914 | 0.014
GEN-2017-010 | North | 16 - Western North Dakota | 659265 | LITTL_MS-BE4 | 230 | 3.323 | 3.486 | 0.163
GEN-2017-010 | North | 16 - Western North Dakota | 659266 | RHAME___-BE4 | 230 | 4.007 | 4.387 | 0.38
GEN-2017-010 | North | 16 - Western North Dakota | 659267 | RHAME___-BE7 | 115 | 2.046 | 2.055 | 0.009
GEN-2017-010 | North | 16 - Western North Dakota | 659302 | CHARL_CK-BE4 | 230 | 10.939 | 10.934 | -0.005
GEN-2017-010 | North | 16 - Western North Dakota | 659306 | S.HEART_-RR7 | 115 | 2.292 | 2.276 | -0.016
GEN-2017-010 | North | 16 - Western North Dakota | 659309 | S.HEART_-RR4 | 230 | 8.803 | 8.895 | 0.092
GEN-2017-010 | North | 16 - Western North Dakota | 659339 | BOWMAN__-BE4 | 230 | 3.556 | 3.745 | 0.189
GEN-2017-010 | North | 16 - Western North Dakota | 659340 | BOWMAN__-BE7 | 115 | 3.417 | 3.395 | -0.022
GEN-2017-010 | North | 16 - Western North Dakota | 659341 | NBURR___-GE7 | 115 | 1.794 | 1.769 | -0.025
GEN-2017-010 | North | 16 - Western North Dakota | 659350 | BISON___-GE7 | 115 | 1.487 | 1.448 | -0.039
GEN-2017-010 | North | 16 - Western North Dakota | 659351 | BISON___-GE4 | 230 | 2.823 | 2.809 | -0.014
GEN-2017-010 | North | 16 - Western North Dakota | 659352 | BISON___-GE8 | 69 | 1.989 | 1.947 | -0.042
GEN-2017-010 | North | 16 - Western North Dakota | 659384 | ROUNDUP_-BE3 | 345 | 8.155 | 8.148 | -0.007
GEN-2017-010 | North | 16 - Western North Dakota | 659390 | PATENTGT-BE3 | 345 | 6.986 | 6.979 | -0.007
GEN-2017-010 | North | 16 - Western North Dakota | 659400 | ND.SUN._-PP4 | 230 | 4.697 | 4.678 | -0.019
GEN-2017-010 | North | 16 - Western North Dakota | 659442 | 32STREET-RR7 | 115 | 1.922 | 1.908 | -0.014
GEN-2017-010 | North | 16 - Western North Dakota | 659448 | DAGLUM__-BE4 | 230 | 6.079 | 6.198 | 0.119
GEN-2017-010 | North | 16 - Western North Dakota | 659450 | BRADYWND 4 | 230 | 3.419 | 3.436 | 0.017
GEN-2017-010 | North | 16 - Western North Dakota | 659535 | BEAVRHIL-GW4 | 230 | 3.662 | 3.676 | 0.014
GEN-2017-010 | North | 16 - Western North Dakota | 661004 | BAKER 4 | 230 | 3.175 | 3.288 | 0.113
GEN-2017-010 | North | 16 - Western North Dakota | 661005 | BAKER 7 | 115 | 3.831 | 3.853 | 0.022
GEN-2017-010 | North | 16 - Western North Dakota | 661019 | MATHSON7 | 115 | 7.269 | 7.247 | -0.022
GEN-2017-010 | North | 16 - Western North Dakota | 661024 | WDICKSN7 | 115 | 6.156 | 6.131 | -0.025
GEN-2017-010 | North | 16 - Western North Dakota | 661032 | GLENDCT7 | 115 | 6.337 | 6.361 | 0.024
GEN-2017-010 | North | 16 - Western North Dakota | 661033 | CABINCR7 | 115 | 3.314 | 3.322 | 0.008
GEN-2017-010 | North | 16 - Western North Dakota | 661047 | HETINGR4 | 230 | 3.437 | 3.493 | 0.056
GEN-2017-010 | North | 16 - Western North Dakota | 661048 | HETINGR7 | 115 | 3.281 | 3.269 | -0.012
GEN-2017-010 | North | 16 - Western North Dakota | 661050 | GASCOYN7 | 115 | 1.825 | 1.808 | -0.017
GEN-2017-010 | North | 16 - Western North Dakota | 661053 | MANDAN 4 | 230 | 15.041 | 14.974 | -0.067
GEN-2017-010 | North | 16 - Western North Dakota | 661070 | N ENGLN7 | 115 | 3.581 | 3.561 | -0.02
GEN-2017-010 | North | 16 - Western North Dakota | 661300 | BAKER 8 | 60 | 5.024 | 5.016 | -0.008
GEN-2017-048 | North | 16 - Western North Dakota | 584870 | GEN-2015-046 | 345 | 4.503 | 4.619 | 0.116
GEN-2017-048 | North | 16 - Western North Dakota | 587030 | GEN-2016-004 | 230 | 7.496 | 7.463 | -0.033
GEN-2017-048 | North | 16 - Western North Dakota | 588870 | GEN-2017-048 | 230 | 4.327 | 5.262 | 0.935
GEN-2017-048 | North | 16 - Western North Dakota | 588874 | G17-048-TAP | 230 | 6.646 | 7.464 | 0.818
GEN-2017-048 | North | 16 - Western North Dakota | 603023 | MALLARD7 | 115 | 9.355 | 9.28 | -0.075
GEN-2017-048 | North | 16 - Western North Dakota | 615901 | GRE-STANTON4 | 230 | 17.86 | 17.837 | -0.023
GEN-2017-048 | North | 16 - Western North Dakota | 652216 | WATFORD4 | 230 | 6.301 | 6.309 | 0.008
GEN-2017-048 | North | 16 - Western North Dakota | 652391 | WILLISTON27 | 115 | 16.112 | 16.327 | 0.215
GEN-2017-048 | North | 16 - Western North Dakota | 652400 | WILISTN4 | 230 | 9.715 | 9.987 | 0.272
GEN-2017-048 | North | 16 - Western North Dakota | 652408 | WATFORD7 | 115 | 7.492 | 7.473 | -0.019
GEN-2017-048 | North | 16 - Western North Dakota | 652421 | WILISTN7 | 115 | 16.118 | 16.332 | 0.214
GEN-2017-048 | North | 16 - Western North Dakota | 652441 | GARRISN4 | 230 | 11.795 | 11.801 | 0.006
GEN-2017-048 | North | 16 - Western North Dakota | 652456 | WASHBRN4 | 230 | 10.055 | 10 | -0.055
GEN-2017-048 | North | 16 - Western North Dakota | 652651 | FAIRVIEW 7 | 115 | 4.697 | 4.682 | -0.015
GEN-2017-048 | North | 16 - Western North Dakota | 655641 | BERTHOLD-CP7 | 115 | 5.506 | 5.448 | -0.058
GEN-2017-048 | North | 16 - Western North Dakota | 655657 | SW.MINOT-CP7 | 115 | 7.249 | 7.184 | -0.065
GEN-2017-048 | North | 16 - Western North Dakota | 655791 | SPRINGLK-LY7 | 115 | 1.905 | 1.896 | -0.009
GEN-2017-048 | North | 16 - Western North Dakota | 655792 | NOHLEY -LY7 | 115 | 3.381 | 3.368 | -0.013
GEN-2017-048 | North | 16 - Western North Dakota | 655793 | MARLEY -LY7 | 115 | 5.603 | 5.597 | -0.006
GEN-2017-048 | North | 16 - Western North Dakota | 655840 | CHRRYCRK-MK7 | 115 | 7.492 | 7.473 | -0.019
GEN-2017-048 | North | 16 - Western North Dakota | 655879 | OASIS___-MK7 | 115 | 4.331 | 4.311 | -0.02
GEN-2017-048 | North | 16 - Western North Dakota | 655897 | COYOTCHR-MK7 | 115 | 5.394 | 5.373 | -0.021
GEN-2017-048 | North | 16 - Western North Dakota | 655902 | PLSNTV_T-MW7 | 115 | 5.662 | 5.637 | -0.025
GEN-2017-048 | North | 16 - Western North Dakota | 655909 | HESS GAS-MW7 | 115 | 9.101 | 9.187 | 0.086
GEN-2017-048 | North | 16 - Western North Dakota | 655916 | PALERMO -MW7 | 115 | 5.205 | 5.158 | -0.047
GEN-2017-048 | North | 16 - Western North Dakota | 655917 | STANLEY -MW7 | 115 | 4.643 | 4.597 | -0.046
GEN-2017-048 | North | 16 - Western North Dakota | 655918 | PALGASPL-MW7 | 115 | 4.589 | 4.542 | -0.047
GEN-2017-048 | North | 16 - Western North Dakota | 655922 | W.BANK__-MW7 | 115 | 6.448 | 6.474 | 0.026
GEN-2017-048 | North | 16 - Western North Dakota | 655923 | FARMVALE-MW7 | 115 | 4.204 | 4.191 | -0.013
GEN-2017-048 | North | 16 - Western North Dakota | 655924 | STATELIN-MW7 | 115 | 13.293 | 13.354 | 0.061
GEN-2017-048 | North | 16 - Western North Dakota | 655925 | JUDSON -MW7 | 115 | 13.251 | 13.363 | 0.112
GEN-2017-048 | North | 16 - Western North Dakota | 655926 | SW.WLSTN-MW7 | 115 | 7.899 | 7.912 | 0.013
GEN-2017-048 | North | 16 - Western North Dakota | 655930 | WHTEARTH-MW7 | 115 | 9.505 | 9.602 | 0.097
GEN-2017-048 | North | 16 - Western North Dakota | 655931 | BLKTLTAP-MW7 | 115 | 5.311 | 5.312 | 0.001
GEN-2017-048 | North | 16 - Western North Dakota | 655933 | N.MISRDG-MW7 | 115 | 9.345 | 9.396 | 0.051
GEN-2017-048 | North | 16 - Western North Dakota | 655934 | N.WLST_T-MW7 | 115 | 9.285 | 9.339 | 0.054
GEN-2017-048 | North | 16 - Western North Dakota | 655935 | NW.WLSTN-MW7 | 115 | 9.249 | 9.297 | 0.048
GEN-2017-048 | North | 16 - Western North Dakota | 655940 | MONT -MW7 | 115 | 11.593 | 11.663 | 0.07
GEN-2017-048 | North | 16 - Western North Dakota | 655941 | STRNDAHL-MW7 | 115 | 5.125 | 5.119 | -0.006
GEN-2017-048 | North | 16 - Western North Dakota | 655942 | N.TWELVE-MW7 | 115 | 5.81 | 5.826 | 0.016
GEN-2017-048 | North | 16 - Western North Dakota | 655943 | FARMVL_T-MW7 | 115 | 6.388 | 6.416 | 0.028
GEN-2017-048 | North | 16 - Western North Dakota | 655944 | PLAZA -MW7 | 115 | 3.965 | 3.931 | -0.034
GEN-2017-048 | North | 16 - Western North Dakota | 655945 | WHEELS_T-MW7 | 115 | 7.714 | 7.81 | 0.096
GEN-2017-048 | North | 16 - Western North Dakota | 655946 | POWERSLK-MW7 | 115 | 4.324 | 4.291 | -0.033
GEN-2017-048 | North | 16 - Western North Dakota | 655947 | PWRSLKTP-MW7 | 115 | 6.444 | 6.433 | -0.011
GEN-2017-048 | North | 16 - Western North Dakota | 655948 | LIBERTY -MW7 | 115 | 5.919 | 5.897 | -0.022
GEN-2017-048 | North | 16 - Western North Dakota | 655949 | BLAISDEL-MW7 | 115 | 6.679 | 6.635 | -0.044
GEN-2017-048 | North | 16 - Western North Dakota | 655952 | TIOGA.N_-MW7 | 115 | 9.132 | 9.22 | 0.088
GEN-2017-048 | North | 16 - Western North Dakota | 655953 | W.BANK_T-MW7 | 115 | 7.407 | 7.447 | 0.04
GEN-2017-048 | North | 16 - Western North Dakota | 655954 | ELLISVIL-MW7 | 115 | 4.929 | 4.934 | 0.005
GEN-2017-048 | North | 16 - Western North Dakota | 655955 | ZAHL -MW7 | 115 | 4.915 | 4.915 | 0
GEN-2017-048 | North | 16 - Western North Dakota | 655959 | EPPING -MW7 | 115 | 6.906 | 6.965 | 0.059
GEN-2017-048 | North | 16 - Western North Dakota | 659105 | LELAND_O-BE3 | 345 | 16.185 | 16.135 | -0.05
GEN-2017-048 | North | 16 - Western North Dakota | 659106 | LELAND_O-BE4 | 230 | 22.621 | 22.557 | -0.064
GEN-2017-048 | North | 16 - Western North Dakota | 659108 | LOGAN___-BE4 | 230 | 5.493 | 5.46 | -0.033
GEN-2017-048 | North | 16 - Western North Dakota | 659112 | CULBRTSN-UM7 | 115 | 4.472 | 4.473 | 0.001
GEN-2017-048 | North | 16 - Western North Dakota | 659138 | NESET___-BE4 | 230 | 8.87 | 9.376 | 0.506
GEN-2017-048 | North | 16 - Western North Dakota | 659139 | NESET___-BE7 | 115 | 10.002 | 10.122 | 0.12
GEN-2017-048 | North | 16 - Western North Dakota | 659143 | BLAISDEL-BE4 | 230 | 5.216 | 5.227 | 0.011
GEN-2017-048 | North | 16 - Western North Dakota | 659144 | BLAISDEL-BE7 | 115 | 6.881 | 6.838 | -0.043
GEN-2017-048 | North | 16 - Western North Dakota | 659151 | RICHLAND-BE7 | 115 | 5.235 | 5.222 | -0.013
GEN-2017-048 | North | 16 - Western North Dakota | 659155 | LOGAN___-BE7 | 115 | 9.459 | 9.387 | -0.072
GEN-2017-048 | North | 16 - Western North Dakota | 659183 | CHARL_CK-BE3 | 345 | 9.948 | 9.972 | 0.024
GEN-2017-048 | North | 16 - Western North Dakota | 659199 | BASIN___-BE4 | 230 | 20.601 | 20.539 | -0.062
GEN-2017-048 | North | 16 - Western North Dakota | 659262 | CULBSN.E-BE7 | 115 | 5.859 | 5.865 | 0.006
GEN-2017-048 | North | 16 - Western North Dakota | 659269 | CULB_GEN-BE7 | 115 | 5.811 | 5.82 | 0.009
GEN-2017-048 | North | 16 - Western North Dakota | 659302 | CHARL_CK-BE4 | 230 | 10.929 | 10.934 | 0.005
GEN-2017-048 | North | 16 - Western North Dakota | 659308 | KENASTON-BE7 | 115 | 3.173 | 3.129 | -0.044
GEN-2017-048 | North | 16 - Western North Dakota | 659333 | JUDSON__-BE3 | 345 | 6.72 | 6.872 | 0.152
GEN-2017-048 | North | 16 - Western North Dakota | 659334 | JUDSON__-BE4 | 230 | 9.589 | 9.838 | 0.249
GEN-2017-048 | North | 16 - Western North Dakota | 659336 | TANDE___-BE3 | 345 | 5.564 | 5.773 | 0.209
GEN-2017-048 | North | 16 - Western North Dakota | 659337 | TANDE___-BE4 | 230 | 8.75 | 9.223 | 0.473
GEN-2017-048 | North | 16 - Western North Dakota | 659362 | WHEELOCK-BE4 | 230 | 6.56 | 7.048 | 0.488
GEN-2017-048 | North | 16 - Western North Dakota | 659363 | WHEELOCK-BE7 | 115 | 7.917 | 8.038 | 0.121
GEN-2017-048 | North | 16 - Western North Dakota | 659390 | PATENTGT-BE3 | 345 | 6.914 | 6.979 | 0.065
GEN-2017-048 | North | 16 - Western North Dakota | 659404 | BURKE___-PP3 | 345 | 4.869 | 5.017 | 0.148
GEN-2017-048 | North | 16 - Western North Dakota | 659427 | TN.LS-JD-BE3 | 345 | 5.564 | 5.773 | 0.209
GEN-2017-048 | North | 16 - Western North Dakota | 661052 | KENMARE7 | 115 | 3.107 | 3.064 | -0.043
GEN-2017-048 | North | 16 - Western North Dakota | 661080 | STANLEY7 | 115 | 3.558 | 3.517 | -0.041
GEN-2017-048 | North | 16 - Western North Dakota | 661084 | TIOGA4 4 | 230 | 8.87 | 9.376 | 0.506
GEN-2017-048 | North | 16 - Western North Dakota | 661085 | TIOGA4 7 | 115 | 9.635 | 9.742 | 0.107
GEN-2017-048 | North | 16 - Western North Dakota | 661086 | TIOGA7 7 | 115 | 7.974 | 8.019 | 0.045
GEN-2017-048 | North | 16 - Western North Dakota | 661087 | RAY JCT7 | 115 | 5.184 | 5.169 | -0.015
GEN-2017-048 | North | 16 - Western North Dakota | 661089 | LTLMUDY7 | 115 | 6.442 | 6.441 | -0.001
GEN-2017-048 | North | 16 - Western North Dakota | 661281 | LIGNITE7 | 115 | 1.511 | 1.484 | -0.027
GEN-2017-048 | North | 16 - Western North Dakota | 672501 | BD 6 | 138 | 13.893 | 13.893 | 0
GEN-2017-048 | North | 16 - Western North Dakota | 672601 | BD 4 | 230 | 14.645 | 14.659 | 0.014
GEN-2017-048 | North | 16 - Western North Dakota | 672602 | BDX 4 | 230 | 5.464 | 5.433 | -0.031
GEN-2017-048 | North | 16 - Western North Dakota | 672603 | BDV 4 | 230 | 5.468 | 5.436 | -0.032
GEN-2017-048 | North | 16 - Western North Dakota | 672607 | REGINA 4 | 230 | 8.12 | 8.114 | -0.006
GEN-2017-048 | North | 16 - Western North Dakota | 672613 | AUBURNTON 4 | 230 | 5.741 | 5.721 | -0.02
GEN-2017-048 | North | 16 - Western North Dakota | 672621 | SHAND 4 | 230 | 10.193 | 10.194 | 0.001
GEN-2017-048 | North | 16 - Western North Dakota | 673601 | KISBEY TAP 4 | 230 | 5.672 | 5.662 | -0.01
GEN-2017-004 | North | 17 - Western South Dakota | 588490 | GEN-2017-004 | 345 | 7.59 | 7.85 | 0.26
GEN-2017-004 | North | 17 - Western South Dakota | 588494 | G17-004-TAP | 345 | 9.522 | 9.737 | 0.215
GEN-2017-004 | North | 17 - Western South Dakota | 532773 | SUMMIT 7 | 345 | 11.329 | 11.526 | 0.197
GEN-2017-004 | North | 17 - Western South Dakota | 587894 | G16-112-TAP | 345 | 10.102 | 10.188 | 0.086
GEN-2017-004 | North | 17 - Western South Dakota | 532873 | SUMMIT 6 | 230 | 14.285 | 14.362 | 0.077
GEN-2017-004 | North | 17 - Western South Dakota | 587884 | G16-111-TAP | 345 | 10.383 | 10.433 | 0.05
GEN-2017-004 | North | 17 - Western South Dakota | 532767 | GEARY 7 | 345 | 10.255 | 10.292 | 0.037
GEN-2017-004 | North | 17 - Western South Dakota | 533381 | SUMMIT 3 | 115 | 18.3 | 18.337 | 0.037
GEN-2017-004 | North | 17 - Western South Dakota | 539805 | ELMCREEK7 | 345 | 5.964 | 6 | 0.036
GEN-2017-004 | North | 17 - Western South Dakota | 539639 | ELMCREK6 | 230 | 8.358 | 8.383 | 0.025
GEN-2017-004 | North | 17 - Western South Dakota | 532771 | RENO 7 | 345 | 12.136 | 12.158 | 0.022
GEN-2017-004 | North | 17 - Western South Dakota | 532766 | JEC N 7 | 345 | 23.907 | 23.923 | 0.016
GEN-2017-004 | North | 17 - Western South Dakota | 587880 | GEN-2016-111 | 345 | 6.788 | 6.8 | 0.012
GEN-2017-004 | North | 17 - Western South Dakota | 530592 | SMOKYHL6 | 230 | 7.162 | 7.17 | 0.008
GEN-2017-004 | North | 17 - Western South Dakota | 530599 | SMKYP2 6 | 230 | 6.637 | 6.645 | 0.008
GEN-2017-004 | North | 17 - Western South Dakota | 533336 | GEARY 3 | 115 | 19.17 | 19.178 | 0.008
GEN-2017-004 | North | 17 - Western South Dakota | 530593 | SMKYP1 6 | 230 | 6.204 | 6.211 | 0.007
GEN-2017-004 | North | 17 - Western South Dakota | 532852 | JEC 6 | 230 | 24.991 | 24.997 | 0.006
GEN-2017-004 | North | 17 - Western South Dakota | 539637 | MRWYP16 | 230 | 7.475 | 7.481 | 0.006
GEN-2017-004 | North | 17 - Western South Dakota | 530561 | KNOLL 3 | 115 | 12.454 | 12.46 | 0.006
GEN-2017-004 | North | 17 - Western South Dakota | 533372 | PHILIPS3 | 115 | 12.921 | 12.924 | 0.003
GEN-2017-004 | North | 17 - Western South Dakota | 533368 | EXIDE J3 | 115 | 12.861 | 12.863 | 0.002
GEN-2017-004 | North | 17 - Western South Dakota | 539658 | CONCRD6 | 230 | 5.91 | 5.911 | 0.001
GEN-2017-004 | North | 17 - Western South Dakota | 533371 | NORTHVW3 | 115 | 12.054 | 12.054 | 0
GEN-2017-004 | North | 17 - Western South Dakota | 539634 | MRWYP26 | 230 | 6.321 | 6.32 | -0.001
GEN-2017-004 | North | 17 - Western South Dakota | 533378 | SMOKYHLLS3 | 115 | 11.508 | 11.506 | -0.002
GEN-2017-004 | North | 17 - Western South Dakota | 532872 | EMCPHER6 | 230 | 9.34 | 9.337 | -0.003
GEN-2017-004 | North | 17 - Western South Dakota | 532874 | UNIONRG6 | 230 | 9.042 | 9.039 | -0.003
GEN-2017-004 | North | 17 - Western South Dakota | 533379 | SO GATE3 | 115 | 11.039 | 11.036 | -0.003
GEN-2017-004 | North | 17 - Western South Dakota | 533367 | EXIDE 3 | 115 | 10.872 | 10.868 | -0.004
GEN-2017-004 | North | 17 - Western South Dakota | 533370 | NORTHST3 | 115 | 10.773 | 10.768 | -0.005
GEN-2017-004 | North | 17 - Western South Dakota | 532875 | GEN-2015-069 | 230 | 6.641 | 6.636 | -0.005
GEN-2017-004 | North | 17 - Western South Dakota | 533416 | RENO 3 | 115 | 26.829 | 26.823 | -0.006
GEN-2017-004 | North | 17 - Western South Dakota | 532861 | EMANHAT6 | 230 | 10.187 | 10.18 | -0.007
GEN-2017-004 | North | 17 - Western South Dakota | 532865 | NMANHT6 | 230 | 9.295 | 9.288 | -0.007
GEN-2017-004 | North | 17 - Western South Dakota | 533328 | FT JCT 3 | 115 | 15.292 | 15.285 | -0.007
GEN-2017-004 | North | 17 - Western South Dakota | 533359 | UNIONRG3 | 115 | 3.873 | 3.866 | -0.007
GEN-2017-004 | North | 17 - Western South Dakota | 533360 | TCHOPE 3 | 115 | 3.439 | 3.432 | -0.007
GEN-2017-004 | North | 17 - Western South Dakota | 532796 | WICHITA7 | 345 | 24.652 | 24.645 | -0.007
GEN-2017-004 | North | 17 - Western South Dakota | 533323 | CLAYCTR3 | 115 | 3.007 | 2.999 | -0.008
GEN-2017-004 | North | 17 - Western South Dakota | 532770 | MORRIS 7 | 345 | 12.943 | 12.934 | -0.009
GEN-2017-004 | North | 17 - Western South Dakota | 533417 | EMCPHER3 | 115 | 15.174 | 15.165 | -0.009
GEN-2017-004 | North | 17 - Western South Dakota | 532862 | MCDOWEL6 | 230 | 7.099 | 7.089 | -0.01
GEN-2017-004 | North | 17 - Western South Dakota | 533342 | WJCCTY 3 | 115 | 13.762 | 13.752 | -0.01
GEN-2017-004 | North | 17 - Western South Dakota | 533344 | WJCCTYW3 | 115 | 13.67 | 13.66 | -0.01
GEN-2017-004 | North | 17 - Western South Dakota | 533426 | MANVILE3 | 115 | 11.695 | 11.685 | -0.01
GEN-2017-004 | North | 17 - Western South Dakota | 539650 | BELOIT 3 | 115 | 3.227 | 3.217 | -0.01
GEN-2017-004 | North | 17 - Western South Dakota | 539669 | JEWELL 3 | 115 | 3.162 | 3.152 | -0.01
GEN-2017-004 | North | 17 - Western South Dakota | 533427 | REFINRY3 | 115 | 14.614 | 14.604 | -0.01
GEN-2017-004 | North | 17 - Western South Dakota | 539657 | CONCORD3 | 115 | 7.65 | 7.639 | -0.011
GEN-2017-004 | North | 17 - Western South Dakota | 533362 | CHAPMAN3 | 115 | 11.166 | 11.155 | -0.011
GEN-2017-004 | North | 17 - Western South Dakota | 533330 | JCTCTY 3 | 115 | 13.033 | 13.021 | -0.012
GEN-2017-004 | North | 17 - Western South Dakota | 533365 | EABILEN3 | 115 | 7.959 | 7.947 | -0.012
GEN-2017-004 | North | 17 - Western South Dakota | 533361 | AEC 3 | 115 | 7.745 | 7.733 | -0.012
GEN-2017-004 | North | 17 - Western South Dakota | 530686 | RICE 6 | 230 | 4.945 | 4.932 | -0.013
GEN-2017-004 | North | 17 - Western South Dakota | 532871 | CIRCLE 6 | 230 | 10.035 | 10.022 | -0.013
GEN-2017-004 | North | 17 - Western South Dakota | 532768 | EMPEC 7 | 345 | 17.609 | 17.596 | -0.013
GEN-2017-004 | North | 17 - Western South Dakota | 530558 | KNOLL 6 | 230 | 12.969 | 12.955 | -0.014
GEN-2017-004 | North | 17 - Western South Dakota | 530584 | POSTROCK6 | 230 | 13.11 | 13.096 | -0.014
GEN-2017-004 | North | 17 - Western South Dakota | 533335 | MCDOWEL3 | 115 | 18.683 | 18.669 | -0.014
GEN-2017-004 | North | 17 - Western South Dakota | 533413 | CIRCLE 3 | 115 | 23.596 | 23.582 | -0.014
GEN-2017-004 | North | 17 - Western South Dakota | 532863 | MORRIS 6 | 230 | 14.082 | 14.067 | -0.015
GEN-2017-004 | North | 17 - Western South Dakota | 539656 | CLIFTON3 | 115 | 4.799 | 4.784 | -0.015
GEN-2017-004 | North | 17 - Western South Dakota | 533341 | STAGGHL3 | 115 | 9.844 | 9.828 | -0.016
GEN-2017-004 | North | 17 - Western South Dakota | 533343 | PEIL 3 | 115 | 10.577 | 10.561 | -0.016
GEN-2017-004 | North | 17 - Western South Dakota | 533347 | NMANHT3 | 115 | 12.946 | 12.93 | -0.016
GEN-2017-004 | North | 17 - Western South Dakota | 533326 | EMANHAT3 | 115 | 13.702 | 13.685 | -0.017
GEN-2017-004 | North | 17 - Western South Dakota | 533333 | KSU W 3 | 115 | 12.036 | 12.019 | -0.017
GEN-2017-004 | North | 17 - Western South Dakota | 539679 | GRTBEND6 | 230 | 8.692 | 8.673 | -0.019
GEN-2017-004 | North | 17 - Western South Dakota | 533340 | SMANHAT3 | 115 | 12.307 | 12.286 | -0.021
GEN-2017-004 | North | 17 - Western South Dakota | 532765 | HOYT 7 | 345 | 15.993 | 15.971 | -0.022
GEN-2017-004 | North | 17 - Western South Dakota | 533305 | MORRIS 3 | 115 | 12.653 | 12.631 | -0.022
GEN-2017-004 | North | 17 - Western South Dakota | 532851 | AUBURN 6 | 230 | 13.159 | 13.135 | -0.024
GEN-2017-004 | North | 17 - Western South Dakota | 532772 | STRANGR7 | 345 | 25.597 | 25.569 | -0.028
GEN-2017-004 | North | 17 - Western South Dakota | 532856 | SWISVAL6 | 230 | 21.208 | 21.17 | -0.038
GEN-2017-004 | North | 17 - Western South Dakota | 533163 | HOYT 3 | 115 | 23.095 | 23.056 | -0.039
GEN-2017-013 | North | 17 - Western South Dakota | 531451 | MINGO 7 | 345 | 6.625 | 6.892 | 0.267
GEN-2017-013 | North | 17 - Western South Dakota | 531632 | GEN-2016-067 | 345 | 6.625 | 6.892 | 0.267
GEN-2017-013 | North | 17 - Western South Dakota | 588580 | GEN-2017-013 | 345 | 6.562 | 6.828 | 0.266
GEN-2017-013 | North | 17 - Western South Dakota | 585030 | GEN-2015-065 | 345 | 6.002 | 6.21 | 0.208
GEN-2017-013 | North | 17 - Western South Dakota | 531429 | MINGO 3 | 115 | 12.961 | 13.169 | 0.208
GEN-2017-013 | North | 17 - Western South Dakota | 585020 | GEN-2015-064 | 115 | 10.183 | 10.287 | 0.104
GEN-2017-013 | North | 17 - Western South Dakota | 531465 | SETAB 7 | 345 | 7.151 | 7.214 | 0.063
GEN-2017-013 | North | 17 - Western South Dakota | 640325 | REDWILO3 | 345 | 9.27 | 9.315 | 0.045
GEN-2017-013 | North | 17 - Western South Dakota | 531449 | HOLCOMB7 | 345 | 10.027 | 10.043 | 0.016
GEN-2017-013 | North | 17 - Western South Dakota | 523853 | FINNEY 7 | 345 | 9.916 | 9.93 | 0.014
GEN-2017-013 | North | 17 - Western South Dakota | 530592 | SMOKYHL6 | 230 | 7.162 | 7.17 | 0.008
GEN-2017-013 | North | 17 - Western South Dakota | 530561 | KNOLL 3 | 115 | 12.454 | 12.46 | 0.006
GEN-2017-013 | North | 17 - Western South Dakota | 640183 | GENTLMN3 | 345 | 16.581 | 16.584 | 0.003
GEN-2017-013 | North | 17 - Western South Dakota | 659131 | LARAMIE_-MB3 | 345 | 6.944 | 6.945 | 0.001
GEN-2017-013 | North | 17 - Western South Dakota | 587874 | G16-110-TAP | 345 | 6.118 | 6.117 | -0.001
GEN-2017-013 | North | 17 - Western South Dakota | 640252 | KEYSTON3 | 345 | 12.176 | 12.174 | -0.002
GEN-2017-013 | North | 17 - Western South Dakota | 530555 | COLBY 3 | 115 | 6.167 | 6.163 | -0.004
GEN-2017-013 | North | 17 - Western South Dakota | 531501 | BUCKNER7 | 345 | 9.2 | 9.195 | -0.005
GEN-2017-013 | North | 17 - Western South Dakota | 659135 | STEGALL_-MB3 | 345 | 5.182 | 5.176 | -0.006
GEN-2017-013 | North | 17 - Western South Dakota | 659133 | SIDNEY__-MB3 | 345 | 7.612 | 7.605 | -0.007
GEN-2017-013 | North | 17 - Western South Dakota | 659425 | SD.LS-KS-MB3 | 345 | 7.612 | 7.605 | -0.007
GEN-2017-013 | North | 17 - Western South Dakota | 659426 | SD.LS-LR-MB3 | 345 | 7.612 | 7.605 | -0.007
GEN-2017-013 | North | 17 - Western South Dakota | 640184 | GENTLMN4 | 230 | 19.353 | 19.346 | -0.007
GEN-2017-013 | North | 17 - Western South Dakota | 531502 | CIMRRN 7 | 345 | 7.327 | 7.319 | -0.008
GEN-2017-013 | North | 17 - Western South Dakota | 531469 | SPERVIL7 | 345 | 13.951 | 13.943 | -0.008
GEN-2017-013 | North | 17 - Western South Dakota | 531504 | CIMWD2 7 | 345 | 7.329 | 7.32 | -0.009
GEN-2017-013 | North | 17 - Western South Dakota | 523118 | BUFF_DUNES 7 | 345 | 6.158 | 6.149 | -0.009
GEN-2017-013 | North | 17 - Western South Dakota | 539803 | IRONWOOD7 | 345 | 13.355 | 13.346 | -0.009
GEN-2017-013 | North | 17 - Western South Dakota | 530553 | S HAYS 3 | 115 | 9.342 | 9.333 | -0.009
GEN-2017-013 | North | 17 - Western South Dakota | 588650 | GEN-2017-021 | 345 | 9.846 | 9.836 | -0.01
GEN-2017-013 | North | 17 - Western South Dakota | 588654 | G17-021-TAP | 345 | 10.312 | 10.302 | -0.01
GEN-2017-013 | North | 17 - Western South Dakota | 589370 | GEN-2017-099 | 345 | 9.837 | 9.827 | -0.01
GEN-2017-013 | North | 17 - Western South Dakota | 640302 | OGALALA4 | 230 | 8.072 | 8.062 | -0.01
GEN-2017-013 | North | 17 - Western South Dakota | 659134 | SIDNEY___TS4 | 230 | 6.976 | 6.966 | -0.01
GEN-2017-013 | North | 17 - Western South Dakota | 659210 | SIDNEY__-MB4 | 230 | 7.625 | 7.615 | -0.01
GEN-2017-013 | North | 17 - Western South Dakota | 530610 | SHAYS_230 | 230 | 4.203 | 4.193 | -0.01
GEN-2017-013 | North | 17 - Western South Dakota | 641244 | ATHEY 7 | 115 | 3.209 | 3.198 | -0.011
GEN-2017-013 | North | 17 - Western South Dakota | 640520 | ANTELOPE 3 | 345 | 8.796 | 8.784 | -0.012
GEN-2017-013 | North | 17 - Western South Dakota | 599950 | LAMAR7 | 345 | 2.562 | 2.55 | -0.012
GEN-2017-013 | North | 17 - Western South Dakota | 531423 | GARDNCY2 | 69 | 3.57 | 3.558 | -0.012
GEN-2017-013 | North | 17 - Western South Dakota | 640101 | CAMBRIG8 | 69 | 2.328 | 2.316 | -0.012
GEN-2017-013 | North | 17 - Western South Dakota | 640168 | ENDERS 8 | 69 | 3.188 | 3.176 | -0.012
GEN-2017-013 | North | 17 - Western South Dakota | 588750 | GEN-2017-032 | 345 | 3.17 | 3.157 | -0.013
GEN-2017-013 | North | 17 - Western South Dakota | 588754 | G17-032-TAP | 345 | 3.17 | 3.157 | -0.013
GEN-2017-013 | North | 17 - Western South Dakota | 589484 | G16-049-TAP | 345 | 9.058 | 9.045 | -0.013
GEN-2017-013 | North | 17 - Western South Dakota | 652832 | GRPRAR1-LNX3 | 345 | 8.072 | 8.059 | -0.013
GEN-2017-013 | North | 17 - Western South Dakota | 640167 | ENDERS 7 | 115 | 3.948 | 3.935 | -0.013
GEN-2017-013 | North | 17 - Western South Dakota | 640359 | STAPLETON 7 | 115 | 4.221 | 4.208 | -0.013
GEN-2017-013 | North | 17 - Western South Dakota | 640288 | N.PLATT8 | 69 | 5.256 | 5.243 | -0.013
GEN-2017-013 | North | 17 - Western South Dakota | 640238 | JEFFREY7 | 115 | 6.174 | 6.161 | -0.013
GEN-2017-013 | North | 17 - Western South Dakota | 530583 | POSTROCK7 | 345 | 9.886 | 9.872 | -0.014
GEN-2017-013 | North | 17 - Western South Dakota | 530558 | KNOLL 6 | 230 | 12.969 | 12.955 | -0.014
GEN-2017-013 | North | 17 - Western South Dakota | 530584 | POSTROCK6 | 230 | 13.11 | 13.096 | -0.014
GEN-2017-013 | North | 17 - Western South Dakota | 530582 | S HAYS6 | 230 | 9.892 | 9.877 | -0.015
GEN-2017-013 | North | 17 - Western South Dakota | 659800 | GRANTNB_-TS7 | 115 | 6.585 | 6.57 | -0.015
GEN-2017-013 | North | 17 - Western South Dakota | 640366 | STOCKVL8 | 69 | 3.433 | 3.418 | -0.015
GEN-2017-013 | North | 17 - Western South Dakota | 530557 | BEACH 3 | 115 | 3.745 | 3.73 | -0.015
GEN-2017-013 | North | 17 - Western South Dakota | 530702 | BUCKEYE_230 | 230 | 9.431 | 9.415 | -0.016
GEN-2017-013 | North | 17 - Western South Dakota | 539695 | SPEARVL6 | 230 | 12.76 | 12.744 | -0.016
GEN-2017-013 | North | 17 - Western South Dakota | 531409 | ARNOLD3 | 115 | 2.75 | 2.734 | -0.016
GEN-2017-013 | North | 17 - Western South Dakota | 531444 | GOODCTY3 | 115 | 2.165 | 2.149 | -0.016
GEN-2017-013 | North | 17 - Western South Dakota | 640096 | CALAMS 7 | 115 | 3.481 | 3.465 | -0.016
GEN-2017-013 | North | 17 - Western South Dakota | 584650 | GEN-2015-023 | 345 | 8.841 | 8.824 | -0.017
GEN-2017-013 | North | 17 - Western South Dakota | 640500 | THEDFRD3 | 345 | 5.377 | 5.36 | -0.017
GEN-2017-013 | North | 17 - Western South Dakota | 640267 | MAXWELS7 | 115 | 6.776 | 6.759 | -0.017
GEN-2017-013 | North | 17 - Western South Dakota | 531489 | ONEOK 3 | 115 | 1.969 | 1.952 | -0.017
GEN-2017-013 | North | 17 - Western South Dakota | 640286 | N.PLATT4 | 230 | 13.198 | 13.181 | -0.017
GEN-2017-013 | North | 17 - Western South Dakota | 531357 | RULETON3 | 115 | 2.63 | 2.612 | -0.018
GEN-2017-013 | North | 17 - Western South Dakota | 531408 | PIERCVL3 | 115 | 3.863 | 3.845 | -0.018
GEN-2017-013 | North | 17 - Western South Dakota | 531487 | MCDONLD3 | 115 | 2.343 | 2.325 | -0.018
GEN-2017-013 | North | 17 - Western South Dakota | 531351 | BREWSTR3 | 115 | 3.18 | 3.162 | -0.018
GEN-2017-013 | North | 17 - Western South Dakota | 531353 | GOODLND3 | 115 | 2.712 | 2.694 | -0.018
GEN-2017-013 | North | 17 - Western South Dakota | 531411 | GOVE 3 | 115 | 2.813 | 2.795 | -0.018
GEN-2017-013 | North | 17 - Western South Dakota | 531443 | GODLNDT3 | 115 | 2.697 | 2.679 | -0.018
GEN-2017-013 | North | 17 - Western South Dakota | 640255 | KINGSLY7 | 115 | 9.736 | 9.718 | -0.018
GEN-2017-013 | North | 17 - Western South Dakota | 640510 | HOLT.CO3 | 345 | 9.892 | 9.873 | -0.019
GEN-2017-013 | North | 17 - Western South Dakota | 539679 | GRTBEND6 | 230 | 8.692 | 8.673 | -0.019
GEN-2017-013 | North | 17 - Western South Dakota | 640093 | C.CREEK4 | 230 | 7.103 | 7.084 | -0.019
GEN-2017-013 | North | 17 - Western South Dakota | 640100 | CAMBRIG7 | 115 | 4.347 | 4.328 | -0.019
GEN-2017-013 | North | 17 - Western South Dakota | 640194 | GOSPER 7 | 115 | 4.505 | 4.486 | -0.019
GEN-2017-013 | North | 17 - Western South Dakota | 640365 | STOCKVL7 | 115 | 4.792 | 4.773 | -0.019
GEN-2017-013 | North | 17 - Western South Dakota | 640271 | MCCOOL 3 | 345 | 10.652 | 10.632 | -0.02
GEN-2017-013 | North | 17 - Western South Dakota | 530559 | PH RUN 3 | 115 | 4.646 | 4.626 | -0.02
GEN-2017-013 | North | 17 - Western South Dakota | 530682 | SEGNTP 3 | 115 | 4.391 | 4.371 | -0.02
GEN-2017-013 | North | 17 - Western South Dakota | 531464 | SETAB 3 | 115 | 10.535 | 10.515 | -0.02
GEN-2017-013 | North | 17 - Western South Dakota | 531220 | LUDELLT3 | 115 | 2.615 | 2.595 | -0.02
GEN-2017-013 | North | 17 - Western South Dakota | 531360 | DIGHTNT3 | 115 | 3.645 | 3.625 | -0.02
GEN-2017-013 | North | 17 - Western South Dakota | 531488 | BVERVLLY | 115 | 2.438 | 2.418 | -0.02
GEN-2017-013 | North | 17 - Western South Dakota | 539759 | SPRVL 3 | 115 | 11.883 | 11.862 | -0.021
GEN-2017-013 | North | 17 - Western South Dakota | 530683 | SEGUIN 3 | 115 | 4.175 | 4.154 | -0.021
GEN-2017-013 | North | 17 - Western South Dakota | 531364 | ATWODSW3 | 115 | 2.709 | 2.688 | -0.021
GEN-2017-013 | North | 17 - Western South Dakota | 531369 | NATWOOD3 | 115 | 2.584 | 2.563 | -0.021
GEN-2017-013 | North | 17 - Western South Dakota | 531440 | WILLIAM3 | 115 | 3.757 | 3.736 | -0.021
GEN-2017-013 | North | 17 - Western South Dakota | 531476 | SWNDTAP3 | 115 | 7.716 | 7.695 | -0.021
GEN-2017-013 | North | 17 - Western South Dakota | 640082 | BEVERLY7 | 115 | 5.119 | 5.098 | -0.021
GEN-2017-013 | North | 17 - Western South Dakota | 530556 | HOXIE 3 | 115 | 3.611 | 3.59 | -0.021
GEN-2017-013 | North | 17 - Western South Dakota | 531412 | GRINNEL3 | 115 | 3.789 | 3.768 | -0.021
GEN-2017-013 | North | 17 - Western South Dakota | 530554 | ATWOOD 3 | 115 | 3.053 | 3.031 | -0.022
GEN-2017-013 | North | 17 - Western South Dakota | 531363 | MANNING3 | 115 | 4.09 | 4.068 | -0.022
GEN-2017-013 | North | 17 - Western South Dakota | 587350 | GEN-2016-050 | 345 | 6.512 | 6.489 | -0.023
GEN-2017-013 | North | 17 - Western South Dakota | 640312 | PAULINE3 | 345 | 8.211 | 8.188 | -0.023
GEN-2017-013 | North | 17 - Western South Dakota | 640265 | MALONEY7 | 115 | 11.44 | 11.417 | -0.023
GEN-2017-013 | North | 17 - Western South Dakota | 640304 | OGALALANPPD7 | 115 | 15.551 | 15.528 | -0.023
GEN-2017-013 | North | 17 - Western South Dakota | 659801 | OGALALA_-TS7 | 115 | 15.551 | 15.528 | -0.023
GEN-2017-013 | North | 17 - Western South Dakota | 587680 | GEN-2016-074 | 345 | 6.575 | 6.552 | -0.023
GEN-2017-013 | North | 17 - Western South Dakota | 531362 | MANNGT 3 | 115 | 5.127 | 5.103 | -0.024
GEN-2017-013 | North | 17 - Western South Dakota | 531392 | PIONTAP3 | 115 | 6.562 | 6.538 | -0.024
GEN-2017-013 | North | 17 - Western South Dakota | 531400 | PK_GOAB3 | 115 | 4.884 | 4.86 | -0.024
GEN-2017-013 | North | 17 - Western South Dakota | 640270 | MCCOOK 8 | 69 | 4.931 | 4.907 | -0.024
GEN-2017-013 | North | 17 - Western South Dakota | 640253 | KEYSTON7 | 115 | 16.246 | 16.221 | -0.025
GEN-2017-013 | North | 17 - Western South Dakota | 560082 | G16-050-TAP | 345 | 7.245 | 7.22 | -0.025
GEN-2017-013 | North | 17 - Western South Dakota | 531434 | SELKIRK3 | 115 | 3.84 | 3.814 | -0.026
GEN-2017-013 | North | 17 - Western South Dakota | 531493 | GANO 3 | 115 | 6.888 | 6.862 | -0.026
GEN-2017-013 | North | 17 - Western South Dakota | 523823 | CARPENTER 7 | 345 | 6.706 | 6.68 | -0.026
GEN-2017-013 | North | 17 - Western South Dakota | 531432 | PILE 3 | 115 | 6.562 | 6.536 | -0.026
GEN-2017-013 | North | 17 - Western South Dakota | 531433 | SCOTCTY3 | 115 | 8.995 | 8.968 | -0.027
GEN-2017-013 | North | 17 - Western South Dakota | 531512 | HARBNGR7 | 345 | 6.686 | 6.659 | -0.027
GEN-2017-013 | North | 17 - Western South Dakota | 530644 | COLBY 2 | 69 | 3.608 | 3.581 | -0.027
GEN-2017-013 | North | 17 - Western South Dakota | 523097 | HITCHLAND 7 | 345 | 15.292 | 15.264 | -0.028
GEN-2017-013 | North | 17 - Western South Dakota | 531428 | LEOTI 3 | 115 | 4.197 | 4.169 | -0.028
GEN-2017-013 | North | 17 - Western South Dakota | 640326 | REDWILO7 | 115 | 13.324 | 13.296 | -0.028
GEN-2017-013 | North | 17 - Western South Dakota | 531445 | GRDNCTY3 | 115 | 14.382 | 14.353 | -0.029
GEN-2017-013 | North | 17 - Western South Dakota | 531480 | KSAVWTP3 | 115 | 13.834 | 13.805 | -0.029
GEN-2017-013 | North | 17 - Western South Dakota | 640269 | MCCOOK 7 | 115 | 9.696 | 9.666 | -0.03
GEN-2017-013 | North | 17 - Western South Dakota | 653871 | GR ISLD-LNX3 | 345 | 12.614 | 12.584 | -0.03
GEN-2017-013 | North | 17 - Western South Dakota | 653571 | GR ISLD3 | 345 | 12.738 | 12.707 | -0.031
GEN-2017-013 | North | 17 - Western South Dakota | 640065 | AXTELL 3 | 345 | 9.625 | 9.593 | -0.032
GEN-2017-013 | North | 17 - Western South Dakota | 531485 | CNTRLPL3 | 115 | 5.732 | 5.7 | -0.032
GEN-2017-013 | North | 17 - Western South Dakota | 640287 | N.PLATT7 | 115 | 18.51 | 18.478 | -0.032
GEN-2017-013 | North | 17 - Western South Dakota | 640381 | THEDFRD7 | 115 | 9.063 | 9.031 | -0.032
GEN-2017-013 | North | 17 - Western South Dakota | 531393 | PLYMELL3 | 115 | 7.654 | 7.621 | -0.033
GEN-2017-013 | North | 17 - Western South Dakota | 531420 | FLETCHR3 | 115 | 6.819 | 6.785 | -0.034
GEN-2017-013 | North | 17 - Western South Dakota | 640374 | SWEET W3 | 345 | 10.906 | 10.871 | -0.035
GEN-2017-013 | North | 17 - Western South Dakota | 531426 | JAMESON3 | 115 | 10.536 | 10.501 | -0.035
GEN-2017-013 | North | 17 - Western South Dakota | 640200 | GR ISLD4 | 230 | 17.113 | 17.076 | -0.037
GEN-2017-013 | North | 17 - Western South Dakota | 531379 | JONES3 | 115 | 11.042 | 11.004 | -0.038
GEN-2017-013 | North | 17 - Western South Dakota | 539800 | CLARKCOUNTY7 | 345 | 13.394 | 13.352 | -0.042
GEN-2017-013 | North | 17 - Western South Dakota | 640066 | AXTELL 7 | 115 | 14.677 | 14.629 | -0.048
GEN-2017-013 | North | 17 - Western South Dakota | 640083 | BEVERLY8 | 69 | 4.542 | 4.493 | -0.049
GEN-2017-013 | North | 17 - Western South Dakota | 531448 | HOLCOMB3 | 115 | 21.971 | 21.912 | -0.059
GEN-2017-014 | North | 17 - Western South Dakota | 652506 | FTTHOMP3 | 345 | 8.869 | 8.882 | 0.013
GEN-2017-014 | North | 17 - Western South Dakota | 652806 | FTTHOM1-LNX3 | 345 | 8.806 | 8.818 | 0.012
GEN-2017-014 | North | 17 - Western South Dakota | 652807 | FTTHOM2-LNX3 | 345 | 8.869 | 8.882 | 0.013
GEN-2017-014 | North | 17 - Western South Dakota | 587760 | GEN-2016-094 | 230 | 9.147 | 9.208 | 0.061
GEN-2017-014 | North | 17 - Western South Dakota | 587764 | G16-094-TAP | 230 | 9.307 | 9.37 | 0.063
GEN-2017-014 | North | 17 - Western South Dakota | 588590 | GEN-2017-014 | 230 | 3.644 | 5.185 | 1.541
GEN-2017-014 | North | 17 - Western South Dakota | 588594 | G17-014-TAP | 230 | 3.644 | 5.185 | 1.541
GEN-2017-014 | North | 17 - Western South Dakota | 589020 | GEN-2017-064 | 230 | 2.833 | 2.937 | 0.104
GEN-2017-014 | North | 17 - Western South Dakota | 589024 | G17-064-TAP | 230 | 2.833 | 2.937 | 0.104
GEN-2017-014 | North | 17 - Western South Dakota | 589320 | GEN-2017-094 | 230 | 11.003 | 11.001 | -0.002
GEN-2017-014 | North | 17 - Western South Dakota | 589324 | G17-094-TAP | 230 | 11.003 | 11.001 | -0.002
GEN-2017-014 | North | 17 - Western South Dakota | 640404 | WAYSIDE4 | 230 | 2.889 | 2.939 | 0.05
GEN-2017-014 | North | 17 - Western South Dakota | 640540 | MEADOWGROVE4 | 230 | 5.662 | 5.663 | 0.001
GEN-2017-014 | North | 17 - Western South Dakota | 652484 | NUNDRWD4 | 230 | 3.581 | 3.99 | 0.409
GEN-2017-014 | North | 17 - Western South Dakota | 652486 | PHILIP 4 | 230 | 3.246 | 4.006 | 0.76
GEN-2017-014 | North | 17 - Western South Dakota | 652497 | MAURINE4 | 230 | 2.922 | 2.983 | 0.061
GEN-2017-014 | North | 17 - Western South Dakota | 652507 | FTTHOMP4 | 230 | 20.055 | 20.221 | 0.166
GEN-2017-014 | North | 17 - Western South Dakota | 652509 | FTRANDL4 | 230 | 10.758 | 10.769 | 0.011
GEN-2017-014 | North | 17 - Western South Dakota | 652514 | HURON 4 | 230 | 11.231 | 11.219 | -0.012
GEN-2017-014 | North | 17 - Western South Dakota | 652519 | OAHE 4 | 230 | 14.062 | 14.617 | 0.555
GEN-2017-014 | North | 17 - Western South Dakota | 652523 | SIOUXFL4 | 230 | 13.231 | 13.189 | -0.042
GEN-2017-014 | North | 17 - Western South Dakota | 652526 | UTICAJC4 | 230 | 7.914 | 7.898 | -0.016
GEN-2017-014 | North | 17 - Western South Dakota | 652540 | BIGBND14 | 230 | 12.15 | 12.223 | 0.073
GEN-2017-014 | North | 17 - Western South Dakota | 652541 | BIGBND24 | 230 | 11.979 | 12.051 | 0.072
GEN-2017-014 | North | 17 - Western South Dakota | 652565 | SIOUXCY4 | 230 | 20.044 | 20.022 | -0.022
GEN-2017-014 | North | 17 - Western South Dakota | 652573 | STEGALL4 | 230 | 5.478 | 5.489 | 0.011
GEN-2017-014 | North | 17 - Western South Dakota | 652606 | LETCHER4 | 230 | 4.757 | 4.729 | -0.028
GEN-2017-014 | North | 17 - Western South Dakota | 652607 | WESSINGTON 4 | 230 | 6.709 | 6.677 | -0.032
GEN-2017-014 | North | 17 - Western South Dakota | 652873 | STEGALL-LNX3 | 230 | 5.461 | 5.472 | 0.011
GEN-2017-014 | North | 17 - Western South Dakota | 652884 | NUNDRWD-LNX3 | 230 | 3.575 | 3.982 | 0.407
GEN-2017-014 | North | 17 - Western South Dakota | 655475 | LAKPLAT-ER4 | 230 | 5.704 | 5.698 | -0.006
GEN-2017-014 | North | 17 - Western South Dakota | 655487 | SULLYBT-ER4 | 230 | 6.43 | 6.512 | 0.082
GEN-2017-014 | North | 17 - Western South Dakota | 655510 | SB.LS-WK-ER4 | 230 | 6.43 | 6.512 | 0.082
GEN-2017-014 | North | 17 - Western South Dakota | 655765 | WHITLOCK_-RM | 230 | 4.556 | 4.579 | 0.023
GEN-2017-014 | North | 17 - Western South Dakota | 659122 | STORLA__-BE4 | 230 | 5.994 | 5.962 | -0.032
GEN-2017-014 | North | 17 - Western South Dakota | 659188 | PHILIP_T-BE4 | 230 | 3.838 | 5.187 | 1.349
GEN-2017-014 | North | 17 - Western South Dakota | 659268 | RCDC.DUM-BE4 | 230 | 7.279 | 6.206 | -1.073
GEN-2017-014 | North | 17 - Western South Dakota | 659271 | RCDC.E__-BE4 | 230 | 2.768 | 2.986 | 0.218
GEN-2017-014 | North | 17 - Western South Dakota | 659295 | SD.PW1__-BE4 | 230 | 5.602 | 5.573 | -0.029
GEN-2017-014 | North | 17 - Western South Dakota | 659303 | RCDC.W__-BE4 | 230 | 2.397 | 2.397 | 0
GEN-2017-014 | North | 17 - Western South Dakota | 659351 | BISON___-GE4 | 230 | 2.96 | 2.975 | 0.015
GEN-2017-014 | North | 17 - Western South Dakota | 659376 | DRYCREEK-BE4 | 230 | 2.774 | 2.993 | 0.219
GEN-2017-014 | North | 17 - Western South Dakota | 661047 | HETINGR4 | 230 | 3.742 | 3.738 | -0.004
GEN-2017-014 | North | 17 - Western South Dakota | 589350 | GEN-2017-097 | 115 | 5.957 | 6.472 | 0.515
GEN-2017-014 | North | 17 - Western South Dakota | 640109 | CHADRON7 | 115 | 3.805 | 3.808 | 0.003
GEN-2017-014 | North | 17 - Western South Dakota | 640405 | WAYSIDE7 | 115 | 4.287 | 4.292 | 0.005
GEN-2017-014 | North | 17 - Western South Dakota | 652243 | FAITH 7 | 115 | 2.436 | 2.45 | 0.014
GEN-2017-014 | North | 17 - Western South Dakota | 652473 | ELKCRK 7 | 115 | 3.593 | 3.707 | 0.114
GEN-2017-014 | North | 17 - Western South Dakota | 652476 | EAGLEBT7 | 115 | 2.038 | 2.052 | 0.014
GEN-2017-014 | North | 17 - Western South Dakota | 652477 | ELSWRTH7 | 115 | 4.067 | 4.255 | 0.188
GEN-2017-014 | North | 17 - Western South Dakota | 652479 | MARTIN 7 | 115 | 2.413 | 2.397 | -0.016
GEN-2017-014 | North | 17 - Western South Dakota | 652480 | MAURINE7 | 115 | 4.161 | 4.178 | 0.017
GEN-2017-014 | North | 17 - Western South Dakota | 652481 | MIDLAND7 | 115 | 3.418 | 3.525 | 0.107
GEN-2017-014 | North | 17 - Western South Dakota | 652485 | NUNDRWD7 | 115 | 6.348 | 6.947 | 0.599
GEN-2017-014 | North | 17 - Western South Dakota | 652487 | PHILIP 7 | 115 | 5.337 | 5.931 | 0.594
GEN-2017-014 | North | 17 - Western South Dakota | 652489 | PIERRE 7 | 115 | 8.149 | 8.299 | 0.15
GEN-2017-014 | North | 17 - Western South Dakota | 652490 | RAPIDCY7 | 115 | 4.814 | 5.091 | 0.277
GEN-2017-014 | North | 17 - Western South Dakota | 652491 | IRVSIMM7 | 115 | 8.104 | 8.26 | 0.156
GEN-2017-014 | North | 17 - Western South Dakota | 652492 | WALL 7 | 115 | 3.539 | 3.721 | 0.182
GEN-2017-014 | North | 17 - Western South Dakota | 652493 | WICKSVL7 | 115 | 4.204 | 4.446 | 0.242
GEN-2017-014 | North | 17 - Western South Dakota | 652510 | FTRANDL7 | 115 | 12.594 | 12.594 | 0
GEN-2017-014 | North | 17 - Western South Dakota | 652520 | OAHE 7 | 115 | 11.233 | 11.481 | 0.248
GEN-2017-014 | North | 17 - Western South Dakota | 652579 | WANBLEE 7 | 115 | 2.485 | 2.49 | 0.005
GEN-2017-014 | North | 17 - Western South Dakota | 652600 | ASH TAP | 115 | 8.574 | 8.734 | 0.16
GEN-2017-014 | North | 17 - Western South Dakota | 652609 | LETCHER7 | 115 | 6.061 | 6.032 | -0.029
GEN-2017-014 | North | 17 - Western South Dakota | 654490 | G14_001IST | 115 | 3.05 | 3.074 | 0.024
GEN-2017-014 | North | 17 - Western South Dakota | 655763 | RUSHMORE-RM7 | 115 | 4.58 | 4.83 | 0.25
GEN-2017-014 | North | 17 - Western South Dakota | 658120 | GARFLD 7 | 115 | 7.101 | 7.212 | 0.111
GEN-2017-014 | North | 17 - Western South Dakota | 659350 | BISON___-GE7 | 115 | 1.591 | 1.567 | -0.024
GEN-2017-014 | North | 17 - Western South Dakota | 659377 | DRYCREEK-BE7 | 115 | 4.601 | 4.856 | 0.255
GEN-2017-014 | North | 17 - Western South Dakota | 652248 | MAURINE8 | 69 | 2.756 | 2.762 | 0.006
GEN-2017-014 | North | 17 - Western South Dakota | 652259 | EAGLEBE8 | 69 | 1.73 | 1.738 | 0.008
GEN-2017-014 | North | 17 - Western South Dakota | 652260 | EAGLEBW8 | 69 | 2.246 | 2.258 | 0.012
GEN-2017-014 | North | 17 - Western South Dakota | 652263 | MIDLAND8 | 69 | 2.222 | 2.231 | 0.009
GEN-2017-014 | North | 17 - Western South Dakota | 652268 | PHILIP 8 | 69 | 2.54 | 2.571 | 0.031
GEN-2017-014 | North | 17 - Western South Dakota | 652276 | FTTHOMP8 | 69 | 4.284 | 4.28 | -0.004
GEN-2017-014 | North | 17 - Western South Dakota | 655153 | MOS-AMES-ER8 | 69 | 4.217 | 4.213 | -0.004
GEN-2017-014 | North | 17 - Western South Dakota | 655334 | OKOBOJO-ER8 | 69 | 2.461 | 2.463 | 0.002
GEN-2017-014 | North | 17 - Western South Dakota | 655373 | MOS-SLY2-ER8 | 69 | 2.468 | 2.47 | 0.002
GEN-2017-014 | North | 17 - Western South Dakota | 655476 | LAKPLAT-ER8 | 69 | 4.099 | 4.089 | -0.01
GEN-2017-014 | North | 17 - Western South Dakota | 655488 | SULLYBT-ER8 | 69 | 2.472 | 2.474 | 0.002
GEN-2017-014 | North | 17 - Western South Dakota | 655762 | RAPIDCTY-RM8 | 69 | 3.665 | 3.709 | 0.044
GEN-2017-014 | North | 17 - Western South Dakota | 655764 | RUSHMORE-RM8 | 69 | 3.324 | 3.351 | 0.027
GEN-2017-085 | North | 17 - Western South Dakota | 562545 | G14-39_17-85 | 115 | 5.599 | 6.516 | 0.917
GEN-2017-085 | North | 17 - Western South Dakota | 640174 | FRIEND 7 | 115 | 5.599 | 6.516 | 0.917
GEN-2017-085 | North | 17 - Western South Dakota | 640153 | CRETE__7 | 115 | 8.339 | 8.691 | 0.352
GEN-2017-085 | North | 17 - Western South Dakota | 640178 | GENEVA 7 | 115 | 9.782 | 10.109 | 0.327
GEN-2017-085 | North | 17 - Western South Dakota | 640278 | SHELDON7 | 115 | 43.627 | 43.915 | 0.288
GEN-2017-085 | North | 17 - Western South Dakota | 560746 | GEN-2013-002 | 115 | 42.216 | 42.459 | 0.243
GEN-2017-085 | North | 17 - Western South Dakota | 583700 | GEN-2013-019 | 115 | 42.216 | 42.459 | 0.243
GEN-2017-085 | North | 17 - Western South Dakota | 640591 | MONOLITH 7 | 115 | 42.216 | 42.459 | 0.243
GEN-2017-085 | North | 17 - Western South Dakota | 640272 | MCCOOL 7 | 115 | 14.244 | 14.375 | 0.131
GEN-2017-085 | North | 17 - Western South Dakota | 640277 | MOORE 3 | 345 | 22.872 | 22.961 | 0.089
GEN-2017-085 | North | 17 - Western South Dakota | 640590 | MONOLITH 3 | 345 | 22.411 | 22.496 | 0.085
GEN-2017-085 | North | 17 - Western South Dakota | 640372 | SUTTON 7 | 115 | 6.455 | 6.521 | 0.066
GEN-2017-085 | North | 17 - Western South Dakota | 640105 | CARLJCT7 | 115 | 5.644 | 5.7 | 0.056
GEN-2017-085 | North | 17 - Western South Dakota | 650242 | FOLSM&PHIL7 | 115 | 28.87 | 28.92 | 0.05
GEN-2017-085 | North | 17 - Western South Dakota | 640271 | MCCOOL 3 | 345 | 10.526 | 10.571 | 0.045
GEN-2017-085 | North | 17 - Western South Dakota | 640179 | GENEVA 8 | 69 | 4.39 | 4.434 | 0.044
GEN-2017-085 | North | 17 - Western South Dakota | 650189 | 103&ROKEBY3 | 345 | 20.487 | 20.528 | 0.041
GEN-2017-085 | North | 17 - Western South Dakota | 650246 | SW7&BENNET7 | 115 | 23.941 | 23.982 | 0.041
GEN-2017-085 | North | 17 - Western South Dakota | 650290 | ROKEBY 7 | 115 | 27.139 | 27.18 | 0.041
GEN-2017-085 | North | 17 - Western South Dakota | 650238 | 20PIONEERS7 | 115 | 27.815 | 27.855 | 0.04
GEN-2017-085 | North | 17 - Western South Dakota | 640218 | HEBRN N7 | 115 | 5.88 | 5.917 | 0.037
GEN-2017-085 | North | 17 - Western South Dakota | 641087 | EGYCNTR7 | 115 | 18.082 | 18.119 | 0.037
GEN-2017-085 | North | 17 - Western South Dakota | 640215 | HASTING7 | 115 | 19.266 | 19.302 | 0.036
GEN-2017-085 | North | 17 - Western South Dakota | 641088 | HASTCTY7 | 115 | 19.266 | 19.302 | 0.036
GEN-2017-085 | North | 17 - Western South Dakota | 650185 | WAGENER 3 | 345 | 20.361 | 20.397 | 0.036
GEN-2017-085 | North | 17 - Western South Dakota | 650114 | NW68HOLDRG3 | 345 | 16.968 | 17.003 | 0.035
GEN-2017-085 | North | 17 - Western South Dakota | 650270 | 70&CALVERT7 | 115 | 27.689 | 27.724 | 0.035
GEN-2017-085 | North | 17 - Western South Dakota | 640220 | HEBRON 7 | 115 | 5.583 | 5.616 | 0.033
GEN-2017-085 | North | 17 - Western South Dakota | 641085 | E7THST 7 | 115 | 18.29 | 18.322 | 0.032
GEN-2017-085 | North | 17 - Western South Dakota | 650214 | NW68HOLDRG7 | 115 | 25.498 | 25.53 | 0.032
GEN-2017-085 | North | 17 - Western South Dakota | 650230 | 2&N 7 | 115 | 26.098 | 26.129 | 0.031
GEN-2017-085 | North | 17 - Western South Dakota | 650247 | 40&BENNET 7 | 115 | 22.275 | 22.306 | 0.031
GEN-2017-085 | North | 17 - Western South Dakota | 640200 | GR ISLD4 | 230 | 16.996 | 17.026 | 0.03
GEN-2017-085 | North | 17 - Western South Dakota | 640413 | YORK SW7 | 115 | 8.211 | 8.24 | 0.029
GEN-2017-085 | North | 17 - Western South Dakota | 650250 | 40&ROKEBY 7 | 115 | 21.869 | 21.896 | 0.027
GEN-2017-085 | North | 17 - Western South Dakota | 653571 | GR ISLD3 | 345 | 12.602 | 12.629 | 0.027
GEN-2017-085 | North | 17 - Western South Dakota | 653871 | GR ISLD-LNX3 | 345 | 12.48 | 12.506 | 0.026
GEN-2017-085 | North | 17 - Western South Dakota | 650258 | 40&GERTIE 7 | 115 | 23.525 | 23.551 | 0.026
GEN-2017-085 | North | 17 - Western South Dakota | 650229 | 27&PLR 7 | 115 | 21.325 | 21.35 | 0.025
GEN-2017-085 | North | 17 - Western South Dakota | 650218 | 3&VANDORN 7 | 115 | 21.979 | 22.002 | 0.023
GEN-2017-085 | North | 17 - Western South Dakota | 650276 | 76&ROKEBY 7 | 115 | 19.085 | 19.105 | 0.02
GEN-2017-085 | North | 17 - Western South Dakota | 640411 | YORK 7 | 115 | 7.674 | 7.693 | 0.019
GEN-2017-085 | North | 17 - Western South Dakota | 640088 | BPS SUB7 | 115 | 16.236 | 16.254 | 0.018
GEN-2017-085 | North | 17 - Western South Dakota | 640415 | CARLJCT8 | 69 | 3.663 | 3.681 | 0.018
GEN-2017-085 | North | 17 - Western South Dakota | 640373 | SUTTON 8 | 69 | 3.943 | 3.961 | 0.018
GEN-2017-085 | North | 17 - Western South Dakota | 560062 | G15-088-TAP | 345 | 11.014 | 11.029 | 0.015
GEN-2017-085 | North | 17 - Western South Dakota | 641083 | D.HENRY7 | 115 | 11.597 | 11.611 | 0.014
GEN-2017-085 | North | 17 - Western South Dakota | 563219 | GEN-2015-088 | 345 | 10.598 | 10.612 | 0.014
GEN-2017-085 | North | 17 - Western South Dakota | 640313 | PAULINE7 | 115 | 16.428 | 16.442 | 0.014
GEN-2017-085 | North | 17 - Western South Dakota | 641090 | S. 281 7 | 115 | 11.458 | 11.472 | 0.014
GEN-2017-085 | North | 17 - Western South Dakota | 640273 | MCCOOL 8 | 69 | 5.574 | 5.587 | 0.013
GEN-2017-085 | North | 17 - Western South Dakota | 640076 | BEATRCE7 | 115 | 13.311 | 13.323 | 0.012
GEN-2017-085 | North | 17 - Western South Dakota | 640111 | CLATONA7 | 115 | 10.877 | 10.889 | 0.012
GEN-2017-085 | North | 17 - Western South Dakota | 640169 | FAIRBRY7 | 115 | 5.112 | 5.121 | 0.009
GEN-2017-085 | North | 17 - Western South Dakota | 640214 | HASTING4 | 230 | 7.436 | 7.444 | 0.008
GEN-2017-085 | North | 17 - Western South Dakota | 640125 | COLMB.E3 | 345 | 9.724 | 9.732 | 0.008
GEN-2017-085 | North | 17 - Western South Dakota | 640368 | SUPEROR7 | 115 | 3.431 | 3.438 | 0.007
GEN-2017-085 | North | 17 - Western South Dakota | 640063 | AURORA_7 | 115 | 7.171 | 7.178 | 0.007
GEN-2017-085 | North | 17 - Western South Dakota | 645458 | S3458 3 | 345 | 28.887 | 28.894 | 0.007
GEN-2017-085 | North | 17 - Western South Dakota | 640312 | PAULINE3 | 345 | 8.134 | 8.14 | 0.006
GEN-2017-085 | North | 17 - Western South Dakota | 640374 | SWEET W3 | 345 | 10.828 | 10.834 | 0.006
GEN-2017-085 | North | 17 - Western South Dakota | 640375 | TAMORA 7 | 115 | 5.985 | 5.99 | 0.005
GEN-2017-085 | North | 17 - Western South Dakota | 640208 | HARBINE7 | 115 | 6.844 | 6.848 | 0.004
GEN-2017-085 | North | 17 - Western South Dakota | 640171 | FIRTH 7 | 115 | 6.882 | 6.885 | 0.003
GEN-2017-085 | North | 17 - Western South Dakota | 640443 | YORK 8 | 69 | 2.682 | 2.684 | 0.002
GEN-2017-085 | North | 17 - Western South Dakota | 640447 | YORK.SW T2 8 | 69 | 2.427 | 2.429 | 0.002
GEN-2017-085 | North | 17 - Western South Dakota | 640139 | COOPER 3 | 345 | 26.142 | 26.144 | 0.002
GEN-2017-085 | North | 17 - Western South Dakota | 640074 | BEAT. S7 | 115 | 5.383 | 5.384 | 0.001
GEN-2017-085 | North | 17 - Western South Dakota | 640362 | STERLNG7 | 115 | 4.599 | 4.598 | -0.001
GEN-2017-085 | North | 17 - Western South Dakota | 640361 | STEINER7 | 115 | 4.46 | 4.456 | -0.004
GEN-2017-094 | North | 17 - Western South Dakota | 589320 | GEN-2017-094 | 230 | 10.49 | 10.974 | 0.484
GEN-2017-094 | North | 17 - Western South Dakota | 589324 | G17-094-TAP | 230 | 10.49 | 10.974 | 0.484
GEN-2017-094 | North | 17 - Western South Dakota | 652514 | HURON 4 | 230 | 10.929 | 11.165 | 0.236
GEN-2017-094 | North | 17 - Western South Dakota | 652507 | FTTHOMP4 | 230 | 19.827 | 20.036 | 0.209
GEN-2017-094 | North | 17 - Western South Dakota | 659205 | BROADLND-BE4 | 230 | 9.93 | 10.117 | 0.187
GEN-2017-094 | North | 17 - Western South Dakota | 652515 | HURON 7 | 115 | 15.505 | 15.61 | 0.105
GEN-2017-094 | North | 17 - Western South Dakota | 660009 | BTAP WP7 | 115 | 15.055 | 15.156 | 0.101
GEN-2017-094 | North | 17 - Western South Dakota | 652540 | BIGBND14 | 230 | 12.08 | 12.156 | 0.076
GEN-2017-094 | North | 17 - Western South Dakota | 652541 | BIGBND24 | 230 | 11.911 | 11.986 | 0.075
GEN-2017-094 | North | 17 - Western South Dakota | 652614 | CARPENTER 4 | 230 | 6.987 | 7.051 | 0.064
GEN-2017-094 | North | 17 - Western South Dakota | 660003 | HURONWP7 | 115 | 10.146 | 10.203 | 0.057
GEN-2017-094 | North | 17 - Western South Dakota | 652519 | OAHE 4 | 230 | 14.59 | 14.634 | 0.044
GEN-2017-094 | North | 17 - Western South Dakota | 652530 | WATERTN4 | 230 | 13.672 | 13.711 | 0.039
GEN-2017-094 | North | 17 - Western South Dakota | 652630 | WATERTNCAP 4 | 230 | 13.52 | 13.558 | 0.038
GEN-2017-094 | North | 17 - Western South Dakota | 660012 | HURON WP 8 | 69 | 6.075 | 6.111 | 0.036
GEN-2017-094 | North | 17 - Western South Dakota | 659120 | BROADLND-BE3 | 345 | 4.063 | 4.098 | 0.035
GEN-2017-094 | North | 17 - Western South Dakota | 659421 | BD.LS-AV-BE3 | 345 | 4.063 | 4.098 | 0.035
GEN-2017-094 | North | 17 - Western South Dakota | 587764 | G16-094-TAP | 230 | 9.328 | 9.355 | 0.027
GEN-2017-094 | North | 17 - Western South Dakota | 587760 | GEN-2016-094 | 230 | 9.168 | 9.194 | 0.026
GEN-2017-094 | North | 17 - Western South Dakota | 652284 | HURON 8 | 69 | 3.749 | 3.772 | 0.023
GEN-2017-094 | North | 17 - Western South Dakota | 655066 | SW352-ER8 | 69 | 3.733 | 3.756 | 0.023
GEN-2017-094 | North | 17 - Western South Dakota | 655067 | SW353-ER8 | 69 | 3.737 | 3.76 | 0.023
GEN-2017-094 | North | 17 - Western South Dakota | 655063 | SW341-ER8 | 69 | 3.695 | 3.717 | 0.022
GEN-2017-094 | North | 17 - Western South Dakota | 655064 | SW343-ER8 | 69 | 3.668 | 3.69 | 0.022
GEN-2017-094 | North | 17 - Western South Dakota | 660040 | DAKOTACCESS7 | 115 | 4.547 | 4.568 | 0.021
GEN-2017-094 | North | 17 - Western South Dakota | 655481 | REDFELD-ER7 | 115 | 4.194 | 4.211 | 0.017
GEN-2017-094 | North | 17 - Western South Dakota | 655058 | MOS-HRON-ER8 | 69 | 2.7 | 2.717 | 0.017
GEN-2017-094 | North | 17 - Western South Dakota | 660002 | REDFLD 7 | 115 | 4.067 | 4.084 | 0.017
GEN-2017-094 | North | 17 - Western South Dakota | 652506 | FTTHOMP3 | 345 | 8.637 | 8.653 | 0.016
GEN-2017-094 | North | 17 - Western South Dakota | 652807 | FTTHOM2-LNX3 | 345 | 8.637 | 8.653 | 0.016
GEN-2017-094 | North | 17 - Western South Dakota | 652806 | FTTHOM1-LNX3 | 345 | 8.578 | 8.593 | 0.015
GEN-2017-094 | North | 17 - Western South Dakota | 652529 | WATERTN3 | 345 | 9.898 | 9.912 | 0.014
GEN-2017-094 | North | 17 - Western South Dakota | 652829 | WATERTN-LNX3 | 345 | 9.895 | 9.909 | 0.014
GEN-2017-094 | North | 17 - Western South Dakota | 655236 | MORNINGS-ER8 | 69 | 1.903 | 1.915 | 0.012
GEN-2017-094 | North | 17 - Western South Dakota | 659187 | GROTON__-BE7 | 115 | 16.4 | 16.411 | 0.011
GEN-2017-094 | North | 17 - Western South Dakota | 652509 | FTRANDL4 | 230 | 10.745 | 10.756 | 0.011
GEN-2017-094 | North | 17 - Western South Dakota | 652512 | GROTON 7 | 115 | 16.38 | 16.391 | 0.011
GEN-2017-094 | North | 17 - Western South Dakota | 652568 | GROTONSOUTH7 | 115 | 16.42 | 16.431 | 0.011
GEN-2017-094 | North | 17 - Western South Dakota | 648506 | PR BRZ 4 | 230 | 4.412 | 4.422 | 0.01
GEN-2017-094 | North | 17 - Western South Dakota | 655482 | REDFELD-ER8 | 69 | 2.873 | 2.883 | 0.01
GEN-2017-094 | North | 17 - Western South Dakota | 659275 | GROTON_G-BE7 | 115 | 16.07 | 16.08 | 0.01
GEN-2017-094 | North | 17 - Western South Dakota | 652531 | WATERTN7 | 115 | 12.413 | 12.422 | 0.009
GEN-2017-094 | North | 17 - Western South Dakota | 652528 | WOONSKT7 | 115 | 5.352 | 5.36 | 0.008
GEN-2017-094 | North | 17 - Western South Dakota | 655054 | MOS-RDFL-ER8 | 69 | 2.094 | 2.101 | 0.007
GEN-2017-094 | North | 17 - Western South Dakota | 655055 | SW311-ER8 | 69 | 1.2 | 1.207 | 0.007
GEN-2017-094 | North | 17 - Western South Dakota | 655238 | FRANKFRT-ER8 | 69 | 2.126 | 2.133 | 0.007
GEN-2017-094 | North | 17 - Western South Dakota | 652520 | OAHE 7 | 115 | 11.413 | 11.42 | 0.007
GEN-2017-094 | North | 17 - Western South Dakota | 659420 | AV.LS-BD-BE3 | 345 | 16.138 | 16.145 | 0.007
GEN-2017-094 | North | 17 - Western South Dakota | 655487 | SULLYBT-ER4 | 230 | 6.51 | 6.516 | 0.006
GEN-2017-094 | North | 17 - Western South Dakota | 655510 | SB.LS-WK-ER4 | 230 | 6.51 | 6.516 | 0.006
GEN-2017-094 | North | 17 - Western South Dakota | 652510 | FTRANDL7 | 115 | 12.572 | 12.578 | 0.006
GEN-2017-094 | North | 17 - Western South Dakota | 655490 | WHTSWAN-ER7 | 115 | 12.263 | 12.269 | 0.006
GEN-2017-094 | North | 17 - Western South Dakota | 658088 | WTREAST7 | 115 | 9.648 | 9.654 | 0.006
GEN-2017-094 | North | 17 - Western South Dakota | 655059 | MOS-ASHT-ER8 | 69 | 1.663 | 1.669 | 0.006
GEN-2017-094 | North | 17 - Western South Dakota | 659165 | G09_001IST | 345 | 6.139 | 6.144 | 0.005
GEN-2017-094 | North | 17 - Western South Dakota | 659424 | LO.LS-FT-BE3 | 345 | 16.339 | 16.343 | 0.004
GEN-2017-094 | North | 17 - Western South Dakota | 655355 | WOONSKT-ER8 | 69 | 3.648 | 3.652 | 0.004
GEN-2017-094 | North | 17 - Western South Dakota | 659160 | GROTON__-BE3 | 345 | 5.902 | 5.906 | 0.004
GEN-2017-094 | North | 17 - Western South Dakota | 659472 | CROCKER_-UA3 | 345 | 5.315 | 5.319 | 0.004
GEN-2017-094 | North | 17 - Western South Dakota | 658090 | WTRTNPP | 115 | 9.118 | 9.122 | 0.004
GEN-2017-094 | North | 17 - Western South Dakota | 658092 | WTRWEST7 | 115 | 8.462 | 8.466 | 0.004
GEN-2017-094 | North | 17 - Western South Dakota | 658094 | WTRPELI7 | 115 | 8.596 | 8.6 | 0.004
GEN-2017-094 | North | 17 - Western South Dakota | 655419 | SW561-ER7 | 115 | 5.139 | 5.142 | 0.003
GEN-2017-094 | North | 17 - Western South Dakota | 652600 | ASH TAP | 115 | 8.668 | 8.67 | 0.002
GEN-2017-094 | North | 17 - Western South Dakota | 655072 | SW373-ER8 | 69 | 2.346 | 2.348 | 0.002
GEN-2017-094 | North | 17 - Western South Dakota | 652489 | PIERRE 7 | 115 | 8.235 | 8.236 | 0.001
GEN-2017-094 | North | 17 - Western South Dakota | 640540 | MEADOWGROVE4 | 230 | 5.665 | 5.666 | 0.001
GEN-2017-094 | North | 17 - Western South Dakota | 655765 | WHITLOCK_-RM | 230 | 4.563 | 4.564 | 0.001
GEN-2017-094 | North | 17 - Western South Dakota | 658120 | GARFLD 7 | 115 | 7.151 | 7.152 | 0.001
GEN-2017-094 | North | 17 - Western South Dakota | 659310 | ORDWAY__-BE7 | 115 | 7.1 | 7.101 | 0.001
GEN-2017-094 | North | 17 - Western South Dakota | 655499 | CARPENTR-ER8 | 69 | 3.324 | 3.325 | 0.001
GEN-2017-094 | North | 17 - Western South Dakota | 655412 | CRPNTR-ER8 | 69 | 2.948 | 2.949 | 0.001
GEN-2017-094 | North | 17 - Western South Dakota | 560074 | G16-017_TAP | 345 | 5.626 | 5.627 | 0.001
GEN-2017-094 | North | 17 - Western South Dakota | 587130 | GEN-2016-017 | 345 | 5.621 | 5.622 | 0.001
GEN-2017-094 | North | 17 - Western South Dakota | 652491 | IRVSIMM7 | 115 | 8.196 | 8.197 | 0.001
GEN-2017-094 | North | 17 - Western South Dakota | 655457 | BRISTOL-ER7 | 115 | 4.667 | 4.667 | 0
GEN-2017-094 | North | 17 - Western South Dakota | 652242 | WATERT18 | 69 | 3.981 | 3.981 | 0
GEN-2017-094 | North | 17 - Western South Dakota | 655056 | SW313-ER8 | 69 | 1.623 | 1.623 | 0
GEN-2017-094 | North | 17 - Western South Dakota | 655073 | MOS-CRPN-ER8 | 69 | 2.544 | 2.544 | 0
GEN-2017-094 | North | 17 - Western South Dakota | 655111 | SW714-ER8 | 69 | 3.335 | 3.335 | 0
GEN-2017-094 | North | 17 - Western South Dakota | 655334 | OKOBOJO-ER8 | 69 | 2.445 | 2.445 | 0
GEN-2017-094 | North | 17 - Western South Dakota | 655488 | SULLYBT-ER8 | 69 | 2.456 | 2.456 | 0
GEN-2017-094 | North | 17 - Western South Dakota | 655108 | MOS-RVLE-ER8 | 69 | 3.944 | 3.943 | -0.001
GEN-2017-094 | North | 17 - Western South Dakota | 655158 | MOS-HYDE-ER8 | 69 | 3.065 | 3.064 | -0.001
GEN-2017-094 | North | 17 - Western South Dakota | 655373 | MOS-SLY2-ER8 | 69 | 2.453 | 2.452 | -0.001
GEN-2017-094 | North | 17 - Western South Dakota | 655329 | GANNVALL-ER8 | 69 | 0.845 | 0.844 | -0.001
GEN-2017-094 | North | 17 - Western South Dakota | 655384 | NWPS8645-ER8 | 69 | 2.027 | 2.026 | -0.001
GEN-2017-094 | North | 17 - Western South Dakota | 652537 | WHITE 3 | 345 | 17.669 | 17.668 | -0.001
GEN-2017-094 | North | 17 - Western South Dakota | 652522 | SUMMIT-7 | 115 | 4.776 | 4.774 | -0.002
GEN-2017-094 | North | 17 - Western South Dakota | 659123 | STORLA__-BE7 | 115 | 6.68 | 6.678 | -0.002
GEN-2017-094 | North | 17 - Western South Dakota | 655463 | ARLNGTN-ER8 | 69 | 2.706 | 2.704 | -0.002
GEN-2017-094 | North | 17 - Western South Dakota | 652259 | EAGLEBE8 | 69 | 1.697 | 1.695 | -0.002
GEN-2017-094 | North | 17 - Western South Dakota | 655040 | MOS-ASTR-ER8 | 69 | 1.242 | 1.24 | -0.002
GEN-2017-094 | North | 17 - Western South Dakota | 655079 | MOS-KLKP-ER8 | 69 | 0.767 | 0.765 | -0.002
GEN-2017-094 | North | 17 - Western South Dakota | 655352 | AMES-ER8 | 69 | 1.304 | 1.302 | -0.002
GEN-2017-094 | North | 17 - Western South Dakota | 652209 | SUMMIT-8 | 69 | 2.754 | 2.752 | -0.002
GEN-2017-094 | North | 17 - Western South Dakota | 655294 | MORITZ-ER8 | 69 | 2.064 | 2.062 | -0.002
GEN-2017-094 | North | 17 - Western South Dakota | 652502 | BERSFRD7 | 115 | 3.945 | 3.942 | -0.003
GEN-2017-094 | North | 17 - Western South Dakota | 652260 | EAGLEBW8 | 69 | 2.207 | 2.204 | -0.003
GEN-2017-094 | North | 17 - Western South Dakota | 655328 | BIGBEND-ER8 | 69 | 3.098 | 3.095 | -0.003
GEN-2017-094 | North | 17 - Western South Dakota | 655080 | MOS-HLTP-ER8 | 69 | 1.315 | 1.312 | -0.003
GEN-2017-094 | North | 17 - Western South Dakota | 652607 | WESSINGTON 4 | 230 | 6.638 | 6.635 | -0.003
GEN-2017-094 | North | 17 - Western South Dakota | 655475 | LAKPLAT-ER4 | 230 | 5.658 | 5.655 | -0.003
GEN-2017-094 | North | 17 - Western South Dakota | 659295 | SD.PW1__-BE4 | 230 | 5.534 | 5.531 | -0.003
GEN-2017-094 | North | 17 - Western South Dakota | 652475 | BONESTL7 | 115 | 3.565 | 3.562 | -0.003
GEN-2017-094 | North | 17 - Western South Dakota | 652476 | EAGLEBT7 | 115 | 2.009 | 2.006 | -0.003
GEN-2017-094 | North | 17 - Western South Dakota | 655462 | ARLNGTN-ER7 | 115 | 4.355 | 4.352 | -0.003
GEN-2017-094 | North | 17 - Western South Dakota | 652225 | BROOKNG8 | 69 | 2.996 | 2.993 | -0.003
GEN-2017-094 | North | 17 - Western South Dakota | 652249 | ARMOUR 8 | 69 | 2.495 | 2.492 | -0.003
GEN-2017-094 | North | 17 - Western South Dakota | 652276 | FTTHOMP8 | 69 | 4.207 | 4.204 | -0.003
GEN-2017-094 | North | 17 - Western South Dakota | 655153 | MOS-AMES-ER8 | 69 | 4.143 | 4.14 | -0.003
GEN-2017-094 | North | 17 - Western South Dakota | 655466 | BLAIR-ER8 | 69 | 2.492 | 2.489 | -0.003
GEN-2017-094 | North | 17 - Western South Dakota | 652243 | FAITH 7 | 115 | 2.398 | 2.394 | -0.004
GEN-2017-094 | North | 17 - Western South Dakota | 652455 | ROBERTSCTY7 | 115 | 3.204 | 3.2 | -0.004
GEN-2017-094 | North | 17 - Western South Dakota | 652478 | GREGORY7 | 115 | 2.187 | 2.183 | -0.004
GEN-2017-094 | North | 17 - Western South Dakota | 655250 | CHMBRLAN-ER8 | 69 | 1.594 | 1.59 | -0.004
GEN-2017-094 | North | 17 - Western South Dakota | 655386 | MOS-RVR1-ER8 | 69 | 2.105 | 2.101 | -0.004
GEN-2017-094 | North | 17 - Western South Dakota | 652501 | ARMOUR 7 | 115 | 4.206 | 4.202 | -0.004
GEN-2017-094 | North | 17 - Western South Dakota | 652474 | AURORA 7 | 115 | 4.457 | 4.452 | -0.005
GEN-2017-094 | North | 17 - Western South Dakota | 652504 | BROOKNG7 | 115 | 7.194 | 7.189 | -0.005
GEN-2017-094 | North | 17 - Western South Dakota | 652518 | MTVERN 7 | 115 | 4.378 | 4.373 | -0.005
GEN-2017-094 | North | 17 - Western South Dakota | 652525 | TYNDALL7 | 115 | 3.88 | 3.875 | -0.005
GEN-2017-094 | North | 17 - Western South Dakota | 655418 | FREEMAN-ER7 | 115 | 2.607 | 2.602 | -0.005
GEN-2017-094 | North | 17 - Western South Dakota | 652563 | SPENCER5 | 161 | 9.484 | 9.479 | -0.005
GEN-2017-094 | North | 17 - Western South Dakota | 563230 | GEN-2015-089 | 230 | 5.395 | 5.389 | -0.006
GEN-2017-094 | North | 17 - Western South Dakota | 652481 | MIDLAND7 | 115 | 3.497 | 3.491 | -0.006
GEN-2017-094 | North | 17 - Western South Dakota | 655465 | BLAIR-ER4 | 230 | 9.286 | 9.28 | -0.006
GEN-2017-094 | North | 17 - Western South Dakota | 659122 | STORLA__-BE4 | 230 | 5.931 | 5.925 | -0.006
GEN-2017-094 | North | 17 - Western South Dakota | 652505 | FLANDRU7 | 115 | 4.11 | 4.104 | -0.006
GEN-2017-094 | North | 17 - Western South Dakota | 652538 | WHITE 7 | 115 | 9.191 | 9.185 | -0.006
GEN-2017-094 | North | 17 - Western South Dakota | 620322 | BSSOUTH4 | 230 | 11.955 | 11.948 | -0.007
GEN-2017-094 | North | 17 - Western South Dakota | 652486 | PHILIP 4 | 230 | 4.029 | 4.022 | -0.007
GEN-2017-094 | North | 17 - Western South Dakota | 640349 | SPENCER7 | 115 | 4.606 | 4.599 | -0.007
GEN-2017-094 | North | 17 - Western South Dakota | 655417 | ROSWELL-ER7 | 115 | 2.627 | 2.62 | -0.007
GEN-2017-094 | North | 17 - Western South Dakota | 620214 | BIGSTON7 | 115 | 2.394 | 2.387 | -0.007
GEN-2017-094 | North | 17 - Western South Dakota | 660005 | TRIPP 7 | 115 | 4.006 | 3.999 | -0.007
GEN-2017-094 | North | 17 - Western South Dakota | 652235 | SIOUXFL8 | 69 | 3.932 | 3.925 | -0.007
GEN-2017-094 | North | 17 - Western South Dakota | 652604 | APPLEDORN 8 | 69 | 2.541 | 2.534 | -0.007
GEN-2017-094 | North | 17 - Western South Dakota | 655485 | RASMUSN-ER8 | 69 | 3.265 | 3.258 | -0.007
GEN-2017-094 | North | 17 - Western South Dakota | 620314 | BIGSTON4 | 230 | 12.119 | 12.111 | -0.008
GEN-2017-094 | North | 17 - Western South Dakota | 588590 | GEN-2017-014 | 230 | 5.258 | 5.25 | -0.008
GEN-2017-094 | North | 17 - Western South Dakota | 588594 | G17-014-TAP | 230 | 5.258 | 5.25 | -0.008
GEN-2017-094 | North | 17 - Western South Dakota | 652567 | DENISON4 | 230 | 4.421 | 4.413 | -0.008
GEN-2017-094 | North | 17 - Western South Dakota | 659188 | PHILIP_T-BE4 | 230 | 5.245 | 5.237 | -0.008
GEN-2017-094 | North | 17 - Western South Dakota | 603009 | GRANT 7 | 115 | 3.957 | 3.949 | -0.008
GEN-2017-094 | North | 17 - Western South Dakota | 640305 | ONEILL 7 | 115 | 4.005 | 3.997 | -0.008
GEN-2017-094 | North | 17 - Western South Dakota | 655385 | MOS-LKPL-ER8 | 69 | 4.054 | 4.046 | -0.008
GEN-2017-094 | North | 17 - Western South Dakota | 655476 | LAKPLAT-ER8 | 69 | 4.069 | 4.061 | -0.008
GEN-2017-094 | North | 17 - Western South Dakota | 652484 | NUNDRWD4 | 230 | 3.983 | 3.974 | -0.009
GEN-2017-094 | North | 17 - Western South Dakota | 655494 | HANLON1-ER8 | 69 | 2.999 | 2.99 | -0.009
GEN-2017-094 | North | 17 - Western South Dakota | 652561 | DENISON5 | 161 | 5.498 | 5.489 | -0.009
GEN-2017-094 | North | 17 - Western South Dakota | 660008 | MITCLNW7 | 115 | 5.383 | 5.374 | -0.009
GEN-2017-094 | North | 17 - Western South Dakota | 655469 | VFODNES-ER8 | 69 | 4.189 | 4.18 | -0.009
GEN-2017-094 | North | 17 - Western South Dakota | 620325 | BROWNSV4 | 230 | 5.476 | 5.466 | -0.01
GEN-2017-094 | North | 17 - Western South Dakota | 652526 | UTICAJC4 | 230 | 7.875 | 7.865 | -0.01
GEN-2017-094 | North | 17 - Western South Dakota | 655468 | VFODNES-ER7 | 115 | 4.974 | 4.964 | -0.01
GEN-2017-094 | North | 17 - Western South Dakota | 660004 | MITCHEL7 | 115 | 5.777 | 5.767 | -0.01
GEN-2017-094 | North | 17 - Western South Dakota | 655495 | HANLON2-ER8 | 69 | 3.002 | 2.992 | -0.01
GEN-2017-094 | North | 17 - Western South Dakota | 560347 | G10-051-TAP | 230 | 7.338 | 7.327 | -0.011
GEN-2017-094 | North | 17 - Western South Dakota | 652606 | LETCHER4 | 230 | 4.747 | 4.736 | -0.011
GEN-2017-094 | North | 17 - Western South Dakota | 660007 | MENNOJT7 | 115 | 6.611 | 6.6 | -0.011
GEN-2017-094 | North | 17 - Western South Dakota | 655493 | HANLON-ER7 | 115 | 3.89 | 3.878 | -0.012
GEN-2017-094 | North | 17 - Western South Dakota | 655484 | RASMUSN-ER4 | 230 | 6.682 | 6.67 | -0.012
GEN-2017-094 | North | 17 - Western South Dakota | 619975 | GRE-WILLMAR4 | 230 | 5.35 | 5.337 | -0.013
GEN-2017-094 | North | 17 - Western South Dakota | 652398 | VFODNES4 | 230 | 6.792 | 6.779 | -0.013
GEN-2017-094 | North | 17 - Western South Dakota | 652609 | LETCHER7 | 115 | 6.055 | 6.042 | -0.013
GEN-2017-094 | North | 17 - Western South Dakota | 652554 | MORRIS 4 | 230 | 4.517 | 4.504 | -0.013
GEN-2017-094 | North | 17 - Western South Dakota | 660026 | NAPA JCT7 | 115 | 8.44 | 8.426 | -0.014
GEN-2017-094 | North | 17 - Western South Dakota | 659735 | CLEVELND-LO4 | 230 | 4.9 | 4.886 | -0.014
GEN-2017-094 | North | 17 - Western South Dakota | 652487 | PHILIP 7 | 115 | 5.92 | 5.906 | -0.014
GEN-2017-094 | North | 17 - Western South Dakota | 652626 | UTICAJC7 | 115 | 8.944 | 8.93 | -0.014
GEN-2017-094 | North | 17 - Western South Dakota | 652564 | SIOUXCY3 | 345 | 15.069 | 15.054 | -0.015
GEN-2017-094 | North | 17 - Western South Dakota | 640386 | TWIN CH4 | 230 | 8.84 | 8.825 | -0.015
GEN-2017-094 | North | 17 - Western South Dakota | 640126 | E.COL. 4 | 230 | 9.618 | 9.602 | -0.016
GEN-2017-094 | North | 17 - Western South Dakota | 652513 | HANLON 4 | 230 | 5.643 | 5.627 | -0.016
GEN-2017-094 | North | 17 - Western South Dakota | 652582 | APPLEDORN 4 | 230 | 6.989 | 6.973 | -0.016
GEN-2017-094 | North | 17 - Western South Dakota | 652583 | DENISON8 | 69 | 11.265 | 11.249 | -0.016
GEN-2017-094 | North | 17 - Western South Dakota | 640131 | COLMB.W4 | 230 | 9.689 | 9.672 | -0.017
GEN-2017-094 | North | 17 - Western South Dakota | 659900 | EAGLE___-NI4 | 230 | 7.235 | 7.217 | -0.018
GEN-2017-094 | North | 17 - Western South Dakota | 635223 | PLYMOTH5 | 161 | 20.471 | 20.453 | -0.018
GEN-2017-094 | North | 17 - Western South Dakota | 652574 | SIOUXCY8 | 69 | 18.012 | 17.994 | -0.018
GEN-2017-094 | North | 17 - Western South Dakota | 640387 | TWIN CH7 | 115 | 11.274 | 11.255 | -0.019
GEN-2017-094 | North | 17 - Western South Dakota | 640133 | COLMBUS4 | 230 | 11.276 | 11.257 | -0.019
GEN-2017-094 | North | 17 - Western South Dakota | 640343 | SHELCRK4 | 230 | 10.685 | 10.666 | -0.019
GEN-2017-094 | North | 17 - Western South Dakota | 659311 | PAHOJA__-BE4 | 230 | 7.352 | 7.333 | -0.019
GEN-2017-094 | North | 17 - Western South Dakota | 659716 | MAPLETAP-LO7 | 115 | 12.775 | 12.755 | -0.02
GEN-2017-094 | North | 17 - Western South Dakota | 652566 | SIOUXCY5 | 161 | 20.911 | 20.891 | -0.02
GEN-2017-094 | North | 17 - Western South Dakota | 602004 | SPLT RK4 | 230 | 12.865 | 12.841 | -0.024
GEN-2017-094 | North | 17 - Western South Dakota | 640134 | KELLY 7 | 115 | 17.647 | 17.622 | -0.025
GEN-2017-094 | North | 17 - Western South Dakota | 652523 | SIOUXFL4 | 230 | 13.301 | 13.276 | -0.025
GEN-2017-094 | North | 17 - Western South Dakota | 652550 | GRANITF4 | 230 | 12.388 | 12.361 | -0.027
GEN-2017-094 | North | 17 - Western South Dakota | 602008 | MINVALT4 | 230 | 12.278 | 12.25 | -0.028
GEN-2017-094 | North | 17 - Western South Dakota | 602009 | MNVLTAP4 | 230 | 12.243 | 12.215 | -0.028
GEN-2017-094 | North | 17 - Western South Dakota | 652552 | SIOUXCY2 | 230 | 19.838 | 19.81 | -0.028
GEN-2017-094 | North | 17 - Western South Dakota | 652565 | SIOUXCY4 | 230 | 19.838 | 19.81 | -0.028
GEN-2017-094 | North | 17 - Western South Dakota | 655377 | SW1145-ER7 | 115 | 25.501 | 25.466 | -0.035
GEN-2017-094 | North | 17 - Western South Dakota | 652524 | SIOUXFL7 | 115 | 26.861 | 26.825 | -0.036
GEN-2017-094 | North | 17 - Western South Dakota | 603012 | LAWRENC7 | 115 | 30.512 | 30.475 | -0.037
GEN-2017-094 | North | 17 - Western South Dakota | 652551 | GRANITF7 | 115 | 16.704 | 16.667 | -0.037
GEN-2017-094 | North | 17 - Western South Dakota | 603016 | SPLT RK7 | 115 | 38.962 | 38.921 | -0.041
GEN-2017-094 | North | 17 - Western South Dakota | 652532 | GR PRAIRIE 3 | 345 | 7.826 | 7.782 | -0.044
GEN-2017-094 | North | 17 - Western South Dakota | 652833 | GRPRAR2-LNX3 | 345 | 7.826 | 7.782 | -0.044
GEN-2017-097 | North | 17 - Western South Dakota | 587764 | G16-094-TAP | 230 | 9.307 | 9.37 | 0.063
GEN-2017-097 | North | 17 - Western South Dakota | 588590 | GEN-2017-014 | 230 | 3.644 | 5.185 | 1.541
GEN-2017-097 | North | 17 - Western South Dakota | 588594 | G17-014-TAP | 230 | 3.644 | 5.185 | 1.541
GEN-2017-097 | North | 17 - Western South Dakota | 589020 | GEN-2017-064 | 230 | 2.833 | 2.937 | 0.104
GEN-2017-097 | North | 17 - Western South Dakota | 589024 | G17-064-TAP | 230 | 2.833 | 2.937 | 0.104
GEN-2017-097 | North | 17 - Western South Dakota | 640404 | WAYSIDE4 | 230 | 2.889 | 2.939 | 0.05
GEN-2017-097 | North | 17 - Western South Dakota | 652484 | NUNDRWD4 | 230 | 3.581 | 3.99 | 0.409
GEN-2017-097 | North | 17 - Western South Dakota | 652486 | PHILIP 4 | 230 | 3.246 | 4.006 | 0.76
GEN-2017-097 | North | 17 - Western South Dakota | 652497 | MAURINE4 | 230 | 2.922 | 2.983 | 0.061
GEN-2017-097 | North | 17 - Western South Dakota | 652507 | FTTHOMP4 | 230 | 20.055 | 20.221 | 0.166
GEN-2017-097 | North | 17 - Western South Dakota | 652519 | OAHE 4 | 230 | 14.062 | 14.617 | 0.555
GEN-2017-097 | North | 17 - Western South Dakota | 652573 | STEGALL4 | 230 | 5.478 | 5.489 | 0.011
GEN-2017-097 | North | 17 - Western South Dakota | 652873 | STEGALL-LNX3 | 230 | 5.461 | 5.472 | 0.011
GEN-2017-097 | North | 17 - Western South Dakota | 652884 | NUNDRWD-LNX3 | 230 | 3.575 | 3.982 | 0.407
GEN-2017-097 | North | 17 - Western South Dakota | 655487 | SULLYBT-ER4 | 230 | 6.43 | 6.512 | 0.082
GEN-2017-097 | North | 17 - Western South Dakota | 659188 | PHILIP_T-BE4 | 230 | 3.838 | 5.187 | 1.349
GEN-2017-097 | North | 17 - Western South Dakota | 659268 | RCDC.DUM-BE4 | 230 | 7.279 | 6.206 | -1.073
GEN-2017-097 | North | 17 - Western South Dakota | 659271 | RCDC.E__-BE4 | 230 | 2.768 | 2.986 | 0.218
GEN-2017-097 | North | 17 - Western South Dakota | 659303 | RCDC.W__-BE4 | 230 | 2.397 | 2.397 | 0
GEN-2017-097 | North | 17 - Western South Dakota | 659351 | BISON___-GE4 | 230 | 2.96 | 2.975 | 0.015
GEN-2017-097 | North | 17 - Western South Dakota | 659376 | DRYCREEK-BE4 | 230 | 2.774 | 2.993 | 0.219
GEN-2017-097 | North | 17 - Western South Dakota | 661047 | HETINGR4 | 230 | 3.742 | 3.738 | -0.004
GEN-2017-097 | North | 17 - Western South Dakota | 589350 | GEN-2017-097 | 115 | 5.957 | 6.472 | 0.515
GEN-2017-097 | North | 17 - Western South Dakota | 640109 | CHADRON7 | 115 | 3.805 | 3.808 | 0.003
GEN-2017-097 | North | 17 - Western South Dakota | 640405 | WAYSIDE7 | 115 | 4.287 | 4.292 | 0.005
GEN-2017-097 | North | 17 - Western South Dakota | 652243 | FAITH 7 | 115 | 2.436 | 2.45 | 0.014
GEN-2017-097 | North | 17 - Western South Dakota | 652473 | ELKCRK 7 | 115 | 3.593 | 3.707 | 0.114
GEN-2017-097 | North | 17 - Western South Dakota | 652477 | ELSWRTH7 | 115 | 4.067 | 4.255 | 0.188
GEN-2017-097 | North | 17 - Western South Dakota | 652479 | MARTIN 7 | 115 | 2.413 | 2.397 | -0.016
GEN-2017-097 | North | 17 - Western South Dakota | 652480 | MAURINE7 | 115 | 4.161 | 4.178 | 0.017
GEN-2017-097 | North | 17 - Western South Dakota | 652481 | MIDLAND7 | 115 | 3.418 | 3.525 | 0.107
GEN-2017-097 | North | 17 - Western South Dakota | 652483 | NEWELL 7 | 115 | 2.713 | 2.746 | 0.033
GEN-2017-097 | North | 17 - Western South Dakota | 652485 | NUNDRWD7 | 115 | 6.348 | 6.947 | 0.599
GEN-2017-097 | North | 17 - Western South Dakota | 652487 | PHILIP 7 | 115 | 5.337 | 5.931 | 0.594
GEN-2017-097 | North | 17 - Western South Dakota | 652490 | RAPIDCY7 | 115 | 4.814 | 5.091 | 0.277
GEN-2017-097 | North | 17 - Western South Dakota | 652491 | IRVSIMM7 | 115 | 8.104 | 8.26 | 0.156
GEN-2017-097 | North | 17 - Western South Dakota | 652492 | WALL 7 | 115 | 3.539 | 3.721 | 0.182
GEN-2017-097 | North | 17 - Western South Dakota | 652493 | WICKSVL7 | 115 | 4.204 | 4.446 | 0.242
GEN-2017-097 | North | 17 - Western South Dakota | 652520 | OAHE 7 | 115 | 11.233 | 11.481 | 0.248
GEN-2017-097 | North | 17 - Western South Dakota | 652579 | WANBLEE 7 | 115 | 2.485 | 2.49 | 0.005
GEN-2017-097 | North | 17 - Western South Dakota | 654490 | G14_001IST | 115 | 3.05 | 3.074 | 0.024
GEN-2017-097 | North | 17 - Western South Dakota | 655763 | RUSHMORE-RM7 | 115 | 4.58 | 4.83 | 0.25
GEN-2017-097 | North | 17 - Western South Dakota | 659350 | BISON___-GE7 | 115 | 1.591 | 1.567 | -0.024
GEN-2017-097 | North | 17 - Western South Dakota | 659377 | DRYCREEK-BE7 | 115 | 4.601 | 4.856 | 0.255
GEN-2017-097 | North | 17 - Western South Dakota | 652248 | MAURINE8 | 69 | 2.756 | 2.762 | 0.006
GEN-2017-097 | North | 17 - Western South Dakota | 652263 | MIDLAND8 | 69 | 2.222 | 2.231 | 0.009
GEN-2017-097 | North | 17 - Western South Dakota | 652265 | NEWELL 8 | 69 | 2.492 | 2.494 | 0.002
GEN-2017-097 | North | 17 - Western South Dakota | 652268 | PHILIP 8 | 69 | 2.54 | 2.571 | 0.031
GEN-2017-097 | North | 17 - Western South Dakota | 655762 | RAPIDCTY-RM8 | 69 | 3.665 | 3.709 | 0.044
GEN-2017-097 | North | 17 - Western South Dakota | 655764 | RUSHMORE-RM8 | 69 | 3.324 | 3.351 | 0.027
GEN-2017-097 | North | 17 - Western South Dakota | 659352 | BISON___-GE8 | 69 | 2.106 | 2.087 | -0.019
GEN-2017-064 | North | 17 - Western South Dakota | 659135 | STEGALL_-MB3 | 345 | 5.179 | 5.191 | 0.012
GEN-2017-064 | North | 17 - Western South Dakota | 587764 | G16-094-TAP | 230 | 9.307 | 9.37 | 0.063
GEN-2017-064 | North | 17 - Western South Dakota | 588590 | GEN-2017-014 | 230 | 3.644 | 5.185 | 1.541
GEN-2017-064 | North | 17 - Western South Dakota | 588594 | G17-014-TAP | 230 | 3.644 | 5.185 | 1.541
GEN-2017-064 | North | 17 - Western South Dakota | 589020 | GEN-2017-064 | 230 | 2.833 | 2.937 | 0.104
GEN-2017-064 | North | 17 - Western South Dakota | 589024 | G17-064-TAP | 230 | 2.833 | 2.937 | 0.104
GEN-2017-064 | North | 17 - Western South Dakota | 640396 | VICTRYH4 | 230 | 3.832 | 3.831 | -0.001
GEN-2017-064 | North | 17 - Western South Dakota | 640404 | WAYSIDE4 | 230 | 2.889 | 2.939 | 0.05
GEN-2017-064 | North | 17 - Western South Dakota | 652484 | NUNDRWD4 | 230 | 3.581 | 3.99 | 0.409
GEN-2017-064 | North | 17 - Western South Dakota | 652486 | PHILIP 4 | 230 | 3.246 | 4.006 | 0.76
GEN-2017-064 | North | 17 - Western South Dakota | 652497 | MAURINE4 | 230 | 2.922 | 2.983 | 0.061
GEN-2017-064 | North | 17 - Western South Dakota | 652507 | FTTHOMP4 | 230 | 20.055 | 20.221 | 0.166
GEN-2017-064 | North | 17 - Western South Dakota | 652519 | OAHE 4 | 230 | 14.062 | 14.617 | 0.555
GEN-2017-064 | North | 17 - Western South Dakota | 652573 | STEGALL4 | 230 | 5.478 | 5.489 | 0.011
GEN-2017-064 | North | 17 - Western South Dakota | 652873 | STEGALL-LNX3 | 230 | 5.461 | 5.472 | 0.011
GEN-2017-064 | North | 17 - Western South Dakota | 652884 | NUNDRWD-LNX3 | 230 | 3.575 | 3.982 | 0.407
GEN-2017-064 | North | 17 - Western South Dakota | 655487 | SULLYBT-ER4 | 230 | 6.43 | 6.512 | 0.082
GEN-2017-064 | North | 17 - Western South Dakota | 659188 | PHILIP_T-BE4 | 230 | 3.838 | 5.187 | 1.349
GEN-2017-064 | North | 17 - Western South Dakota | 659206 | STEGALL_-MB4 | 230 | 5.751 | 5.76 | 0.009
GEN-2017-064 | North | 17 - Western South Dakota | 659268 | RCDC.DUM-BE4 | 230 | 7.279 | 6.206 | -1.073
GEN-2017-064 | North | 17 - Western South Dakota | 659271 | RCDC.E__-BE4 | 230 | 2.768 | 2.986 | 0.218
GEN-2017-064 | North | 17 - Western South Dakota | 659303 | RCDC.W__-BE4 | 230 | 2.397 | 2.397 | 0
GEN-2017-064 | North | 17 - Western South Dakota | 659351 | BISON___-GE4 | 230 | 2.96 | 2.975 | 0.015
GEN-2017-064 | North | 17 - Western South Dakota | 659376 | DRYCREEK-BE4 | 230 | 2.774 | 2.993 | 0.219
GEN-2017-064 | North | 17 - Western South Dakota | 659829 | DH_CS_EA-TS4 | 230 | 5.478 | 5.489 | 0.011
GEN-2017-064 | North | 17 - Western South Dakota | 659830 | DH_CS.WE-TS4 | 230 | 6.023 | 6.023 | 0
GEN-2017-064 | North | 17 - Western South Dakota | 661047 | HETINGR4 | 230 | 3.742 | 3.738 | -0.004
GEN-2017-064 | North | 17 - Western South Dakota | 589350 | GEN-2017-097 | 115 | 5.957 | 6.472 | 0.515
GEN-2017-064 | North | 17 - Western South Dakota | 640109 | CHADRON7 | 115 | 3.805 | 3.808 | 0.003
GEN-2017-064 | North | 17 - Western South Dakota | 640147 | CRAWFRD7 | 115 | 2.694 | 2.689 | -0.005
GEN-2017-064 | North | 17 - Western South Dakota | 640192 | GORDON 7 | 115 | 1.934 | 1.923 | -0.011
GEN-2017-064 | North | 17 - Western South Dakota | 640334 | RUSHVIL7 | 115 | 2.127 | 2.118 | -0.009
GEN-2017-064 | North | 17 - Western South Dakota | 640397 | VICTRYH7 | 115 | 6.178 | 6.173 | -0.005
GEN-2017-064 | North | 17 - Western South Dakota | 640405 | WAYSIDE7 | 115 | 4.287 | 4.292 | 0.005
GEN-2017-064 | North | 17 - Western South Dakota | 652243 | FAITH 7 | 115 | 2.436 | 2.45 | 0.014
GEN-2017-064 | North | 17 - Western South Dakota | 652473 | ELKCRK 7 | 115 | 3.593 | 3.707 | 0.114
GEN-2017-064 | North | 17 - Western South Dakota | 652477 | ELSWRTH7 | 115 | 4.067 | 4.255 | 0.188
GEN-2017-064 | North | 17 - Western South Dakota | 652480 | MAURINE7 | 115 | 4.161 | 4.178 | 0.017
GEN-2017-064 | North | 17 - Western South Dakota | 652485 | NUNDRWD7 | 115 | 6.348 | 6.947 | 0.599
GEN-2017-064 | North | 17 - Western South Dakota | 652487 | PHILIP 7 | 115 | 5.337 | 5.931 | 0.594
GEN-2017-064 | North | 17 - Western South Dakota | 652490 | RAPIDCY7 | 115 | 4.814 | 5.091 | 0.277
GEN-2017-064 | North | 17 - Western South Dakota | 652492 | WALL 7 | 115 | 3.539 | 3.721 | 0.182
GEN-2017-064 | North | 17 - Western South Dakota | 652493 | WICKSVL7 | 115 | 4.204 | 4.446 | 0.242
GEN-2017-064 | North | 17 - Western South Dakota | 652520 | OAHE 7 | 115 | 11.233 | 11.481 | 0.248
GEN-2017-064 | North | 17 - Western South Dakota | 653311 | DUNLAP 7 | 115 | 2.615 | 2.602 | -0.013
GEN-2017-064 | North | 17 - Western South Dakota | 654490 | G14_001IST | 115 | 3.05 | 3.074 | 0.024
GEN-2017-064 | North | 17 - Western South Dakota | 655763 | RUSHMORE-RM7 | 115 | 4.58 | 4.83 | 0.25
GEN-2017-064 | North | 17 - Western South Dakota | 659350 | BISON___-GE7 | 115 | 1.591 | 1.567 | -0.024
GEN-2017-064 | North | 17 - Western South Dakota | 659377 | DRYCREEK-BE7 | 115 | 4.601 | 4.856 | 0.255
GEN-2017-064 | North | 17 - Western South Dakota | 659815 | BOXBUTE_-TS7 | 115 | 2.499 | 2.487 | -0.012
GEN-2017-064 | North | 17 - Western South Dakota | 652248 | MAURINE8 | 69 | 2.756 | 2.762 | 0.006
GEN-2017-064 | North | 17 - Western South Dakota | 655762 | RAPIDCTY-RM8 | 69 | 3.665 | 3.709 | 0.044
GEN-2017-064 | North | 17 - Western South Dakota | 655764 | RUSHMORE-RM8 | 69 | 3.324 | 3.351 | 0.027
GEN-2017-064 | North | 17 - Western South Dakota | 659352 | BISON___-GE8 | 69 | 2.106 | 2.087 | -0.019